PG&E | 2017-07-11 22:13 | 22:12 | 37.0122 | -121.9497 | Vegetation | Rural | < 3 Meters | Fire Agency | CAPT PHIL CRAMBLET 831-479-6842 | 101676689 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42927.9254 | 22:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1244 | 2017 | 7 | 11 | 22 | 12 | 17-0062198 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 714 | 7.2694 | 158_185 | <25mph | <15mph | HFTD - Distribution | 2017-07-11 22:12:00 | 983 | 9.7577 | FALSE | <25mph | E5038 | 3.28 | 2018-08-21T07:49:00Z | 8.01 | 40 | < 25mph | UCYL | 7.78 | 2018-08-21T07:40:00Z | 11.41 | 179 | < 25mph | E5038 | 3.28 | 2018-08-21T07:49:00Z | 8.01 | 81 | < 25mph | UCYL | 7.78 | 2018-08-21T07:40:00Z | 11.41 | 354 | < 25mph
PG&E | 2016-05-18 | 18:24 | 39.7381 | -123.1587 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42508 | 18:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0735 | 2016 | 5 | 18 | 18 | 24 | 16-0036911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1482 | 13.4862 | 108_336 | <25mph | <15mph | HFTD - Distribution | 2016-05-18 18:24:00 | 480 | 21.4181 | FALSE | <25mph | C3111 | 2.79 | 2016-12-19T22:27:00Z | 3 | 4 | < 25mph | EELC1 | 7.26 | 2016-12-19T22:45:00Z | 4.99 | 5 | < 25mph | C3111 | 2.79 | 2016-12-19T22:27:00Z | 3 | 8 | < 25mph | EELC1 | 7.26 | 2016-12-19T22:45:00Z | 4.99 | 10 | < 25mph
PG&E | 2015-10-31 07:45 | 2015-10-31 07:45 | 38.1157 | -120.8931 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal FIRE | 103763040 |  | 12000 | Conductor | Overhead | Yes | 42308.3229 | 2015-10-31 07:45 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0663 | 2015 | 10 | 31 | 7 | 45 | 15-0074424 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 314565 | 11.8471 | 204_245 | <25mph | <15mph | HFTD - Distribution | 2015-10-31 07:45:00 | 407 | 12.187 | FALSE | <25mph | PG375 | 2.03 | 2019-08-16T06:30:00Z | 5.91 | 6 | < 25mph | PG375 | 2.03 | 2019-08-16T06:30:00Z | 5.91 | 19 | < 25mph | PG375 | 2.03 | 2019-08-16T07:00:00Z | 7.9 | 12 | < 25mph | PG375 | 2.03 | 2019-08-16T07:00:00Z | 7.9 | 38 | < 25mph
PG&E | 2017-07-07 | 15:09 | 40.9054 | -122.3806 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101455950 | Unknown | 12000 | Conductor | Overhead | Yes | 42923 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1229 | 2017 | 7 | 7 | 15 | 9 | 17-0061903 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.0906 | 142_400 | <25mph | <15mph | HFTD - Distribution | 2017-07-07 15:09:00 | 969 | 11.4161 | FALSE | <25mph | SLFC1 | 2.92 | 2015-02-13T01:19:00Z | 13 | 7 | < 25mph | SLFC1 | 2.92 | 2015-02-13T01:19:00Z | 13 | 7 | < 25mph | SLFC1 | 2.92 | 2015-02-13T02:19:00Z | 14 | 16 | < 25mph | SLFC1 | 2.92 | 2015-02-13T02:19:00Z | 14 | 16 | < 25mph
PG&E | 2017-07-12 15:09 | 15:09 | 37.1491 | -122.0037 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 103565794 | Unknown | 21000 | Conductor | Overhead | Yes | 42928.6313 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1248 | 2017 | 7 | 12 | 15 | 9 | 17-0062439 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24690 | 9.5326 | 155_192 | <25mph | <15mph | HFTD - Distribution | 2017-07-12 15:09:00 | 986 | 9.5326 | FALSE | <25mph | D8979 | 3.17 | 2016-07-19T19:38:00Z | 8.99 | 27 | < 25mph | E5965 | 5.98 | 2016-07-19T20:25:00Z | 13 | 125 | < 25mph | D8979 | 3.17 | 2016-07-19T19:38:00Z | 8.99 | 53 | < 25mph | E5965 | 5.98 | 2016-07-19T20:25:00Z | 13 | 250 | < 25mph
PG&E | 2016-08-08 | 2016-08-08 15:44 | 37.1382 | -121.9672 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100519919 |  | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0912 | 2016 | 8 | 8 | 15 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 8.8992 | 157_192 | <25mph | <15mph | HFTD - Distribution | 2016-08-08 15:44:00 | 655 | 10.1741 | FALSE | <25mph | D9791 | 1.67 | 2019-08-22T16:01:00Z | 4.99 | 31 | < 25mph | PG154 | 6.66 | 2019-08-22T16:10:00Z | 12.93 | 153 | < 25mph | PG057 | 2.38 | 2019-08-22T17:20:00Z | 6.35 | 66 | < 25mph | PG154 | 6.66 | 2019-08-22T16:10:00Z | 12.93 | 312 | < 25mph
PG&E | 2016-09-16 20:56 | 2016-09-16 20:56 | 39.8387 | -121.7023 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 100441760 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42629.8722 | 2016-09-16 20:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0983 | 2016 | 9 | 16 | 20 | 56 | 16-0065273 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 314427 | 11.5178 | 170_340 | <25mph | <15mph | HFTD - Distribution | 2016-09-16 20:56:00 | 725 | 12.6422 | FALSE | <25mph | C8878 | 3.59 | 2015-07-17T01:23:00Z | 7 | 13 | < 25mph | CSTC1 | 4.21 | 2015-07-17T00:51:00Z | 14.99 | 25 | < 25mph | C8878 | 3.59 | 2015-07-17T01:23:00Z | 7 | 25 | < 25mph | CSTC1 | 4.21 | 2015-07-17T01:51:00Z | 15.99 | 49 | < 25mph
PG&E | 2016-10-09 18:52 | 18:52 | 38.656 | -120.9725 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101376768 |  | 12000 | Conductor | Overhead | Yes | 42652.7862 | 18:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1024 | 2016 | 10 | 9 | 18 | 52 | 16-0070676 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 98361 | 11.3582 | 201_275 | <25mph | <15mph | HFTD - Distribution | 2016-10-09 18:52:00 | 765 | 14.948 | FALSE | <25mph | D7401 | 2.79 | 2016-09-30T20:57:00Z | 7 | 8 | < 25mph | BENC1 | 4.97 | 2016-09-30T20:59:00Z | 14.99 | 63 | < 25mph | D7401 | 2.79 | 2016-09-30T21:41:00Z | 8.99 | 16 | < 25mph | BENC1 | 4.97 | 2016-09-30T20:59:00Z | 14.99 | 125 | < 25mph
PG&E | 2017-08-27 | 20:04 | 38.9165 | -121.151 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-477-0641 x7, log 22629 | 100077184 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42974 | 20:04 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1352 | 2017 | 8 | 27 | 20 | 4 | 17-0073228 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 905 | 9.7822 | 193_290 | <25mph | <15mph | HFTD - Distribution | 2017-08-27 20:04:00 | 1090 | 16.757 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LICC1 | 6.69 | 2016-12-25T23:13:00Z | 5.99 | 17 | < 25mph |  |  |  | 0 | 0 | No data | LICC1 | 6.69 | 2016-12-25T23:13:00Z | 5.99 | 31 | < 25mph
PG&E | 2016-06-26 | 2016-06-26 16:38 | 39.5042 | -121.4475 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100375810 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42547 | 2016-06-26 16:38 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0823 | 2016 | 6 | 26 | 16 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 9.04 | 180_322 | <25mph | <15mph | HFTD - Distribution | 2016-06-26 16:38:00 | 567 | 14.524 | FALSE | <25mph | TT309 | 3.14 | 2015-11-30T13:45:00Z | 7 | 1 | < 25mph | TT309 | 3.14 | 2015-11-30T13:45:00Z | 7 | 1 | < 25mph | TT309 | 3.14 | 2015-11-30T14:45:00Z | 10 | 2 | < 25mph | TT309 | 3.14 | 2015-11-30T14:45:00Z | 10 | 2 | < 25mph
PG&E | 2019-03-13 | 16:08 | 39.8831 | -122.5498 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 6Fn0313191607 |  | 12000 | Conductor | Overhead | Yes | 43537 | 16:08 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-194 | 2019 | 3 | 13 | 16 | 8 | 19-0033617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 21012 | 20.7105 | 134_343 | <25mph | <15mph | HFTD - Distribution | 2019-03-13 16:08:00 | 1734 | 26.4067 | FALSE | 25-40mph | TCKC1 | 3.76 | 2017-03-25T11:28:00Z | 13 | 1 | < 25mph | TCKC1 | 3.76 | 2017-03-25T11:28:00Z | 13 | 2 | < 25mph | TCKC1 | 3.76 | 2017-03-25T12:28:00Z | 14.99 | 2 | < 25mph | TCKC1 | 3.76 | 2017-03-25T12:28:00Z | 14.99 | 4 | < 25mph
PG&E | 2015-12-31 19:12 | 2015-12-31 19:12 | 37.1568 | -121.9868 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LOS GATOS MONTE SERENO SARATOGA | 100518215 | Verizon | 21000 | Conductor | Overhead | Yes | 42369.8 | 2015-12-31 19:12 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0689 | 2015 | 12 | 31 | 19 | 12 | 15-0087962 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7979 | 7.4149 | 156_193 | <25mph | <15mph | HFTD - Distribution | 2015-12-31 19:12:00 | 433 | 10.9251 | FALSE | <25mph | LSGC1 | 3.83 | 2016-08-25T13:32:00Z | 4 | 23 | < 25mph | E3877 | 7.37 | 2016-08-25T13:40:00Z | 5.99 | 161 | < 25mph | LSGC1 | 3.83 | 2016-08-25T14:32:00Z | 5.99 | 45 | < 25mph | E3877 | 7.37 | 2016-08-25T13:40:00Z | 5.99 | 319 | < 25mph
PG&E | 2016-05-18 | 18:24 | 39.7381 | -123.1587 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42508 | 18:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0735 | 2016 | 5 | 18 | 18 | 24 | 16-0036911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1482 | 13.4862 | 108_336 | <25mph | <15mph | HFTD - Distribution | 2016-05-18 18:24:00 | 480 | 21.4181 | FALSE | <25mph | C3111 | 2.79 | 2017-08-18T17:00:00Z | 3 | 2 | < 25mph | EELC1 | 7.26 | 2017-08-18T16:45:00Z | 5.99 | 3 | < 25mph | C3111 | 2.79 | 2017-08-18T18:00:00Z | 3 | 4 | < 25mph | EELC1 | 7.26 | 2017-08-18T17:45:00Z | 8.01 | 6 | < 25mph
PG&E | 2018-07-23 | 17:27 | 39.734 | -121.4965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103843963 | AT&T | 12000 | Conductor | Overhead | Yes | 43304 | 17:27 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1782 | 2018 | 7 | 23 | 17 | 27 | 18-0062874 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 183629 | 9.1915 | 178_335 | <25mph | <15mph | HFTD - Distribution | 2018-07-23 17:27:00 | 1522 | 13.4352 | FALSE | <25mph | JBGC1 | 0.42 | 2016-08-13T21:13:00Z | 8.01 | 1 | < 25mph | JBGC1 | 0.42 | 2016-08-13T21:13:00Z | 8.01 | 10 | < 25mph | JBGC1 | 0.42 | 2016-08-13T22:13:00Z | 8.01 | 2 | < 25mph | JBGC1 | 0.42 | 2016-08-13T22:13:00Z | 8.01 | 21 | < 25mph
PG&E | 2018-10-14 | 20:08 | 38.8935 | -120.8497 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103674516 | Unknown | 21000 | Conductor | Overhead | Yes | 43387 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1940 | 2018 | 10 | 14 | 20 | 8 | 18-0090299 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 48095 | 8.663 | 206_288 | <25mph | <15mph | HFTD - Distribution | 2018-10-14 20:08:00 | 1679 | 24.0259 | FALSE | <25mph | C6662 | 3.02 | 2017-09-01T19:03:00Z | 4 | 16 | < 25mph | BDMC1 | 7.81 | 2017-09-01T18:36:00Z | 11.01 | 17 | < 25mph | E6476 | 2.71 | 2017-09-01T19:55:00Z | 4.99 | 33 | < 25mph | BDMC1 | 7.81 | 2017-09-01T18:36:00Z | 11.01 | 35 | < 25mph
PG&E | 2018-07-17 | 19:40 | 40.5927 | -122.4886 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101477082 | AT&T | 12000 | Conductor | Overhead | Yes | 43298 | 19:40 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1760 | 2018 | 7 | 17 | 19 | 40 | 18-0060840 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 30162 | 14.3022 | 137_382 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 19:40:00 | 1500 | 21.6282 | FALSE | <25mph | AU138 | 1.18 | 2015-12-08T17:33:00Z | 3 | 5 | < 25mph | E6886 | 7.8 | 2015-12-08T17:32:00Z | 5.99 | 15 | < 25mph | AU138 | 1.18 | 2015-12-08T17:33:00Z | 3 | 10 | < 25mph | E6886 | 7.8 | 2015-12-08T17:32:00Z | 5.99 | 31 | < 25mph
PG&E | 2016-06-20 | 2016-06-20 16:45 | 41.0697 | -123.6789 | Vegetation | RURAL | < 3 meters | Fire Agency | Hoopa FD | 101011420 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42541 | 2016-06-20 16:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0811 | 2016 | 6 | 20 | 16 | 45 | 16-0044577 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7361 | 15.1157 | 88_410 | <25mph | <15mph | HFTD - Distribution | 2016-06-20 16:45:00 | 554 | 15.1157 | FALSE | <25mph | HOAC1 | 1.56 | 2016-04-16T01:40:00Z | 20 | 1 | < 25mph | HOAC1 | 1.56 | 2016-04-16T01:40:00Z | 20 | 1 | < 25mph | HOAC1 | 1.56 | 2016-04-16T01:40:00Z | 20 | 2 | < 25mph | HOAC1 | 1.56 | 2016-04-16T01:40:00Z | 20 | 2 | < 25mph
PG&E | 2019-09-13 | 6:30 | 37.3348 | -121.7716 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 83392110 |  | 21000 | Splice/Clamp/Connector | Overhead | Yes | 43721 | 6:30 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-444 | 2019 | 9 | 13 | 6 | 30 | 19-0098560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 35534 | 3.3882 | 166_202 | <25mph | <15mph | HFTD - Distribution | 2019-09-13 06:30:00 | 2037 | 14.1926 | FALSE | <25mph | E8563 | 3.34 | 2018-05-17T00:57:00Z | 21 | 20 | < 25mph | SJS01 | 6.07 | 2018-05-17T01:30:00Z | 24.56 | 92 | < 25mph | E8563 | 3.34 | 2018-05-17T00:57:00Z | 21 | 44 | < 25mph | SJS01 | 6.07 | 2018-05-17T01:30:00Z | 24.56 | 188 | < 25mph
PG&E | 2017-10-31 | 21:02 | 39.1119 | -122.9163 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Structure 020/003 | Unknown | 60000 | Conductor | Overhead | Yes | 43039 | 21:02 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | no-match | 1513 | 2017 | 10 | 31 | 21 | 2 | INT-10325 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | 50730 | 1.8727 | 117_301 | <25mph | <15mph | HFTD - Transmission | 2017-10-31 21:02:00 | 1255 | 9.8895 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG088 | 6.81 | 2019-06-17T16:10:00Z | 6.58 | 18 | < 25mph |  |  |  | 0 | 0 | No data | PG088 | 6.81 | 2019-06-17T16:10:00Z | 6.58 | 36 | < 25mph
PG&E | 2017-10-11 | 11:57 | 38.5015 | -123.0237 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101974930 | Unknown | 12000 | Conductor | Overhead | Yes | 43019 | 11:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1484 | 2017 | 10 | 11 | 11 | 57 | 17-0086350 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 226925 | 16.5068 | 112_268 | <25mph | <15mph | HFTD - Distribution | 2017-10-11 11:57:00 | 1227 | 19.0479 | FALSE | <25mph | D3481 | 2.38 | 2015-05-13T03:57:00Z | 5.99 | 28 | < 25mph | D3481 | 2.38 | 2015-05-13T03:57:00Z | 5.99 | 28 | < 25mph | D3481 | 2.38 | 2015-05-13T05:02:00Z | 5.99 | 56 | < 25mph | D3481 | 2.38 | 2015-05-13T05:02:00Z | 5.99 | 56 | < 25mph
PG&E | 2018-02-07 | 5:44 | 40.6543 | -122.5198 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 103922730 | Unknown | 12000 | Conductor | Overhead | Yes | 43138 | 5:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1558 | 2018 | 2 | 7 | 5 | 44 | 18-0012073 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 9610 | 17.8768 | 136_386 | <25mph | <15mph | HFTD - Distribution | 2018-02-07 05:44:00 | 1300 | 25.5948 | FALSE | 25-40mph | OBRC1 | 3.05 | 2017-11-15T14:00:00Z | 3 | 4 | < 25mph | MMOC1 | 5.95 | 2017-11-15T14:00:00Z | 7 | 6 | < 25mph | OBRC1 | 3.05 | 2017-11-15T15:00:00Z | 8.99 | 6 | < 25mph | MMOC1 | 5.95 | 2017-11-15T15:00:00Z | 12.01 | 10 | < 25mph
PG&E | 2016-09-12 | 4:24 | 36.3999 | -121.902 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire Hwy 1 Carmel Hill | 101669614 |  | 12000 | Conductor | Overhead | Yes | 42625 | 4:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0973 | 2016 | 9 | 12 | 4 | 24 | 16-0063826 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 130604 | 5.4712 | 159_151 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 04:24:00 | 715 | 8.1881 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TR419 | 7.81 | 2019-05-21T01:15:00Z | 14.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | TR419 | 7.81 | 2019-05-21T01:15:00Z | 14.99 | 2 | < 25mph
PG&E | 2016-07-15 14:26 | 2016-07-15 14:26 | 38.1366 | -122.7092 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | NOVATO FIRE AND OTHERS | 102013570 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.6014 | 2016-07-15 14:26 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0853 | 2016 | 7 | 15 | 14 | 26 | 16-0050269 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 758 | 13.1533 | 125_247 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 14:26:00 | 596 | 15.659 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E0433 | 5.38 | 2016-12-11T12:35:00Z | 7 | 20 | < 25mph |  |  |  | 0 | 0 | No data | E0433 | 5.38 | 2016-12-11T13:10:00Z | 7 | 40 | < 25mph
PG&E | 2015-05-21 09:23 | 2015-05-21 09:23 | 38.5996 | -122.9935 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 4 SPANS LOAD SIDE 2993 |  | 12000 | Conductor | Overhead | Yes | 42145.391 | 2015-05-21 09:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0324 | 2015 | 5 | 21 | 9 | 23 | 15-0035686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2850 | 1.6525 | 114_273 | <25mph | <15mph | HFTD - Distribution | 2015-05-21 09:23:00 | 70 | 15.124 | FALSE | <25mph |  |  |  | 0 | 0 | No data | DRYWW | 5.5 | 2018-01-17T10:00:00Z | 2.91 | 28 | < 25mph |  |  |  | 0 | 0 | No data | DRYWW | 5.5 | 2018-01-17T10:00:00Z | 2.91 | 56 | < 25mph
PG&E | 2019-10-04 | 19:07 | 40.4964 | -122.0448 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | Yes | 43742 | 19:07 | Equipment - Overloaded | Other |  |  |  |  | no-match | 2019-257 | 2019 | 10 | 4 | 19 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 6.2955 | 155_377 | <25mph | <15mph | HFTD - Distribution | 2019-10-04 19:07:00 | 2076 | 10.3362 | FALSE | <25mph | AR225 | 3.27 | 2015-10-08T04:15:00Z | 3 | 11 | < 25mph | AR225 | 3.27 | 2015-10-08T04:15:00Z | 3 | 11 | < 25mph | AR225 | 3.27 | 2015-10-08T04:50:00Z | 4.99 | 23 | < 25mph | AR225 | 3.27 | 2015-10-08T04:50:00Z | 4.99 | 23 | < 25mph
PG&E | 2015-09-25 17:28 | 2015-09-25 17:28 | 38.7169 | -120.7693 | Vegetation | Rural | < 0.25 Acres | Fire Agency | el dorado F D | 101405928 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42272.7278 | 2015-09-25 17:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0616 | 2015 | 9 | 25 | 17 | 28 | 15-0063666 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 111180 | 8.3925 | 209_279 | <25mph | <15mph | HFTD - Distribution | 2015-09-25 17:28:00 | 361 | 11.4196 | FALSE | <25mph | E6490 | 3.78 | 2019-10-29T17:47:00Z | 12.01 | 19 | < 25mph | E6490 | 3.78 | 2019-10-29T17:47:00Z | 12.01 | 66 | < 25mph | E6490 | 3.78 | 2019-10-29T19:12:00Z | 12.01 | 33 | < 25mph | PG077 | 4.76 | 2019-10-29T19:00:00Z | 12.12 | 120 | < 25mph
PG&E | 2017-09-11 | 8:50 | 36.9515 | -121.842 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101790954 | PACIFIC BELL | 21000 | Fuse | Overhead | Yes | 42989 | 8:50 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | no-match | 1408 | 2017 | 9 | 11 | 8 | 50 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | N.A. | 9.6414 | 162_181 | <25mph | <15mph | HFTD - Distribution | 2017-09-11 08:50:00 | 1146 | 17.9559 | FALSE | <25mph | CTOC1 | 3.41 | 2019-12-11T03:27:00Z | 7 | 33 | < 25mph | CTOC1 | 3.41 | 2019-12-11T03:27:00Z | 7 | 93 | < 25mph | CTOC1 | 3.41 | 2019-12-11T05:27:00Z | 7 | 66 | < 25mph | PG370 | 7.97 | 2019-12-11T05:10:00Z | 11.1 | 185 | < 25mph
PG&E | 2016-09-18 | 14:33 | 37.1619 | -122.1347 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire & Boulder Creek Fire Dept. | 103410909 | Yes | 12000 | Conductor | Overhead | Yes | 42631 | 14:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0986 | 2016 | 9 | 18 | 14 | 33 | 16-0065437 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 54983 | 5.897 | 150_193 | <25mph | <15mph | HFTD - Distribution | 2016-09-18 14:33:00 | 728 | 11.3228 | FALSE | <25mph | BNDC1 | 2.99 | 2015-08-21T03:50:00Z | 7 | 21 | < 25mph | BNDC1 | 2.99 | 2015-08-21T03:50:00Z | 7 | 38 | < 25mph | BNDC1 | 2.99 | 2015-08-21T03:50:00Z | 7 | 42 | < 25mph | E6800 | 4.63 | 2015-08-21T05:18:00Z | 7 | 74 | < 25mph
PG&E | 2019-09-22 | 11:56 | 37.5168 | -119.9159 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103967994 |  | 21000 | Pole | Overhead | Yes | 43730 | 11:56 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-452 | 2019 | 9 | 22 | 11 | 56 | 19-0102232 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 133232 | 11.5782 | 247_213 | <25mph | <15mph | HFTD - Distribution | 2019-09-22 11:56:00 | 2051 | 13.905 | FALSE | <25mph | MPOC1 | 3.98 | 2016-08-11T13:07:00Z | 7 | 1 | < 25mph | MPOC1 | 3.98 | 2016-08-11T13:07:00Z | 7 | 8 | < 25mph | MPOC1 | 3.98 | 2016-08-11T14:07:00Z | 8.99 | 2 | < 25mph | MPOC1 | 3.98 | 2016-08-11T14:07:00Z | 8.99 | 17 | < 25mph
PG&E | 2017-07-24 14:02 | 14:01 | 37.2635 | -122.3364 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike klink 650-879-0121 | 100322130 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42940.5845 | 14:01 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1286 | 2017 | 7 | 24 | 14 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 18.4533 | 141_199 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 14:01:00 | 1025 | 18.6394 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 5.31 | 2017-06-23T09:07:00Z | 5.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 5.31 | 2017-06-23T10:07:00Z | 5.99 | 2 | < 25mph
PG&E | 2017-10-20 | 13:45 | 34.5532 | -120.5303 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 101921492 | Unknown | 12000 | Conductor | Overhead | Yes | 43028 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1502 | 2017 | 10 | 20 | 13 | 45 | 17-0089249 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 173 | 31.847 | 221_49 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-20 13:45:00 | 1245 | 35.5655 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PTGC1 | 6.9 | 2017-12-31T13:00:00Z | 5.82 | 7 | < 25mph |  |  |  | 0 | 0 | No data | PTGC1 | 6.9 | 2017-12-31T14:00:00Z | 6.93 | 14 | < 25mph
PG&E | 2015-04-02 09:44 | 2015-04-02 09:44 | 39.6772 | -121.492 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100338726 |  | 12000 | Conductor | Overhead | Yes | 42096.4056 | 2015-04-02 09:44 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0284 | 2015 | 4 | 2 | 9 | 44 | 15-0023747 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 100204 | 15.7458 | 178_332 | <25mph | <15mph | HFTD - Distribution | 2015-04-02 09:44:00 | 30 | 15.7458 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JBGC1 | 4.06 | 2018-12-21T05:13:00Z | 12.01 | 7 | < 25mph |  |  |  | 0 | 0 | No data | JBGC1 | 4.06 | 2018-12-21T06:13:00Z | 14 | 14 | < 25mph
PG&E | 2016-07-31 12:11 | 2016-07-31 12:11 | 38.7827 | -120.9168 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101417359 |  | 21000 | Conductor | Overhead | Yes | 42582.5076 | 2016-07-31 12:11 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0895 | 2016 | 7 | 31 | 12 | 11 | 16-0053949 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 10.9662 | 203_282 | <25mph | <15mph | HFTD - Distribution | 2016-07-31 12:11:00 | 638 | 14.1387 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 6.02 | 2015-01-10T03:56:00Z | 4.99 | 48 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 6.02 | 2015-01-10T03:56:00Z | 4.99 | 95 | < 25mph
PG&E | 2018-06-21 | 18:58 | 35.1224 | -120.3938 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101878933 | AT&T | 12000 | Conductor | Overhead | Yes | 43272 | 18:58 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1683 | 2018 | 6 | 21 | 18 | 58 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 13.9909 | 227_80 | <25mph | <15mph | HFTD - Distribution | 2018-06-21 18:58:00 | 1425 | 15.3983 | FALSE | <25mph | AU609 | 1.36 | 2017-06-25T03:49:00Z | 8.99 | 4 | < 25mph | AU609 | 1.36 | 2017-06-25T03:49:00Z | 8.99 | 10 | < 25mph | AU609 | 1.36 | 2017-06-25T03:49:00Z | 8.99 | 8 | < 25mph | AU609 | 1.36 | 2017-06-25T03:49:00Z | 8.99 | 20 | < 25mph
PG&E | 2015-06-12 23:32 | 2015-06-12 23:32 | 39.2308 | -121.1559 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 10903 PROSPECTOR RD ROUGH AND READY | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42167.9806 | 2015-06-12 23:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0380 | 2015 | 6 | 12 | 23 | 32 | 15-0040789 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 20 | 12.2901 | 193_307 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 23:32:00 | 126 | 14.4252 | FALSE | <25mph | E2572 | 1.63 | 2015-01-24T10:29:00Z | 5.99 | 18 | < 25mph | E1789 | 6.1 | 2015-01-24T09:54:00Z | 10 | 53 | < 25mph | E2572 | 1.63 | 2015-01-24T10:29:00Z | 5.99 | 35 | < 25mph | E1789 | 6.1 | 2015-01-24T10:54:00Z | 14 | 105 | < 25mph
PG&E | 2018-07-18 | 1:14 | 38.3671 | -120.5578 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101247987 | Unknown | 12000 | Conductor | Overhead | Yes | 43299 | 1:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1761 | 2018 | 7 | 18 | 1 | 14 | 18-0060882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6420 | 6.6576 | 219_259 | <25mph | <15mph | HFTD - Distribution | 2018-07-18 01:14:00 | 1501 | 11.9385 | FALSE | <25mph | AT450 | 3.1 | 2015-03-26T21:25:00Z | 13 | 13 | < 25mph | ESPC1 | 6.8 | 2015-03-26T21:13:00Z | 14.99 | 21 | < 25mph | AT450 | 3.1 | 2015-03-26T21:25:00Z | 13 | 25 | < 25mph | ESPC1 | 6.8 | 2015-03-26T22:13:00Z | 14.99 | 41 | < 25mph
PG&E | 2016-10-02 16:41 | 16:41 | 39.8888 | -121.6648 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103358082 |  | 12000 | Other | Overhead | Yes | 42645.6954 | 16:41 | Other | N.A. | N.A. | N.A. | Weather | lightning strike | Other/Unknown | 1013 | 2016 | 10 | 2 | 16 | 41 | 16-0069050 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 339550 | 8.5152 | 171_343 | <25mph | <15mph | HFTD - Distribution | 2016-10-02 16:41:00 | 755 | 17.2989 | FALSE | <25mph | C8878 | 1.4 | 2019-05-30T16:12:00Z | 5.99 | 16 | < 25mph | PG333 | 6.67 | 2019-05-30T16:20:00Z | 8.55 | 41 | < 25mph | PG075 | 3.35 | 2019-05-30T17:20:00Z | 6.58 | 38 | < 25mph | PG382 | 7.99 | 2019-05-30T17:00:00Z | 12.28 | 92 | < 25mph
PG&E | 2016-08-22 | 2016-08-22 16:10 | 37.9666 | -120.2395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Toulumne City FD | 101043683 |  | 17000 | Conductor | Overhead | Yes | 42604 | 2016-08-22 16:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0941 | 2016 | 8 | 22 | 16 | 10 | 16-0059149 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 78534 | 13.4322 | 233_237 | <25mph | <15mph | HFTD - Distribution | 2016-08-22 16:10:00 | 684 | 13.7297 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.67 | 2016-04-26T00:02:00Z | 24.99 | 5 | < 25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.67 | 2016-04-26T00:02:00Z | 24.99 | 10 | < 25mph
PG&E | 2015-10-16 09:43 | 2015-10-16 09:43 | 39.187 | -123.2015 | Vegetation | Rural | < 3 meters | Unknown |  | 102196855 |  | 12000 | Conductor | Overhead | Yes | 42293.4049 | 2015-10-16 09:43 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0653 | 2015 | 10 | 16 | 9 | 43 | 15-0070948 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 65228 | 2.2696 | 105_305 | <25mph | <15mph | HFTD - Distribution | 2015-10-16 09:43:00 | 397 | 16.8813 | FALSE | <25mph | E7513 | 1.34 | 2016-02-19T03:03:00Z | 2.01 | 11 | < 25mph | E6035 | 6.13 | 2016-02-19T03:27:00Z | 4 | 19 | < 25mph | E7513 | 1.34 | 2016-02-19T04:43:00Z | 4 | 22 | < 25mph | E7513 | 1.34 | 2016-02-19T04:43:00Z | 4 | 42 | < 25mph
PG&E | 2016-05-15 15:54 | 2016-05-15 15:54 | 36.7948 | -119.3966 | Vegetation | RURAL | 100 - 299 Acres | Fire Agency | Cal Fire | 100729685 | None | 12000 | Conductor | Overhead | Yes | 42505.6625 | 2016-05-15 15:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0730 | 2016 | 5 | 15 | 15 | 54 | 16-0036136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 180310 | 10.5903 | 270_173 | <25mph | <15mph | HFTD - Distribution | 2016-05-15 15:54:00 | 474 | 14.7659 | FALSE | <25mph |  |  |  | 0 | 0 | No data | FCHC1 | 7.54 | 2019-07-20T22:00:00Z | 14 | 7 | < 25mph |  |  |  | 0 | 0 | No data | FCHC1 | 7.54 | 2019-07-20T23:00:00Z | 14.99 | 14 | < 25mph
PG&E | 2017-08-05 08:33 | 08:33 | 38.4583 | -120.8695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JEFF MICHEL- 530 409 2223 | 101236223 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42952.3565 | 08:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1317 | 2017 | 8 | 5 | 8 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 6.5905 | 205_264 | <25mph | <15mph | HFTD - Distribution | 2017-08-05 08:33:00 | 1055 | 14.6063 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 6.33 | 2017-10-23T02:05:00Z | 17 | 10 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 6.33 | 2017-10-23T02:05:00Z | 17 | 16 | < 25mph
PG&E | 2018-07-17 | 11:58 | 37.2217 | -121.6778 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Luis Morado state arson fire fighter | 100601345 | Unknown | 12000 | Conductor | Overhead | Yes | 43298 | 11:58 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1756 | 2018 | 7 | 17 | 11 | 58 | 18-0060617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 5865 | 5.1834 | 170_196 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 11:58:00 | 1496 | 14.408 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C7794 | 7.07 | 2017-05-29T21:05:00Z | 11.01 | 36 | < 25mph |  |  |  | 0 | 0 | No data | C7794 | 7.07 | 2017-05-29T21:55:00Z | 12.01 | 75 | < 25mph
PG&E | 2016-07-03 15:00 | 2016-07-03 15:00 | 38.0348 | -120.3809 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101050507 |  | 17000 | Conductor | Overhead | Yes | 42554.625 | 2016-07-03 15:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0837 | 2016 | 7 | 3 | 15 | 0 | 16-0047689 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38812 | 10.6263 | 226_241 | <25mph | <15mph | HFTD - Distribution | 2016-07-03 15:00:00 | 580 | 12.5395 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MOUC1 | 7.53 | 2015-12-20T21:02:00Z | 14 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MOUC1 | 7.53 | 2015-12-20T22:02:00Z | 18.01 | 2 | < 25mph
PG&E | 2015-11-09 05:55 | 2015-11-09 05:55 | 34.9984 | -120.3634 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42317.2465 | 2015-11-09 05:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0673 | 2015 | 11 | 9 | 5 | 55 | 15-0076534 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 205393 | 8.4294 | 228_73 | <25mph | <15mph | HFTD - Distribution | 2015-11-09 05:55:00 | 417 | 17.7768 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AU609 | 7.47 | 2018-11-09T20:32:00Z | 20 | 10 | < 25mph |  |  |  | 0 | 0 | No data | AU609 | 7.47 | 2018-11-09T20:32:00Z | 20 | 20 | < 25mph
PG&E | 2019-05-08 | 10:23 | 39.3851 | -122.557 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | Colusa FD | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-312 | 2019 | 5 | 8 | 10 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 11.1721 | 133_316 | <25mph | <15mph | HFTD - Distribution | 2019-05-08 10:23:00 | 1764 | 11.4886 | FALSE | <25mph | SYWC1 | 1.49 | 2017-08-22T19:26:00Z | 8.01 | 1 | < 25mph | SYWC1 | 1.49 | 2017-08-22T19:26:00Z | 8.01 | 2 | < 25mph | SYWC1 | 1.49 | 2017-08-22T19:26:00Z | 8.01 | 2 | < 25mph | SYWC1 | 1.49 | 2017-08-22T19:26:00Z | 8.01 | 4 | < 25mph
PG&E | 2017-07-30 09:47 | 09:46 | 38.9132 | -122.6179 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike wink | 102151066 | None | 0 – 750 | Conductor | Overhead | Yes | 42946.4075 | 09:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1302 | 2017 | 7 | 30 | 9 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.2785 | 130_290 | <25mph | <15mph | HFTD - Distribution | 2017-07-30 09:46:00 | 1040 | 13.7198 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 4.76 | 2018-04-06T19:57:00Z | 14 | 9 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 4.76 | 2018-04-06T20:57:00Z | 17 | 18 | < 25mph
PG&E | 2019-09-01 | 16:50 | 35.908 | -121.011 |  | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 103477437 |  | 12000 | Pole | Overhead | Yes | 43709 | 16:50 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-17 | 2019 | 9 | 1 | 16 | 50 | 19-0094475 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45432 | 5.8888 | 199_124 | <25mph | <15mph | HFTD - Distribution | 2019-09-01 16:50:00 | 2009 | 25.5842 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
7. Camp Fire | 2018-11-08 | 6:33 | 39.8134 | -121.4347 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 60000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1993 | 2018 | 11 | 8 | 6 | 33 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Conductor | 826291590 | 33.1236 | 181_339 | 25-40mph | 30-45mph | HFTD - Transmission | 2018-11-08 06:33:00 | 1699 | 39.0185 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | JBGC1 | 6.08 | 2018-07-22T16:13:00Z | 8.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | JBGC1 | 6.08 | 2018-07-22T16:13:00Z | 8.99 | 2 | < 25mph
PG&E | 2016-10-11 23:17 | 23:16 | 39.0201 | -120.8294 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire.foresthill fire | 100025501 |  | 60000 | Conductor | Overhead | Yes | 42654.9701 | 23:16 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error |  | no-match | 1028 | 2016 | 10 | 11 | 23 | 16 | INT-08640 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 0 | 7.6312 | 207_295 | <25mph | <15mph | HFTD - Transmission | 2016-10-11 23:16:00 | 769 | 11.1078 | FALSE | <25mph | AU268 | 0.89 | 2017-07-07T10:46:00Z | 0 | 1 | < 25mph | FSHC1 | 7.19 | 2017-07-07T11:33:00Z | 5.99 | 5 | < 25mph | AU268 | 0.89 | 2017-07-07T12:25:00Z | 0 | 4 | < 25mph | FSHC1 | 7.19 | 2017-07-07T12:33:00Z | 7 | 15 | < 25mph
PG&E | 2015-05-02 16:51 | 2015-05-02 16:51 | 37.3284 | -119.643 | Vegetation | Rural | < 0.25 Acres | Fire Agency | MADERA COUNTY | 103768995 |  | 12000 | Conductor | Overhead | Yes | 42126.7021 | 2015-05-02 16:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0305 | 2015 | 5 | 2 | 16 | 51 | 15-0031285 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 79805 | 9.7158 | 259_202 | <25mph | <15mph | HFTD - Distribution | 2015-05-02 16:51:00 | 51 | 12.4769 | FALSE | <25mph | BSNC1 | 3.53 | 2019-02-09T16:48:00Z | 5.99 | 36 | < 25mph | BSNC1 | 3.53 | 2019-02-09T16:48:00Z | 5.99 | 64 | < 25mph | D7171 | 2.96 | 2019-02-09T18:10:00Z | 8.99 | 70 | < 25mph | D7171 | 2.96 | 2019-02-09T18:10:00Z | 8.99 | 126 | < 25mph
PG&E | 2018-06-13 | 22:40 | 38.4901 | -122.6661 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SRS181640125 | 101966547 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 22:40 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1656 | 2018 | 6 | 13 | 22 | 40 | 18-0050782 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 295146 | 2.5247 | 128_267 | <25mph | <15mph | HFTD - Distribution | 2018-06-13 22:40:00 | 1398 | 17.8767 | FALSE | <25mph | E1582 | 2.84 | 2018-11-03T01:33:00Z | 5.99 | 15 | < 25mph | E1582 | 2.84 | 2018-11-03T01:33:00Z | 5.99 | 63 | < 25mph | E1582 | 2.84 | 2018-11-03T01:53:00Z | 8.01 | 30 | < 25mph | E1582 | 2.84 | 2018-11-03T01:53:00Z | 8.01 | 126 | < 25mph
PG&E | 2015-10-07 15:04 | 2015-10-07 15:04 | 35.3079 | -120.8328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101924901 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42284.6277 | 2015-10-07 15:04 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0640 | 2015 | 10 | 7 | 15 | 3 | 15-0068730 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 77896 | 15.4357 | 207_90 | <25mph | <15mph | HFTD - Distribution | 2015-10-07 15:03:00 | 384 | 16.4418 | FALSE | <25mph | E6113 | 0.7 | 2016-05-29T22:14:00Z | 14.99 | 8 | < 25mph | E6113 | 0.7 | 2016-05-29T22:14:00Z | 14.99 | 9 | < 25mph | E6113 | 0.7 | 2016-05-29T22:14:00Z | 14.99 | 16 | < 25mph | E6113 | 0.7 | 2016-05-29T22:14:00Z | 14.99 | 19 | < 25mph
PG&E | 2018-08-13 | 15:33 | 38.708 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101377799 | Unknown | 21000 | Conductor | Overhead | Yes | 43325 | 15:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1840 | 2018 | 8 | 13 | 15 | 33 | 18-0069470 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1004 | 11.7134 | 201_278 | <25mph | <15mph | HFTD - Distribution | 2018-08-13 15:33:00 | 1579 | 13.7748 | FALSE | <25mph | PG073 | 2.99 | 2018-10-18T13:00:00Z | 12.06 | 62 | < 25mph | PG073 | 2.99 | 2018-10-18T13:00:00Z | 12.06 | 130 | < 25mph | PG073 | 2.99 | 2018-10-18T14:10:00Z | 12.28 | 124 | < 25mph | E4740 | 5.14 | 2018-10-18T13:46:00Z | 14 | 258 | < 25mph
PG&E | 2016-10-08 15:05 | 15:04 | 38.6686 | -120.9091 | Vegetation | RURAL | < 0.25 Acres | Customer | N.A. | 101380856 |  | 0 – 750 | Capacitor Bank | Overhead | Yes | 42651.6284 | 15:04 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1021 | 2016 | 10 | 8 | 15 | 4 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 10.4532 | 203_276 | <25mph | <15mph | HFTD - Distribution | 2016-10-08 15:04:00 | 762 | 14.8776 | FALSE | <25mph | PG359 | 2.1 | 2019-07-14T06:50:00Z | 6.58 | 52 | < 25mph | PG073 | 6.84 | 2019-07-14T06:10:00Z | 14.47 | 165 | < 25mph | PG359 | 2.1 | 2019-07-14T07:00:00Z | 7.9 | 103 | < 25mph | PG073 | 6.84 | 2019-07-14T06:10:00Z | 14.47 | 327 | < 25mph
PG&E | 2016-08-22 | 2016-08-22 16:10 | 37.9666 | -120.2395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Toulumne City FD | 101043683 |  | 17000 | Conductor | Overhead | Yes | 42604 | 2016-08-22 16:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0941 | 2016 | 8 | 22 | 16 | 10 | 16-0059149 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 78534 | 13.4322 | 233_237 | <25mph | <15mph | HFTD - Distribution | 2016-08-22 16:10:00 | 684 | 13.7297 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.67 | 2018-04-22T18:02:00Z | 8.01 | 5 | < 25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.67 | 2018-04-22T19:02:00Z | 14 | 11 | < 25mph
PG&E | 2018-06-16 | 19:58 | 37.907 | -121.8063 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100483910 | Unknown | 21000 | Conductor | Overhead | Yes | 43267 | 19:58 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1670 | 2018 | 6 | 16 | 19 | 58 | 18-0051687 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 3322 | 40.9858 | 164_234 | 40-55mph | 30-45mph | HFTD - Distribution | 2018-06-16 19:58:00 | 1412 | 43.1884 | FALSE | 40-55mph | PG071 | 2.97 | 2019-05-21T06:50:00Z | 23.44 | 12 | < 25mph | SJS02 | 6.13 | 2019-05-21T06:20:00Z | 43.4 | 118 | 40-55mph | PG069 | 2.66 | 2019-05-21T08:00:00Z | 25.66 | 24 | 25-40mph | PG066 | 6.3 | 2019-05-21T07:30:00Z | 44.29 | 234 | 40-55mph
PG&E | 2017-07-02 | 13:28 | 39.8605 | -121.6274 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 000/017c | Unknown | 60000 | Conductor | Overhead | Yes | 42918 | 13:28 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1216 | 2017 | 7 | 2 | 13 | 28 | INT-09794 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 10.1141 | 173_342 | <25mph | <15mph | HFTD - Transmission | 2017-07-02 13:28:00 | 956 | 11.4462 | FALSE | <25mph | PG134 | 2.93 | 2018-12-14T01:20:00Z | 5.91 | 31 | < 25mph | CSTC1 | 7.55 | 2018-12-14T00:51:00Z | 5.99 | 40 | < 25mph | PG134 | 2.93 | 2018-12-14T01:20:00Z | 5.91 | 59 | < 25mph | CSTC1 | 7.55 | 2018-12-14T00:51:00Z | 5.99 | 76 | < 25mph
PG&E | 2018-07-23 | 17:27 | 39.734 | -121.4965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103843963 | AT&T | 12000 | Conductor | Overhead | Yes | 43304 | 17:27 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1782 | 2018 | 7 | 23 | 17 | 27 | 18-0062874 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 183629 | 9.1915 | 178_335 | <25mph | <15mph | HFTD - Distribution | 2018-07-23 17:27:00 | 1522 | 13.4352 | FALSE | <25mph | JBGC1 | 0.42 | 2015-07-23T18:13:00Z | 7 | 1 | < 25mph | E2076 | 4.98 | 2015-07-23T18:27:00Z | 8.99 | 20 | < 25mph | JBGC1 | 0.42 | 2015-07-23T19:13:00Z | 8.01 | 2 | < 25mph | E2076 | 4.98 | 2015-07-23T18:27:00Z | 8.99 | 36 | < 25mph
PG&E | 2019-09-27 | 10:30 | 36.5336 | -121.1464 | Vegetation | Barren/Other | 0.25 - 10 Acres | Cal Fire |  | 182492105 |  | 21000 | Conductor | Overhead | Yes | 43735 | 10:30 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-359 | 2019 | 9 | 27 | 10 | 30 | 19-0104536 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20631 | 5.3593 | 193_158 | <25mph | <15mph | HFTD - Distribution | 2019-09-27 10:30:00 | 2062 | 16.3021 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.34 | 2016-02-07T21:37:00Z | 10 | 1 | < 25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.34 | 2016-02-07T21:37:00Z | 10 | 2 | < 25mph
PG&E | 2016-08-03 | 2016-08-03 12:41 | 39.3269 | -120.6033 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100001032 |  | 12000 | Conductor | Overhead | Yes | 42585 | 2016-08-03 12:41 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0902 | 2016 | 8 | 3 | 12 | 41 | 16-0054769 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 20554 | 9.0542 | 216_312 | <25mph | <15mph | HFTD - Distribution | 2016-08-03 12:41:00 | 645 | 12.3394 | FALSE | <25mph | CISCO | 2.6 | 2017-01-24T19:00:00Z | 11.01 | 6 | < 25mph | CISCO | 2.6 | 2017-01-24T19:00:00Z | 11.01 | 6 | < 25mph | CISCO | 2.6 | 2017-01-24T19:00:00Z | 11.01 | 12 | < 25mph | CISCO | 2.6 | 2017-01-24T19:00:00Z | 11.01 | 12 | < 25mph
PG&E | 2018-10-24 | 14:18 | 36.7265 | -119.1086 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CHRIS CHRISTOPHERSON (559)493-4320 I.C #18CAFKUO15649 | 100691946 | None | 12000 | Conductor | Overhead | Yes | 43397 | 14:18 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1950 | 2018 | 10 | 24 | 14 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 7.8375 | 283_170 | <25mph | <15mph | HFTD - Distribution | 2018-10-24 14:18:00 | 1689 | 7.8887 | FALSE | <25mph | PG258 | 2.78 | 2019-12-03T22:00:00Z | 7.38 | 18 | < 25mph | PG258 | 2.78 | 2019-12-03T22:00:00Z | 7.38 | 59 | < 25mph | PG267 | 3.52 | 2019-12-03T22:50:00Z | 7.38 | 36 | < 25mph | PG267 | 3.52 | 2019-12-03T22:50:00Z | 7.38 | 118 | < 25mph
PG&E | 2019-05-15 | 21:31 | 38.5731 | -122.9603 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Unknown |  | 103931177 |  | 12000 | Conductor | Overhead | Yes | 43600 | 21:31 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-316 | 2019 | 5 | 15 | 21 | 31 | 19-0052480 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 27780 | 16.5892 | 115_271 | <25mph | <15mph | HFTD - Distribution | 2019-05-15 21:31:00 | 1774 | 23.8094 | FALSE | <25mph | D9841 | 3.34 | 2016-08-18T19:50:00Z | 3 | 4 | < 25mph | AR798 | 4.72 | 2016-08-18T19:30:00Z | 8.01 | 41 | < 25mph | D9841 | 3.34 | 2016-08-18T19:50:00Z | 3 | 6 | < 25mph | AR798 | 4.72 | 2016-08-18T21:09:00Z | 8.99 | 63 | < 25mph
PG&E | 2019-05-08 | 10:23 | 39.3851 | -122.557 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | Colusa FD | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-312 | 2019 | 5 | 8 | 10 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 11.1721 | 133_316 | <25mph | <15mph | HFTD - Distribution | 2019-05-08 10:23:00 | 1764 | 11.4886 | FALSE | <25mph | SYWC1 | 1.49 | 2015-10-29T18:26:00Z | 17 | 1 | < 25mph | SYWC1 | 1.49 | 2015-10-29T18:26:00Z | 17 | 2 | < 25mph | SYWC1 | 1.49 | 2015-10-29T18:26:00Z | 17 | 2 | < 25mph | SYWC1 | 1.49 | 2015-10-29T18:26:00Z | 17 | 4 | < 25mph
PG&E | 2015-10-25 05:50 | 2015-10-25 05:50 | 37.7843 | -121.7683 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | cutouts 9504 |  | 21000 | Conductor | Overhead | Yes | 42302.2431 | 2015-10-25 05:50 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0657 | 2015 | 10 | 25 | 5 | 50 | 15-0073203 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 10710 | 23.3456 | 166_227 | <25mph | <15mph | HFTD - Distribution | 2015-10-25 05:50:00 | 401 | 23.3456 | FALSE | <25mph | LVMC1 | 2.34 | 2018-04-16T05:02:00Z | 22.01 | 2 | < 25mph | LVMC1 | 2.34 | 2018-04-16T05:02:00Z | 22.01 | 6 | < 25mph | LVMC1 | 2.34 | 2018-04-16T05:02:00Z | 22.01 | 4 | < 25mph | LVMC1 | 2.34 | 2018-04-16T05:02:00Z | 22.01 | 12 | < 25mph
PG&E | 2015-07-18 17:00 | 2015-07-18 17:00 | 38.8383 | -123.6297 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | off HWY 1 PA |  | 12000 | Conductor | Overhead | Yes | 42203.7083 | 2015-07-18 17:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0470 | 2015 | 7 | 18 | 17 | 0 | 15-0048394 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 51806 | 18.0824 | 86_287 | <25mph | <15mph | HFTD - Distribution | 2015-07-18 17:00:00 | 215 | 27.3037 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | ANVC1 | 6.68 | 2018-09-21T09:36:00Z | 10 | 11 | < 25mph |  |  |  | 0 | 0 | No data | ANVC1 | 6.68 | 2018-09-21T10:36:00Z | 10 | 21 | < 25mph
PG&E | 2018-08-22 | 21:56 | 39.0425 | -120.9695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100024728 | Verizon | 12000 | Conductor | Overhead | Yes | 43334 | 21:56 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1854 | 2018 | 8 | 22 | 21 | 56 | 18-0072654 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29727 | 9.3137 | 201_296 | <25mph | <15mph | HFTD - Distribution | 2018-08-22 21:56:00 | 1593 | 10.5291 | FALSE | <25mph | C5488 | 3.82 | 2016-02-20T17:40:00Z | 2.01 | 10 | < 25mph | AU268 | 6.84 | 2016-02-20T17:28:00Z | 4 | 33 | < 25mph | D9434 | 1.28 | 2016-02-20T19:04:00Z | 2.01 | 20 | < 25mph | AU268 | 6.84 | 2016-02-20T17:28:00Z | 4 | 66 | < 25mph
PG&E | 2017-10-20 | 13:45 | 34.5532 | -120.5303 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 101921492 | Unknown | 12000 | Conductor | Overhead | Yes | 43028 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1502 | 2017 | 10 | 20 | 13 | 45 | 17-0089249 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 173 | 31.847 | 221_49 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-20 13:45:00 | 1245 | 35.5655 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E2332 | 4.19 | 2018-01-23T06:06:00Z | 23 | 18 | < 25mph |  |  |  | 0 | 0 | No data | E2332 | 4.19 | 2018-01-23T07:33:00Z | 24.99 | 36 | < 25mph
PG&E | 2015-06-27 12:48 | 2015-06-27 12:48 | 37.9474 | -120.4274 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101034512 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.5333 | 2015-06-27 12:48 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0414 | 2015 | 6 | 27 | 12 | 48 | 15-0043755 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 150075 | 11.0891 | 224_236 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 12:48:00 | 159 | 19.6587 | FALSE | <25mph | PG167 | 1.8 | 2019-02-21T23:40:00Z | 25.43 | 12 | 25-40mph | PG167 | 1.8 | 2019-02-21T23:40:00Z | 25.43 | 30 | 25-40mph | PG167 | 1.8 | 2019-02-21T23:40:00Z | 25.43 | 24 | 25-40mph | PG161 | 6.71 | 2019-02-22T00:50:00Z | 26.53 | 60 | 25-40mph
PG&E | 2018-06-15 | 10:05 | 38.6238 | -121.0221 | Vegetation | Rural | < 3 meters | Customer | N.A. | 101376538 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43266 | 10:05 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1661 | 2018 | 6 | 15 | 10 | 5 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 10.3423 | 199_273 | <25mph | <15mph | HFTD - Distribution | 2018-06-15 10:05:00 | 1403 | 17.1425 | FALSE | <25mph | E8856 | 3.9 | 2018-09-14T00:55:00Z | 8.01 | 13 | < 25mph | FSLC1 | 7.47 | 2018-09-14T01:20:00Z | 11.41 | 91 | < 25mph | E8856 | 3.9 | 2018-09-14T01:55:00Z | 8.01 | 25 | < 25mph | FSLC1 | 7.47 | 2018-09-14T01:20:00Z | 11.41 | 177 | < 25mph
PG&E | 2018-06-08 | 19:03 | 35.154 | -120.594 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101852092 | AT&T | 12000 | Conductor | Overhead | Yes | 43259 | 19:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1644 | 2018 | 6 | 8 | 19 | 3 | 18-0049130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2473 | 24.0333 | 218_82 | <25mph | <15mph | HFTD - Distribution | 2018-06-08 19:03:00 | 1386 | 25.9327 | FALSE | 25-40mph | D6295 | 3.26 | 2015-01-20T10:49:00Z | 5.99 | 10 | < 25mph | D6295 | 3.26 | 2015-01-20T10:49:00Z | 5.99 | 14 | < 25mph | D6295 | 3.26 | 2015-01-20T11:44:00Z | 7 | 24 | < 25mph | D6295 | 3.26 | 2015-01-20T11:44:00Z | 7 | 32 | < 25mph
PG&E | 2019-06-15 | 14:08 | 38.8802 | -122.6125 | Tree - cutting, 3rd party | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 43361103 |  | 12000 | Pole | Overhead | Yes | 43631 | 14:08 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | Other/Unknown | 2019-19 | 2019 | 6 | 15 | 14 | 8 | 19-0068074 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 259562 | 11.2331 | 130_288 | <25mph | <15mph | HFTD - Distribution | 2019-06-15 14:08:00 | 1841 | 15.703 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5568 | 5.92 | 2015-01-01T08:29:00Z | 11.99 | 9 | < 25mph |  |  |  | 0 | 0 | No data | E5568 | 5.92 | 2015-01-01T09:44:00Z | 14 | 18 | < 25mph
PG&E | 2016-09-28 | 14:00 | 35.2145 | -118.5625 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire |  |  | 0 – 750 | Conductor | Overhead | Yes | 42641 | 14:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1008 | 2016 | 9 | 28 | 14 | 0 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.8467 | 310_87 | <25mph | <15mph | HFTD - Distribution | 2016-09-28 14:00:00 | 750 | 26.957 | FALSE | 25-40mph | HFLC1 | 3.31 | 2018-12-16T05:13:00Z | 24 | 9 | < 25mph | HFLC1 | 3.31 | 2018-12-16T05:13:00Z | 24 | 57 | < 25mph | HFLC1 | 3.31 | 2018-12-16T06:13:00Z | 24 | 19 | < 25mph | HFLC1 | 3.31 | 2018-12-16T06:13:00Z | 24 | 115 | < 25mph
PG&E | 2015-06-12 23:32 | 2015-06-12 23:32 | 39.2308 | -121.1559 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 10903 PROSPECTOR RD ROUGH AND READY | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42167.9806 | 2015-06-12 23:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0380 | 2015 | 6 | 12 | 23 | 32 | 15-0040789 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 20 | 12.2901 | 193_307 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 23:32:00 | 126 | 14.4252 | FALSE | <25mph | E2572 | 1.63 | 2015-03-31T05:13:00Z | 4 | 18 | < 25mph | E1789 | 6.1 | 2015-03-31T05:42:00Z | 8.99 | 64 | < 25mph | E2572 | 1.63 | 2015-03-31T05:13:00Z | 4 | 36 | < 25mph | E1789 | 6.1 | 2015-03-31T06:30:00Z | 11.99 | 117 | < 25mph
PG&E | 2018-10-14 | 19:39 | 38.446 | -120.5147 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | IC- Dillon Gissell- 209-295-7735 | 103384485 | Unknown | 12000 | Conductor | Overhead | Yes | 43387 | 19:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1939 | 2018 | 10 | 14 | 19 | 39 | 18-0090288 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3497327 | 25.4932 | 220_264 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-14 19:39:00 | 1678 | 30.9108 | FALSE | 25-40mph | PG178 | 2.05 | 2019-02-27T00:20:00Z | 28.72 | 31 | 25-40mph | PG178 | 2.05 | 2019-02-27T00:20:00Z | 28.72 | 43 | 25-40mph | PG094 | 1.42 | 2019-02-27T00:40:00Z | 40.33 | 62 | 40-55mph | PG094 | 1.42 | 2019-02-27T00:40:00Z | 40.33 | 86 | 40-55mph
PG&E | 2019-05-30 | 8:18 | 35.7005 | -120.8104 | Vehicle | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 101871463 |  | 12000 | Pole | Overhead | Yes | 43615 | 8:18 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-274 | 2019 | 5 | 30 | 8 | 18 | 19-0059906 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 171603 | 10.8019 | 208_112 | <25mph | <15mph | HFTD - Distribution | 2019-05-30 08:18:00 | 1791 | 17.2262 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D4060 | 4.58 | 2018-05-31T20:07:00Z | 11.01 | 5 | < 25mph |  |  |  | 0 | 0 | No data | D4060 | 4.58 | 2018-05-31T21:08:00Z | 12.01 | 10 | < 25mph
PG&E | 2017-07-02 | 13:28 | 39.8605 | -121.6274 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 000/017c | Unknown | 60000 | Conductor | Overhead | Yes | 42918 | 13:28 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1216 | 2017 | 7 | 2 | 13 | 28 | INT-09794 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 10.1141 | 173_342 | <25mph | <15mph | HFTD - Transmission | 2017-07-02 13:28:00 | 956 | 11.4462 | FALSE | <25mph | C8878 | 1.44 | 2019-01-03T08:58:00Z | 7 | 35 | < 25mph | CSTC1 | 7.55 | 2019-01-03T08:51:00Z | 11.01 | 43 | < 25mph | C8878 | 1.44 | 2019-01-03T09:13:00Z | 7 | 69 | < 25mph | CSTC1 | 7.55 | 2019-01-03T08:51:00Z | 11.01 | 85 | < 25mph
PG&E | 2015-12-08 12:41 | 2015-12-08 12:41 | 38.2489 | -120.5228 | Other | Rural | Structure Only | Unknown |  | 7026 Railroad Flat Road, Mountain Ranch |  | 12000 | Conductor | Overhead | Yes | 42346.5285 | 2015-12-08 12:41 | Contact From Object | N.A. | Other | Electric Facility | Human Error | AT&T work error | Other/Unknown | 0684 | 2015 | 12 | 8 | 12 | 41 | 15-0083435 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1120 | 3.9918 | 220_253 | <25mph | <15mph | HFTD - Distribution | 2015-12-08 12:41:00 | 428 | 10.4116 | FALSE | <25mph | ESPC1 | 3.04 | 2015-03-07T17:13:00Z | 5.99 | 7 | < 25mph | ESPC1 | 3.04 | 2015-03-07T17:13:00Z | 5.99 | 7 | < 25mph | ESPC1 | 3.04 | 2015-03-07T18:13:00Z | 7 | 14 | < 25mph | ESPC1 | 3.04 | 2015-03-07T18:13:00Z | 7 | 14 | < 25mph
PG&E | 2018-06-09 | 0:46 | 35.0745 | -120.5167 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101927520 | Unknown | 12000 | Conductor | Overhead | Yes | 43260 | 0:46 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1645 | 2018 | 6 | 9 | 0 | 46 | 18-0049171 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 16825 | 5.84 | 221_78 | <25mph | <15mph | HFTD - Distribution | 2018-06-09 00:46:00 | 1387 | 22.9582 | FALSE | <25mph | E8214 | 3.18 | 2017-07-21T21:39:00Z | 8.99 | 9 | < 25mph | AU609 | 7.04 | 2017-07-21T21:59:00Z | 12.01 | 28 | < 25mph | E8214 | 3.18 | 2017-07-21T21:39:00Z | 8.99 | 21 | < 25mph | AU609 | 7.04 | 2017-07-21T21:59:00Z | 12.01 | 57 | < 25mph
7. Camp Fire | 2018-11-08 | 6:33 | 39.8134 | -121.4347 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 60000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1993 | 2018 | 11 | 8 | 6 | 33 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Conductor | 826291590 | 33.1236 | 181_339 | 25-40mph | 30-45mph | HFTD - Transmission | 2018-11-08 06:33:00 | 1699 | 39.0185 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | JBGC1 | 6.08 | 2016-07-31T22:13:00Z | 8.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | JBGC1 | 6.08 | 2016-07-31T22:13:00Z | 8.01 | 2 | < 25mph
PG&E | 2015-06-30 18:18 | 2015-06-30 18:18 | 36.2199 | -121.7534 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | loadside of 88973 | unknown | 12000 | Conductor | Overhead | Yes | 42185.7625 | 2015-06-30 18:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0432 | 2015 | 6 | 30 | 18 | 18 | 15-0044405 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 158 | 5.7006 | 166_141 | <25mph | <15mph | HFTD - Distribution | 2015-06-30 18:18:00 | 177 | 8.2628 | FALSE | <25mph | PPSC1 | 2.3 | 2015-03-26T04:04:00Z | 4.99 | 1 | < 25mph | E4662 | 6.7 | 2015-03-26T04:24:00Z | 10.98 | 5 | < 25mph | PPSC1 | 2.3 | 2015-03-26T05:04:00Z | 8.99 | 2 | < 25mph | E4662 | 6.7 | 2015-03-26T05:09:00Z | 14 | 10 | < 25mph
PG&E | 2015-02-06 06:01 | 2015-02-06 06:01 | 38.6059 | -121.0221 | Vegetation | Rural | < 3 meters | Fire Agency |  | 6661 Ryan Ranch Road, El Dorado Hills |  | 21000 | Conductor | Overhead | Yes | 42041.2507 | 2015-02-06 06:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0259 | 2015 | 2 | 6 | 6 | 1 | 15-0009876 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 51996 | 16.7927 | 199_272 | <25mph | <15mph | HFTD - Distribution | 2015-02-06 06:01:00 | 6 | 30.3484 | FALSE | 25-40mph | PG357 | 3.83 | 2019-11-07T13:20:00Z | 7.09 | 18 | < 25mph | BENC1 | 4.89 | 2019-11-07T12:59:00Z | 8.01 | 100 | < 25mph | PG357 | 3.83 | 2019-11-07T13:20:00Z | 7.09 | 36 | < 25mph | BENC1 | 4.89 | 2019-11-07T12:59:00Z | 8.01 | 199 | < 25mph
PG&E | 2019-01-16 | 0:17 | 38.0621 | -120.1964 | Vegetation | Conifer Forest | Structure Only | Cal Fire |  | 163661701 |  | 17000 | Conductor | Overhead | Yes | 43481 | 0:17 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-01 | 2019 | 1 | 16 | 0 | 17 | 19-0010443 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1041827 | 14.8061 | 234_243 | <25mph | <15mph | HFTD - Distribution | 2019-01-16 00:17:00 | 1728 | 28.2081 | FALSE | 25-40mph | MOUC1 | 2.77 | 2016-06-18T04:02:00Z | 7 | 1 | < 25mph | MOUC1 | 2.77 | 2016-06-18T04:02:00Z | 7 | 1 | < 25mph | MOUC1 | 2.77 | 2016-06-18T05:02:00Z | 8.01 | 2 | < 25mph | MOUC1 | 2.77 | 2016-06-18T05:02:00Z | 8.01 | 2 | < 25mph
PG&E | 2015-05-09 13:10 | 2015-05-09 13:10 | 39.2343 | -121.2468 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100000103 | None | 21000 | Conductor | Overhead | Yes | 42133.5486 | 2015-05-09 13:10 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0311 | 2015 | 5 | 9 | 13 | 10 | 15-0033085 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 382926 | 12.172 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 13:10:00 | 57 | 17.071 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6355 | 7.8 | 2018-12-15T16:19:00Z | 4 | 6 | < 25mph |  |  |  | 0 | 0 | No data | E6355 | 7.8 | 2018-12-15T16:19:00Z | 4 | 13 | < 25mph
PG&E | 2016-09-25 | 19:19 | 37.0993 | -122.1155 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire ben lomond fire | 101670837 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42638 | 19:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1003 | 2016 | 9 | 25 | 19 | 19 | 16-0067346 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1497 | 2.1111 | 150_190 | <25mph | <15mph | HFTD - Distribution | 2016-09-25 19:19:00 | 746 | 9.8702 | FALSE | <25mph | BNDC1 | 3.83 | 2018-12-05T03:50:00Z | 23 | 32 | < 25mph | BNDC1 | 3.83 | 2018-12-05T03:50:00Z | 23 | 59 | < 25mph | BNDC1 | 3.83 | 2018-12-05T03:50:00Z | 23 | 65 | < 25mph | BNDC1 | 3.83 | 2018-12-05T03:50:00Z | 23 | 122 | < 25mph
PG&E | 2019-08-01 | 13:28 | 38.5721 | -120.6803 | Equipment Failure/Involved, Overhead | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 153662102 |  | 21000 | Conductor | Overhead | Yes | 43678 | 13:28 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-170 | 2019 | 8 | 1 | 13 | 28 | 19-0083500 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1374 | 13.6823 | 213_271 | <25mph | <15mph | HFTD - Distribution | 2019-08-01 13:28:00 | 1945 | 13.6823 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-12-14 | 10:32 | 40.4379 | -123.7834 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101009136 | Unknown | 12000 | Conductor | Overhead | Yes | 43448 | 10:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1985 | 2018 | 12 | 14 | 10 | 32 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 36.1442 | 82_375 | 25-40mph | 30-45mph | HFTD - Distribution | 2018-12-14 10:32:00 | 1725 | 36.1442 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E8593 | 4.88 | 2017-10-13T16:15:00Z | 0 | 1 | < 25mph |  |  |  | 0 | 0 | No data | E8593 | 4.88 | 2017-10-13T17:15:00Z | 4.99 | 13 | < 25mph
PG&E | 2019-07-27 | 8:22 | 40.3789 | -122.1873 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Self Extinguished |  | 103461102 |  | 12000 | Conductor | Overhead | Yes | 43673 | 8:22 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-382 | 2019 | 7 | 27 | 8 | 22 | 19-0081756 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 456 | 4.4493 | 149_370 | <25mph | <15mph | HFTD - Distribution | 2019-07-27 08:22:00 | 1935 | 12.5056 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AP525 | 5.17 | 2016-07-05T09:00:00Z | 2.01 | 6 | < 25mph |  |  |  | 0 | 0 | No data | AP525 | 5.17 | 2016-07-05T09:00:00Z | 2.01 | 12 | < 25mph
PG&E | 2016-05-12 20:15 | 2016-05-12 20:15 | 35.1922 | -120.4563 | Vegetation | RURAL | < 3 meters | Self Extinguished | N.A. | 101857280 |  | 12000 | Conductor | Overhead | Yes | 42502.8438 | 2016-05-12 20:15 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0727 | 2016 | 5 | 12 | 20 | 15 | 16-0035728 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 54088 | 8.5669 | 224_84 | <25mph | <15mph | HFTD - Distribution | 2016-05-12 20:15:00 | 471 | 14.182 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG168 | 7.57 | 2019-05-10T16:30:00Z | 4.61 | 25 | < 25mph |  |  |  | 0 | 0 | No data | D6295 | 7.33 | 2019-05-10T16:44:00Z | 4.99 | 49 | < 25mph
PG&E | 2017-12-29 | 16:31 | 37.8517 | -122.1586 | Vegetation | Rural | < 3 Meters | Fire Agency | 925-933-1313 | 100488954 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1552 | 2017 | 12 | 29 | 16 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 4.4772 | 149_231 | <25mph | <15mph | HFTD - Distribution | 2017-12-29 16:31:00 | 1294 | 9.6531 | FALSE | <25mph | E5555 | 3.67 | 2016-02-07T05:00:00Z | 13 | 38 | < 25mph | LBNL1 | 5.21 | 2016-02-07T05:00:00Z | 13.22 | 143 | < 25mph | E5555 | 3.67 | 2016-02-07T06:00:00Z | 18.01 | 75 | < 25mph | E5555 | 3.67 | 2016-02-07T06:00:00Z | 18.01 | 286 | < 25mph
PG&E | 2015-08-22 20:38 | 2015-08-22 20:38 | 38.7748 | -120.8564 | Vegetation | Rural | < 3 meters | Self Extinguished |  | at base of co pole 21721 - 720 Woodridge Rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42238.8597 | 2015-08-22 20:38 | Contact From Object | N.A. | Vegetation | Communication Facility | Unknown | tree hit phone lines | Fell into (Moderate-Severe defect) | 0549 | 2015 | 8 | 22 | 20 | 38 | 15-0056766 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26513 | 9.2929 | 206_282 | <25mph | <15mph | HFTD - Distribution | 2015-08-22 20:38:00 | 293 | 10.7008 | FALSE | <25mph | E5691 | 3.87 | 2017-01-24T04:05:00Z | 5.99 | 12 | < 25mph | E5691 | 3.87 | 2017-01-24T04:05:00Z | 5.99 | 70 | < 25mph | E5691 | 3.87 | 2017-01-24T04:10:00Z | 5.99 | 24 | < 25mph | E5691 | 3.87 | 2017-01-24T04:10:00Z | 5.99 | 136 | < 25mph
PG&E | 2018-10-21 | 0:32 | 35.5035 | -120.6025 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101886776 | Unknown | 21000 | Conductor | Overhead | Yes | 43394 | 0:32 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1948 | 2018 | 10 | 21 | 0 | 32 | 18-0092526 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 302559 | 9.0366 | 217_101 | <25mph | <15mph | HFTD - Distribution | 2018-10-21 00:32:00 | 1687 | 16.4549 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F1939 | 4.05 | 2018-03-01T16:23:00Z | 23 | 28 | < 25mph |  |  |  | 0 | 0 | No data | F1939 | 4.05 | 2018-03-01T16:23:00Z | 23 | 56 | < 25mph
PG&E | 2017-10-20 | 13:45 | 34.5532 | -120.5303 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 101921492 | Unknown | 12000 | Conductor | Overhead | Yes | 43028 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1502 | 2017 | 10 | 20 | 13 | 45 | 17-0089249 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 173 | 31.847 | 221_49 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-20 13:45:00 | 1245 | 35.5655 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PTGC1 | 6.9 | 2016-09-18T00:00:00Z | 26.37 | 15 | 25-40mph |  |  |  | 0 | 0 | No data | PTGC1 | 6.9 | 2016-09-18T01:00:00Z | 27.72 | 31 | 25-40mph
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 9:36 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 14.8685 | 222_261 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 09:36:00 | 925 | 23.4839 | FALSE | <25mph | AT450 | 2.61 | 2016-02-20T13:47:00Z | 4 | 17 | < 25mph | C9148 | 7.6 | 2016-02-20T14:03:00Z | 8.99 | 27 | < 25mph | AT450 | 2.61 | 2016-02-20T13:47:00Z | 4 | 33 | < 25mph | C9148 | 7.6 | 2016-02-20T15:03:00Z | 11.01 | 52 | < 25mph
PG&E | 2018-06-05 | 13:45 | 38.5432 | -122.7202 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 102031673 | Unknown | 12000 | Conductor | Overhead | Yes | 43256 | 13:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1633 | 2018 | 6 | 5 | 13 | 45 | 18-0047625 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 40599 | 7.3889 | 125_270 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 13:45:00 | 1375 | 15.9614 | FALSE | <25mph | E6724 | 3.93 | 2018-01-17T19:20:00Z | 4.99 | 5 | < 25mph | F39WW | 6.96 | 2018-01-17T19:30:00Z | 6.4 | 50 | < 25mph | E6724 | 3.93 | 2018-01-17T19:20:00Z | 4.99 | 11 | < 25mph | DENWW | 7.73 | 2018-01-17T20:00:00Z | 7.49 | 101 | < 25mph
PG&E | 2019-06-27 | 2:23 | 36.8198 | -119.3334 | Bird Found | Hardwood Woodland | 0.25 - 10 Acres | Self Extinguished |  | Kings River-Sanger-Reedley 115Kv At 16/089 |  | 115000 | Insulator | Overhead | Yes | 43643 | 2:23 | Equipment - PG&E | Insulator |  |  |  |  | no-match | 2019-104 | 2019 | 6 | 27 | 2 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | N.A. | 13.572 | 273_175 | <25mph | <15mph | HFTD - Transmission | 2019-06-27 02:23:00 | 1872 | 13.572 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TRMC1 | 6.47 | 2015-11-30T14:52:00Z | 8.01 | 13 | < 25mph |  |  |  | 0 | 0 | No data | TRMC1 | 6.47 | 2015-11-30T15:52:00Z | 8.01 | 25 | < 25mph
PG&E | 2016-11-09 | 9:06 | 37.4532 | -119.6413 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | US FOREST SERVICE | 101017062 |  | 12000 | Conductor | Overhead | Yes | 42683 | 9:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1046 | 2016 | 11 | 9 | 9 | 6 | 16-0078863 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1586 | 6.3162 | 259_209 | <25mph | <15mph | HFTD - Distribution | 2016-11-09 09:06:00 | 787 | 14.6769 | FALSE | <25mph | D0826 | 0.25 | 2019-09-26T07:32:00Z | 4 | 5 | < 25mph | MIAC1 | 6.17 | 2019-09-26T06:59:00Z | 8.01 | 45 | < 25mph | D0826 | 0.25 | 2019-09-26T08:32:00Z | 5.99 | 10 | < 25mph | MIAC1 | 6.17 | 2019-09-26T07:59:00Z | 8.99 | 92 | < 25mph
PG&E | 2016-07-31 12:11 | 2016-07-31 12:11 | 38.7827 | -120.9168 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101417359 |  | 21000 | Conductor | Overhead | Yes | 42582.5076 | 2016-07-31 12:11 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0895 | 2016 | 7 | 31 | 12 | 11 | 16-0053949 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 10.9662 | 203_282 | <25mph | <15mph | HFTD - Distribution | 2016-07-31 12:11:00 | 638 | 14.1387 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 6.02 | 2017-03-03T02:56:00Z | 4 | 54 | < 25mph |  |  |  | 0 | 0 | No data | D4464 | 7.25 | 2017-03-03T04:25:00Z | 5.99 | 107 | < 25mph
PG&E | 2019-04-20 | 6:57 | 37.8686 | -121.6843 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | East County FD | Unknown |  | 17000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-321 | 2019 | 4 | 20 | 6 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 39.0116 | 170_232 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-20 06:57:00 | 1744 | 39.0116 | FALSE | 25-40mph | D3588 | 2.98 | 2018-09-13T08:21:00Z | 11.01 | 6 | < 25mph | VAQC1 | 6.19 | 2018-09-13T08:45:00Z | 30 | 99 | 25-40mph | D3588 | 2.98 | 2018-09-13T08:21:00Z | 11.01 | 12 | < 25mph | VAQC1 | 6.19 | 2018-09-13T09:45:00Z | 31 | 198 | 25-40mph
PG&E | 2018-07-29 | 11:39 | 39.0968 | -123.5018 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102177329 | Unknown | 12000 | Conductor | Overhead | Yes | 43310 | 11:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1796 | 2018 | 7 | 29 | 11 | 39 | 18-0064779 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4329 | 14.6452 | 92_301 | <25mph | <15mph | HFTD - Distribution | 2018-07-29 11:39:00 | 1536 | 18.4465 | FALSE | <25mph | E1763 | 2 | 2016-11-23T09:25:00Z | 4 | 4 | < 25mph | E1763 | 2 | 2016-11-23T09:25:00Z | 4 | 4 | < 25mph | E1763 | 2 | 2016-11-23T09:25:00Z | 4 | 8 | < 25mph | E1763 | 2 | 2016-11-23T09:25:00Z | 4 | 8 | < 25mph
PG&E | 2018-07-27 | 23:12 | 37.18 | -122.029 | Vegetation | Rural | < 3 meters | Fire Agency | Jeremy Wise 408-378-4010 Incident # C182080066 | 100518365 | Unknown | 12000 | Conductor | Overhead | Yes | 43308 | 23:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1793 | 2018 | 7 | 27 | 23 | 12 | 18-0064525 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 30475 | 3.2895 | 154_194 | <25mph | <15mph | HFTD - Distribution | 2018-07-27 23:12:00 | 1533 | 9.1823 | FALSE | <25mph | D9791 | 2.82 | 2017-10-12T13:21:00Z | 2.01 | 10 | < 25mph | E6800 | 7.18 | 2017-10-12T13:42:00Z | 13 | 133 | < 25mph | D9791 | 2.82 | 2017-10-12T15:01:00Z | 3 | 20 | < 25mph | E6800 | 7.18 | 2017-10-12T13:42:00Z | 13 | 262 | < 25mph
PG&E | 2018-10-24 | 14:18 | 36.7265 | -119.1086 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CHRIS CHRISTOPHERSON (559)493-4320 I.C #18CAFKUO15649 | 100691946 | None | 12000 | Conductor | Overhead | Yes | 43397 | 14:18 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1950 | 2018 | 10 | 24 | 14 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 7.8375 | 283_170 | <25mph | <15mph | HFTD - Distribution | 2018-10-24 14:18:00 | 1689 | 7.8887 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PHRC1 | 5.37 | 2018-07-07T10:58:00Z | 8.99 | 18 | < 25mph |  |  |  | 0 | 0 | No data | PHRC1 | 5.37 | 2018-07-07T11:58:00Z | 8.99 | 34 | < 25mph
PG&E | 2019-09-01 | 16:50 | 35.908 | -121.011 |  | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 103477437 |  | 12000 | Pole | Overhead | Yes | 43709 | 16:50 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-17 | 2019 | 9 | 1 | 16 | 50 | 19-0094475 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45432 | 5.8888 | 199_124 | <25mph | <15mph | HFTD - Distribution | 2019-09-01 16:50:00 | 2009 | 25.5842 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-10-07 | 1:44 | 37.178 | -122.0267 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Mike Mathiesen 408-472-1613 Incident # SCU7096 | 100518363 | Unknown | 12000 | Conductor | Overhead | Yes | 43380 | 1:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1929 | 2018 | 10 | 7 | 1 | 44 | 18-0087807 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 224444 | 25.0906 | 154_194 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-07 01:44:00 | 1668 | 25.864 | FALSE | 25-40mph | D9791 | 2.63 | 2017-07-02T03:31:00Z | 4.99 | 10 | < 25mph | E8391 | 7.92 | 2017-07-02T03:37:00Z | 10 | 133 | < 25mph | D9791 | 2.63 | 2017-07-02T03:31:00Z | 4.99 | 20 | < 25mph | E8391 | 7.92 | 2017-07-02T03:37:00Z | 10 | 266 | < 25mph
PG&E | 2018-08-05 | 13:56 | 37.4005 | -119.7532 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | JIM FORGA 209-966-3621 | 101017235 | Unknown | 12000 | Conductor | Overhead | Yes | 43317 | 13:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1821 | 2018 | 8 | 5 | 13 | 56 | 18-0066905 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 7325 | 10.7759 | 254_206 | <25mph | <15mph | HFTD - Distribution | 2018-08-05 13:56:00 | 1561 | 13.3386 | FALSE | <25mph | MCFC1 | 1.01 | 2016-05-13T19:02:00Z | 10 | 2 | < 25mph | TR172 | 6.44 | 2016-05-13T18:45:00Z | 14.99 | 40 | < 25mph | MIAC1 | 1.36 | 2016-05-13T19:59:00Z | 13 | 4 | < 25mph | TR172 | 6.44 | 2016-05-13T19:45:00Z | 20 | 83 | < 25mph
PG&E | 2017-05-25 15:05 | 15:05 | 36.5217 | -121.8473 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Buddy Bloxham 831-236-5659 | 101778611 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42880.6288 | 15:05 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1113 | 2017 | 5 | 25 | 15 | 5 | 17-0050761 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 13965 | 25.8899 | 162_158 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-05-25 15:05:00 | 853 | 26.2648 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E8505 | 7.82 | 2016-04-26T04:26:00Z | 30 | 62 | 25-40mph |  |  |  | 0 | 0 | No data | E8505 | 7.82 | 2016-04-26T04:26:00Z | 30 | 126 | 25-40mph
PG&E | 2017-08-27 | 20:04 | 38.9165 | -121.151 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-477-0641 x7, log 22629 | 100077184 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42974 | 20:04 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1352 | 2017 | 8 | 27 | 20 | 4 | 17-0073228 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 905 | 9.7822 | 193_290 | <25mph | <15mph | HFTD - Distribution | 2017-08-27 20:04:00 | 1090 | 16.757 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LICC1 | 6.69 | 2017-12-09T20:13:00Z | 5.99 | 19 | < 25mph |  |  |  | 0 | 0 | No data | E6168 | 7.43 | 2017-12-09T20:48:00Z | 8.01 | 37 | < 25mph
PG&E | 2019-09-30 | 14:29 | 34.6139 | -120.1799 | Contact with High Voltage, 3rd party | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 183041102 |  | 12000 | Conductor | Overhead | Yes | 43738 | 14:29 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-13 | 2019 | 9 | 30 | 14 | 29 | 19-0105582 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 4080 | 26.8876 | 237_52 | 25-40mph | 15-30mph | HFTD - Distribution | 2019-09-30 14:29:00 | 2072 | 27.9753 | FALSE | 25-40mph | C9206 | 2.6 | 2017-01-04T16:15:00Z | 7 | 5 | < 25mph | AP901 | 4.92 | 2017-01-04T16:00:00Z | 20 | 8 | < 25mph | C9206 | 2.6 | 2017-01-04T16:15:00Z | 7 | 9 | < 25mph | AP901 | 4.92 | 2017-01-04T16:00:00Z | 20 | 16 | < 25mph
PG&E | 2016-09-15 | 15:56 | 37.1102 | -121.9509 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100520198 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42628 | 15:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0982 | 2016 | 9 | 15 | 15 | 56 | 16-0065001 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 28900 | 4.729 | 158_190 | <25mph | <15mph | HFTD - Distribution | 2016-09-15 15:56:00 | 724 | 12.2674 | FALSE | <25mph | AP191 | 0.61 | 2015-06-17T02:13:00Z | 8.01 | 51 | < 25mph | LSGC1 | 6.49 | 2015-06-17T02:32:00Z | 8.99 | 83 | < 25mph | AP191 | 0.61 | 2015-06-17T03:13:00Z | 8.01 | 107 | < 25mph | LSGC1 | 6.49 | 2015-06-17T02:32:00Z | 8.99 | 171 | < 25mph
PG&E | 2018-08-05 | 13:56 | 37.4005 | -119.7532 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | JIM FORGA 209-966-3621 | 101017235 | Unknown | 12000 | Conductor | Overhead | Yes | 43317 | 13:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1821 | 2018 | 8 | 5 | 13 | 56 | 18-0066905 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 7325 | 10.7759 | 254_206 | <25mph | <15mph | HFTD - Distribution | 2018-08-05 13:56:00 | 1561 | 13.3386 | FALSE | <25mph | MIAC1 | 1.36 | 2015-03-17T02:59:00Z | 8.01 | 2 | < 25mph | MIAC1 | 1.36 | 2015-03-17T02:59:00Z | 8.01 | 35 | < 25mph | MIAC1 | 1.36 | 2015-03-17T03:59:00Z | 11.01 | 4 | < 25mph | MIAC1 | 1.36 | 2015-03-17T03:59:00Z | 11.01 | 73 | < 25mph
1. Butte | 2015-09-09 | 14:26 | 38.3297 | -120.7042 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1987 | 2015 | 9 | 9 | 14 | 26 |  | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 1353755 | 12.0917 | 212_257 | <25mph | <15mph | HFTD - Distribution | 2015-09-09 14:26:00 | 332 | 14.8248 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TS389 | 4.75 | 2018-04-20T15:53:00Z | 8.99 | 3 | < 25mph |  |  |  | 0 | 0 | No data | TS389 | 4.75 | 2018-04-20T15:53:00Z | 8.99 | 6 | < 25mph
PG&E | 2018-06-30 | 22:18 | 40.6043 | -122.24 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101469808 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43281 | 22:18 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1716 | 2018 | 6 | 30 | 22 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 10.6263 | 147_383 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 22:18:00 | 1457 | 24.79 | FALSE | <25mph | PG516 | 1.75 | 2019-09-18T22:00:00Z | 17.6 | 6 | < 25mph | RRAC1 | 6.7 | 2019-09-18T22:24:00Z | 20 | 37 | < 25mph | PG516 | 1.75 | 2019-09-18T22:00:00Z | 17.6 | 12 | < 25mph | RRAC1 | 6.7 | 2019-09-18T22:24:00Z | 20 | 74 | < 25mph
PG&E | 2017-05-06 11:23 | 11:18 | 40.7951 | -124.029 | Vegetation | Rural | < 3 Meters | Fire Agency | chief rick harden 7074423352 | 103661154 | Unknown | 12000 | Conductor | Overhead | Yes | 42861.4744 | 11:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1086 | 2017 | 5 | 6 | 11 | 18 | 17-0045785 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 113630 | 26.2788 | 73_395 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-05-06 11:18:00 | 826 | 28.8261 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.4 | 2016-03-06T15:55:00Z | 22.01 | 54 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.4 | 2016-03-06T16:55:00Z | 23 | 96 | < 25mph
PG&E | 2017-07-25 15:52 | 15:51 | 38.3779 | -122.5388 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102031447 | Unknown | 12000 | Conductor | Overhead | Yes | 42941.6609 | 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1290 | 2017 | 7 | 25 | 15 | 51 | 17-0065437 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 18584 | 12.338 | 133_260 | <25mph | <15mph | HFTD - Distribution | 2017-07-25 15:51:00 | 1029 | 16.6773 | FALSE | <25mph | KENWW | 2.06 | 2018-04-06T15:00:00Z | 9.89 | 2 | < 25mph | E1582 | 7.55 | 2018-04-06T14:23:00Z | 18.01 | 9 | < 25mph | KENWW | 2.06 | 2018-04-06T16:00:00Z | 15.3 | 4 | < 25mph | E1582 | 7.55 | 2018-04-06T15:53:00Z | 20 | 18 | < 25mph
PG&E | 2017-10-23 | 21:24 | 37.3713 | -122.348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100270421 | Unknown | 12000 | Conductor | Overhead | Yes | 43031 | 21:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1507 | 2017 | 10 | 23 | 21 | 24 | 17-0089820 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1768 | 13.1103 | 140_205 | <25mph | <15mph | HFTD - Distribution | 2017-10-23 21:24:00 | 1249 | 22.0037 | FALSE | <25mph | E4551 | 1.61 | 2017-04-26T04:12:00Z | 0 | 6 | < 25mph | PUGC1 | 7.55 | 2017-04-26T03:18:00Z | 18.99 | 21 | < 25mph | E4551 | 1.61 | 2017-04-26T05:12:00Z | 0 | 10 | < 25mph | PUGC1 | 7.55 | 2017-04-26T03:18:00Z | 18.99 | 35 | < 25mph
PG&E | 2018-07-14 | 14:44 | 38.9524 | -121.2467 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100035452 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 14:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1748 | 2018 | 7 | 14 | 14 | 44 | 18-0059847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2430 | 9.5304 | 189_291 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 14:44:00 | 1488 | 13.6375 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LICC1 | 5.05 | 2017-03-04T04:13:00Z | 4.99 | 3 | < 25mph |  |  |  | 0 | 0 | No data | LICC1 | 5.05 | 2017-03-04T05:13:00Z | 4.99 | 9 | < 25mph
PG&E | 2015-07-05 21:21 | 2015-07-05 21:21 | 38.6524 | -120.6278 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | one span east of c/o 1055 |  | 21000 | Conductor | Overhead | Yes | 42190.8896 | 2015-07-05 21:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0445 | 2015 | 7 | 5 | 21 | 21 | 15-0045605 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 22374 | 5.6191 | 215_275 | <25mph | <15mph | HFTD - Distribution | 2015-07-05 21:21:00 | 190 | 12.9317 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG105 | 7 | 2019-01-06T03:30:00Z | 21.7 | 15 | < 25mph |  |  |  | 0 | 0 | No data | GZFC1 | 5.69 | 2019-01-06T04:17:00Z | 24 | 30 | < 25mph
PG&E | 2017-08-31 | 11:33 | 37.1379 | -121.9966 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100519201 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 11:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1373 | 2017 | 8 | 31 | 11 | 33 | 17-0074457 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 99153 | 14.3205 | 156_192 | <25mph | <15mph | HFTD - Distribution | 2017-08-31 11:33:00 | 1111 | 14.3569 | FALSE | <25mph | D8979 | 2.5 | 2016-06-18T17:07:00Z | 12.01 | 32 | < 25mph | D8979 | 2.5 | 2016-06-18T17:07:00Z | 12.01 | 118 | < 25mph | D8979 | 2.5 | 2016-06-18T18:23:00Z | 14 | 64 | < 25mph | D8979 | 2.5 | 2016-06-18T18:23:00Z | 14 | 233 | < 25mph
PG&E | 2016-10-14 19:45 | 19:44 | 39.6245 | -121.5382 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100435570 |  | 0 – 750 | Conductor | Overhead | Yes | 42657.8228 | 19:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1036 | 2016 | 10 | 14 | 19 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.5623 | 177_329 | <25mph | <15mph | HFTD - Distribution | 2016-10-14 19:44:00 | 777 | 22.2526 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG295 | 4.06 | 2019-04-18T06:50:00Z | 7.25 | 13 | < 25mph |  |  |  | 0 | 0 | No data | PG295 | 4.06 | 2019-04-18T07:00:00Z | 7.45 | 26 | < 25mph
PG&E | 2018-08-13 | 15:33 | 38.708 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101377799 | Unknown | 21000 | Conductor | Overhead | Yes | 43325 | 15:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1840 | 2018 | 8 | 13 | 15 | 33 | 18-0069470 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1004 | 11.7134 | 201_278 | <25mph | <15mph | HFTD - Distribution | 2018-08-13 15:33:00 | 1579 | 13.7748 | FALSE | <25mph | D7401 | 3.18 | 2015-03-18T19:22:00Z | 8.01 | 33 | < 25mph | D4314 | 7.77 | 2015-03-18T19:18:00Z | 10.98 | 64 | < 25mph | D7401 | 3.18 | 2015-03-18T19:52:00Z | 10 | 65 | < 25mph | D4314 | 7.77 | 2015-03-18T20:13:00Z | 10.98 | 126 | < 25mph
PG&E | 2016-07-03 15:00 | 2016-07-03 15:00 | 38.0348 | -120.3809 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101050507 |  | 17000 | Conductor | Overhead | Yes | 42554.625 | 2016-07-03 15:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0837 | 2016 | 7 | 3 | 15 | 0 | 16-0047689 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38812 | 10.6263 | 226_241 | <25mph | <15mph | HFTD - Distribution | 2016-07-03 15:00:00 | 580 | 12.5395 | FALSE | <25mph | F0305 | 3.78 | 2017-07-10T02:10:00Z | 0 | 11 | < 25mph | MOUC1 | 7.53 | 2017-07-10T02:02:00Z | 14 | 12 | < 25mph | F0305 | 3.78 | 2017-07-10T03:10:00Z | 0 | 20 | < 25mph | MOUC1 | 7.53 | 2017-07-10T02:02:00Z | 14 | 22 | < 25mph
PG&E | 2019-09-10 | 7:13 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 82841102 |  | 12000 | Conductor | Overhead | Yes | 43718 | 7:13 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-369 | 2019 | 9 | 10 | 7 | 13 | 19-0097264 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 23500 | 14.6244 | 147_193 | <25mph | <15mph | HFTD - Distribution | 2019-09-10 07:13:00 | 2029 | 17.7422 | FALSE | <25mph | BNDC1 | 2.84 | 2015-01-25T02:50:00Z | 18.99 | 1 | < 25mph | BNDC1 | 2.84 | 2015-01-25T02:50:00Z | 18.99 | 27 | < 25mph | BNDC1 | 2.84 | 2015-01-25T02:50:00Z | 18.99 | 2 | < 25mph | BNDC1 | 2.84 | 2015-01-25T02:50:00Z | 18.99 | 54 | < 25mph
PG&E | 2017-07-24 14:02 | 14:01 | 37.2635 | -122.3364 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike klink 650-879-0121 | 100322130 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42940.5845 | 14:01 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1286 | 2017 | 7 | 24 | 14 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 18.4533 | 141_199 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 14:01:00 | 1025 | 18.6394 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 5.31 | 2016-02-06T19:07:00Z | 14 | 1 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 5.31 | 2016-02-06T19:07:00Z | 14 | 2 | < 25mph
PG&E | 2018-09-29 | 16:16 | 41.0219 | -123.655 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Hoopa Fire Dept | 100962165 | Unknown | 12000 | Conductor | Overhead | Yes | 43372 | 16:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1923 | 2018 | 9 | 29 | 16 | 16 | 18-0084877 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 16028 | 7.8421 | 89_407 | <25mph | <15mph | HFTD - Distribution | 2018-09-29 16:16:00 | 1662 | 11.5265 | FALSE | <25mph | HOAC1 | 1.98 | 2016-02-22T15:40:00Z | 7 | 1 | < 25mph | BHTC1 | 7.5 | 2016-02-22T15:46:00Z | 7 | 3 | < 25mph | HOAC1 | 1.98 | 2016-02-22T16:40:00Z | 7 | 2 | < 25mph | BHTC1 | 7.5 | 2016-02-22T15:46:00Z | 7 | 7 | < 25mph
PG&E | 2019-07-30 | 15:15 | 39.1207 | -121.072 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 152691104 |  | 12000 | Conductor | Overhead | Yes | 43676 | 15:15 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-386 | 2019 | 7 | 30 | 15 | 15 | 19-0082713 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 31302 | 12.2921 | 196_301 | <25mph | <15mph | HFTD - Distribution | 2019-07-30 15:15:00 | 1942 | 13.0851 | FALSE | <25mph | E1789 | 3.69 | 2017-05-27T19:24:00Z | 8.99 | 20 | < 25mph | C5488 | 4.01 | 2017-05-27T20:14:00Z | 11.01 | 48 | < 25mph | E1789 | 3.69 | 2017-05-27T20:54:00Z | 11.01 | 39 | < 25mph | C5488 | 4.01 | 2017-05-27T21:13:00Z | 14.99 | 92 | < 25mph
PG&E | 2017-09-20 | 2:06 | 37.2597 | -122.3222 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100322388 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42998 | 2:06 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1424 | 2017 | 9 | 20 | 2 | 6 | 17-0080179 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 36593 | 8.989 | 141_198 | <25mph | <15mph | HFTD - Distribution | 2017-09-20 02:06:00 | 1162 | 20.1127 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.84 | 2015-06-28T09:07:00Z | 3 | 1 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.84 | 2015-06-28T10:07:00Z | 3 | 2 | < 25mph
PG&E | 2016-07-28 14:24 | 2016-07-28 14:24 | 37.8232 | -120.1356 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101037045 |  | 17000 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Guy/Span Wire | N.A. | N.A. | Unknown |  | no-match | 0888 | 2016 | 7 | 28 | 14 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Guy/Span Wire | N.A. | 10.9021 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 14:24:00 | 631 | 11.4062 | FALSE | <25mph | SEWC1 | 2.46 | 2019-01-02T13:16:00Z | 11.01 | 18 | < 25mph | SEWC1 | 2.46 | 2019-01-02T13:16:00Z | 11.01 | 30 | < 25mph | SEWC1 | 2.46 | 2019-01-02T13:16:00Z | 11.01 | 35 | < 25mph | SEWC1 | 2.46 | 2019-01-02T13:16:00Z | 11.01 | 59 | < 25mph
PG&E | 2019-08-12 | 17:42 | 38.6618 | -120.7451 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 101415488, 101404439 |  | 12000 | Pole | Overhead | Yes | 43689 | 17:42 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (slight defect) | 2019-241 | 2019 | 8 | 12 | 17 | 42 | 19-0087080 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 54604 | 8.3029 | 210_275 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 17:42:00 | 1968 | 11.2889 | FALSE | <25mph | E4543 | 3.82 | 2016-10-12T14:35:00Z | 0 | 7 | < 25mph | AV185 | 4.45 | 2016-10-12T14:20:00Z | 1.01 | 45 | < 25mph | C5121 | 3.8 | 2016-10-12T15:15:00Z | 3 | 12 | < 25mph | C5121 | 3.8 | 2016-10-12T15:15:00Z | 3 | 88 | < 25mph
PG&E | 2016-08-15 | 2016-08-15 15:43 | 37.8784 | -120.4488 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101020079 |  | 17000 | Conductor | Overhead | Yes | 42597 | 2016-08-15 15:43 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0928 | 2016 | 8 | 15 | 15 | 43 | 16-0057465 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 122905 | 10.0906 | 223_232 | <25mph | <15mph | HFTD - Distribution | 2016-08-15 15:43:00 | 671 | 12.9875 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.26 | 2018-09-20T18:03:00Z | 12.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.26 | 2018-09-20T19:03:00Z | 13 | 2 | < 25mph
PG&E | 2019-07-21 | 10:14 | 38.9716 | -120.9991 |  | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire | Placer Hill FD | 152241102 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43667 | 10:14 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-127 | 2019 | 7 | 21 | 10 | 14 | 19-0079578 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 32850 | 6.8026 | 199_293 | <25mph | <15mph | HFTD - Distribution | 2019-07-21 10:14:00 | 1916 | 10.8012 | FALSE | <25mph | C0713 | 3.87 | 2016-06-15T14:34:00Z | 11.01 | 17 | < 25mph | KAUN | 4.82 | 2016-06-15T14:35:00Z | 16.11 | 34 | < 25mph | C0713 | 3.87 | 2016-06-15T15:39:00Z | 13 | 32 | < 25mph | KAUN | 4.82 | 2016-06-15T15:35:00Z | 18.41 | 66 | < 25mph
PG&E | 2015-05-09 13:10 | 2015-05-09 13:10 | 39.2343 | -121.2468 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100000103 | None | 21000 | Conductor | Overhead | Yes | 42133.5486 | 2015-05-09 13:10 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0311 | 2015 | 5 | 9 | 13 | 10 | 15-0033085 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 382926 | 12.172 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 13:10:00 | 57 | 17.071 | FALSE | <25mph | E2572 | 3.27 | 2016-01-02T10:28:00Z | 1.01 | 12 | < 25mph | E2572 | 3.27 | 2016-01-02T10:28:00Z | 1.01 | 18 | < 25mph | E2572 | 3.27 | 2016-01-02T11:18:00Z | 1.01 | 23 | < 25mph | E2572 | 3.27 | 2016-01-02T11:18:00Z | 1.01 | 35 | < 25mph
PG&E | 2015-05-21 09:23 | 2015-05-21 09:23 | 38.5996 | -122.9935 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 4 SPANS LOAD SIDE 2993 |  | 12000 | Conductor | Overhead | Yes | 42145.391 | 2015-05-21 09:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0324 | 2015 | 5 | 21 | 9 | 23 | 15-0035686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2850 | 1.6525 | 114_273 | <25mph | <15mph | HFTD - Distribution | 2015-05-21 09:23:00 | 70 | 15.124 | FALSE | <25mph | PG549 | 0.94 | 2019-10-07T17:30:00Z | 4.54 | 6 | < 25mph | DRYWW | 5.5 | 2019-10-07T16:45:00Z | 5.7 | 53 | < 25mph | PG549 | 0.94 | 2019-10-07T17:50:00Z | 5.41 | 12 | < 25mph | DRYWW | 5.5 | 2019-10-07T16:45:00Z | 5.7 | 105 | < 25mph
PG&E | 2018-09-11 | 5:23 | 37.376 | -119.6304 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | TROY CHEEK 209-966-3621 | 101023184 | Unknown | 12000 | Conductor | Overhead | Yes | 43354 | 5:23 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1891 | 2018 | 9 | 11 | 5 | 23 | 18-0078387 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 288 | 4.3046 | 260_205 | <25mph | <15mph | HFTD - Distribution | 2018-09-11 05:23:00 | 1630 | 11.3584 | FALSE | <25mph | BSNC1 | 0.17 | 2015-12-26T14:48:00Z | 8.01 | 28 | < 25mph | MIAC1 | 6.99 | 2015-12-26T14:59:00Z | 12.01 | 63 | < 25mph | BSNC1 | 0.17 | 2015-12-26T15:48:00Z | 8.01 | 57 | < 25mph | MIAC1 | 6.99 | 2015-12-26T14:59:00Z | 12.01 | 126 | < 25mph
PG&E | 2017-07-24 21:45 | 21:45 | 35.6024 | -120.9211 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101860186 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.9063 | 21:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1289 | 2017 | 7 | 24 | 21 | 45 | 17-0065191 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 21231 | 19.4445 | 203_107 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 21:45:00 | 1028 | 30.0108 | FALSE | 25-40mph | TABC1 | 3.74 | 2016-10-27T01:07:00Z | 4.99 | 1 | < 25mph | TABC1 | 3.74 | 2016-10-27T01:07:00Z | 4.99 | 1 | < 25mph | TABC1 | 3.74 | 2016-10-27T01:07:00Z | 4.99 | 2 | < 25mph | TABC1 | 3.74 | 2016-10-27T01:07:00Z | 4.99 | 2 | < 25mph
PG&E | 2016-06-19 | 2016-06-19 17:19 | 38.4508 | -122.3546 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire--napa fire | 102256859 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 17:19 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0808 | 2016 | 6 | 19 | 17 | 19 | 16-0044337 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 672 | 13.296 | 141_264 | <25mph | <15mph | HFTD - Distribution | 2016-06-19 17:19:00 | 552 | 13.7776 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.13 | 2015-10-09T00:29:00Z | 11.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.13 | 2015-10-09T01:29:00Z | 13 | 2 | < 25mph
PG&E | 2018-10-15 | 3:23 | 38.2897 | -120.5803 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103378003 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43388 | 3:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1941 | 2018 | 10 | 15 | 3 | 23 | 18-0090342 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1464 | 26.0611 | 218_255 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-15 03:23:00 | 1680 | 26.2858 | FALSE | 25-40mph | AT317 | 3.74 | 2015-02-16T18:57:00Z | 4 | 6 | < 25mph | MTZC1 | 7.96 | 2015-02-16T18:56:00Z | 7 | 12 | < 25mph | AT317 | 3.74 | 2015-02-16T19:57:00Z | 4.99 | 12 | < 25mph | ESPC1 | 4.93 | 2015-02-16T19:13:00Z | 8.01 | 24 | < 25mph
PG&E | 2018-11-16 | 17:02 | 38.7574 | -120.9012 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101409894 | AT&T | 21000 | Conductor | Overhead | Yes | 43420 | 17:02 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1976 | 2018 | 11 | 16 | 17 | 2 | 18-0100490 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 119860 | 5.5125 | 204_281 | <25mph | <15mph | HFTD - Distribution | 2018-11-16 17:02:00 | 1716 | 12.5682 | FALSE | <25mph | PG106 | 3.02 | 2019-07-04T23:30:00Z | 12.93 | 18 | < 25mph | PG359 | 7.49 | 2019-07-04T23:10:00Z | 16.44 | 126 | < 25mph | PG106 | 3.02 | 2019-07-05T00:00:00Z | 15.12 | 36 | < 25mph | PG359 | 7.49 | 2019-07-04T23:10:00Z | 16.44 | 251 | < 25mph
PG&E | 2015-03-07 13:35 | 2015-03-07 13:35 | 38.7091 | -122.6484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 14417 western mine rd, Middletown |  | 12000 | Conductor | Overhead | Yes | 42070.566 | 2015-03-07 13:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0272 | 2015 | 3 | 7 | 13 | 35 | 15-0018003 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2263 | 3.8777 | 128_279 | <25mph | <15mph | HFTD - Distribution | 2015-03-07 13:35:00 | 18 | 14.4715 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2050 | 7.98 | 2015-04-01T06:18:00Z | 7 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E2050 | 7.98 | 2015-04-01T07:33:00Z | 8.99 | 8 | < 25mph
PG&E | 2017-09-08 | 21:14 | 37.9604 | -120.3764 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | John Lite 209-984-5623 | 101042521 | Unknown | 17000 | Conductor | Overhead | Yes | 42986 | 21:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1403 | 2017 | 9 | 8 | 21 | 14 | 17-0077137 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49858 | 11.2644 | 227_237 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 21:14:00 | 1141 | 11.9927 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C3161 | 5.93 | 2016-12-29T19:25:00Z | 4.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | C3161 | 5.93 | 2016-12-29T20:25:00Z | 8.01 | 7 | < 25mph
PG&E | 2018-07-27 | 23:12 | 37.18 | -122.029 | Vegetation | Rural | < 3 meters | Fire Agency | Jeremy Wise 408-378-4010 Incident # C182080066 | 100518365 | Unknown | 12000 | Conductor | Overhead | Yes | 43308 | 23:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1793 | 2018 | 7 | 27 | 23 | 12 | 18-0064525 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 30475 | 3.2895 | 154_194 | <25mph | <15mph | HFTD - Distribution | 2018-07-27 23:12:00 | 1533 | 9.1823 | FALSE | <25mph | AV005 | 3.55 | 2016-09-17T07:04:00Z | 4 | 10 | < 25mph | D8979 | 5.55 | 2016-09-17T07:03:00Z | 8.01 | 139 | < 25mph | AV005 | 3.55 | 2016-09-17T07:04:00Z | 4 | 20 | < 25mph | D8979 | 5.55 | 2016-09-17T07:03:00Z | 8.01 | 273 | < 25mph
PG&E | 2018-10-07 | 1:44 | 37.178 | -122.0267 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Mike Mathiesen 408-472-1613 Incident # SCU7096 | 100518363 | Unknown | 12000 | Conductor | Overhead | Yes | 43380 | 1:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1929 | 2018 | 10 | 7 | 1 | 44 | 18-0087807 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 224444 | 25.0906 | 154_194 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-07 01:44:00 | 1668 | 25.864 | FALSE | 25-40mph | D9791 | 2.63 | 2018-01-25T03:31:00Z | 4.99 | 6 | < 25mph | D3546 | 4.3 | 2018-01-25T03:10:00Z | 28.99 | 108 | 25-40mph | D9791 | 2.63 | 2018-01-25T04:01:00Z | 10 | 12 | < 25mph | LSGC1 | 4.55 | 2018-01-25T04:32:00Z | 34 | 215 | 25-40mph
PG&E | 2016-07-25 15:32 | 2016-07-25 15:32 | 38.3522 | -120.7107 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42576.6472 | 2016-07-25 15:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0878 | 2016 | 7 | 25 | 15 | 32 | 16-0052398 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 19951 | 10.4912 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-25 15:32:00 | 621 | 14.4675 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ANUC1 | 4.12 | 2016-01-18T08:53:00Z | 13 | 2 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2016-01-18T09:56:00Z | 15.99 | 4 | < 25mph
PG&E | 2016-10-09 18:52 | 18:52 | 38.656 | -120.9725 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101376768 |  | 12000 | Conductor | Overhead | Yes | 42652.7862 | 18:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1024 | 2016 | 10 | 9 | 18 | 52 | 16-0070676 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 98361 | 11.3582 | 201_275 | <25mph | <15mph | HFTD - Distribution | 2016-10-09 18:52:00 | 765 | 14.948 | FALSE | <25mph | PG181 | 2.8 | 2019-02-06T04:40:00Z | 5.03 | 26 | < 25mph | PG073 | 5.23 | 2019-02-06T04:30:00Z | 8.55 | 129 | < 25mph | PG181 | 2.8 | 2019-02-06T04:40:00Z | 5.03 | 52 | < 25mph | PG073 | 5.23 | 2019-02-06T04:30:00Z | 8.55 | 258 | < 25mph
PG&E | 2016-10-13 23:23 | 23:14 | 40.4901 | -122.3729 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | SHASTA COUNTY FIRE | 101502366 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42656.9745 | 23:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1029 | 2016 | 10 | 13 | 23 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 30.3025 | 142_377 | 25-40mph | 30-45mph | HFTD - Distribution | 2016-10-13 23:14:00 | 770 | 30.3025 | FALSE | 25-40mph | E6886 | 3.41 | 2017-06-08T22:56:00Z | 7 | 3 | < 25mph | RRAC1 | 4.59 | 2017-06-08T22:24:00Z | 10 | 9 | < 25mph | E6886 | 3.41 | 2017-06-08T22:56:00Z | 7 | 6 | < 25mph | RRAC1 | 4.59 | 2017-06-08T23:24:00Z | 11.01 | 19 | < 25mph
PG&E | 2018-07-25 | 0:42 | 39.7791 | -121.6173 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100327443 | Unknown | 12000 | Conductor | Overhead | Yes | 43306 | 0:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1788 | 2018 | 7 | 25 | 0 | 42 | 18-0063320 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6742 | 1.3279 | 173_337 | <25mph | <15mph | HFTD - Distribution | 2018-07-25 00:42:00 | 1528 | 11.7229 | FALSE | <25mph | PG487 | 0.59 | 2019-10-14T21:40:00Z | 11.34 | 43 | < 25mph | PG487 | 0.59 | 2019-10-14T21:40:00Z | 11.34 | 140 | < 25mph | PG347 | 3.03 | 2019-10-14T22:00:00Z | 12.64 | 80 | < 25mph | PG347 | 3.03 | 2019-10-14T22:00:00Z | 12.64 | 262 | < 25mph
PG&E | 2015-10-16 09:43 | 2015-10-16 09:43 | 39.187 | -123.2015 | Vegetation | Rural | < 3 meters | Unknown |  | 102196855 |  | 12000 | Conductor | Overhead | Yes | 42293.4049 | 2015-10-16 09:43 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0653 | 2015 | 10 | 16 | 9 | 43 | 15-0070948 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 65228 | 2.2696 | 105_305 | <25mph | <15mph | HFTD - Distribution | 2015-10-16 09:43:00 | 397 | 16.8813 | FALSE | <25mph | E7513 | 1.34 | 2016-04-06T03:23:00Z | 1.01 | 12 | < 25mph | E7513 | 1.34 | 2016-04-06T03:23:00Z | 1.01 | 24 | < 25mph | E7513 | 1.34 | 2016-04-06T04:08:00Z | 3 | 24 | < 25mph | E7513 | 1.34 | 2016-04-06T04:08:00Z | 3 | 48 | < 25mph
PG&E | 2015-12-01 12:03 | 2015-12-01 12:03 | 35.6744 | -120.9932 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal FIRE | 101860660 |  | 21000 | Conductor | Overhead | Yes | 42339.5021 | 2015-12-01 12:03 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0680 | 2015 | 12 | 1 | 12 | 3 | 15-0081983 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 42427 | 6.9865 | 200_111 | <25mph | <15mph | HFTD - Distribution | 2015-12-01 12:03:00 | 424 | 12.3916 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E9175 | 5.21 | 2019-02-19T20:20:00Z | 10 | 14 | < 25mph |  |  |  | 0 | 0 | No data | TABC1 | 4.07 | 2019-02-19T21:07:00Z | 11.01 | 27 | < 25mph
PG&E | 2015-03-07 13:35 | 2015-03-07 13:35 | 38.7091 | -122.6484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 14417 western mine rd, Middletown |  | 12000 | Conductor | Overhead | Yes | 42070.566 | 2015-03-07 13:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0272 | 2015 | 3 | 7 | 13 | 35 | 15-0018003 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2263 | 3.8777 | 128_279 | <25mph | <15mph | HFTD - Distribution | 2015-03-07 13:35:00 | 18 | 14.4715 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2050 | 7.98 | 2015-11-16T20:00:00Z | 8.01 | 3 | < 25mph |  |  |  | 0 | 0 | No data | E2050 | 7.98 | 2015-11-16T21:45:00Z | 8.99 | 7 | < 25mph
PG&E | 2017-12-14 | 17:16 | 34.5878 | -120.3566 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101911004 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 43083 | 17:16 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1538 | 2017 | 12 | 14 | 17 | 16 | 17-0101672 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2896 | 2.7073 | 229_51 | <25mph | <15mph | HFTD - Distribution | 2017-12-14 17:16:00 | 1280 | 11.3138 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2332 | 7.61 | 2016-10-23T17:10:00Z | 24 | 18 | < 25mph |  |  |  | 0 | 0 | No data | E2332 | 7.61 | 2016-10-23T18:17:00Z | 28.99 | 36 | 25-40mph
3. Redwood Valley (Mendocino Lake Complex) | 2017-10-08 | 23:36 | 39.2487 | -123.1663 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1989 | 2017 | 10 | 8 | 23 | 36 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 24.7673 | 107_309 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 23:36:00 | 1212 | 30.3049 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PG089 | 4.94 | 2018-09-04T14:20:00Z | 3.06 | 24 | < 25mph |  |  |  | 0 | 0 | No data | PG089 | 4.94 | 2018-09-04T16:10:00Z | 5.26 | 48 | < 25mph
PG&E | 2017-08-14 | 6:14 | 40.1164 | -123.8064 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100986364 | Unknown | 12000 | Conductor | Overhead | Yes | 42961 | 6:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1332 | 2017 | 8 | 14 | 6 | 14 | 17-0070003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 959989 | 9.3352 | 81_357 | <25mph | <15mph | HFTD - Distribution | 2017-08-14 06:14:00 | 1070 | 20.8696 | FALSE | <25mph | ERCC1 | 1.77 | 2018-06-13T15:28:00Z | 13 | 4 | < 25mph | ERCC1 | 1.77 | 2018-06-13T15:28:00Z | 13 | 4 | < 25mph | ERCC1 | 1.77 | 2018-06-13T16:28:00Z | 14 | 9 | < 25mph | ERCC1 | 1.77 | 2018-06-13T16:28:00Z | 14 | 9 | < 25mph
PG&E | 2017-07-16 12:10 | 12:10 | 35.6613 | -120.922 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101942626 | Unknown | 21000 | Conductor | Overhead | Yes | 42932.5072 | 12:10 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1260 | 2017 | 7 | 16 | 12 | 10 | 17-0063242 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 1304 | 7.6377 | 203_110 | <25mph | <15mph | HFTD - Distribution | 2017-07-16 12:10:00 | 999 | 17.3186 | FALSE | <25mph | TABC1 | 0.35 | 2019-01-03T22:07:00Z | 5.99 | 1 | < 25mph | D4060 | 6.39 | 2019-01-03T22:31:00Z | 7 | 18 | < 25mph | TABC1 | 0.35 | 2019-01-03T22:07:00Z | 5.99 | 2 | < 25mph | D4060 | 6.39 | 2019-01-03T22:31:00Z | 7 | 35 | < 25mph
PG&E | 2017-08-30 | 22:37 | 38.9993 | -120.9887 | Vegetation | Rural | < 3 Meters | Fire Agency | Andy 530-889-0111 | 100026238 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42977 | 22:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1370 | 2017 | 8 | 30 | 22 | 37 | 17-0074333 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 3750 | 7.3126 | 200_294 | <25mph | <15mph | HFTD - Distribution | 2017-08-30 22:37:00 | 1108 | 12.9461 | FALSE | <25mph | D9434 | 3.56 | 2019-02-19T07:15:00Z | 2.01 | 18 | < 25mph | C5488 | 5.56 | 2019-02-19T07:17:00Z | 11.01 | 31 | < 25mph | D9434 | 3.56 | 2019-02-19T08:01:00Z | 4 | 38 | < 25mph | C5488 | 5.56 | 2019-02-19T07:47:00Z | 12.01 | 64 | < 25mph
PG&E | 2018-09-01 | 14:25 | 36.8088 | -121.5916 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Twr 35/222 | None | 115000 | Conductor | Overhead | Yes | 43344 | 14:25 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1875 | 2018 | 9 | 1 | 14 | 25 | INT-11331 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 702145 | 13.8683 | 173_173 | <25mph | <15mph | HFTD - Transmission | 2018-09-01 14:25:00 | 1614 | 16.3299 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG402 | 7.86 | 2019-07-10T13:30:00Z | 6.35 | 12 | < 25mph |  |  |  | 0 | 0 | No data | PG402 | 7.86 | 2019-07-10T13:30:00Z | 6.35 | 23 | < 25mph
PG&E | 2017-10-10 | 13:36 | 38.931 | -123.3023 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 102214553 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43018 | 13:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1481 | 2017 | 10 | 10 | 13 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.7263 | 101_291 | <25mph | <15mph | HFTD - Distribution | 2017-10-10 13:36:00 | 1224 | 17.0479 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E4371 | 5.14 | 2016-05-05T06:13:00Z | 4.99 | 6 | < 25mph |  |  |  | 0 | 0 | No data | BNVC1 | 4.62 | 2016-05-05T06:50:00Z | 8.01 | 13 | < 25mph
PG&E | 2017-08-26 | 20:53 | 38.7066 | -121.0193 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101382231 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42973 | 20:53 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1350 | 2017 | 8 | 26 | 20 | 53 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.4442 | 199_278 | <25mph | <15mph | HFTD - Distribution | 2017-08-26 20:53:00 | 1088 | 14.1326 | FALSE | <25mph | D7413 | 2.42 | 2015-06-08T20:51:00Z | 10.98 | 33 | < 25mph | D7413 | 2.42 | 2015-06-08T20:51:00Z | 10.98 | 45 | < 25mph | D7413 | 2.42 | 2015-06-08T20:51:00Z | 10.98 | 65 | < 25mph | D7413 | 2.42 | 2015-06-08T20:51:00Z | 10.98 | 89 | < 25mph
PG&E | 2016-11-09 | 9:06 | 37.4532 | -119.6413 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | US FOREST SERVICE | 101017062 |  | 12000 | Conductor | Overhead | Yes | 42683 | 9:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1046 | 2016 | 11 | 9 | 9 | 6 | 16-0078863 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1586 | 6.3162 | 259_209 | <25mph | <15mph | HFTD - Distribution | 2016-11-09 09:06:00 | 787 | 14.6769 | FALSE | <25mph | E7845 | 1.7 | 2017-11-23T15:00:00Z | 0 | 3 | < 25mph | BSNC1 | 5.2 | 2017-11-23T14:48:00Z | 10 | 28 | < 25mph | E7845 | 1.7 | 2017-11-23T16:00:00Z | 0 | 5 | < 25mph | BSNC1 | 5.2 | 2017-11-23T15:48:00Z | 10 | 55 | < 25mph
PG&E | 2017-08-31 | 11:33 | 37.1379 | -121.9966 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100519201 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 11:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1373 | 2017 | 8 | 31 | 11 | 33 | 17-0074457 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 99153 | 14.3205 | 156_192 | <25mph | <15mph | HFTD - Distribution | 2017-08-31 11:33:00 | 1111 | 14.3569 | FALSE | <25mph | D8979 | 2.5 | 2017-09-01T06:59:00Z | 8.99 | 20 | < 25mph | E9039 | 6.76 | 2017-09-01T06:59:00Z | 8.99 | 88 | < 25mph | D8979 | 2.5 | 2017-09-01T07:59:00Z | 10 | 42 | < 25mph | D8979 | 2.5 | 2017-09-01T07:59:00Z | 10 | 189 | < 25mph
PG&E | 2016-05-18 | 18:24 | 39.7381 | -123.1587 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42508 | 18:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0735 | 2016 | 5 | 18 | 18 | 24 | 16-0036911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1482 | 13.4862 | 108_336 | <25mph | <15mph | HFTD - Distribution | 2016-05-18 18:24:00 | 480 | 21.4181 | FALSE | <25mph | C3111 | 2.79 | 2015-05-08T09:29:00Z | 2.01 | 4 | < 25mph | EELC1 | 7.26 | 2015-05-08T09:45:00Z | 4 | 5 | < 25mph | C3111 | 2.79 | 2015-05-08T09:29:00Z | 2.01 | 8 | < 25mph | EELC1 | 7.26 | 2015-05-08T09:45:00Z | 4 | 10 | < 25mph
PG&E | 2019-03-19 | 12:52 | 37.9956 | -120.3244 | Tree - cutting, 3rd party | Hardwood Forest | 1 meter - < 3 meters | Self Extinguished |  | 101045032 |  | 17000 | Conductor | Overhead | Yes | 43543 | 12:52 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-187 | 2019 | 3 | 19 | 12 | 52 | 19-0035101 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 70602 | 12.9023 | 229_239 | <25mph | <15mph | HFTD - Distribution | 2019-03-19 12:52:00 | 1736 | 14.3226 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.27 | 2015-04-11T13:02:00Z | 7 | 5 | < 25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.27 | 2015-04-11T14:02:00Z | 8.99 | 10 | < 25mph
PG&E | 2017-09-03 | 17:52 | 37.4956 | -119.8367 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101086621 | Unknown | 21000 | Transformer | Overhead | Yes | 42981 | 17:52 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 1389 | 2017 | 9 | 3 | 17 | 52 | 17-0075617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 4512 | 13.9592 | 250_212 | <25mph | <15mph | HFTD - Distribution | 2017-09-03 17:52:00 | 1127 | 22.0754 | FALSE | <25mph | JSDC1 | 3.33 | 2017-10-06T21:47:00Z | 7 | 1 | < 25mph | MIAC1 | 7.27 | 2017-10-06T21:59:00Z | 11.01 | 10 | < 25mph | JSDC1 | 3.33 | 2017-10-06T22:47:00Z | 8.99 | 2 | < 25mph | MIAC1 | 7.27 | 2017-10-06T21:59:00Z | 11.01 | 20 | < 25mph
PG&E | 2018-06-15 | 2:56 | 37.4869 | -122.4223 | Vegetation | Rural | < 0.25 Acres | Utility: PG&E | N.A. | Pole 10/5 | None | 60000 | Conductor | Overhead | Yes | 43266 | 2:56 | Contamination | N.A. | N.A. | N.A. | Unknown |  | no-match | 1659 | 2018 | 6 | 15 | 2 | 56 | INT-11115 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 0 | 6.5721 | 137_211 | <25mph | <15mph | HFTD - Transmission | 2018-06-15 02:56:00 | 1401 | 18.0175 | FALSE | <25mph | PG515 | 3.08 | 2019-09-02T07:30:00Z | 15.48 | 20 | < 25mph | E4863 | 6.2 | 2019-09-02T07:28:00Z | 118 | 103 | 55mph+ | PG515 | 3.08 | 2019-09-02T07:30:00Z | 15.48 | 43 | < 25mph | E4863 | 6.2 | 2019-09-02T08:58:00Z | 118 | 204 | 55mph+
PG&E | 2019-07-22 | 8:11 | 38.7687 | -120.9633 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | El Dorado County FD | 6Ht0722190809 |  | 21000 | Other | Overhead | Yes | 43668 | 8:11 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-49 | 2019 | 7 | 22 | 8 | 11 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.6529 | 201_281 | <25mph | <15mph | HFTD - Distribution | 2019-07-22 08:11:00 | 1920 | 11.9774 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D7413 | 7.66 | 2015-12-04T14:30:00Z | 3 | 54 | < 25mph |  |  |  | 0 | 0 | No data | D7413 | 7.66 | 2015-12-04T15:30:00Z | 3 | 105 | < 25mph
PG&E | 2015-09-10 18:39 | 2015-09-10 18:39 | 40.7569 | -123.7958 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 096/004 |  | 115000 | Conductor | Overhead | Yes | 42257.7771 | 2015-09-10 18:39 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0590 | 2015 | 9 | 10 | 18 | 39 | RM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 2.2423 | 82_393 | <25mph | <15mph | HFTD - Transmission | 2015-09-10 18:39:00 | 335 | 12.4043 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.39 | 2016-02-24T11:55:00Z | 5.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.39 | 2016-02-24T12:55:00Z | 10 | 2 | < 25mph
PG&E | 2019-07-21 | 10:14 | 38.9716 | -120.9991 |  | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire | Placer Hill FD | 152241102 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43667 | 10:14 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-127 | 2019 | 7 | 21 | 10 | 14 | 19-0079578 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 32850 | 6.8026 | 199_293 | <25mph | <15mph | HFTD - Distribution | 2019-07-21 10:14:00 | 1916 | 10.8012 | FALSE | <25mph | C0713 | 3.87 | 2016-05-25T19:04:00Z | 11.01 | 16 | < 25mph | C5488 | 7.22 | 2016-05-25T18:48:00Z | 11.01 | 30 | < 25mph | C0713 | 3.87 | 2016-05-25T19:21:00Z | 12.01 | 32 | < 25mph | C0713 | 3.87 | 2016-05-25T19:21:00Z | 12.01 | 60 | < 25mph
PG&E | 2019-07-17 | 7:49 | 34.5066 | -120.2247 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Santa Barbara County FD | 4Bx0717190747 |  | 12000 | Other | Overhead | Yes | 43663 | 7:49 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-425 | 2019 | 7 | 17 | 7 | 49 | 19-0078239 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 19608 | 17.3045 | 235_46 | <25mph | <15mph | HFTD - Distribution | 2019-07-17 07:49:00 | 1908 | 28.4942 | FALSE | 25-40mph | GVTC1 | 1.4 | 2018-03-09T00:09:00Z | 34.99 | 17 | 25-40mph | GVTC1 | 1.4 | 2018-03-09T00:09:00Z | 34.99 | 17 | 25-40mph | GVTC1 | 1.4 | 2018-03-09T00:09:00Z | 34.99 | 34 | 25-40mph | GVTC1 | 1.4 | 2018-03-09T00:09:00Z | 34.99 | 34 | 25-40mph
PG&E | 2016-10-19 10:42 | 10:42 | 38.5098 | -122.45 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | st helena | 102242552 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42662.4459 | 10:42 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1040 | 2016 | 10 | 19 | 10 | 42 | 16-0073955 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 693 | 4.5329 | 137_268 | <25mph | <15mph | HFTD - Distribution | 2016-10-19 10:42:00 | 781 | 13.4953 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AT925 | 4.5 | 2016-12-16T12:25:00Z | 8.99 | 12 | < 25mph |  |  |  | 0 | 0 | No data | AT925 | 4.5 | 2016-12-16T12:25:00Z | 8.99 | 24 | < 25mph
PG&E | 2017-09-06 | 20:08 | 37.2925 | -122.294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100256917 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1400 | 2017 | 9 | 6 | 20 | 8 | 17-0076502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4914 | 6.7999 | 143_200 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 20:08:00 | 1138 | 13.6021 | FALSE | <25mph | LAHC1 | 2.3 | 2015-03-17T18:07:00Z | 11.01 | 7 | < 25mph | LAHC1 | 2.3 | 2015-03-17T18:07:00Z | 11.01 | 24 | < 25mph | LAHC1 | 2.3 | 2015-03-17T19:07:00Z | 11.01 | 13 | < 25mph | E4825 | 7.69 | 2015-03-17T19:00:00Z | 11.99 | 47 | < 25mph
PG&E | 2019-06-26 | 13:14 | 40.0185 | -122.4107 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | Circuit Id 103331101 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43642 | 13:14 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-331 | 2019 | 6 | 26 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2684 | 140_351 | <25mph | <15mph | HFTD - Distribution | 2019-06-26 13:14:00 | 1870 | 19.4401 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2015-08-19 06:20 | 2015-08-19 06:20 | 39.2831 | -123.2931 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | MTR#50001225 | None | 12000 | Conductor | Overhead | Yes | 42235.2639 | 2015-08-19 06:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0545 | 2015 | 8 | 19 | 6 | 20 | 15-0055982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5403 | 1.4303 | 102_311 | <25mph | <15mph | HFTD - Distribution | 2015-08-19 06:20:00 | 289 | 19.8186 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AT319 | 6.89 | 2018-08-01T13:38:00Z | 4.99 | 20 | < 25mph |  |  |  | 0 | 0 | No data | AT319 | 6.89 | 2018-08-01T14:43:00Z | 4.99 | 40 | < 25mph
PG&E | 2018-06-13 | 22:40 | 38.4901 | -122.6661 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SRS181640125 | 101966547 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 22:40 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1656 | 2018 | 6 | 13 | 22 | 40 | 18-0050782 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 295146 | 2.5247 | 128_267 | <25mph | <15mph | HFTD - Distribution | 2018-06-13 22:40:00 | 1398 | 17.8767 | FALSE | <25mph | RSAC1 | 2.6 | 2015-10-18T13:29:00Z | 4.99 | 21 | < 25mph | RSAC1 | 2.6 | 2015-10-18T13:29:00Z | 4.99 | 60 | < 25mph | RSAC1 | 2.6 | 2015-10-18T13:29:00Z | 4.99 | 44 | < 25mph | RSAC1 | 2.6 | 2015-10-18T13:29:00Z | 4.99 | 120 | < 25mph
PG&E | 2015-08-16 07:35 | 2015-08-16 07:35 | 35.4572 | -120.6567 | Vegetation | Rural | < 3 meters | Utility: PG&E |  | 8932 SAN GABRIEL RD. SW C/O OF LOT, Atascadero | None | 0 – 750 | Conductor | Overhead | Yes | 42232.316 | 2015-08-16 07:35 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0534 | 2015 | 8 | 16 | 7 | 35 | 15-0055284 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.0129 | 215_99 | <25mph | <15mph | HFTD - Distribution | 2015-08-16 07:35:00 | 278 | 16.9932 | FALSE | <25mph | E2260 | 2.13 | 2017-05-07T13:43:00Z | 13 | 9 | < 25mph | E2260 | 2.13 | 2017-05-07T13:43:00Z | 13 | 12 | < 25mph | E2260 | 2.13 | 2017-05-07T13:43:00Z | 13 | 18 | < 25mph | E2260 | 2.13 | 2017-05-07T13:43:00Z | 13 | 24 | < 25mph
PG&E | 2017-09-11 | 7:18 | 37.0008 | -121.6667 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100621936 | VERIZON CALIFORNIA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1407 | 2017 | 9 | 11 | 7 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.0313 | 170_184 | <25mph | <15mph | HFTD - Distribution | 2017-09-11 07:18:00 | 1145 | 32.6801 | FALSE | 25-40mph | AU710 | 3.82 | 2015-03-20T08:09:00Z | 4 | 4 | < 25mph | C4787 | 7.93 | 2015-03-20T07:14:00Z | 5.99 | 27 | < 25mph | AU710 | 3.82 | 2015-03-20T08:54:00Z | 4 | 8 | < 25mph | C4787 | 7.93 | 2015-03-20T07:14:00Z | 5.99 | 54 | < 25mph
PG&E | 2016-05-29 14:19 | 2016-05-29 14:19 | 40.5795 | -122.4694 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103156596 | Yes | 12000 | Conductor | Overhead | Yes | 42519.5965 | 2016-05-29 14:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0751 | 2016 | 5 | 29 | 14 | 19 | 16-0039619 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3860 | 1.6611 | 138_382 | <25mph | <15mph | HFTD - Distribution | 2016-05-29 14:19:00 | 494 | 20.6013 | FALSE | <25mph | MMOC1 | 1.91 | 2016-02-04T07:00:00Z | 7 | 5 | < 25mph | MMOC1 | 1.91 | 2016-02-04T07:00:00Z | 7 | 19 | < 25mph | MMOC1 | 1.91 | 2016-02-04T08:00:00Z | 8.01 | 10 | < 25mph | MMOC1 | 1.91 | 2016-02-04T08:00:00Z | 8.01 | 38 | < 25mph
PG&E | 2015-09-10 18:39 | 2015-09-10 18:39 | 40.7569 | -123.7958 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 096/004 |  | 115000 | Conductor | Overhead | Yes | 42257.7771 | 2015-09-10 18:39 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0590 | 2015 | 9 | 10 | 18 | 39 | RM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 2.2423 | 82_393 | <25mph | <15mph | HFTD - Transmission | 2015-09-10 18:39:00 | 335 | 12.4043 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.39 | 2018-09-13T10:55:00Z | 8.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.39 | 2018-09-13T10:55:00Z | 8.01 | 2 | < 25mph
PG&E | 2018-08-10 | 12:54 | 38.799 | -120.73 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101386272 | AT&T | 12000 | Conductor | Overhead | Yes | 43322 | 12:54 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1832 | 2018 | 8 | 10 | 12 | 54 | 18-0068798 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 26532 | 10.1607 | 211_283 | <25mph | <15mph | HFTD - Distribution | 2018-08-10 12:54:00 | 1571 | 17.3224 | FALSE | <25mph | E3165 | 0.86 | 2015-03-17T02:56:00Z | 1.01 | 6 | < 25mph | BDMC1 | 7.39 | 2015-03-17T02:36:00Z | 4.99 | 33 | < 25mph | E3165 | 0.86 | 2015-03-17T04:06:00Z | 2.01 | 12 | < 25mph | BDMC1 | 7.39 | 2015-03-17T03:36:00Z | 5.99 | 65 | < 25mph
PG&E | 2017-10-31 | 21:02 | 39.1119 | -122.9163 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Structure 020/003 | Unknown | 60000 | Conductor | Overhead | Yes | 43039 | 21:02 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | no-match | 1513 | 2017 | 10 | 31 | 21 | 2 | INT-10325 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | 50730 | 1.8727 | 117_301 | <25mph | <15mph | HFTD - Transmission | 2017-10-31 21:02:00 | 1255 | 9.8895 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5780 | 6.35 | 2015-09-09T04:48:00Z | 4 | 12 | < 25mph |  |  |  | 0 | 0 | No data | E5780 | 6.35 | 2015-09-09T04:48:00Z | 4 | 24 | < 25mph
PG&E | 2017-08-02 06:01 | 5:54 | 40.7986 | -123.3961 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 100974913 | Unknown | 12000 | Conductor | Overhead | Yes | 42949.251 | 5:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1308 | 2017 | 8 | 2 | 5 | 54 | 17-0067270 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 5832 | 11.2488 | 99_395 | <25mph | <15mph | HFTD - Distribution | 2017-08-02 05:54:00 | 1045 | 15.9988 | FALSE | <25mph |  |  |  | 0 | 0 | No data | UDWC1 | 7.47 | 2019-02-08T01:24:00Z | 8.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | UDWC1 | 7.47 | 2019-02-08T01:24:00Z | 8.01 | 2 | < 25mph
PG&E | 2015-08-12 17:38 | 2015-08-12 17:38 | 40.2153 | -123.8681 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 1 SP LD SD METER 1007960761 |  | 12000 | Conductor | Overhead | Yes | 42228.7347 | 2015-08-12 17:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0525 | 2015 | 8 | 12 | 17 | 38 | 15-0054643 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 14640 | 10.9518 | 79_363 | <25mph | <15mph | HFTD - Distribution | 2015-08-12 17:38:00 | 269 | 13.2342 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ERCC1 | 5.81 | 2017-04-24T08:28:00Z | 3 | 1 | < 25mph |  |  |  | 0 | 0 | No data | ERCC1 | 5.81 | 2017-04-24T09:28:00Z | 3 | 2 | < 25mph
PG&E | 2017-10-08 | 19:44 | 39.7446 | -121.597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100330456 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 19:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1464 | 2017 | 10 | 8 | 19 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 33.2724 | 174_335 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-08 19:44:00 | 1202 | 34.7906 | FALSE | 25-40mph | PDEC1 | 1.6 | 2015-06-26T21:00:00Z | 7 | 1 | < 25mph | E4833 | 4.34 | 2015-06-26T20:56:00Z | 8.99 | 13 | < 25mph | PDEC1 | 1.6 | 2015-06-26T21:00:00Z | 7 | 2 | < 25mph | E4833 | 4.34 | 2015-06-26T20:56:00Z | 8.99 | 25 | < 25mph
PG&E | 2017-06-03 13:35 | 13:26 | 38.9017 | -121.2056 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100043664 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42889.5662 | 13:26 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1122 | 2017 | 6 | 3 | 13 | 26 | 17-0052543 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29512 | 13.2044 | 191_289 | <25mph | <15mph | HFTD - Distribution | 2017-06-03 13:26:00 | 862 | 14.9142 | FALSE | <25mph | LICC1 | 3.58 | 2017-07-25T12:13:00Z | 3 | 1 | < 25mph | AR944 | 7.74 | 2017-07-25T12:00:00Z | 7 | 16 | < 25mph | LICC1 | 3.58 | 2017-07-25T12:13:00Z | 3 | 2 | < 25mph | AR944 | 7.74 | 2017-07-25T12:00:00Z | 7 | 29 | < 25mph
PG&E | 2015-08-24 22:48 | 2015-08-24 22:48 | 37.896 | -122.6011 | Vegetation | Rural | < 3 meters | Fire Agency | marin county fire | 200' east of pan toll rd 50' north of panoramic hwy |  | 12000 | Unknown | Overhead | Yes | 42240.95 | 2015-08-24 22:48 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0552 | 2015 | 8 | 24 | 22 | 48 | 15-0057082 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 1128 | 8.5935 | 130_234 | <25mph | <15mph | HFTD - Distribution | 2015-08-24 22:48:00 | 296 | 14.2171 | FALSE | <25mph | MDEC1 | 2.32 | 2017-10-30T14:36:00Z | 22.01 | 9 | < 25mph | MDEC1 | 2.32 | 2017-10-30T14:36:00Z | 22.01 | 16 | < 25mph | MDEC1 | 2.32 | 2017-10-30T14:36:00Z | 22.01 | 18 | < 25mph | MDEC1 | 2.32 | 2017-10-30T14:36:00Z | 22.01 | 33 | < 25mph
PG&E | 2019-06-06 | 9:01 | 35.6384 | -118.9687 | Bird Found | Herbaceous | 0.25 - 10 Acres | Fire Dept | Kern County FD | 100216096 |  | 21000 | Conductor | Overhead | No |  |  | Contact - Animal - Other |  | Animal contact |  | Animal Contact |  | no-match | 2019-228 | 2019 | 6 | 6 | 9 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 4.6796 | 291_110 | <25mph | <15mph | HFTD - Distribution | 2019-06-06 09:01:00 | 1803 | 21.162 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2015-10-03 21:11 | 2015-10-03 21:11 | 39.7358 | -121.6855 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | honey run rd at cutouts 16015 |  | 12000 | Conductor | Overhead | Yes | 42280.8826 | 2015-10-03 21:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0632 | 2015 | 10 | 3 | 21 | 11 | 15-0067708 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 10499 | 20.0626 | 170_335 | <25mph | <15mph | HFTD - Distribution | 2015-10-03 21:11:00 | 377 | 26.1472 | FALSE | 25-40mph | PDEC1 | 3.46 | 2016-08-16T16:00:00Z | 1.01 | 1 | < 25mph | E2076 | 5.67 | 2016-08-16T16:33:00Z | 2.01 | 10 | < 25mph | PDEC1 | 3.46 | 2016-08-16T17:00:00Z | 1.01 | 2 | < 25mph | E2076 | 5.67 | 2016-08-16T17:53:00Z | 4 | 21 | < 25mph
PG&E | 2016-08-21 | 2016-08-21 13:02 | 38.4445 | -122.2496 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102291451 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42603 | 2016-08-21 13:02 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0940 | 2016 | 8 | 21 | 13 | 2 | 16-0058847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 12780 | 10.3444 | 145_264 | <25mph | <15mph | HFTD - Distribution | 2016-08-21 13:02:00 | 683 | 21.5044 | FALSE | <25mph | ATLC1 | 2.26 | 2016-07-20T14:29:00Z | 14 | 1 | < 25mph | ATLC1 | 2.26 | 2016-07-20T14:29:00Z | 14 | 2 | < 25mph | ATLC1 | 2.26 | 2016-07-20T15:29:00Z | 14 | 2 | < 25mph | ATLC1 | 2.26 | 2016-07-20T15:29:00Z | 14 | 3 | < 25mph
PG&E | 2016-09-22 | 13:53 | 40.224 | -122.3417 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101539450 | None | 12000 | Conductor | Overhead | Yes | 42635 | 13:53 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0996 | 2016 | 9 | 22 | 13 | 53 | 16-0066692 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 14706 | 14.6017 | 143_362 | <25mph | <15mph | HFTD - Distribution | 2016-09-22 13:53:00 | 739 | 20.1469 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KRBL | 6.93 | 2015-05-06T21:54:00Z | 31.07 | 5 | 25-40mph |  |  |  | 0 | 0 | No data | KRBL | 6.93 | 2015-05-06T21:54:00Z | 31.07 | 10 | 25-40mph
PG&E | 2017-04-25 12:39 | 12:38 | 38.6583 | -120.9762 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101376746 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 42850.5271 | 12:38 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1072 | 2017 | 4 | 25 | 12 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 9.948 | 200_275 | <25mph | <15mph | HFTD - Distribution | 2017-04-25 12:38:00 | 812 | 10.5664 | FALSE | <25mph | D7401 | 2.53 | 2017-05-11T02:51:00Z | 3 | 5 | < 25mph | BENC1 | 5.2 | 2017-05-11T02:59:00Z | 11.01 | 62 | < 25mph | D7401 | 2.53 | 2017-05-11T03:21:00Z | 3 | 7 | < 25mph | BENC1 | 5.2 | 2017-05-11T02:59:00Z | 11.01 | 108 | < 25mph
PG&E | 2019-03-19 | 12:52 | 37.9956 | -120.3244 | Tree - cutting, 3rd party | Hardwood Forest | 1 meter - < 3 meters | Self Extinguished |  | 101045032 |  | 17000 | Conductor | Overhead | Yes | 43543 | 12:52 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-187 | 2019 | 3 | 19 | 12 | 52 | 19-0035101 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 70602 | 12.9023 | 229_239 | <25mph | <15mph | HFTD - Distribution | 2019-03-19 12:52:00 | 1736 | 14.3226 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.27 | 2016-07-15T02:02:00Z | 14 | 5 | < 25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.27 | 2016-07-15T03:02:00Z | 14.99 | 10 | < 25mph
PG&E | 2017-09-01 | 8:00 | 37.3757 | -119.8886 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101067028 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42979 | 8:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1378 | 2017 | 9 | 1 | 8 | 0 | 17-0074724 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 680 | 5.98 | 248_205 | <25mph | <15mph | HFTD - Distribution | 2017-09-01 08:00:00 | 1116 | 14.9658 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E9110 | 4.96 | 2019-01-06T00:16:00Z | 21 | 6 | < 25mph |  |  |  | 0 | 0 | No data | E9110 | 4.96 | 2019-01-06T01:00:00Z | 21 | 13 | < 25mph
1. Butte | 2015-09-09 | 14:26 | 38.3297 | -120.7042 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1987 | 2015 | 9 | 9 | 14 | 26 |  | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 1353755 | 12.0917 | 212_257 | <25mph | <15mph | HFTD - Distribution | 2015-09-09 14:26:00 | 332 | 14.8248 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 5.02 | 2015-03-04T02:56:00Z | 8.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 5.02 | 2015-03-04T03:56:00Z | 11.01 | 2 | < 25mph
PG&E | 2018-08-24 | 5:03 | 39.1184 | -121.0154 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JIM SMITH BATT CHIEF 3 | 100097647 | Unknown | 12000 | Conductor | Overhead | Yes | 43336 | 5:03 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1858 | 2018 | 8 | 24 | 5 | 3 | 18-0073024 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 4048 | 6.5682 | 199_301 | <25mph | <15mph | HFTD - Distribution | 2018-08-24 05:03:00 | 1597 | 12.3049 | FALSE | <25mph | C5488 | 3.16 | 2017-12-10T23:11:00Z | 4.99 | 22 | < 25mph | C0713 | 7.21 | 2017-12-10T22:56:00Z | 5.99 | 69 | < 25mph | C5488 | 3.16 | 2017-12-10T23:11:00Z | 4.99 | 44 | < 25mph | C0713 | 7.21 | 2017-12-10T22:56:00Z | 5.99 | 139 | < 25mph
PG&E | 2016-06-10 15:51 | 2016-06-10 15:51 | 39.9934 | -123.7883 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100992291 |  | 12000 | Conductor | Overhead | Yes | 42531.6604 | 2016-06-10 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0788 | 2016 | 6 | 10 | 15 | 51 | 16-0042501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | N.A. | 22.4156 | 82_351 | <25mph | <15mph | HFTD - Distribution | 2016-06-10 15:51:00 | 531 | 22.7996 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AV037 | 5.5 | 2018-07-12T02:23:00Z | 5.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | AV037 | 5.5 | 2018-07-12T03:23:00Z | 8.99 | 8 | < 25mph
PG&E | 2017-12-19 | 19:45 | 40.7271 | -122.3263 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101457738 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43088 | 19:45 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1545 | 2017 | 12 | 19 | 19 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 12.0712 | 144_390 | <25mph | <15mph | HFTD - Distribution | 2017-12-19 19:45:00 | 1287 | 14.9625 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2019-09-12 | 14:25 | 37.3144 | -122.1865 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 024131103 |  | 12000 | Conductor | Overhead | Yes | 43720 | 14:25 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-217 | 2019 | 9 | 12 | 14 | 25 | 19-0098386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 89097 | 5.2412 | 147_201 | <25mph | <15mph | HFTD - Distribution | 2019-09-12 14:25:00 | 2036 | 15.0249 | FALSE | <25mph | E6994 | 3.65 | 2015-06-12T05:20:00Z | 10.98 | 44 | < 25mph | E6994 | 3.65 | 2015-06-12T05:20:00Z | 10.98 | 105 | < 25mph | E6994 | 3.65 | 2015-06-12T05:20:00Z | 10.98 | 88 | < 25mph | E6994 | 3.65 | 2015-06-12T05:20:00Z | 10.98 | 208 | < 25mph
PG&E | 2016-06-12 01:45 | 1:45 | 37.4643 | -122.3459 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Unknown | 100265854 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42533.0729 | 1:45 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0796 | 2016 | 6 | 12 | 1 | 45 | 16-0042637 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 19836 | 11.0705 | 141_210 | <25mph | <15mph | HFTD - Distribution | 2016-06-12 01:45:00 | 534 | 17.9563 | FALSE | <25mph | PUGC1 | 2.7 | 2017-08-23T10:18:00Z | 4.99 | 9 | < 25mph | E9502 | 4.61 | 2017-08-23T10:15:00Z | 5.99 | 87 | < 25mph | PUGC1 | 2.7 | 2017-08-23T11:18:00Z | 4.99 | 15 | < 25mph | AU981 | 5.46 | 2017-08-23T11:54:00Z | 8.99 | 164 | < 25mph
PG&E | 2017-08-12 09:09 | 09:08 | 34.6689 | -120.0286 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103391912 | Unknown | 12000 | Conductor | Overhead | Yes | 42959.3812 | 09:08 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | wire cut | Other/Unknown | 1330 | 2017 | 8 | 12 | 9 | 8 | 17-0069829 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 26070 | 3.5662 | 244_55 | <25mph | <15mph | HFTD - Distribution | 2017-08-12 09:08:00 | 1068 | 23.4799 | FALSE | <25mph | UCSE | 1.88 | 2017-10-30T15:30:00Z | 5.1 | 7 | < 25mph | FGMC1 | 4.7 | 2017-10-30T14:35:00Z | 8.01 | 17 | < 25mph | SXWC1 | 1.34 | 2017-10-30T16:09:00Z | 5.99 | 14 | < 25mph | FGMC1 | 4.7 | 2017-10-30T14:35:00Z | 8.01 | 29 | < 25mph
PG&E | 2017-08-27 | 20:04 | 38.9165 | -121.151 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-477-0641 x7, log 22629 | 100077184 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42974 | 20:04 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1352 | 2017 | 8 | 27 | 20 | 4 | 17-0073228 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 905 | 9.7822 | 193_290 | <25mph | <15mph | HFTD - Distribution | 2017-08-27 20:04:00 | 1090 | 16.757 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8862 | 4.91 | 2017-01-17T16:13:00Z | 5.99 | 9 | < 25mph |  |  |  | 0 | 0 | No data | D8862 | 4.91 | 2017-01-17T16:28:00Z | 8.99 | 29 | < 25mph
PG&E | 2017-05-06 11:23 | 11:18 | 40.7951 | -124.029 | Vegetation | Rural | < 3 Meters | Fire Agency | chief rick harden 7074423352 | 103661154 | Unknown | 12000 | Conductor | Overhead | Yes | 42861.4744 | 11:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1086 | 2017 | 5 | 6 | 11 | 18 | 17-0045785 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 113630 | 26.2788 | 73_395 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-05-06 11:18:00 | 826 | 28.8261 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.4 | 2015-05-29T15:55:00Z | 8.01 | 46 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.4 | 2015-05-29T15:55:00Z | 8.01 | 92 | < 25mph
PG&E | 2019-06-27 | 2:23 | 36.8198 | -119.3334 | Bird Found | Hardwood Woodland | 0.25 - 10 Acres | Self Extinguished |  | Kings River-Sanger-Reedley 115Kv At 16/089 |  | 115000 | Insulator | Overhead | Yes | 43643 | 2:23 | Equipment - PG&E | Insulator |  |  |  |  | no-match | 2019-104 | 2019 | 6 | 27 | 2 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | N.A. | 13.572 | 273_175 | <25mph | <15mph | HFTD - Transmission | 2019-06-27 02:23:00 | 1872 | 13.572 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2888 | 7.11 | 2018-07-17T01:59:00Z | 13 | 7 | < 25mph |  |  |  | 0 | 0 | No data | E2888 | 7.11 | 2018-07-17T01:59:00Z | 13 | 14 | < 25mph
PG&E | 2015-10-16 09:43 | 2015-10-16 09:43 | 39.187 | -123.2015 | Vegetation | Rural | < 3 meters | Unknown |  | 102196855 |  | 12000 | Conductor | Overhead | Yes | 42293.4049 | 2015-10-16 09:43 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0653 | 2015 | 10 | 16 | 9 | 43 | 15-0070948 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 65228 | 2.2696 | 105_305 | <25mph | <15mph | HFTD - Distribution | 2015-10-16 09:43:00 | 397 | 16.8813 | FALSE | <25mph | E7513 | 1.34 | 2019-06-25T16:08:00Z | 2.01 | 12 | < 25mph | PG122 | 6.24 | 2019-06-25T15:20:00Z | 17.98 | 36 | < 25mph | E7513 | 1.34 | 2019-06-25T17:03:00Z | 4 | 24 | < 25mph | PG122 | 6.24 | 2019-06-25T15:20:00Z | 17.98 | 72 | < 25mph
PG&E | 2018-08-01 | 17:58 | 38.9155 | -122.799 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102156435 | Unknown | 12000 | Conductor | Overhead | Yes | 43313 | 17:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1805 | 2018 | 8 | 1 | 17 | 58 | 18-0065921 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2744 | 14.8702 | 122_290 | <25mph | <15mph | HFTD - Distribution | 2018-08-01 17:58:00 | 1545 | 14.8702 | FALSE | <25mph | E4393 | 3.97 | 2019-01-29T01:01:00Z | 2.01 | 4 | < 25mph | PG125 | 6.93 | 2019-01-29T01:00:00Z | 8.32 | 35 | < 25mph | E4393 | 3.97 | 2019-01-29T01:45:00Z | 4.99 | 8 | < 25mph | PG125 | 6.93 | 2019-01-29T01:00:00Z | 8.32 | 70 | < 25mph
PG&E | 2018-07-17 | 11:11 | 35.6986 | -120.9777 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | dennis byrnes 8055434244 inc # = 18ca-slu-007640 | 103886652 | Unknown | 21000 | Conductor | Overhead | Yes | 43298 | 11:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1755 | 2018 | 7 | 17 | 11 | 11 | 18-0060637 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 9121 | 4.768 | 201_112 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 11:11:00 | 1495 | 12.6145 | FALSE | <25mph | E9175 | 3.58 | 2017-09-07T10:50:00Z | 1.01 | 10 | < 25mph | D4060 | 6.73 | 2017-09-07T11:30:00Z | 4 | 15 | < 25mph | E9175 | 3.58 | 2017-09-07T10:50:00Z | 1.01 | 19 | < 25mph | D4060 | 6.73 | 2017-09-07T11:45:00Z | 4.99 | 29 | < 25mph
PG&E | 2016-07-24 16:24 | 2016-07-24 16:24 | 38.0105 | -122.1941 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | CCD | 103049639 |  | 115000 | Conductor | Overhead | Yes | 42575.6833 | 2016-07-24 16:24 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0876 | 2016 | 7 | 24 | 16 | 24 | PS-2016-013 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 0 | 18.9534 | 148_240 | <25mph | <15mph | HFTD - Transmission | 2016-07-24 16:24:00 | 619 | 23.7155 | FALSE | <25mph | E6179 | 3.92 | 2019-02-18T11:10:00Z | 11.01 | 36 | < 25mph | UPBC1 | 4.44 | 2019-02-18T12:00:00Z | 15.99 | 121 | < 25mph | E6179 | 3.92 | 2019-02-18T11:10:00Z | 11.01 | 72 | < 25mph | UPBC1 | 4.44 | 2019-02-18T12:00:00Z | 15.99 | 238 | < 25mph
PG&E | 2017-07-18 | 21:40 | 38.0031 | -122.2093 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | Pole 000/002 to 000/003 | Unknown | 60000 | Conductor | Overhead | Yes | 42934 | 21:40 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1266 | 2017 | 7 | 18 | 21 | 40 | INT-09875 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 0 | 11.7142 | 147_239 | <25mph | <15mph | HFTD - Transmission | 2017-07-18 21:40:00 | 1007 | 20.8699 | FALSE | <25mph | PG042 | 3.01 | 2019-08-17T07:20:00Z | 17.31 | 30 | < 25mph | DPXC1 | 4.61 | 2019-08-17T07:00:00Z | 27.98 | 139 | 25-40mph | PG042 | 3.01 | 2019-08-17T07:20:00Z | 17.31 | 60 | < 25mph | DPXC1 | 4.61 | 2019-08-17T07:00:00Z | 27.98 | 278 | 25-40mph
PG&E | 2015-09-06 19:27 | 2015-09-06 19:27 | 34.6195 | -120.2534 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Santa Barbara County Fire | meter# 1008400678 | Verizon | 12000 | Conductor | Overhead | Yes | 42253.8104 | 2015-09-06 19:27 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0582 | 2015 | 9 | 6 | 19 | 27 | 15-0059612 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 863 | 14.7315 | 234_53 | <25mph | <15mph | HFTD - Distribution | 2015-09-06 19:27:00 | 326 | 17.7534 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C9206 | 6.79 | 2015-12-14T22:51:00Z | 17 | 8 | < 25mph |  |  |  | 0 | 0 | No data | C9206 | 6.79 | 2015-12-14T23:51:00Z | 17 | 15 | < 25mph
PG&E | 2018-06-19 | 0:27 | 38.7604 | -120.8224 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101388356 | Unknown | 12000 | Conductor | Overhead | Yes | 43270 | 0:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1675 | 2018 | 6 | 19 | 0 | 27 | 18-0052111 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 141652 | 7.2853 | 207_281 | <25mph | <15mph | HFTD - Distribution | 2018-06-19 00:27:00 | 1417 | 13.5304 | FALSE | <25mph | PG068 | 3.2 | 2018-11-14T22:10:00Z | 7.45 | 18 | < 25mph | C6129 | 4.72 | 2018-11-14T21:49:00Z | 12.01 | 109 | < 25mph | PG068 | 3.2 | 2018-11-14T22:10:00Z | 7.45 | 36 | < 25mph | C6129 | 4.72 | 2018-11-14T21:49:00Z | 12.01 | 205 | < 25mph
PG&E | 2017-12-16 | 11:51 | 38.8171 | -122.7041 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Shawn Ohare | 102167231 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43085 | 11:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1540 | 2017 | 12 | 16 | 11 | 51 | 17-0102101 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26120 | 34.3488 | 126_285 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-12-16 11:51:00 | 1282 | 35.345 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | KELC1 | 6.55 | 2015-04-19T18:57:00Z | 14.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.55 | 2015-04-19T19:57:00Z | 18.01 | 2 | < 25mph
PG&E | 2018-10-08 | 11:03 | 38.2621 | -122.7881 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101987186 | AT&T | 12000 | Conductor | Overhead | No | N.A. | N.A. | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1933 | 2018 | 10 | 8 | 11 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 15.6859 | 122_254 | <25mph | <15mph | HFTD - Distribution | 2018-10-08 11:03:00 | 1672 | 17.3485 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E8654 | 6.76 | 2017-04-11T07:21:00Z | 3 | 10 | < 25mph |  |  |  | 0 | 0 | No data | E8654 | 6.76 | 2017-04-11T08:21:00Z | 3 | 19 | < 25mph
PG&E | 2017-06-30 23:55 | 23:54 | 38.5794 | -122.8835 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 101958804 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42916.9965 | 23:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1211 | 2017 | 6 | 30 | 23 | 54 | 17-0059922 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2025 | 14.1552 | 118_272 | <25mph | <15mph | HFTD - Distribution | 2017-06-30 23:54:00 | 950 | 23.4555 | FALSE | <25mph | R08WW | 2.5 | 2018-09-06T16:00:00Z | 4.21 | 5 | < 25mph | F40WW | 7.41 | 2018-09-06T16:45:00Z | 5.1 | 37 | < 25mph | R08WW | 2.5 | 2018-09-06T17:00:00Z | 5.39 | 10 | < 25mph | F40WW | 7.41 | 2018-09-06T17:30:00Z | 6.8 | 77 | < 25mph
PG&E | 2019-08-05 | 22:38 | 37.1869 | -119.7902 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Unknown |  | 322066125092 |  | 21000 | Transformer | Overhead | Yes | 43682 | 22:38 | Equipment - Overloaded | Transformer |  |  |  |  | Other/Unknown | 2019-134 | 2019 | 8 | 5 | 22 | 38 | 19-0084586 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 996 | 7.0886 | 253_195 | <25mph | <15mph | HFTD - Distribution | 2019-08-05 22:38:00 | 1952 | 12.3468 | FALSE | <25mph | D7022 | 1.42 | 2017-01-15T16:54:00Z | 2.01 | 20 | < 25mph | D7022 | 1.42 | 2017-01-15T16:54:00Z | 2.01 | 20 | < 25mph | E5766 | 3.69 | 2017-01-15T17:39:00Z | 3 | 38 | < 25mph | E5766 | 3.69 | 2017-01-15T17:39:00Z | 3 | 38 | < 25mph
PG&E | 2019-01-16 | 0:17 | 38.0621 | -120.1964 | Vegetation | Conifer Forest | Structure Only | Cal Fire |  | 163661701 |  | 17000 | Conductor | Overhead | Yes | 43481 | 0:17 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-01 | 2019 | 1 | 16 | 0 | 17 | 19-0010443 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1041827 | 14.8061 | 234_243 | <25mph | <15mph | HFTD - Distribution | 2019-01-16 00:17:00 | 1728 | 28.2081 | FALSE | 25-40mph | MOUC1 | 2.77 | 2018-04-11T11:02:00Z | 15.99 | 1 | < 25mph | MOUC1 | 2.77 | 2018-04-11T11:02:00Z | 15.99 | 1 | < 25mph | MOUC1 | 2.77 | 2018-04-11T11:02:00Z | 15.99 | 2 | < 25mph | MOUC1 | 2.77 | 2018-04-11T11:02:00Z | 15.99 | 2 | < 25mph
PG&E | 2017-05-09 18:41 | 18:26 | 40.8689 | -123.5156 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | todd wright fire chief. 5307392493 | 103796045 | Unknown | 12000 | Conductor | Overhead | Yes | 42864.7782 | 18:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1092 | 2017 | 5 | 9 | 18 | 26 | 17-0046642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 108117 | 15.9566 | 94_399 | <25mph | <15mph | HFTD - Distribution | 2017-05-09 18:26:00 | 832 | 17.9691 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-09-12 | 4:24 | 36.3999 | -121.902 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire Hwy 1 Carmel Hill | 101669614 |  | 12000 | Conductor | Overhead | Yes | 42625 | 4:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0973 | 2016 | 9 | 12 | 4 | 24 | 16-0063826 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 130604 | 5.4712 | 159_151 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 04:24:00 | 715 | 8.1881 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TR419 | 7.81 | 2017-05-27T18:15:00Z | 14 | 1 | < 25mph |  |  |  | 0 | 0 | No data | TR419 | 7.81 | 2017-05-27T18:15:00Z | 14 | 2 | < 25mph
PG&E | 2018-06-11 | 17:49 | 34.7329 | -120.0861 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103015183 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43262 | 17:49 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1649 | 2018 | 6 | 11 | 17 | 49 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 16.7571 | 241_59 | <25mph | <15mph | HFTD - Distribution | 2018-06-11 17:49:00 | 1391 | 18.839 | FALSE | <25mph | PG214 | 2.52 | 2019-07-16T22:30:00Z | 21.47 | 18 | < 25mph | PG214 | 2.52 | 2019-07-16T22:30:00Z | 21.47 | 27 | < 25mph | PG214 | 2.52 | 2019-07-16T23:40:00Z | 24.11 | 36 | < 25mph | PG214 | 2.52 | 2019-07-16T23:40:00Z | 24.11 | 54 | < 25mph
PG&E | 2017-06-03 13:35 | 13:26 | 38.9017 | -121.2056 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100043664 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42889.5662 | 13:26 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1122 | 2017 | 6 | 3 | 13 | 26 | 17-0052543 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29512 | 13.2044 | 191_289 | <25mph | <15mph | HFTD - Distribution | 2017-06-03 13:26:00 | 862 | 14.9142 | FALSE | <25mph | F5165 | 2.96 | 2019-10-08T10:10:00Z | 7 | 14 | < 25mph | D8862 | 7.4 | 2019-10-08T10:16:00Z | 13 | 46 | < 25mph | F5165 | 2.96 | 2019-10-08T10:10:00Z | 7 | 27 | < 25mph | D8862 | 7.4 | 2019-10-08T10:16:00Z | 13 | 93 | < 25mph
PG&E | 2018-06-13 | 22:40 | 38.4901 | -122.6661 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SRS181640125 | 101966547 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 22:40 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1656 | 2018 | 6 | 13 | 22 | 40 | 18-0050782 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 295146 | 2.5247 | 128_267 | <25mph | <15mph | HFTD - Distribution | 2018-06-13 22:40:00 | 1398 | 17.8767 | FALSE | <25mph | E1582 | 2.84 | 2018-03-05T11:33:00Z | 5.99 | 15 | < 25mph | E1582 | 2.84 | 2018-03-05T11:33:00Z | 5.99 | 59 | < 25mph | E1582 | 2.84 | 2018-03-05T11:53:00Z | 5.99 | 30 | < 25mph | E1582 | 2.84 | 2018-03-05T11:53:00Z | 5.99 | 117 | < 25mph
PG&E | 2017-07-22 14:38 | 14:38 | 37.2994 | -122.1631 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100265488 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.6101 | 14:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1280 | 2017 | 7 | 22 | 14 | 38 | 17-0064738 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49181 | 4.6185 | 148_201 | <25mph | <15mph | HFTD - Distribution | 2017-07-22 14:38:00 | 1019 | 12.5156 | FALSE | <25mph | E0516 | 3.56 | 2016-06-17T15:55:00Z | 7 | 5 | < 25mph | E8945 | 7.92 | 2016-06-17T15:59:00Z | 14 | 91 | < 25mph | E0516 | 3.56 | 2016-06-17T17:11:00Z | 7 | 10 | < 25mph | E8945 | 7.92 | 2016-06-17T15:59:00Z | 14 | 180 | < 25mph
PG&E | 2017-08-02 06:01 | 5:54 | 40.7986 | -123.3961 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 100974913 | Unknown | 12000 | Conductor | Overhead | Yes | 42949.251 | 5:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1308 | 2017 | 8 | 2 | 5 | 54 | 17-0067270 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 5832 | 11.2488 | 99_395 | <25mph | <15mph | HFTD - Distribution | 2017-08-02 05:54:00 | 1045 | 15.9988 | FALSE | <25mph |  |  |  | 0 | 0 | No data | UDWC1 | 7.47 | 2017-02-16T10:24:00Z | 17 | 1 | < 25mph |  |  |  | 0 | 0 | No data | UDWC1 | 7.47 | 2017-02-16T11:24:00Z | 22.01 | 2 | < 25mph
PG&E | 2016-04-21 09:25 | 2016-04-21 09:25 | 39.293 | -123.769 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 103312287 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0711 | 2016 | 4 | 21 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 8.8774 | 81_312 | <25mph | <15mph | HFTD - Distribution | 2016-04-21 09:25:00 | 455 | 20.2474 | FALSE | <25mph | E6025 | 0.21 | 2015-02-17T15:02:00Z | 0 | 6 | < 25mph | E6025 | 0.21 | 2015-02-17T15:02:00Z | 0 | 8 | < 25mph | E6025 | 0.21 | 2015-02-17T16:03:00Z | 0 | 12 | < 25mph | E2582 | 6.32 | 2015-02-17T15:33:00Z | 1.01 | 16 | < 25mph
PG&E | 2018-07-14 | 12:40 | 38.5793 | -122.878 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103122744 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 12:40 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1746 | 2018 | 7 | 14 | 12 | 40 | 18-0059799 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20804 | 12.0574 | 118_272 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 12:40:00 | 1486 | 14.4502 | FALSE | <25mph | AU487 | 3.65 | 2015-09-11T16:40:00Z | 2.01 | 8 | < 25mph | E6724 | 5.13 | 2015-09-11T16:09:00Z | 2.01 | 14 | < 25mph | AU487 | 3.65 | 2015-09-11T17:30:00Z | 3 | 24 | < 25mph | E6724 | 5.13 | 2015-09-11T17:39:00Z | 4.99 | 40 | < 25mph
PG&E | 2019-09-28 | 13:16 | 37.2553 | -119.5057 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 252531103 |  | 12000 | Conductor | Overhead | Yes | 43736 | 13:16 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-36 | 2019 | 9 | 28 | 13 | 16 | 19-0104972 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 1296 | 12.1111 | 265_198 | <25mph | <15mph | HFTD - Distribution | 2019-09-28 13:16:00 | 2064 | 13.545 | FALSE | <25mph | NFRC1 | 1.54 | 2018-03-25T02:55:00Z | 7 | 4 | < 25mph | AT344 | 5.5 | 2018-03-25T02:15:00Z | 8.01 | 36 | < 25mph | NFRC1 | 1.54 | 2018-03-25T03:55:00Z | 7 | 8 | < 25mph | AT344 | 5.5 | 2018-03-25T02:15:00Z | 8.01 | 73 | < 25mph
PG&E | 2017-06-23 13:01 | 13:00 | 39.3051 | -122.4862 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 100329817 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42909.5421 | 13:00 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | no-match | 1190 | 2017 | 6 | 23 | 13 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 8.6467 | 136_311 | <25mph | <15mph | HFTD - Distribution | 2017-06-23 13:00:00 | 929 | 13.2674 | FALSE | <25mph |  |  |  | 0 | 0 | No data | SYWC1 | 6.32 | 2017-06-30T09:26:00Z | 5.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | SYWC1 | 6.32 | 2017-06-30T10:26:00Z | 7 | 2 | < 25mph
PG&E | 2018-06-30 | 22:36 | 39.1141 | -121.077 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Matt Wallen (530) 277-3312 Incident # NEU015486 | 100105380 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 22:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1717 | 2018 | 6 | 30 | 22 | 36 | 18-0056039 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 8004 | 7.8488 | 196_300 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 22:36:00 | 1458 | 15.8656 | FALSE | <25mph | C5488 | 3.83 | 2015-08-20T19:40:00Z | 8.99 | 16 | < 25mph | AS856 | 7.28 | 2015-08-20T19:26:00Z | 10 | 64 | < 25mph | C5488 | 3.83 | 2015-08-20T21:02:00Z | 11.01 | 32 | < 25mph | C5488 | 3.83 | 2015-08-20T21:02:00Z | 11.01 | 128 | < 25mph
PG&E | 2018-09-29 | 16:16 | 41.0219 | -123.655 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Hoopa Fire Dept | 100962165 | Unknown | 12000 | Conductor | Overhead | Yes | 43372 | 16:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1923 | 2018 | 9 | 29 | 16 | 16 | 18-0084877 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 16028 | 7.8421 | 89_407 | <25mph | <15mph | HFTD - Distribution | 2018-09-29 16:16:00 | 1662 | 11.5265 | FALSE | <25mph | HOAC1 | 1.98 | 2015-09-05T00:40:00Z | 24 | 1 | < 25mph | HOAC1 | 1.98 | 2015-09-05T00:40:00Z | 24 | 3 | < 25mph | HOAC1 | 1.98 | 2015-09-05T00:40:00Z | 24 | 2 | < 25mph | HOAC1 | 1.98 | 2015-09-05T00:40:00Z | 24 | 6 | < 25mph
PG&E | 2015-08-08 07:42 | 2015-08-08 07:42 | 39.2007 | -121.2137 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100076217 | Pacific Bell | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0519 | 2015 | 8 | 8 | 7 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 14.1661 | 190_305 | <25mph | <15mph | HFTD - Distribution | 2015-08-08 07:42:00 | 263 | 14.9803 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1789 | 5.79 | 2018-12-21T07:42:00Z | 8.99 | 32 | < 25mph |  |  |  | 0 | 0 | No data | E1789 | 5.79 | 2018-12-21T07:42:00Z | 8.99 | 64 | < 25mph
PG&E | 2015-06-28 21:07 | 2015-06-28 21:07 | 39.7405 | -121.4974 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | DEADWOOD RD, JARBO GAP |  | 12000 | Conductor | Overhead | Yes | 42183.8799 | 2015-06-28 21:07 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0424 | 2015 | 6 | 28 | 21 | 7 | 15-0043869 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 45683 | 12.2547 | 178_335 | <25mph | <15mph | HFTD - Distribution | 2015-06-28 21:07:00 | 169 | 17.5682 | FALSE | <25mph | JBGC1 | 0.55 | 2019-10-06T18:13:00Z | 41 | 19 | 40-55mph | JBGC1 | 0.55 | 2019-10-06T18:13:00Z | 41 | 86 | 40-55mph | JBGC1 | 0.55 | 2019-10-06T18:13:00Z | 41 | 38 | 40-55mph | JBGC1 | 0.55 | 2019-10-06T18:13:00Z | 41 | 172 | 40-55mph
PG&E | 2015-06-27 12:48 | 2015-06-27 12:48 | 37.9474 | -120.4274 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101034512 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.5333 | 2015-06-27 12:48 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0414 | 2015 | 6 | 27 | 12 | 48 | 15-0043755 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 150075 | 11.0891 | 224_236 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 12:48:00 | 159 | 19.6587 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-06-28 | 12:27 | 38.5982 | -121.0081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | John Reis, 530-622-3858 | 101376954 | Unknown | 21000 | Conductor | Overhead | Yes | 43279 | 12:27 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1702 | 2018 | 6 | 28 | 12 | 27 | 18-0055479 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 24671 | 12.7651 | 199_272 | <25mph | <15mph | HFTD - Distribution | 2018-06-28 12:27:00 | 1443 | 13.4512 | FALSE | <25mph | E8856 | 2.62 | 2019-05-28T11:20:00Z | 0 | 12 | < 25mph | PG357 | 4.52 | 2019-05-28T10:30:00Z | 6.13 | 96 | < 25mph | E8856 | 2.62 | 2019-05-28T12:20:00Z | 0 | 24 | < 25mph | PG357 | 4.52 | 2019-05-28T10:30:00Z | 6.13 | 193 | < 25mph
PG&E | 2015-12-31 19:12 | 2015-12-31 19:12 | 37.1568 | -121.9868 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LOS GATOS MONTE SERENO SARATOGA | 100518215 | Verizon | 21000 | Conductor | Overhead | Yes | 42369.8 | 2015-12-31 19:12 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0689 | 2015 | 12 | 31 | 19 | 12 | 15-0087962 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7979 | 7.4149 | 156_193 | <25mph | <15mph | HFTD - Distribution | 2015-12-31 19:12:00 | 433 | 10.9251 | FALSE | <25mph | D8979 | 2.76 | 2018-01-19T08:08:00Z | 7 | 19 | < 25mph | D3546 | 6.48 | 2018-01-19T08:10:00Z | 8.01 | 158 | < 25mph | D8979 | 2.76 | 2018-01-19T08:08:00Z | 7 | 42 | < 25mph | D3546 | 6.48 | 2018-01-19T08:10:00Z | 8.01 | 319 | < 25mph
PG&E | 2017-04-25 12:39 | 12:38 | 38.6583 | -120.9762 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101376746 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 42850.5271 | 12:38 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1072 | 2017 | 4 | 25 | 12 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 9.948 | 200_275 | <25mph | <15mph | HFTD - Distribution | 2017-04-25 12:38:00 | 812 | 10.5664 | FALSE | <25mph | PG357 | 3.05 | 2019-08-16T07:40:00Z | 9.42 | 43 | < 25mph | PG073 | 5.01 | 2019-08-16T08:10:00Z | 15.99 | 140 | < 25mph | PG357 | 3.05 | 2019-08-16T09:00:00Z | 14.47 | 85 | < 25mph | PG073 | 5.01 | 2019-08-16T09:10:00Z | 16.89 | 279 | < 25mph
PG&E | 2019-04-09 | 15:27 | 37.7341 | -120.0776 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 101076921 |  | 21000 | Pole | Overhead | Yes | 43564 | 15:27 | Vegetation |  | Veg. contact | Pole |  |  | Branch (Not overhanging, > 12ft) | 2019-313 | 2019 | 4 | 9 | 15 | 27 | 19-0041008 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 179862 | 22.8983 | 240_225 | <25mph | <15mph | HFTD - Distribution | 2019-04-09 15:27:00 | 1738 | 29.8749 | FALSE | 25-40mph | PG184 | 1.78 | 2019-02-16T21:00:00Z | 6.35 | 14 | < 25mph | PG155 | 7.32 | 2019-02-16T21:20:00Z | 12.71 | 25 | < 25mph | PG112 | 3.29 | 2019-02-16T21:30:00Z | 7.67 | 26 | < 25mph | PG155 | 7.32 | 2019-02-16T21:40:00Z | 15.99 | 50 | < 25mph
PG&E | 2016-06-10 15:51 | 2016-06-10 15:51 | 39.9934 | -123.7883 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100992291 |  | 12000 | Conductor | Overhead | Yes | 42531.6604 | 2016-06-10 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0788 | 2016 | 6 | 10 | 15 | 51 | 16-0042501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | N.A. | 22.4156 | 82_351 | <25mph | <15mph | HFTD - Distribution | 2016-06-10 15:51:00 | 531 | 22.7996 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AV037 | 5.5 | 2017-04-08T12:13:00Z | 1.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | AV037 | 5.5 | 2017-04-08T13:33:00Z | 2.01 | 5 | < 25mph
PG&E | 2019-08-14 | 10:16 | 35.379 | -120.4232 | Vegetation | Hardwood Woodland | < 1 meter | Cal Fire |  | 512769069280 |  | 21000 | Conductor | Overhead | Yes | 43691 | 10:16 | Vegetation | [5 empty] | no-match |  | 2019 | 8 | 14 | 10 | 16 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.0314 | 226_94 | <25mph | <15mph | HFTD - Distribution | 2019-08-14 10:16:00 | 1976 | 14.3934 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-09-26 | 10:40 | 38.0157 | -122.6889 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | marin county fire | 102252082 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42639 | 10:40 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1005 | 2016 | 9 | 26 | 10 | 40 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 4.5159 | 126_240 | <25mph | <15mph | HFTD - Distribution | 2016-09-26 10:40:00 | 747 | 11.2091 | FALSE | <25mph | PG601 | 3.15 | 2019-10-17T10:40:00Z | 22.15 | 45 | < 25mph | PG493 | 4.03 | 2019-10-17T10:40:00Z | 25.34 | 126 | 25-40mph | PG601 | 3.15 | 2019-10-17T10:40:00Z | 22.15 | 89 | < 25mph | PG123 | 5.71 | 2019-10-17T11:30:00Z | 29.66 | 249 | 25-40mph
PG&E | 2016-08-31 | 2016-08-31 14:52 | 35.1918 | -120.4697 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101942860 |  | 12000 | Conductor | Overhead | Yes | 42613 | 2016-08-31 14:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0955 | 2016 | 8 | 31 | 14 | 52 | 16-0061423 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 156294 | 16.7717 | 224_84 | <25mph | <15mph | HFTD - Distribution | 2016-08-31 14:52:00 | 697 | 16.7717 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AU609 | 7.39 | 2016-07-08T09:59:00Z | 2.01 | 14 | < 25mph |  |  |  | 0 | 0 | No data | AU609 | 7.39 | 2016-07-08T11:29:00Z | 2.01 | 28 | < 25mph
PG&E | 2015-06-27 22:28 | 2015-06-27 22:28 | 38.1194 | -120.6218 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 101281699 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.9361 | 2015-06-27 22:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0417 | 2015 | 6 | 27 | 22 | 28 | 15-0043798 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 517 | 14.2862 | 216_246 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 22:28:00 | 162 | 15.5829 | FALSE | <25mph | C9085 | 3.92 | 2016-03-03T14:38:00Z | 0 | 4 | < 25mph | C9085 | 3.92 | 2016-03-03T14:38:00Z | 0 | 4 | < 25mph | C9085 | 3.92 | 2016-03-03T15:28:00Z | 0 | 7 | < 25mph | C9085 | 3.92 | 2016-03-03T15:28:00Z | 0 | 7 | < 25mph
PG&E | 2019-08-01 | 13:28 | 38.5721 | -120.6803 | Equipment Failure/Involved, Overhead | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 153662102 |  | 21000 | Conductor | Overhead | Yes | 43678 | 13:28 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-170 | 2019 | 8 | 1 | 13 | 28 | 19-0083500 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1374 | 13.6823 | 213_271 | <25mph | <15mph | HFTD - Distribution | 2019-08-01 13:28:00 | 1945 | 13.6823 | FALSE | <25mph | PG604 | 1.64 | 2019-10-22T05:20:00Z | 3.74 | 6 | < 25mph | PG433 | 7.73 | 2019-10-22T05:50:00Z | 11.48 | 36 | < 25mph | PG604 | 1.64 | 2019-10-22T05:20:00Z | 3.74 | 12 | < 25mph | PG433 | 7.73 | 2019-10-22T06:30:00Z | 15.35 | 72 | < 25mph
PG&E | 2015-07-01 12:57 | 2015-07-01 12:57 | 39.4146 | -121.379 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42186.5396 | 2015-07-01 12:57 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0434 | 2015 | 7 | 1 | 12 | 57 | 15-0044609 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 12.6482 | 183_317 | <25mph | <15mph | HFTD - Distribution | 2015-07-01 12:57:00 | 179 | 18.7031 | FALSE | <25mph | BNGC1 | 2.37 | 2017-09-20T22:51:00Z | 18.01 | 1 | < 25mph | TT309 | 4.14 | 2017-09-20T22:45:00Z | 18.99 | 2 | < 25mph | BNGC1 | 2.37 | 2017-09-20T22:51:00Z | 18.01 | 2 | < 25mph | TT309 | 4.14 | 2017-09-20T22:45:00Z | 18.99 | 4 | < 25mph
PG&E | 2017-08-28 | 9:14 | 38.7443 | -122.6491 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 103781085 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42975 | 9:14 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1356 | 2017 | 8 | 28 | 9 | 14 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 4.693 | 128_281 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 09:14:00 | 1094 | 16.6198 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LKRC1 | 6.54 | 2016-06-15T23:05:00Z | 20 | 5 | < 25mph |  |  |  | 0 | 0 | No data | LKRC1 | 6.54 | 2016-06-15T23:05:00Z | 20 | 10 | < 25mph
PG&E | 2019-05-31 | 15:25 | 40.4431 | -121.8211 |  | Hardwood Woodland | 1 meter - < 3 meters | Self Extinguished |  | 101556319 |  | 12000 | Conductor | Overhead | Yes | 43616 | 15:25 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-88 | 2019 | 5 | 31 | 15 | 25 | 19-0060901 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 55546 | 8.5736 | 165_374 | <25mph | <15mph | HFTD - Distribution | 2019-05-31 15:25:00 | 1795 | 18.5418 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-07-25 15:32 | 2016-07-25 15:32 | 38.3522 | -120.7107 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42576.6472 | 2016-07-25 15:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0878 | 2016 | 7 | 25 | 15 | 32 | 16-0052398 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 19951 | 10.4912 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-25 15:32:00 | 621 | 14.4675 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2017-11-18T20:56:00Z | 7 | 2 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2017-11-18T21:56:00Z | 8.99 | 4 | < 25mph
PG&E | 2019-07-23 | 16:55 | 37.2128 | -119.505 | Gun Shot | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | 252521103 |  | 12000 | Conductor | Overhead | Yes | 43669 | 16:55 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-434 | 2019 | 7 | 23 | 16 | 55 | 19-0080383 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 513358 | 13.6168 | 265_196 | <25mph | <15mph | HFTD - Distribution | 2019-07-23 16:55:00 | 1923 | 13.6168 | FALSE | <25mph | PG467 | 3.77 | 2019-10-30T10:30:00Z | 13.73 | 13 | < 25mph | SE370 | 7.71 | 2019-10-30T10:00:00Z | 15.7 | 49 | < 25mph | PG467 | 3.77 | 2019-10-30T10:30:00Z | 13.73 | 26 | < 25mph | SE370 | 7.71 | 2019-10-30T11:30:00Z | 16.51 | 97 | < 25mph
PG&E | 2017-12-19 | 19:45 | 40.7271 | -122.3263 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101457738 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43088 | 19:45 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1545 | 2017 | 12 | 19 | 19 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 12.0712 | 144_390 | <25mph | <15mph | HFTD - Distribution | 2017-12-19 19:45:00 | 1287 | 14.9625 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F0355 | 7.84 | 2017-07-17T07:41:00Z | 0 | 6 | < 25mph |  |  |  | 0 | 0 | No data | F0355 | 7.84 | 2017-07-17T08:01:00Z | 3 | 12 | < 25mph
PG&E | 2019-07-18 | 10:27 | 38.3033 | -120.6718 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | B561 |  | 12000 | Other | Overhead | Yes | 43664 | 10:27 | Equipment - PG&E | Other |  |  |  |  | Other/Unknown | 2019-68 | 2019 | 7 | 18 | 10 | 27 | 19-0078904 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45558 | 8.6789 | 214_256 | <25mph | <15mph | HFTD - Distribution | 2019-07-18 10:27:00 | 1910 | 16.0413 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG116 | 7.98 | 2019-01-22T20:20:00Z | 10.51 | 14 | < 25mph |  |  |  | 0 | 0 | No data | PG116 | 7.98 | 2019-01-22T21:40:00Z | 12.48 | 28 | < 25mph
PG&E | 2015-06-04 20:00 | 2015-06-04 20:00 | 38.6916 | -120.8606 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101412760 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42159.8333 | 2015-06-04 20:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0347 | 2015 | 6 | 4 | 20 | 0 | 15-0038597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 9640 | 2.0731 | 205_277 | <25mph | <15mph | HFTD - Distribution | 2015-06-04 20:00:00 | 93 | 11.0268 | FALSE | <25mph | E6490 | 1.72 | 2017-02-24T02:58:00Z | 0 | 38 | < 25mph | BENC1 | 8 | 2017-02-24T01:59:00Z | 10 | 70 | < 25mph | E6490 | 1.72 | 2017-02-24T03:59:00Z | 0 | 73 | < 25mph | BENC1 | 8 | 2017-02-24T01:59:00Z | 10 | 138 | < 25mph
PG&E | 2016-07-16 00:58 | 2016-07-16 00:58 | 36.4379 | -121.9198 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101669758 |  | 12000 | Other | Overhead | Yes | 42567.0403 | 2016-07-16 00:58 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0855 | 2016 | 7 | 16 | 0 | 58 | 16-0050335 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 8976 | 11.1025 | 159_153 | <25mph | <15mph | HFTD - Distribution | 2016-07-16 00:58:00 | 598 | 18.5622 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6019 | 7.86 | 2017-07-29T06:44:00Z | 4 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6019 | 7.86 | 2017-07-29T06:44:00Z | 4 | 8 | < 25mph
PG&E | 2017-08-06 11:38 | 11:38 | 36.5857 | -121.7121 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101747125 | Unknown | 12000 | Conductor | Overhead | Yes | 42953.4849 | 11:38 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1321 | 2017 | 8 | 6 | 11 | 38 | 17-0068279 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 87172 | 7.0101 | 168_161 | <25mph | <15mph | HFTD - Distribution | 2017-08-06 11:38:00 | 1059 | 12.123 | FALSE | <25mph | F1964 | 0.83 | 2019-01-02T04:45:00Z | 0 | 4 | < 25mph | PG206 | 6.5 | 2019-01-02T04:30:00Z | 6.8 | 26 | < 25mph | F1964 | 0.83 | 2019-01-02T05:45:00Z | 0 | 8 | < 25mph | E8875 | 7.87 | 2019-01-02T05:00:00Z | 7 | 51 | < 25mph
PG&E | 2015-11-21 10:36 | 2015-11-21 10:36 | 38.0679 | -120.1872 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101045952 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42329.4417 | 2015-11-21 10:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0677 | 2015 | 11 | 21 | 10 | 36 | 15-0079868 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18350 | 7.816 | 235_243 | <25mph | <15mph | HFTD - Distribution | 2015-11-21 10:36:00 | 421 | 16.6927 | FALSE | <25mph | MOUC1 | 3.29 | 2016-02-14T13:02:00Z | 20 | 1 | < 25mph | MOUC1 | 3.29 | 2016-02-14T13:02:00Z | 20 | 1 | < 25mph | MOUC1 | 3.29 | 2016-02-14T13:02:00Z | 20 | 2 | < 25mph | MOUC1 | 3.29 | 2016-02-14T13:02:00Z | 20 | 2 | < 25mph
PG&E | 2016-08-09 | 2016-08-09 19:21 | 38.9187 | -120.9525 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | El Dorado County FD | 100038028 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0915 | 2016 | 8 | 9 | 19 | 21 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.2678 | 201_290 | <25mph | <15mph | HFTD - Distribution | 2016-08-09 19:21:00 | 658 | 10.7446 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8862 | 6.76 | 2016-04-26T13:43:00Z | 8.99 | 17 | < 25mph |  |  |  | 0 | 0 | No data | D8862 | 6.76 | 2016-04-26T13:43:00Z | 8.99 | 34 | < 25mph
PG&E | 2017-07-16 11:59 | 11:59 | 36.6669 | -121.7515 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101761892 | None | 21000 | Fuse | Overhead | Yes | 42932.4994 | 11:59 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1259 | 2017 | 7 | 16 | 11 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 22.4318 | 166_166 | <25mph | <15mph | HFTD - Distribution | 2017-07-16 11:59:00 | 998 | 30.0095 | FALSE | 25-40mph | E4669 | 2.51 | 2015-01-10T12:51:00Z | 4.99 | 6 | < 25mph | E4669 | 2.51 | 2015-01-10T12:51:00Z | 4.99 | 6 | < 25mph | E4669 | 2.51 | 2015-01-10T13:31:00Z | 4.99 | 12 | < 25mph | E4669 | 2.51 | 2015-01-10T13:31:00Z | 4.99 | 12 | < 25mph
PG&E | 2017-06-30 01:20 | 01:20 | 39.821 | -121.5883 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103840463 | YES | 12000 | Conductor | Overhead | Yes | 42916.0559 | 01:20 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1210 | 2017 | 6 | 30 | 1 | 20 | 17-0059647 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 2888 | 7.4054 | 174_339 | <25mph | <15mph | HFTD - Distribution | 2017-06-30 01:20:00 | 948 | 9.8944 | FALSE | <25mph | C4565 | 1.69 | 2016-01-28T06:10:00Z | 2.01 | 13 | < 25mph | JBGC1 | 7.9 | 2016-01-28T06:13:00Z | 14.99 | 28 | < 25mph | E4833 | 1.34 | 2016-01-28T07:08:00Z | 3 | 24 | < 25mph | JBGC1 | 7.9 | 2016-01-28T07:13:00Z | 15.99 | 53 | < 25mph
PG&E | 2015-09-04 07:49 | 2015-09-04 07:49 | 40.2318 | -122.3643 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | E/O FRONTIER RD & N/O WAGON WAY |  | 12000 | Conductor | Overhead | Yes | 42251.3257 | 2015-09-04 07:49 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0577 | 2015 | 9 | 4 | 7 | 49 | 15-0059323 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 9563 | 2.343 | 142_362 | <25mph | <15mph | HFTD - Distribution | 2015-09-04 07:49:00 | 321 | 17.9748 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 5.07 | 2019-01-13T11:30:00Z | 0 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 5.07 | 2019-01-13T12:30:00Z | 0 | 8 | < 25mph
PG&E | 2018-06-15 | 2:56 | 37.4869 | -122.4223 | Vegetation | Rural | < 0.25 Acres | Utility: PG&E | N.A. | Pole 10/5 | None | 60000 | Conductor | Overhead | Yes | 43266 | 2:56 | Contamination | N.A. | N.A. | N.A. | Unknown |  | no-match | 1659 | 2018 | 6 | 15 | 2 | 56 | INT-11115 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 0 | 6.5721 | 137_211 | <25mph | <15mph | HFTD - Transmission | 2018-06-15 02:56:00 | 1401 | 18.0175 | FALSE | <25mph | PG056 | 3.55 | 2019-04-03T06:30:00Z | 14.92 | 7 | < 25mph | PG056 | 3.55 | 2019-04-03T06:30:00Z | 14.92 | 77 | < 25mph | PG056 | 3.55 | 2019-04-03T06:30:00Z | 14.92 | 15 | < 25mph | PG056 | 3.55 | 2019-04-03T06:30:00Z | 14.92 | 152 | < 25mph
PG&E | 2017-08-08 04:23 | 4:10 | 38.4949 | -122.6685 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 102025742 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42955.1829 | 4:10 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1325 | 2017 | 8 | 8 | 4 | 10 | 17-0068642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 2750 | 5.2658 | 127_267 | <25mph | <15mph | HFTD - Distribution | 2017-08-08 04:10:00 | 1062 | 14.7124 | FALSE | <25mph | RSAC1 | 2.6 | 2017-03-05T15:29:00Z | 7 | 25 | < 25mph | RSAC1 | 2.6 | 2017-03-05T15:29:00Z | 7 | 66 | < 25mph | RSAC1 | 2.6 | 2017-03-05T16:29:00Z | 8.99 | 50 | < 25mph | RSAC1 | 2.6 | 2017-03-05T16:29:00Z | 8.99 | 133 | < 25mph
PG&E | 2015-04-11 17:16 | 2015-04-11 17:16 | 40.5462 | -122.2343 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101491414 |  | 12000 | Conductor | Overhead | Yes | 42105.7194 | 2015-04-11 17:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0286 | 2015 | 4 | 11 | 17 | 16 | 15-0026023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 11914 | 19.429 | 148_380 | <25mph | <15mph | HFTD - Distribution | 2015-04-11 17:16:00 | 32 | 19.429 | FALSE | <25mph | RRAC1 | 3.7 | 2019-03-31T20:24:00Z | 8.01 | 1 | < 25mph | RRAC1 | 3.7 | 2019-03-31T20:24:00Z | 8.01 | 7 | < 25mph | RRAC1 | 3.7 | 2019-03-31T20:24:00Z | 8.01 | 2 | < 25mph | RRAC1 | 3.7 | 2019-03-31T20:24:00Z | 8.01 | 14 | < 25mph
PG&E | 2016-06-06 | 2016-06-06 19:48 | 38.9129 | -121.1192 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire/placer fire | 100050264 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42527 | 2016-06-06 19:48 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0775 | 2016 | 6 | 6 | 19 | 48 | 16-0041497 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 2039 | 14.8039 | 194_289 | <25mph | <15mph | HFTD - Distribution | 2016-06-06 19:48:00 | 518 | 15.3816 | FALSE | <25mph | D7393 | 3.4 | 2015-04-11T21:03:00Z | 10 | 11 | < 25mph | D7393 | 3.4 | 2015-04-11T21:03:00Z | 10 | 11 | < 25mph | D7393 | 3.4 | 2015-04-11T21:03:00Z | 10 | 21 | < 25mph | D7393 | 3.4 | 2015-04-11T21:03:00Z | 10 | 21 | < 25mph
PG&E | 2016-07-27 11:53 | 2016-07-27 11:53 | 37.8649 | -120.5134 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101041792 |  | 17000 | Conductor | Overhead | Yes | 42578.4951 | 2016-07-27 11:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0880 | 2016 | 7 | 27 | 11 | 53 | 16-0052942 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 14734 | 9.7065 | 221_232 | <25mph | <15mph | HFTD - Distribution | 2016-07-27 11:53:00 | 622 | 14.5426 | FALSE | <25mph | GNSC1 | 2.2 | 2017-12-13T22:03:00Z | 8.01 | 1 | < 25mph | GNSC1 | 2.2 | 2017-12-13T22:03:00Z | 8.01 | 8 | < 25mph | GNSC1 | 2.2 | 2017-12-13T22:03:00Z | 8.01 | 2 | < 25mph | GNSC1 | 2.2 | 2017-12-13T22:03:00Z | 8.01 | 15 | < 25mph
PG&E | 2015-04-27 12:54 | 2015-04-27 12:54 | 35.4871 | -120.6756 | Vegetation | Rural | < 3 meters | Unknown |  | 103310601 |  | 21000 | Conductor | Overhead | Yes | 42121.5375 | 2015-04-27 12:54 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0301 | 2015 | 4 | 27 | 12 | 54 | 15-0029875 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 5836 | 7.5834 | 214_100 | <25mph | <15mph | HFTD - Distribution | 2015-04-27 12:54:00 | 47 | 19.0974 | FALSE | <25mph | PG142 | 3.91 | 2019-02-23T23:30:00Z | 11.41 | 33 | < 25mph | PG191 | 4.86 | 2019-02-23T23:10:00Z | 15.57 | 52 | < 25mph | PG142 | 3.91 | 2019-02-23T23:30:00Z | 11.41 | 64 | < 25mph | TT469 | 7.86 | 2019-02-24T00:14:00Z | 15.99 | 103 | < 25mph
PG&E | 2017-07-30 09:47 | 09:46 | 38.9132 | -122.6179 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike wink | 102151066 | None | 0 – 750 | Conductor | Overhead | Yes | 42946.4075 | 09:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1302 | 2017 | 7 | 30 | 9 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.2785 | 130_290 | <25mph | <15mph | HFTD - Distribution | 2017-07-30 09:46:00 | 1040 | 13.7198 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 4.76 | 2015-01-27T03:57:00Z | 4 | 6 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 4.76 | 2015-01-27T03:57:00Z | 4 | 11 | < 25mph
PG&E | 2016-10-19 10:42 | 10:42 | 38.5098 | -122.45 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | st helena | 102242552 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42662.4459 | 10:42 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1040 | 2016 | 10 | 19 | 10 | 42 | 16-0073955 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 693 | 4.5329 | 137_268 | <25mph | <15mph | HFTD - Distribution | 2016-10-19 10:42:00 | 781 | 13.4953 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AT925 | 4.5 | 2015-09-17T00:55:00Z | 4.99 | 8 | < 25mph |  |  |  | 0 | 0 | No data | AT925 | 4.5 | 2015-09-17T00:55:00Z | 4.99 | 8 | < 25mph
PG&E | 2015-08-03 00:07 | 2015-08-03 00:07 | 40.5056 | -122.347 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | COTTONWOOD FIRE DEPT | 101503428 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42219.0049 | 2015-08-03 00:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0509 | 2015 | 8 | 3 | 0 | 7 | 15-0052184 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 10427 | 9.7241 | 143_378 | <25mph | <15mph | HFTD - Distribution | 2015-08-03 00:07:00 | 254 | 13.2206 | FALSE | <25mph | D1852 | 2.41 | 2015-01-23T17:58:00Z | 0 | 7 | < 25mph | C5599 | 6.84 | 2015-01-23T18:04:00Z | 15.99 | 19 | < 25mph | D1852 | 2.41 | 2015-01-23T19:01:00Z | 0 | 14 | < 25mph | C5599 | 6.84 | 2015-01-23T18:34:00Z | 20 | 38 | < 25mph
PG&E | 2017-10-11 | 11:57 | 38.5015 | -123.0237 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101974930 | Unknown | 12000 | Conductor | Overhead | Yes | 43019 | 11:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1484 | 2017 | 10 | 11 | 11 | 57 | 17-0086350 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 226925 | 16.5068 | 112_268 | <25mph | <15mph | HFTD - Distribution | 2017-10-11 11:57:00 | 1227 | 19.0479 | FALSE | <25mph | D3481 | 2.38 | 2015-07-06T12:37:00Z | 4.99 | 31 | < 25mph | D3481 | 2.38 | 2015-07-06T12:37:00Z | 4.99 | 31 | < 25mph | D3481 | 2.38 | 2015-07-06T13:52:00Z | 4.99 | 60 | < 25mph | D3481 | 2.38 | 2015-07-06T13:52:00Z | 4.99 | 60 | < 25mph
PG&E | 2017-08-14 07:56 | 07:56 | 39.1794 | -120.9761 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100083743 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42961.3308 | 07:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1334 | 2017 | 8 | 14 | 7 | 56 | 17-0070063 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3012 | 6.4958 | 200_304 | <25mph | <15mph | HFTD - Distribution | 2017-08-14 07:56:00 | 1071 | 15.2686 | FALSE | <25mph | D8321 | 3.61 | 2015-04-13T12:30:00Z | 3 | 18 | < 25mph | E5439 | 6.04 | 2015-04-13T13:05:00Z | 4.99 | 57 | < 25mph | D8321 | 3.61 | 2015-04-13T12:30:00Z | 3 | 36 | < 25mph | E5439 | 6.04 | 2015-04-13T13:40:00Z | 7 | 114 | < 25mph
PG&E | 2018-08-08 | 16:02 | 36.4703 | -121.7143 | Vegetation | Rural | < 3 meters | Customer | N.A. | 103910535 | None | 12000 | Conductor | Overhead | Yes | 43320 | 16:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1830 | 2018 | 8 | 8 | 16 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 14.7322 | 168_155 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:02:00 | 1569 | 15.5625 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F1964 | 7.27 | 2018-08-16T02:50:00Z | 8.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | F1964 | 7.27 | 2018-08-16T02:50:00Z | 8.99 | 8 | < 25mph
PG&E | 2015-06-12 13:07 | 2015-06-12 13:07 | 40.4077 | -122.4104 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS STREET FROM 4139 OLD HAPPY VALLEY RD |  | 12000 | Lightning Arrestor | Overhead | No |  |  | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | no-match | 0378 | 2015 | 6 | 12 | 13 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Lightning Arrestor | N.A. | 9.7698 | 140_372 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 13:07:00 | 124 | 24.3549 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6886 | 5.64 | 2016-12-22T14:12:00Z | 2.01 | 7 | < 25mph |  |  |  | 0 | 0 | No data | E6886 | 5.64 | 2016-12-22T14:42:00Z | 2.01 | 13 | < 25mph
PG&E | 2015-04-30 00:26 | 2015-04-30 00:26 | 37.2401 | -122.2472 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 1145 VERDE R |  | 12000 | Conductor | Overhead | Yes | 42124.0181 | 2015-04-30 00:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0304 | 2015 | 4 | 30 | 0 | 26 | 15-0030607 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1256 | 5.7566 | 145_197 | <25mph | <15mph | HFTD - Distribution | 2015-04-30 00:26:00 | 50 | 15.5915 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.52 | 2017-05-16T07:07:00Z | 5.99 | 13 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.52 | 2017-05-16T08:07:00Z | 13 | 26 | < 25mph
PG&E | 2017-10-16 | 12:26 | 36.6641 | -121.0995 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Nick Shawkey E4462 209-402-1645 Cover Engine from Tuolumne Calaveras Unit | 101689865 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43024 | 12:26 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1495 | 2017 | 10 | 16 | 12 | 26 | 17-0087754 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 519 | 1.3904 | 195_165 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:26:00 | 1238 | 14.8173 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1697 | 6.85 | 2017-01-25T22:21:00Z | 5.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E1697 | 6.85 | 2017-01-25T22:51:00Z | 7 | 7 | < 25mph
PG&E | 2016-07-29 | 18:16 | 38.5769 | -122.6187 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Selma Fire Department |  |  | 12000 | Conductor | Overhead | Yes | 42580 | 18:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0890 | 2016 | 7 | 29 | 18 | 16 | 16-0053726 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 177834 | 13.7145 | 130_271 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 18:16:00 | 635 | 15.1116 | FALSE | <25mph | E2050 | 1.89 | 2016-04-06T14:59:00Z | 14 | 20 | < 25mph | E2050 | 1.89 | 2016-04-06T14:59:00Z | 14 | 28 | < 25mph | E2050 | 1.89 | 2016-04-06T15:59:00Z | 14.99 | 40 | < 25mph | E2050 | 1.89 | 2016-04-06T15:59:00Z | 14.99 | 56 | < 25mph
PG&E | 2017-07-22 12:26 | 12:25 | 40.8795 | -123.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Josh , comander chief of forest service. | 100980577 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.518 | 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1279 | 2017 | 7 | 22 | 12 | 25 | 17-0064721 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 23227 | 10.7493 | 84_399 | <25mph | <15mph | HFTD - Distribution | 2017-07-22 12:25:00 | 1018 | 13.5476 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BHTC1 | 5.5 | 2019-04-19T05:46:00Z | 8.99 | 13 | < 25mph |  |  |  | 0 | 0 | No data | BHTC1 | 5.5 | 2019-04-19T05:46:00Z | 8.99 | 26 | < 25mph
PG&E | 2017-06-30 23:55 | 23:54 | 38.5794 | -122.8835 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 101958804 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42916.9965 | 23:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1211 | 2017 | 6 | 30 | 23 | 54 | 17-0059922 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2025 | 14.1552 | 118_272 | <25mph | <15mph | HFTD - Distribution | 2017-06-30 23:54:00 | 950 | 23.4555 | FALSE | <25mph | R08WW | 2.5 | 2017-09-14T03:00:00Z | 7.2 | 9 | < 25mph | RVOWW | 6.37 | 2017-09-14T03:00:00Z | 8.81 | 41 | < 25mph | R08WW | 2.5 | 2017-09-14T04:00:00Z | 8.21 | 18 | < 25mph | R30WW | 5.58 | 2017-09-14T04:00:00Z | 8.9 | 82 | < 25mph
PG&E | 2015-07-07 15:27 | 2015-07-07 15:27 | 35.155 | -120.5442 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 303corraltos cyn rd | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42192.6438 | 2015-07-07 15:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0449 | 2015 | 7 | 7 | 15 | 27 | 15-0046127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 98566 | 24.1391 | 220_82 | <25mph | <15mph | HFTD - Distribution | 2015-07-07 15:27:00 | 194 | 24.1391 | FALSE | <25mph | C9687 | 1.46 | 2019-10-21T18:00:00Z | 23 | 39 | < 25mph | KSBP | 7.64 | 2019-10-21T17:56:00Z | 31.07 | 64 | 25-40mph | C9687 | 1.46 | 2019-10-21T18:00:00Z | 23 | 73 | < 25mph | KSBP | 7.64 | 2019-10-21T17:56:00Z | 31.07 | 122 | 25-40mph
PG&E | 2019-05-17 | 15:12 | 38.4797 | -123.1486 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 42811111 |  | 12000 | Conductor | Overhead | Yes | 43602 | 15:12 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-200 | 2019 | 5 | 17 | 15 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 19.5511 | 107_266 | <25mph | <15mph | HFTD - Distribution | 2019-05-17 15:12:00 | 1775 | 20.334 | FALSE | <25mph | PG556 | 1.84 | 2019-12-22T08:10:00Z | 22.64 | 10 | < 25mph | PG257 | 5.68 | 2019-12-22T08:10:00Z | 26.37 | 22 | 25-40mph | PG556 | 1.84 | 2019-12-22T09:00:00Z | 27.25 | 20 | 25-40mph | PG560 | 6.79 | 2019-12-22T09:10:00Z | 31.41 | 44 | 25-40mph
PG&E | 2015-06-04 13:17 | 2015-06-04 13:17 | 39.2694 | -123.7841 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42159.5535 | 2015-06-04 13:17 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0344 | 2015 | 6 | 4 | 13 | 17 | 15-0038501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20525 | 22.1312 | 81_311 | <25mph | <15mph | HFTD - Distribution | 2015-06-04 13:17:00 | 90 | 22.6218 | FALSE | <25mph | E6025 | 1.61 | 2016-04-08T09:15:00Z | 0 | 4 | < 25mph | E6025 | 1.61 | 2016-04-08T09:15:00Z | 0 | 4 | < 25mph | E6025 | 1.61 | 2016-04-08T10:15:00Z | 0 | 8 | < 25mph | E6025 | 1.61 | 2016-04-08T10:15:00Z | 0 | 8 | < 25mph
PG&E | 2017-07-30 09:47 | 09:46 | 38.9132 | -122.6179 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike wink | 102151066 | None | 0 – 750 | Conductor | Overhead | Yes | 42946.4075 | 09:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1302 | 2017 | 7 | 30 | 9 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.2785 | 130_290 | <25mph | <15mph | HFTD - Distribution | 2017-07-30 09:46:00 | 1040 | 13.7198 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 4.76 | 2017-08-21T08:57:00Z | 5.99 | 9 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 4.76 | 2017-08-21T08:57:00Z | 5.99 | 18 | < 25mph
PG&E | 2019-07-22 | 21:39 | 38.8618 | -121.1044 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 152561103 |  | 12000 | Conductor | Overhead | Yes | 43668 | 21:39 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-336 | 2019 | 7 | 22 | 21 | 39 | 19-0080025 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 9842 | 9.5984 | 195_286 | <25mph | <15mph | HFTD - Distribution | 2019-07-22 21:39:00 | 1921 | 13.5446 | FALSE | <25mph | D8862 | 2.4 | 2016-02-28T23:41:00Z | 7 | 10 | < 25mph | PLTC1 | 5.53 | 2016-02-28T23:56:00Z | 8.99 | 15 | < 25mph | D8862 | 2.4 | 2016-02-28T23:41:00Z | 7 | 20 | < 25mph | PLTC1 | 5.53 | 2016-02-29T00:56:00Z | 10 | 32 | < 25mph
PG&E | 2016-05-15 15:54 | 2016-05-15 15:54 | 36.7948 | -119.3966 | Vegetation | RURAL | 100 - 299 Acres | Fire Agency | Cal Fire | 100729685 | None | 12000 | Conductor | Overhead | Yes | 42505.6625 | 2016-05-15 15:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0730 | 2016 | 5 | 15 | 15 | 54 | 16-0036136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 180310 | 10.5903 | 270_173 | <25mph | <15mph | HFTD - Distribution | 2016-05-15 15:54:00 | 474 | 14.7659 | FALSE | <25mph |  |  |  | 0 | 0 | No data | FCHC1 | 7.54 | 2017-11-02T07:00:00Z | 4.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | FCHC1 | 7.54 | 2017-11-02T08:00:00Z | 4.99 | 2 | < 25mph
PG&E | 2018-09-10 | 20:37 | 38.0188 | -122.7225 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 102252760 | Unknown | 12000 | Conductor | Overhead | Yes | 43353 | 20:37 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1889 | 2018 | 9 | 10 | 20 | 37 | 18-0078359 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 219903 | 12.2581 | 125_241 | <25mph | <15mph | HFTD - Distribution | 2018-09-10 20:37:00 | 1628 | 18.8462 | FALSE | <25mph | PG041 | 2.1 | 2018-12-11T13:10:00Z | 3.06 | 7 | < 25mph | PG123 | 7.3 | 2018-12-11T13:20:00Z | 13.8 | 56 | < 25mph | PG041 | 2.1 | 2018-12-11T13:10:00Z | 3.06 | 14 | < 25mph | PG133 | 5.41 | 2018-12-11T14:30:00Z | 15.57 | 111 | < 25mph
PG&E | 2015-12-08 12:41 | 2015-12-08 12:41 | 38.2489 | -120.5228 | Other | Rural | Structure Only | Unknown |  | 7026 Railroad Flat Road, Mountain Ranch |  | 12000 | Conductor | Overhead | Yes | 42346.5285 | 2015-12-08 12:41 | Contact From Object | N.A. | Other | Electric Facility | Human Error | AT&T work error | Other/Unknown | 0684 | 2015 | 12 | 8 | 12 | 41 | 15-0083435 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1120 | 3.9918 | 220_253 | <25mph | <15mph | HFTD - Distribution | 2015-12-08 12:41:00 | 428 | 10.4116 | FALSE | <25mph | ESPC1 | 3.04 | 2015-03-22T02:13:00Z | 8.01 | 7 | < 25mph | ESPC1 | 3.04 | 2015-03-22T02:13:00Z | 8.01 | 7 | < 25mph | ESPC1 | 3.04 | 2015-03-22T02:13:00Z | 8.01 | 14 | < 25mph | ESPC1 | 3.04 | 2015-03-22T02:13:00Z | 8.01 | 14 | < 25mph
PG&E | 2019-06-06 | 20:30 | 38.4969 | -122.6435 |  | Barren/Other | < 1 meter | Self Extinguished |  | Unknown |  | 230000 | Circuit Breaker | Overhead | Yes | 43622 | 20:30 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | no-match | 2019-102 | 2019 | 6 | 6 | 20 | 30 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 16.883 | 129_267 | <25mph | <15mph | HFTD - Transmission | 2019-06-06 20:30:00 | 1804 | 23.129 | FALSE | <25mph | RSAC1 | 3.91 | 2017-10-20T05:29:00Z | 34 | 11 | 25-40mph | RSAC1 | 3.91 | 2017-10-20T05:29:00Z | 34 | 36 | 25-40mph | RSAC1 | 3.91 | 2017-10-20T05:29:00Z | 34 | 22 | 25-40mph | RSAC1 | 3.91 | 2017-10-20T05:29:00Z | 34 | 72 | 25-40mph
PG&E | 2015-07-12 17:04 | 2015-07-12 17:04 | 37.4713 | -122.4256 | Vegetation | Rural | < 0.25 Acres | Fire Agency | COUNTY FIRE | 1 s w c509 |  | 12000 | Conductor | Overhead | Yes | 42197.7111 | 2015-07-12 17:04 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown | Jumper | Other/Unknown | 0456 | 2015 | 7 | 12 | 17 | 4 | 15-0047023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 117853 | 14.8289 | 137_210 | <25mph | <15mph | HFTD - Distribution | 2015-07-12 17:04:00 | 201 | 14.9925 | FALSE | <25mph | D9259 | 3.49 | 2015-12-14T14:50:00Z | 4.99 | 4 | < 25mph | KHAF | 5 | 2015-12-14T14:55:00Z | 26.46 | 60 | 25-40mph | D9259 | 3.49 | 2015-12-14T14:50:00Z | 4.99 | 8 | < 25mph | KHAF | 5 | 2015-12-14T16:35:00Z | 27.63 | 120 | 25-40mph
PG&E | 2017-08-02 | 9:42 | 39.2274 | -123.1081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 5/0 | None | 60000 | Conductor | Overhead | Yes | 42949 | 9:42 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1307 | 2017 | 8 | 2 | 9 | 42 | INT-09925 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 4.0697 | 109_308 | <25mph | <15mph | HFTD - Transmission | 2017-08-02 09:42:00 | 1047 | 15.4312 | FALSE | <25mph |  |  |  | 0 | 0 | No data | COWC1 | 7.26 | 2015-02-28T08:01:00Z | 27 | 14 | 25-40mph |  |  |  | 0 | 0 | No data | COWC1 | 7.26 | 2015-02-28T08:01:00Z | 27 | 27 | 25-40mph
PG&E | 2017-05-15 16:14 | 16:00 | 37.1766 | -119.8189 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SHAUN FAIRBANKS 559-683-4823 | 101108423 | SIERRA | 21000 | Conductor | Overhead | Yes | 42870.6767 | 16:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1099 | 2017 | 5 | 15 | 16 | 0 | 17-0048096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20007 | 15.7465 | 251_194 | <25mph | <15mph | HFTD - Distribution | 2017-05-15 16:00:00 | 839 | 20.7849 | FALSE | <25mph | PG434 | 1.78 | 2019-10-22T11:00:00Z | 8.25 | 6 | < 25mph | PG434 | 1.78 | 2019-10-22T11:00:00Z | 8.25 | 42 | < 25mph | PG434 | 1.78 | 2019-10-22T11:00:00Z | 8.25 | 12 | < 25mph | PG434 | 1.78 | 2019-10-22T11:00:00Z | 8.25 | 84 | < 25mph
PG&E | 2017-11-29 17:35 | 17:34 | 38.6841 | -120.6546 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 101419450 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 43068.7326 | 17:34 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1533 | 2017 | 11 | 29 | 17 | 34 | 17-0098456 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 582825 | 2.2539 | 214_277 | <25mph | <15mph | HFTD - Distribution | 2017-11-29 17:34:00 | 1275 | 13.1335 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GZFC1 | 7.93 | 2017-11-17T16:17:00Z | 4 | 8 | < 25mph |  |  |  | 0 | 0 | No data | GZFC1 | 7.93 | 2017-11-17T16:17:00Z | 4 | 16 | < 25mph
PG&E | 2019-06-08 | 18:51 | 38.6105 | -122.9732 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 42751113 |  | 12000 | Conductor | Overhead | Yes | 43624 | 18:51 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-355 | 2019 | 6 | 8 | 18 | 51 | 19-0064689 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 44664 | 14.8219 | 114_273 | <25mph | <15mph | HFTD - Distribution | 2019-06-08 18:51:00 | 1812 | 19.8533 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG243 | 5.7 | 2019-07-08T09:10:00Z | 10.09 | 46 | < 25mph |  |  |  | 0 | 0 | No data | PG243 | 5.7 | 2019-07-08T09:10:00Z | 10.09 | 90 | < 25mph
PG&E | 2018-06-15 | 9:51 | 37.1986 | -119.4709 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RANCHARIA ENGINE 4255 USFS ENG 52 | 101058060 | Unknown | 12000 | Conductor | Overhead | Yes | 43266 | 9:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1660 | 2018 | 6 | 15 | 9 | 51 | 18-0051354 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 35146 | 7.0865 | 267_195 | <25mph | <15mph | HFTD - Distribution | 2018-06-15 09:51:00 | 1402 | 16.2916 | FALSE | <25mph | NFRC1 | 3.06 | 2017-05-12T07:55:00Z | 4.99 | 3 | < 25mph | NFRC1 | 3.06 | 2017-05-12T07:55:00Z | 4.99 | 3 | < 25mph | NFRC1 | 3.06 | 2017-05-12T08:55:00Z | 4.99 | 6 | < 25mph | NFRC1 | 3.06 | 2017-05-12T08:55:00Z | 4.99 | 6 | < 25mph
PG&E | 2016-08-17 | 2016-08-17 12:23 | 41.2495 | -123.7671 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103315791 |  | 12000 | Conductor | Overhead | Yes | 42599 | 2016-08-17 12:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0932 | 2016 | 8 | 17 | 12 | 23 | 16-0058002 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 16544 | 13.4388 | 84_420 | <25mph | <15mph | HFTD - Distribution | 2016-08-17 12:23:00 | 675 | 14.3475 | FALSE | <25mph |  |  |  | 0 | 0 | No data | NTCC1 | 5.46 | 2017-11-24T17:45:00Z | 4.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | NTCC1 | 5.46 | 2017-11-24T18:45:00Z | 7 | 2 | < 25mph
PG&E | 2019-07-18 | 10:27 | 38.3033 | -120.6718 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | B561 |  | 12000 | Other | Overhead | Yes | 43664 | 10:27 | Equipment - PG&E | Other |  |  |  |  | Other/Unknown | 2019-68 | 2019 | 7 | 18 | 10 | 27 | 19-0078904 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45558 | 8.6789 | 214_256 | <25mph | <15mph | HFTD - Distribution | 2019-07-18 10:27:00 | 1910 | 16.0413 | FALSE | <25mph | PG372 | 0.86 | 2019-09-09T01:40:00Z | 9.57 | 12 | < 25mph | TS389 | 7.11 | 2019-09-09T01:53:00Z | 14 | 51 | < 25mph | PG372 | 0.86 | 2019-09-09T01:40:00Z | 9.57 | 24 | < 25mph | TS389 | 7.11 | 2019-09-09T02:53:00Z | 14.99 | 102 | < 25mph
PG&E | 2016-07-28 13:19 | 2016-07-28 13:19 | 39.7127 | -123.4973 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102195566 |  | 12000 | Conductor | Overhead | Yes | 42579.5549 | 2016-07-28 13:19 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0886 | 2016 | 7 | 28 | 13 | 19 | 16-0053369 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 4447 | 11.1949 | 93_335 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 13:19:00 | 629 | 12.238 | FALSE | <25mph | LAYC1 | 0.97 | 2015-06-28T16:29:00Z | 4 | 1 | < 25mph | LAYC1 | 0.97 | 2015-06-28T16:29:00Z | 4 | 1 | < 25mph | LAYC1 | 0.97 | 2015-06-28T17:29:00Z | 8.01 | 2 | < 25mph | LAYC1 | 0.97 | 2015-06-28T17:29:00Z | 8.01 | 2 | < 25mph
PG&E | 2015-07-15 09:00 | 2015-07-15 09:00 | 36.997 | -121.7381 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101795728 |  | 21000 | Conductor | Overhead | Yes | 42200.375 | 2015-07-15 09:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0463 | 2015 | 7 | 15 | 9 | 0 | 15-0047650 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3800 | 8.5113 | 167_184 | <25mph | <15mph | HFTD - Distribution | 2015-07-15 09:00:00 | 208 | 13.379 | FALSE | <25mph | CTOC1 | 3.71 | 2015-08-20T22:27:00Z | 10 | 1 | < 25mph | C4503 | 7.38 | 2015-08-20T23:10:00Z | 14.99 | 32 | < 25mph | CTOC1 | 3.71 | 2015-08-20T22:27:00Z | 10 | 2 | < 25mph | C4503 | 7.38 | 2015-08-20T23:30:00Z | 14.99 | 58 | < 25mph
PG&E | 2015-08-31 14:28 | 2015-08-31 14:28 | 36.5325 | -121.1462 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 29401 Hwy 25 |  | 21000 | Conductor | Overhead | Yes | 42247.6028 | 2015-08-31 14:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0568 | 2015 | 8 | 31 | 14 | 28 | 15-0058455 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25668 | 4.8975 | 193_158 | <25mph | <15mph | HFTD - Distribution | 2015-08-31 14:28:00 | 312 | 19.6836 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.27 | 2015-09-13T16:37:00Z | 4 | 1 | < 25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.27 | 2015-09-13T17:37:00Z | 7 | 2 | < 25mph
PG&E | 2017-07-04 20:17 | 20:16 | 40.4228 | -122.3975 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SCOTT CORN 530-448-2414 | 101481860 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42920.8451 | 20:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1221 | 2017 | 7 | 4 | 20 | 16 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 13.3568 | 141_373 | <25mph | <15mph | HFTD - Distribution | 2017-07-04 20:16:00 | 960 | 18.8443 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6886 | 4.89 | 2015-08-15T01:20:00Z | 7 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6886 | 4.89 | 2015-08-15T01:20:00Z | 7 | 8 | < 25mph
PG&E | 2017-06-10 07:38 | 07:37 | 35.4359 | -120.4957 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101890429 | Unknown | 21000 | Conductor | Overhead | Yes | 42896.3177 | 07:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1140 | 2017 | 6 | 10 | 7 | 37 | 17-0054182 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 34397 | 9.2577 | 222_98 | <25mph | <15mph | HFTD - Distribution | 2017-06-10 07:37:00 | 879 | 18.05 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2260 | 7.67 | 2016-10-25T06:46:00Z | 2.01 | 7 | < 25mph |  |  |  | 0 | 0 | No data | E2260 | 7.67 | 2016-10-25T07:49:00Z | 3 | 14 | < 25mph
PG&E | 2018-07-17 | 11:58 | 37.2217 | -121.6778 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Luis Morado state arson fire fighter | 100601345 | Unknown | 12000 | Conductor | Overhead | Yes | 43298 | 11:58 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1756 | 2018 | 7 | 17 | 11 | 58 | 18-0060617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 5865 | 5.1834 | 170_196 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 11:58:00 | 1496 | 14.408 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C7794 | 7.07 | 2019-07-19T07:30:00Z | 8.99 | 21 | < 25mph |  |  |  | 0 | 0 | No data | C7794 | 7.07 | 2019-07-19T07:30:00Z | 8.99 | 43 | < 25mph
PG&E | 2017-10-16 | 12:10 | 36.5831 | -121.9368 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101781248 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43024 | 12:10 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | Other/Unknown | 1493 | 2017 | 10 | 16 | 12 | 10 | 17-0087767 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 6313 | 5.0415 | 158_161 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:10:00 | 1236 | 13.6905 | FALSE | <25mph | E6407 | 2.44 | 2018-10-25T10:13:00Z | 4.99 | 37 | < 25mph | E6407 | 2.44 | 2018-10-25T10:13:00Z | 4.99 | 39 | < 25mph | E6407 | 2.44 | 2018-10-25T10:13:00Z | 4.99 | 74 | < 25mph | E8875 | 5.44 | 2018-10-25T11:00:00Z | 4.99 | 80 | < 25mph
PG&E | 2018-11-10 | 13:31 | 37.0467 | -121.9853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101671641 | Unknown | 21000 | Conductor | Overhead | Yes | 43414 | 13:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1966 | 2018 | 11 | 10 | 13 | 31 | 18-0098856 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 1482 | 7.3629 | 156_187 | <25mph | <15mph | HFTD - Distribution | 2018-11-10 13:31:00 | 1706 | 13.8913 | FALSE | <25mph | E9039 | 2.83 | 2018-01-26T21:50:00Z | 10 | 48 | < 25mph | F0794 | 7.61 | 2018-01-26T21:49:00Z | 10 | 168 | < 25mph | E5965 | 2.24 | 2018-01-26T22:11:00Z | 12.01 | 87 | < 25mph | C8539 | 5.67 | 2018-01-26T22:46:00Z | 13 | 320 | < 25mph
PG&E | 2018-09-02 | 15:36 | 37.4714 | -122.4248 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Arie Delay 659-740-4636 | 103808872 | Unknown | 12000 | Capacitor Bank | Overhead | Yes | 43345 | 15:36 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1876 | 2018 | 9 | 2 | 15 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 11.73 | 137_210 | <25mph | <15mph | HFTD - Distribution | 2018-09-02 15:36:00 | 1615 | 13.6047 | FALSE | <25mph | D9259 | 3.46 | 2017-07-22T21:17:00Z | 10 | 4 | < 25mph | MBWC1 | 6.8 | 2017-07-22T21:00:00Z | 15.99 | 51 | < 25mph | D9259 | 3.46 | 2017-07-22T21:17:00Z | 10 | 8 | < 25mph | MBWC1 | 6.8 | 2017-07-22T22:00:00Z | 15.99 | 107 | < 25mph
PG&E | 2019-04-28 | 12:36 | 39.6756 | -121.5677 |  | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 100404366 |  | 12000 | Conductor | Overhead | Yes | 43583 | 12:36 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-166 | 2019 | 4 | 28 | 12 | 36 | 19-0046853 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 79810 | 6.7497 | 175_331 | <25mph | <15mph | HFTD - Distribution | 2019-04-28 12:36:00 | 1752 | 11.2512 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JBGC1 | 5.9 | 2019-01-02T08:13:00Z | 35.99 | 9 | 25-40mph |  |  |  | 0 | 0 | No data | JBGC1 | 5.9 | 2019-01-02T08:13:00Z | 35.99 | 18 | 25-40mph
PG&E | 2018-09-02 | 15:36 | 37.4714 | -122.4248 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Arie Delay 659-740-4636 | 103808872 | Unknown | 12000 | Capacitor Bank | Overhead | Yes | 43345 | 15:36 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1876 | 2018 | 9 | 2 | 15 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 11.73 | 137_210 | <25mph | <15mph | HFTD - Distribution | 2018-09-02 15:36:00 | 1615 | 13.6047 | FALSE | <25mph | D9259 | 3.46 | 2017-10-25T21:15:00Z | 4.99 | 4 | < 25mph | AV272 | 5.7 | 2017-10-25T21:26:00Z | 14 | 62 | < 25mph | D9259 | 3.46 | 2017-10-25T22:00:00Z | 7 | 8 | < 25mph | AV272 | 5.7 | 2017-10-25T21:26:00Z | 14 | 127 | < 25mph
PG&E | 2015-06-08 14:18 | 2015-06-08 14:18 | 38.1796 | -120.959 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 102048579 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42163.5958 | 2015-06-08 14:18 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0360 | 2015 | 6 | 8 | 14 | 18 | 15-0039368 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 65168 | 7.0021 | 201_249 | <25mph | <15mph | HFTD - Distribution | 2015-06-08 14:18:00 | 106 | 9.7763 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CMAC1 | 5.88 | 2016-05-14T19:59:00Z | 11.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CMAC1 | 5.88 | 2016-05-14T20:59:00Z | 11.01 | 2 | < 25mph
PG&E | 2017-10-02 | 14:56 | 38.9102 | -120.9185 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100110800 | None | 21000 | Other | Overhead | Yes | 43010 | 14:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1447 | 2017 | 10 | 2 | 14 | 56 | 17-0083516 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 160 | 17.2967 | 203_289 | <25mph | <15mph | HFTD - Distribution | 2017-10-02 14:56:00 | 1185 | 22.7009 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.3 | 2017-06-29T00:56:00Z | 8.99 | 20 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.3 | 2017-06-29T00:56:00Z | 8.99 | 39 | < 25mph
PG&E | 2017-06-22 17:54 | 18:07 | 38.7583 | -120.7176 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101401088 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.7461 | 18:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1188 | 2017 | 6 | 22 | 18 | 7 | 17-0057857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 8517 | 11.5365 | 212_281 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 18:07:00 | 927 | 16.1873 | FALSE | <25mph | E5691 | 3.88 | 2016-07-20T11:17:00Z | 3 | 25 | < 25mph | E5691 | 3.88 | 2016-07-20T11:17:00Z | 3 | 37 | < 25mph | E5691 | 3.88 | 2016-07-20T12:02:00Z | 3 | 54 | < 25mph | E5691 | 3.88 | 2016-07-20T12:02:00Z | 3 | 78 | < 25mph
PG&E | 2018-07-09 | 7:27 | 35.0785 | -120.3948 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101861366 | Unknown | 12000 | Conductor | Overhead | Yes | 43290 | 7:27 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1735 | 2018 | 7 | 9 | 7 | 27 | 18-0057904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 21045 | 9.782 | 227_78 | <25mph | <15mph | HFTD - Distribution | 2018-07-09 07:27:00 | 1475 | 17.5911 | FALSE | <25mph | AU609 | 1.69 | 2019-06-13T08:16:00Z | 0 | 4 | < 25mph | PG168 | 5.21 | 2019-06-13T07:30:00Z | 4.16 | 16 | < 25mph | AU609 | 1.69 | 2019-06-13T09:16:00Z | 0 | 8 | < 25mph | PG168 | 5.21 | 2019-06-13T08:40:00Z | 4.38 | 32 | < 25mph
PG&E | 2019-07-01 | 2:15 | 38.2955 | -120.8335 |  | Shrub | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-252 | 2019 | 7 | 1 | 2 | 15 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.9479 | 207_255 | <25mph | <15mph | HFTD - Distribution | 2019-07-01 02:15:00 | 1878 | 14.184 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.85 | 2018-01-06T00:05:00Z | 8.99 | 14 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.85 | 2018-01-06T01:05:00Z | 10 | 30 | < 25mph
PG&E | 2018-11-17 | 17:20 | 38.7082 | -120.6927 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101421319 | Unknown | 12000 | Conductor | Overhead | Yes | 43421 | 17:20 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1977 | 2018 | 11 | 17 | 17 | 20 | 18-0100697 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 35749 | 6.6792 | 213_278 | <25mph | <15mph | HFTD - Distribution | 2018-11-17 17:20:00 | 1717 | 12.841 | FALSE | <25mph | E4543 | 3.98 | 2015-11-03T13:03:00Z | 0 | 4 | < 25mph | E3165 | 7.06 | 2015-11-03T12:56:00Z | 2.01 | 26 | < 25mph | E4543 | 3.98 | 2015-11-03T14:04:00Z | 0 | 8 | < 25mph | E5691 | 6.11 | 2015-11-03T13:50:00Z | 5.99 | 52 | < 25mph
PG&E | 2019-09-27 | 10:30 | 36.5336 | -121.1464 | Vegetation | Barren/Other | 0.25 - 10 Acres | Cal Fire |  | 182492105 |  | 21000 | Conductor | Overhead | Yes | 43735 | 10:30 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-359 | 2019 | 9 | 27 | 10 | 30 | 19-0104536 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20631 | 5.3593 | 193_158 | <25mph | <15mph | HFTD - Distribution | 2019-09-27 10:30:00 | 2062 | 16.3021 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.34 | 2019-04-06T10:37:00Z | 4 | 1 | < 25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.34 | 2019-04-06T10:37:00Z | 4 | 2 | < 25mph
PG&E | 2017-07-16 12:10 | 12:10 | 35.6613 | -120.922 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101942626 | Unknown | 21000 | Conductor | Overhead | Yes | 42932.5072 | 12:10 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1260 | 2017 | 7 | 16 | 12 | 10 | 17-0063242 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 1304 | 7.6377 | 203_110 | <25mph | <15mph | HFTD - Distribution | 2017-07-16 12:10:00 | 999 | 17.3186 | FALSE | <25mph | TABC1 | 0.35 | 2017-04-10T18:07:00Z | 8.01 | 1 | < 25mph | D4060 | 6.39 | 2017-04-10T18:52:00Z | 8.01 | 13 | < 25mph | TABC1 | 0.35 | 2017-04-10T18:07:00Z | 8.01 | 2 | < 25mph | D4060 | 6.39 | 2017-04-10T19:22:00Z | 8.99 | 29 | < 25mph
PG&E | 2016-06-04 | 22:15 | 38.5117 | -122.9373 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42525 | 22:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0768 | 2016 | 6 | 4 | 22 | 15 | 16-0041119 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7220 | 6.1483 | 116_268 | <25mph | <15mph | HFTD - Distribution | 2016-06-04 22:15:00 | 514 | 16.4728 | FALSE | <25mph | RTVWW | 2.68 | 2018-05-10T10:00:00Z | 2.91 | 39 | < 25mph | R08WW | 5.92 | 2018-05-10T10:00:00Z | 12.3 | 69 | < 25mph | RTVWW | 2.68 | 2018-05-10T11:00:00Z | 3.31 | 78 | < 25mph | R08WW | 5.92 | 2018-05-10T10:00:00Z | 12.3 | 140 | < 25mph
PG&E | 2017-10-20 | 13:45 | 34.5532 | -120.5303 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 101921492 | Unknown | 12000 | Conductor | Overhead | Yes | 43028 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1502 | 2017 | 10 | 20 | 13 | 45 | 17-0089249 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 173 | 31.847 | 221_49 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-20 13:45:00 | 1245 | 35.5655 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E7619 | 7.82 | 2016-06-18T09:10:00Z | 5.99 | 6 | < 25mph |  |  |  | 0 | 0 | No data | E2332 | 4.19 | 2016-06-18T10:28:00Z | 13 | 13 | < 25mph
PG&E | 2017-06-10 07:38 | 07:37 | 35.4359 | -120.4957 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101890429 | Unknown | 21000 | Conductor | Overhead | Yes | 42896.3177 | 07:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1140 | 2017 | 6 | 10 | 7 | 37 | 17-0054182 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 34397 | 9.2577 | 222_98 | <25mph | <15mph | HFTD - Distribution | 2017-06-10 07:37:00 | 879 | 18.05 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2260 | 7.67 | 2016-04-16T21:35:00Z | 17 | 7 | < 25mph |  |  |  | 0 | 0 | No data | E2260 | 7.67 | 2016-04-16T21:35:00Z | 17 | 14 | < 25mph
PG&E | 2017-10-10 | 13:36 | 38.931 | -123.3023 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 102214553 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43018 | 13:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1481 | 2017 | 10 | 10 | 13 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.7263 | 101_291 | <25mph | <15mph | HFTD - Distribution | 2017-10-10 13:36:00 | 1224 | 17.0479 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BNVC1 | 4.62 | 2017-01-01T20:50:00Z | 28.99 | 6 | 25-40mph |  |  |  | 0 | 0 | No data | BNVC1 | 4.62 | 2017-01-01T20:50:00Z | 28.99 | 11 | 25-40mph
PG&E | 2015-01-16 07:07 | 2015-01-16 07:07 | 38.7753 | -122.7004 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 102167494 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0257 | 2015 | 1 | 16 | 7 | 7 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 19.4177 | 126_282 | <25mph | <15mph | HFTD - Distribution | 2015-01-16 07:07:00 | 4 | 24.2776 | FALSE | <25mph | LKRC1 | 3.05 | 2018-01-16T18:05:00Z | 5.99 | 1 | < 25mph | LKRC1 | 3.05 | 2018-01-16T18:05:00Z | 5.99 | 2 | < 25mph | LKRC1 | 3.05 | 2018-01-16T19:05:00Z | 7 | 2 | < 25mph | LKRC1 | 3.05 | 2018-01-16T19:05:00Z | 7 | 4 | < 25mph
PG&E | 2017-05-05 15:52 | 15:52 | 40.3776 | -123.0019 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101501566 | None | 12000 | Conductor | Overhead | Yes | 42860.6614 | 15:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1084 | 2017 | 5 | 5 | 15 | 52 | 17-0045707 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 56893 | 24.5621 | 115_371 | <25mph | <15mph | HFTD - Distribution | 2017-05-05 15:52:00 | 824 | 35.0644 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | YOBC1 | 4.35 | 2015-12-14T01:35:00Z | 0 | 1 | < 25mph |  |  |  | 0 | 0 | No data | YOBC1 | 4.35 | 2015-12-14T02:35:00Z | 0 | 2 | < 25mph
PG&E | 2017-08-31 | 11:33 | 37.1379 | -121.9966 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100519201 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 11:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1373 | 2017 | 8 | 31 | 11 | 33 | 17-0074457 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 99153 | 14.3205 | 156_192 | <25mph | <15mph | HFTD - Distribution | 2017-08-31 11:33:00 | 1111 | 14.3569 | FALSE | <25mph | D9791 | 1.35 | 2018-02-15T15:11:00Z | 4.99 | 17 | < 25mph | E6085 | 5.96 | 2018-02-15T15:09:00Z | 17 | 88 | < 25mph | D9737 | 2.87 | 2018-02-15T15:56:00Z | 8.99 | 31 | < 25mph | E5965 | 5.11 | 2018-02-15T15:25:00Z | 20 | 172 | < 25mph
PG&E | 2017-08-30 | 18:21 | 40.6243 | -122.3039 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CASHU008896 | 103151338 | YES | 12000 | Conductor | Overhead | Yes | 42977 | 18:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1369 | 2017 | 8 | 30 | 18 | 21 | 17-0074287 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 76344 | 5.8461 | 145_384 | <25mph | <15mph | HFTD - Distribution | 2017-08-30 18:21:00 | 1107 | 16.2636 | FALSE | <25mph | C5599 | 2.06 | 2015-05-13T10:03:00Z | 4 | 2 | < 25mph | RRAC1 | 7.52 | 2015-05-13T10:24:00Z | 10 | 13 | < 25mph | C5599 | 2.06 | 2015-05-13T10:03:00Z | 4 | 3 | < 25mph | RRAC1 | 7.52 | 2015-05-13T10:24:00Z | 10 | 25 | < 25mph
PG&E | 2018-07-14 | 11:34 | 38.4026 | -122.5489 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103141862 | Verizon | 12000 | Conductor | Overhead | Yes | 43295 | 11:34 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1745 | 2018 | 7 | 14 | 11 | 34 | 18-0059821 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 6426 | 11.4725 | 133_262 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 11:34:00 | 1485 | 15.7933 | FALSE | <25mph | KENWW | 0.52 | 2017-10-12T15:00:00Z | 6.4 | 1 | < 25mph | KENWW | 0.52 | 2017-10-12T15:00:00Z | 6.4 | 3 | < 25mph | KENWW | 0.52 | 2017-10-12T15:00:00Z | 6.4 | 2 | < 25mph | KENWW | 0.52 | 2017-10-12T15:00:00Z | 6.4 | 6 | < 25mph
PG&E | 2017-08-19 | 21:16 | 40.5752 | -122.2985 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464623 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42966 | 21:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1341 | 2017 | 8 | 19 | 21 | 16 | 17-0071522 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 19044 | 8.8981 | 145_381 | <25mph | <15mph | HFTD - Distribution | 2017-08-19 21:16:00 | 1079 | 13.341 | FALSE | <25mph | C5599 | 2.67 | 2015-04-24T22:34:00Z | 13 | 1 | < 25mph | RRAC1 | 4.12 | 2015-04-24T22:24:00Z | 22.01 | 13 | < 25mph | C5599 | 2.67 | 2015-04-24T23:34:00Z | 17.98 | 3 | < 25mph | RRAC1 | 4.12 | 2015-04-24T23:24:00Z | 22.01 | 26 | < 25mph
PG&E | 2018-06-22 | 17:44 | 37.2485 | -119.5625 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Madera County | 101117749 | None | 0 – 750 | Conductor | Overhead | Yes | 43273 | 17:44 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1686 | 2018 | 6 | 22 | 17 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 10.123 | 263_198 | <25mph | <15mph | HFTD - Distribution | 2018-06-22 17:44:00 | 1428 | 12.3323 | FALSE | <25mph | NFRC1 | 3.29 | 2018-07-14T17:55:00Z | 8.99 | 1 | < 25mph | D7778 | 5.05 | 2018-07-14T17:51:00Z | 10 | 38 | < 25mph | NFRC1 | 3.29 | 2018-07-14T18:55:00Z | 11.01 | 2 | < 25mph | D2149 | 5.52 | 2018-07-14T18:45:00Z | 12.01 | 75 | < 25mph
PG&E | 2016-10-02 16:41 | 16:41 | 39.8888 | -121.6648 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103358082 |  | 12000 | Other | Overhead | Yes | 42645.6954 | 16:41 | Other | N.A. | N.A. | N.A. | Weather | lightning strike | Other/Unknown | 1013 | 2016 | 10 | 2 | 16 | 41 | 16-0069050 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 339550 | 8.5152 | 171_343 | <25mph | <15mph | HFTD - Distribution | 2016-10-02 16:41:00 | 755 | 17.2989 | FALSE | <25mph | C8878 | 1.4 | 2016-11-13T21:23:00Z | 4.99 | 12 | < 25mph | CSTC1 | 5.65 | 2016-11-13T21:51:00Z | 8.99 | 17 | < 25mph | C8878 | 1.4 | 2016-11-13T21:23:00Z | 4.99 | 24 | < 25mph | CSTC1 | 5.65 | 2016-11-13T21:51:00Z | 8.99 | 38 | < 25mph
PG&E | 2016-08-08 | 2016-08-08 15:44 | 37.1382 | -121.9672 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100519919 |  | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0912 | 2016 | 8 | 8 | 15 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 8.8992 | 157_192 | <25mph | <15mph | HFTD - Distribution | 2016-08-08 15:44:00 | 655 | 10.1741 | FALSE | <25mph | D9791 | 1.67 | 2015-12-13T15:50:00Z | 15.99 | 26 | < 25mph | LSGC1 | 4.65 | 2015-12-13T15:32:00Z | 44 | 115 | 40-55mph | D9791 | 1.67 | 2015-12-13T16:30:00Z | 21 | 52 | < 25mph | LSGC1 | 4.65 | 2015-12-13T16:32:00Z | 53.02 | 238 | 40-55mph
PG&E | 2016-06-21 | 2016-06-21 10:09 | 39.0294 | -121.2927 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100024816 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | no-match | 0813 | 2016 | 6 | 21 | 10 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 5.0939 | 187_296 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 10:09:00 | 555 | 12.3682 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5440 | 6.7 | 2015-08-20T23:06:00Z | 7 | 15 | < 25mph |  |  |  | 0 | 0 | No data | E5440 | 6.7 | 2015-08-20T23:06:00Z | 7 | 31 | < 25mph
PG&E | 2015-06-03 09:33 | 2015-06-03 09:33 | 39.6896 | -121.6216 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42158.3979 | 2015-06-03 09:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0341 | 2015 | 6 | 3 | 9 | 33 | 15-0038091 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 28146 | 6.3564 | 173_332 | <25mph | <15mph | HFTD - Distribution | 2015-06-03 09:33:00 | 87 | 12.6567 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CICC1 | 6.93 | 2016-03-12T21:54:00Z | 25.99 | 14 | 25-40mph |  |  |  | 0 | 0 | No data | CICC1 | 6.93 | 2016-03-12T22:54:00Z | 28.99 | 27 | 25-40mph
PG&E | 2017-06-16 22:30 | 22:30 | 38.0373 | -122.1847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101424286 | Unknown | 21000 | Conductor | Overhead | Yes | 42902.9378 | 22:30 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1156 | 2017 | 6 | 16 | 22 | 30 | 17-0055882 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 12000 | 25.2975 | 148_241 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-06-16 22:30:00 | 895 | 25.6656 | FALSE | 25-40mph | MZXC1 | 3.24 | 2016-10-26T22:54:00Z | 17.98 | 18 | < 25mph | MZXC1 | 3.24 | 2016-10-26T22:54:00Z | 17.98 | 82 | < 25mph | MZXC1 | 3.24 | 2016-10-26T22:54:00Z | 17.98 | 36 | < 25mph | MZXC1 | 3.24 | 2016-10-26T22:54:00Z | 17.98 | 161 | < 25mph
PG&E | 2016-08-15 | 2016-08-15 15:43 | 37.8784 | -120.4488 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101020079 |  | 17000 | Conductor | Overhead | Yes | 42597 | 2016-08-15 15:43 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0928 | 2016 | 8 | 15 | 15 | 43 | 16-0057465 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 122905 | 10.0906 | 223_232 | <25mph | <15mph | HFTD - Distribution | 2016-08-15 15:43:00 | 671 | 12.9875 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.26 | 2016-03-21T06:03:00Z | 4 | 1 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.26 | 2016-03-21T07:03:00Z | 4 | 2 | < 25mph
PG&E | 2019-09-22 | 11:56 | 37.5168 | -119.9159 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103967994 |  | 21000 | Pole | Overhead | Yes | 43730 | 11:56 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-452 | 2019 | 9 | 22 | 11 | 56 | 19-0102232 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 133232 | 11.5782 | 247_213 | <25mph | <15mph | HFTD - Distribution | 2019-09-22 11:56:00 | 2051 | 13.905 | FALSE | <25mph | MPOC1 | 3.98 | 2016-05-06T21:07:00Z | 12.01 | 1 | < 25mph | MPOC1 | 3.98 | 2016-05-06T21:07:00Z | 12.01 | 8 | < 25mph | MPOC1 | 3.98 | 2016-05-06T21:07:00Z | 12.01 | 2 | < 25mph | MPOC1 | 3.98 | 2016-05-06T21:07:00Z | 12.01 | 17 | < 25mph
PG&E | 2015-06-12 13:07 | 2015-06-12 13:07 | 40.4077 | -122.4104 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS STREET FROM 4139 OLD HAPPY VALLEY RD |  | 12000 | Lightning Arrestor | Overhead | No |  |  | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | no-match | 0378 | 2015 | 6 | 12 | 13 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Lightning Arrestor | N.A. | 9.7698 | 140_372 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 13:07:00 | 124 | 24.3549 | FALSE | <25mph | PG174 | 1.82 | 2019-10-10T18:00:00Z | 27.47 | 6 | 25-40mph | PG174 | 1.82 | 2019-10-10T18:00:00Z | 27.47 | 16 | 25-40mph | PG174 | 1.82 | 2019-10-10T18:00:00Z | 27.47 | 12 | 25-40mph | PG174 | 1.82 | 2019-10-10T18:00:00Z | 27.47 | 34 | 25-40mph
PG&E | 2019-09-10 | 7:13 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 82841102 |  | 12000 | Conductor | Overhead | Yes | 43718 | 7:13 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-369 | 2019 | 9 | 10 | 7 | 13 | 19-0097264 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 23500 | 14.6244 | 147_193 | <25mph | <15mph | HFTD - Distribution | 2019-09-10 07:13:00 | 2029 | 17.7422 | FALSE | <25mph | BNDC1 | 2.84 | 2016-12-03T15:50:00Z | 14.99 | 1 | < 25mph | BNDC1 | 2.84 | 2016-12-03T15:50:00Z | 14.99 | 21 | < 25mph | BNDC1 | 2.84 | 2016-12-03T15:50:00Z | 14.99 | 2 | < 25mph | BNDC1 | 2.84 | 2016-12-03T15:50:00Z | 14.99 | 41 | < 25mph
PG&E | 2018-06-22 | 17:44 | 37.2485 | -119.5625 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Madera County | 101117749 | None | 0 – 750 | Conductor | Overhead | Yes | 43273 | 17:44 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1686 | 2018 | 6 | 22 | 17 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 10.123 | 263_198 | <25mph | <15mph | HFTD - Distribution | 2018-06-22 17:44:00 | 1428 | 12.3323 | FALSE | <25mph | NFRC1 | 3.29 | 2018-10-19T00:55:00Z | 5.99 | 2 | < 25mph | NFRC1 | 3.29 | 2018-10-19T00:55:00Z | 5.99 | 40 | < 25mph | NFRC1 | 3.29 | 2018-10-19T00:55:00Z | 5.99 | 3 | < 25mph | NFRC1 | 3.29 | 2018-10-19T00:55:00Z | 5.99 | 75 | < 25mph
PG&E | 2019-06-17 | 10:25 | 38.511 | -122.2134 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 43051101 |  | 12000 | Conductor | Overhead | Yes | 43633 | 10:25 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-84 | 2019 | 6 | 17 | 10 | 25 | 19-0068579 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 306900 | 10.2943 | 147_267 | <25mph | <15mph | HFTD - Distribution | 2019-06-17 10:25:00 | 1843 | 15.8677 | FALSE | <25mph | ATLC1 | 3.74 | 2017-03-14T11:29:00Z | 5.99 | 1 | < 25mph | ATLC1 | 3.74 | 2017-03-14T11:29:00Z | 5.99 | 1 | < 25mph | ATLC1 | 3.74 | 2017-03-14T12:29:00Z | 7 | 2 | < 25mph | ATLC1 | 3.74 | 2017-03-14T12:29:00Z | 7 | 2 | < 25mph
PG&E | 2017-04-04 13:36 | 13:29 | 35.6885 | -120.7653 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101945026 | None | 12000 | Conductor | Overhead | Yes | 42829.567 | 13:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1064 | 2017 | 4 | 4 | 13 | 29 | 17-0036460 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 167151 | 3.61 | 210_111 | <25mph | <15mph | HFTD - Distribution | 2017-04-04 13:29:00 | 804 | 8.6409 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D4060 | 7.1 | 2018-10-29T12:46:00Z | 1.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | D4060 | 7.1 | 2018-10-29T13:01:00Z | 1.01 | 8 | < 25mph
PG&E | 2015-09-06 19:27 | 2015-09-06 19:27 | 34.6195 | -120.2534 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Santa Barbara County Fire | meter# 1008400678 | Verizon | 12000 | Conductor | Overhead | Yes | 42253.8104 | 2015-09-06 19:27 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0582 | 2015 | 9 | 6 | 19 | 27 | 15-0059612 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 863 | 14.7315 | 234_53 | <25mph | <15mph | HFTD - Distribution | 2015-09-06 19:27:00 | 326 | 17.7534 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TT480 | 6.18 | 2019-10-24T21:20:00Z | 22.01 | 13 | < 25mph |  |  |  | 0 | 0 | No data | TT480 | 6.18 | 2019-10-24T22:20:00Z | 22.01 | 26 | < 25mph
PG&E | 2017-10-08 | 22:58 | 39.3642 | -121.1131 | Vegetation | Rural | < 3 Meters | Fire Agency | INCIDENT NUMBER 26268 | 100068104 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43016 | 22:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Fell into (No defect) | 1471 | 2017 | 10 | 8 | 22 | 58 | 17-0085355 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 198802 | 15.5554 | 195_314 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 22:58:00 | 1211 | 22.0344 | FALSE | <25mph | E3651 | 3.94 | 2015-06-18T04:05:00Z | 2.01 | 12 | < 25mph | RRRC1 | 4.2 | 2015-06-18T03:13:00Z | 8.01 | 19 | < 25mph | E3651 | 3.94 | 2015-06-18T05:05:00Z | 3 | 24 | < 25mph | RRRC1 | 4.2 | 2015-06-18T03:13:00Z | 8.01 | 38 | < 25mph
PG&E | 2017-12-20 07:55 | 07:54 | 37.4012 | -122.3606 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100318864 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43089.3298 | 07:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1546 | 2017 | 12 | 20 | 7 | 54 | 17-0102756 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6602 | 16.1413 | 140_206 | <25mph | <15mph | HFTD - Distribution | 2017-12-20 07:54:00 | 1288 | 21.2088 | FALSE | <25mph | D9259 | 2.53 | 2019-06-21T11:30:00Z | 4.99 | 10 | < 25mph | PG150 | 6.83 | 2019-06-21T12:10:00Z | 10.54 | 27 | < 25mph | D9259 | 2.53 | 2019-06-21T12:16:00Z | 4.99 | 20 | < 25mph | PG150 | 6.83 | 2019-06-21T12:20:00Z | 12.71 | 52 | < 25mph
PG&E | 2017-06-15 08:08 | 7:39 | 39.2276 | -121.2348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE CHIEF | 103676075 | Unknown | 21000 | Conductor | Overhead | Yes | 42901.3391 | 7:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1147 | 2017 | 6 | 15 | 7 | 39 | 17-0055387 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 740 | 10.5195 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 07:39:00 | 886 | 12.4202 | FALSE | <25mph | E2572 | 2.6 | 2015-06-04T18:04:00Z | 4.99 | 13 | < 25mph | E1789 | 7.9 | 2015-06-04T18:06:00Z | 10 | 29 | < 25mph | E2572 | 2.6 | 2015-06-04T19:09:00Z | 4.99 | 25 | < 25mph | E1789 | 7.9 | 2015-06-04T18:18:00Z | 10 | 57 | < 25mph
PG&E | 2018-08-07 | 21:03 | 38.2129 | -120.9184 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102042811 | Unknown | 12000 | Conductor | Overhead | Yes | 43319 | 21:03 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1828 | 2018 | 8 | 7 | 21 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2018-08-07 21:03:00 | NA | 0 | FALSE | <25mph | PG404 | 3.58 | 2019-10-15T06:10:00Z | 6.51 | 7 | < 25mph | PG375 | 5.2 | 2019-10-15T06:10:00Z | 7.74 | 25 | < 25mph | PG404 | 3.58 | 2019-10-15T06:20:00Z | 6.71 | 14 | < 25mph | PG375 | 5.2 | 2019-10-15T07:10:00Z | 11.9 | 50 | < 25mph
PG&E | 2017-07-12 | 16:04 | 40.6531 | -122.3343 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 000/001 | Unknown | 60000 | Conductor | Overhead | Yes | 42928 | 16:04 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1245 | 2017 | 7 | 12 | 16 | 4 | INT-09837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 13.5069 | 143_386 | <25mph | <15mph | HFTD - Transmission | 2017-07-12 16:04:00 | 987 | 13.828 | FALSE | <25mph | C5599 | 3.4 | 2015-05-23T07:33:00Z | 0 | 2 | < 25mph | TS583 | 7.96 | 2015-05-23T07:27:00Z | 4.99 | 7 | < 25mph | C5599 | 3.4 | 2015-05-23T08:33:00Z | 0 | 4 | < 25mph | E1536 | 7.57 | 2015-05-23T08:51:00Z | 5.99 | 14 | < 25mph
PG&E | 2019-05-29 | 20:25 | 39.0194 | -121.0608 |  | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match |  | 2019 | 5 | 29 | 20 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 14.177 | 197_295 | <25mph | <15mph | HFTD - Distribution | 2019-05-29 20:25:00 | 1789 | 14.177 | FALSE | <25mph | C0713 | 0.99 | 2015-03-02T16:40:00Z | 7 | 12 | < 25mph | C0713 | 0.99 | 2015-03-02T16:40:00Z | 7 | 34 | < 25mph | C0713 | 0.99 | 2015-03-02T17:40:00Z | 8.99 | 24 | < 25mph | C5488 | 4.14 | 2015-03-02T17:36:00Z | 11.99 | 60 | < 25mph
PG&E | 2018-07-30 | 14:36 | 38.1987 | -120.3638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NICK WEBB ( 209) 532-7424 | 103336176 | Unknown | 17000 | Conductor | Overhead | Yes | 43311 | 14:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1800 | 2018 | 7 | 30 | 14 | 36 | 18-0065131 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18530 | 10.5817 | 227_250 | <25mph | <15mph | HFTD - Distribution | 2018-07-30 14:36:00 | 1540 | 14.4256 | FALSE | <25mph | E8204 | 0 | 2017-09-28T23:52:00Z | 4.99 | 9 | < 25mph | E9838 | 7.59 | 2017-09-29T00:06:00Z | 8.99 | 24 | < 25mph | E8204 | 0 | 2017-09-29T01:08:00Z | 4.99 | 15 | < 25mph | E9838 | 7.59 | 2017-09-29T00:06:00Z | 8.99 | 46 | < 25mph
PG&E | 2018-07-18 | 1:14 | 38.3671 | -120.5578 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101247987 | Unknown | 12000 | Conductor | Overhead | Yes | 43299 | 1:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1761 | 2018 | 7 | 18 | 1 | 14 | 18-0060882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6420 | 6.6576 | 219_259 | <25mph | <15mph | HFTD - Distribution | 2018-07-18 01:14:00 | 1501 | 11.9385 | FALSE | <25mph | D9396 | 3.78 | 2015-06-09T06:37:00Z | 3 | 17 | < 25mph | ESPC1 | 6.8 | 2015-06-09T06:13:00Z | 11.01 | 25 | < 25mph | AT450 | 3.1 | 2015-06-09T07:10:00Z | 4 | 30 | < 25mph | ESPC1 | 6.8 | 2015-06-09T06:13:00Z | 11.01 | 46 | < 25mph
PG&E | 2015-06-15 15:35 | 2015-06-15 15:35 | 37.1852 | -121.7595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Jose city | 100618215 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42170.6493 | 2015-06-15 15:35 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0384 | 2015 | 6 | 15 | 15 | 35 | 15-0041178 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 345 | 20.7397 | 166_194 | <25mph | <15mph | HFTD - Distribution | 2015-06-15 15:35:00 | 130 | 21.599 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5617 | 5.37 | 2017-06-20T06:06:00Z | 4 | 84 | < 25mph |  |  |  | 0 | 0 | No data | E5617 | 5.37 | 2017-06-20T06:31:00Z | 4.99 | 176 | < 25mph
PG&E | 2018-06-30 | 11:14 | 39.3621 | -121.0809 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ENGINEER YUREK | 100091354 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 11:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1713 | 2018 | 6 | 30 | 11 | 14 | 18-0055945 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5724 | 3.7745 | 196_314 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 11:14:00 | 1454 | 12.1468 | FALSE | <25mph | E3651 | 2.44 | 2015-04-27T17:10:00Z | 4.99 | 12 | < 25mph | E6355 | 7.85 | 2015-04-27T17:11:00Z | 5.99 | 19 | < 25mph | E3651 | 2.44 | 2015-04-27T17:25:00Z | 5.99 | 24 | < 25mph | E6355 | 7.85 | 2015-04-27T18:12:00Z | 8.99 | 38 | < 25mph
PG&E | 2019-06-03 | 14:31 | 40.6822 | -122.2806 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 101466598 |  | 12000 | Transformer | Overhead | Yes | 43619 | 14:31 | Equipment - Overloaded | Transformer |  |  |  |  | no-match | 2019-161 | 2019 | 6 | 3 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 6.522 | 146_387 | <25mph | <15mph | HFTD - Distribution | 2019-06-03 14:31:00 | 1798 | 12.4331 | FALSE | <25mph | PG526 | 0.4 | 2019-10-31T21:20:00Z | 8.19 | 6 | < 25mph | PG519 | 4.92 | 2019-10-31T21:10:00Z | 15.35 | 48 | < 25mph | PG526 | 0.4 | 2019-10-31T21:20:00Z | 8.19 | 12 | < 25mph | PG519 | 4.92 | 2019-10-31T21:10:00Z | 15.35 | 94 | < 25mph
PG&E | 2017-07-07 | 15:09 | 40.9054 | -122.3806 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101455950 | Unknown | 12000 | Conductor | Overhead | Yes | 42923 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1229 | 2017 | 7 | 7 | 15 | 9 | 17-0061903 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.0906 | 142_400 | <25mph | <15mph | HFTD - Distribution | 2017-07-07 15:09:00 | 969 | 11.4161 | FALSE | <25mph | SLFC1 | 2.92 | 2018-10-05T07:19:00Z | 5.99 | 5 | < 25mph | SLFC1 | 2.92 | 2018-10-05T07:19:00Z | 5.99 | 5 | < 25mph | SLFC1 | 2.92 | 2018-10-05T08:19:00Z | 7 | 10 | < 25mph | SLFC1 | 2.92 | 2018-10-05T08:19:00Z | 7 | 10 | < 25mph
PG&E | 2017-10-02 | 14:56 | 38.9102 | -120.9185 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100110800 | None | 21000 | Other | Overhead | Yes | 43010 | 14:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1447 | 2017 | 10 | 2 | 14 | 56 | 17-0083516 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 160 | 17.2967 | 203_289 | <25mph | <15mph | HFTD - Distribution | 2017-10-02 14:56:00 | 1185 | 22.7009 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG180 | 7.45 | 2019-04-19T22:40:00Z | 12.71 | 37 | < 25mph |  |  |  | 0 | 0 | No data | PG180 | 7.45 | 2019-04-20T00:10:00Z | 13.8 | 74 | < 25mph
PG&E | 2017-05-14 | 11:59 | 38.0798 | -122.8665 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102247059 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42869 | 11:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1095 | 2017 | 5 | 14 | 11 | 59 | 17-0047802 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 377483 | 24.3878 | 118_244 | <25mph | <15mph | HFTD - Distribution | 2017-05-14 11:59:00 | 835 | 24.3878 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PREC1 | 4.12 | 2015-03-04T05:05:00Z | 4 | 7 | < 25mph |  |  |  | 0 | 0 | No data | PREC1 | 4.12 | 2015-03-04T06:05:00Z | 4 | 14 | < 25mph
PG&E | 2016-05-29 14:19 | 2016-05-29 14:19 | 40.5795 | -122.4694 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103156596 | Yes | 12000 | Conductor | Overhead | Yes | 42519.5965 | 2016-05-29 14:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0751 | 2016 | 5 | 29 | 14 | 19 | 16-0039619 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3860 | 1.6611 | 138_382 | <25mph | <15mph | HFTD - Distribution | 2016-05-29 14:19:00 | 494 | 20.6013 | FALSE | <25mph | MMOC1 | 1.91 | 2015-05-29T08:00:00Z | 4.99 | 10 | < 25mph | MMOC1 | 1.91 | 2015-05-29T08:00:00Z | 4.99 | 21 | < 25mph | MMOC1 | 1.91 | 2015-05-29T09:00:00Z | 5.99 | 19 | < 25mph | MMOC1 | 1.91 | 2015-05-29T09:00:00Z | 5.99 | 42 | < 25mph
PG&E | 2019-05-29 | 16:54 | 37.0371 | -119.5209 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 100680674 |  | 12000 | Pole | Overhead | Yes | 43614 | 16:54 | Vegetation |  | Veg. contact | Pole |  |  | Dead | 2019-202 | 2019 | 5 | 29 | 16 | 54 | 19-0059237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 6780 | 6.6167 | 265_186 | <25mph | <15mph | HFTD - Distribution | 2019-05-29 16:54:00 | 1787 | 9.3593 | FALSE | <25mph | PRHC1 | 3 | 2015-06-05T11:27:00Z | 3 | 1 | < 25mph | PRHC1 | 3 | 2015-06-05T11:27:00Z | 3 | 1 | < 25mph | PRHC1 | 3 | 2015-06-05T11:27:00Z | 3 | 2 | < 25mph | PRHC1 | 3 | 2015-06-05T11:27:00Z | 3 | 2 | < 25mph
PG&E | 2015-06-06 15:38 | 2015-06-06 15:38 | 39.0409 | -123.4019 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 11480 ANDERSON VALLEY WAY @ BRIDGE |  | 12000 | Conductor | Overhead | Yes | 42161.6514 | 2015-06-06 15:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0355 | 2015 | 6 | 6 | 15 | 38 | 15-0039056 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 1748 | 19.2204 | 97_298 | <25mph | <15mph | HFTD - Distribution | 2015-06-06 15:38:00 | 101 | 19.2204 | FALSE | <25mph | E4777 | 3.27 | 2018-11-10T14:20:00Z | 7 | 3 | < 25mph | BNVC1 | 4.68 | 2018-11-10T14:50:00Z | 14 | 9 | < 25mph | E4777 | 3.27 | 2018-11-10T14:20:00Z | 7 | 7 | < 25mph | BNVC1 | 4.68 | 2018-11-10T15:50:00Z | 17 | 17 | < 25mph
PG&E | 2017-12-07 12:26 | 12:25 | 34.7115 | -120.1772 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 015/220 | Unknown | 115000 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1534 | 2017 | 12 | 7 | 12 | 25 | 17-0097211 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 4.373 | 237_58 | <25mph | <15mph | HFTD - Transmission | 2017-12-07 12:25:00 | 1276 | 13.3077 | FALSE | <25mph |  |  |  | 0 | 0 | No data | SXWC1 | 7.67 | 2018-05-14T01:09:00Z | 18.99 | 20 | < 25mph |  |  |  | 0 | 0 | No data | SXWC1 | 7.67 | 2018-05-14T02:09:00Z | 20 | 39 | < 25mph
PG&E | 2015-10-31 07:45 | 2015-10-31 07:45 | 38.1157 | -120.8931 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal FIRE | 103763040 |  | 12000 | Conductor | Overhead | Yes | 42308.3229 | 2015-10-31 07:45 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0663 | 2015 | 10 | 31 | 7 | 45 | 15-0074424 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 314565 | 11.8471 | 204_245 | <25mph | <15mph | HFTD - Distribution | 2015-10-31 07:45:00 | 407 | 12.187 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CMAC1 | 7.6 | 2017-01-16T11:59:00Z | 4 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CMAC1 | 7.6 | 2017-01-16T12:59:00Z | 4.99 | 2 | < 25mph
PG&E | 2019-09-15 | 12:38 | 38.1194 | -120.8013 | Vehicle | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103959405 |  | 12000 | Pole | Overhead | Yes | 43723 | 12:38 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-118 | 2019 | 9 | 15 | 12 | 38 | 19-0099234 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 5378 | 7.5852 | 208_246 | <25mph | <15mph | HFTD - Distribution | 2019-09-15 12:38:00 | 2043 | 14.1961 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2015-06-09 15:24 | 2015-06-09 15:24 | 38.3651 | -122.2541 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | load side 2987 | Yes | 21000 | Conductor | Overhead | Yes | 42164.6417 | 2015-06-09 15:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0368 | 2015 | 6 | 9 | 15 | 24 | 15-0039825 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 651298 | 15.2247 | 145_259 | <25mph | <15mph | HFTD - Distribution | 2015-06-09 15:24:00 | 114 | 15.4726 | FALSE | <25mph | PG185 | 3.78 | 2019-10-30T10:20:00Z | 30.53 | 18 | 25-40mph | PG185 | 3.78 | 2019-10-30T10:20:00Z | 30.53 | 55 | 25-40mph | PG185 | 3.78 | 2019-10-30T11:40:00Z | 30.6 | 35 | 25-40mph | PG185 | 3.78 | 2019-10-30T11:40:00Z | 30.6 | 109 | 25-40mph
PG&E | 2019-06-17 | 10:25 | 38.511 | -122.2134 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 43051101 |  | 12000 | Conductor | Overhead | Yes | 43633 | 10:25 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-84 | 2019 | 6 | 17 | 10 | 25 | 19-0068579 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 306900 | 10.2943 | 147_267 | <25mph | <15mph | HFTD - Distribution | 2019-06-17 10:25:00 | 1843 | 15.8677 | FALSE | <25mph | ATLC1 | 3.74 | 2015-12-08T16:29:00Z | 8.99 | 1 | < 25mph | ATLC1 | 3.74 | 2015-12-08T16:29:00Z | 8.99 | 1 | < 25mph | ATLC1 | 3.74 | 2015-12-08T17:29:00Z | 11.01 | 2 | < 25mph | ATLC1 | 3.74 | 2015-12-08T17:29:00Z | 11.01 | 2 | < 25mph
PG&E | 2016-10-19 10:42 | 10:42 | 38.5098 | -122.45 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | st helena | 102242552 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42662.4459 | 10:42 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1040 | 2016 | 10 | 19 | 10 | 42 | 16-0073955 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 693 | 4.5329 | 137_268 | <25mph | <15mph | HFTD - Distribution | 2016-10-19 10:42:00 | 781 | 13.4953 | FALSE | <25mph | PG091 | 3.91 | 2019-08-18T13:40:00Z | 12.06 | 6 | < 25mph | PG162 | 5.04 | 2019-08-18T14:10:00Z | 14.92 | 60 | < 25mph | PG091 | 3.91 | 2019-08-18T13:40:00Z | 12.06 | 12 | < 25mph | PG162 | 5.04 | 2019-08-18T14:10:00Z | 14.92 | 126 | < 25mph
PG&E | 2016-09-21 | 10:01 | 39.1173 | -121.071 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100014315 | PACIFIC BELL | 115000 | Conductor | Overhead | Yes | 42634 | 10:01 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0991 | 2016 | 9 | 21 | 10 | 1 | INT-08560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 18.3543 | 196_301 | <25mph | <15mph | HFTD - Transmission | 2016-09-21 10:01:00 | 734 | 24.3978 | FALSE | <25mph | E1789 | 3.84 | 2018-10-08T09:12:00Z | 14 | 21 | < 25mph | E1789 | 3.84 | 2018-10-08T09:12:00Z | 14 | 65 | < 25mph | E1789 | 3.84 | 2018-10-08T09:12:00Z | 14 | 41 | < 25mph | E1789 | 3.84 | 2018-10-08T09:12:00Z | 14 | 127 | < 25mph
PG&E | 2016-02-08 03:55 | 2016-02-08 03:55 | 39.7852 | -121.5056 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100337507 |  | 12000 | Conductor | Overhead | Yes | 42408.1632 | 2016-02-08 03:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0694 | 2016 | 2 | 8 | 3 | 55 | 16-0011201 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 87046 | 36.3276 | 178_337 | 25-40mph | 30-45mph | HFTD - Distribution | 2016-02-08 03:55:00 | 438 | 40.0336 | FALSE | 40-55mph | JBGC1 | 3.52 | 2016-02-07T11:13:00Z | 35.99 | 1 | 25-40mph | JBGC1 | 3.52 | 2016-02-07T11:13:00Z | 35.99 | 18 | 25-40mph | JBGC1 | 3.52 | 2016-02-07T12:13:00Z | 38.99 | 2 | 25-40mph | JBGC1 | 3.52 | 2016-02-07T12:13:00Z | 38.99 | 37 | 25-40mph
PG&E | 2015-06-08 14:18 | 2015-06-08 14:18 | 38.1796 | -120.959 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 102048579 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42163.5958 | 2015-06-08 14:18 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0360 | 2015 | 6 | 8 | 14 | 18 | 15-0039368 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 65168 | 7.0021 | 201_249 | <25mph | <15mph | HFTD - Distribution | 2015-06-08 14:18:00 | 106 | 9.7763 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CMAC1 | 5.88 | 2015-01-29T03:59:00Z | 3 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CMAC1 | 5.88 | 2015-01-29T03:59:00Z | 3 | 2 | < 25mph
PG&E | 2019-07-30 | 15:15 | 39.1207 | -121.072 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 152691104 |  | 12000 | Conductor | Overhead | Yes | 43676 | 15:15 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-386 | 2019 | 7 | 30 | 15 | 15 | 19-0082713 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 31302 | 12.2921 | 196_301 | <25mph | <15mph | HFTD - Distribution | 2019-07-30 15:15:00 | 1942 | 13.0851 | FALSE | <25mph | E1789 | 3.69 | 2015-06-25T00:12:00Z | 10 | 10 | < 25mph | E1789 | 3.69 | 2015-06-25T00:12:00Z | 10 | 61 | < 25mph | E1789 | 3.69 | 2015-06-25T00:12:00Z | 10 | 20 | < 25mph | E1789 | 3.69 | 2015-06-25T00:12:00Z | 10 | 128 | < 25mph
PG&E | 2017-08-06 11:38 | 11:38 | 36.5857 | -121.7121 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101747125 | Unknown | 12000 | Conductor | Overhead | Yes | 42953.4849 | 11:38 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1321 | 2017 | 8 | 6 | 11 | 38 | 17-0068279 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 87172 | 7.0101 | 168_161 | <25mph | <15mph | HFTD - Distribution | 2017-08-06 11:38:00 | 1059 | 12.123 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6666 | 7.23 | 2015-03-17T10:55:00Z | 8.01 | 19 | < 25mph |  |  |  | 0 | 0 | No data | E6666 | 7.23 | 2015-03-17T11:15:00Z | 10.98 | 37 | < 25mph
PG&E | 2019-07-19 | 11:59 | 37.9162 | -120.349 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 163351703 |  | 17000 | Conductor | Overhead | Yes | 43665 | 11:59 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-376 | 2019 | 7 | 19 | 11 | 59 | 19-0079030 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24042 | 10.7946 | 228_234 | <25mph | <15mph | HFTD - Distribution | 2019-07-19 11:59:00 | 1915 | 10.8841 | FALSE | <25mph | C3161 | 3.6 | 2015-06-06T12:08:00Z | 2.01 | 4 | < 25mph | C3161 | 3.6 | 2015-06-06T12:08:00Z | 2.01 | 4 | < 25mph | C3161 | 3.6 | 2015-06-06T13:09:00Z | 3 | 8 | < 25mph | C3161 | 3.6 | 2015-06-06T13:09:00Z | 3 | 8 | < 25mph
PG&E | 2018-07-28 | 6:51 | 38.7473 | -120.7866 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101418155 | AT&T | 21000 | Conductor | Overhead | Yes | 43309 | 6:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1794 | 2018 | 7 | 28 | 6 | 51 | 18-0064545 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 15429 | 14.6813 | 209_280 | <25mph | <15mph | HFTD - Distribution | 2018-07-28 06:51:00 | 1534 | 14.6813 | FALSE | <25mph | E5691 | 0.5 | 2016-09-18T08:51:00Z | 7 | 21 | < 25mph | E5691 | 0.5 | 2016-09-18T08:51:00Z | 7 | 57 | < 25mph | E5691 | 0.5 | 2016-09-18T08:51:00Z | 7 | 45 | < 25mph | E5691 | 0.5 | 2016-09-18T08:51:00Z | 7 | 117 | < 25mph
PG&E | 2016-06-04 | 22:15 | 38.5117 | -122.9373 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42525 | 22:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0768 | 2016 | 6 | 4 | 22 | 15 | 16-0041119 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7220 | 6.1483 | 116_268 | <25mph | <15mph | HFTD - Distribution | 2016-06-04 22:15:00 | 514 | 16.4728 | FALSE | <25mph | D3481 | 2.53 | 2015-08-15T00:17:00Z | 11.01 | 24 | < 25mph | D3481 | 2.53 | 2015-08-15T00:17:00Z | 11.01 | 56 | < 25mph | D3481 | 2.53 | 2015-08-15T00:17:00Z | 11.01 | 47 | < 25mph | D3481 | 2.53 | 2015-08-15T00:17:00Z | 11.01 | 111 | < 25mph
PG&E | 2018-09-14 | 15:08 | 35.328 | -120.6982 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Sean Hernandez Cell # 805 903 3423 | 103400199 | Unknown | 12000 | Conductor | Overhead | Yes | 43357 | 15:08 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1898 | 2018 | 9 | 14 | 15 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 24.1105 | 213_92 | <25mph | <15mph | HFTD - Distribution | 2018-09-14 15:08:00 | 1637 | 24.1304 | FALSE | <25mph | ARGC1 | 2.05 | 2015-07-13T18:54:00Z | 10 | 1 | < 25mph | E6113 | 7.29 | 2015-07-13T19:11:00Z | 18.01 | 5 | < 25mph | ARGC1 | 2.05 | 2015-07-13T19:54:00Z | 12.01 | 2 | < 25mph | E6113 | 7.29 | 2015-07-13T19:11:00Z | 18.01 | 10 | < 25mph
PG&E | 2017-07-23 18:25 | 18:25 | 39.6723 | -123.5336 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103823226 | Unknown | 12000 | Conductor | Overhead | Yes | 42939.7676 | 18:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1284 | 2017 | 7 | 23 | 18 | 25 | 17-0064854 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 12864 | 11.8402 | 92_333 | <25mph | <15mph | HFTD - Distribution | 2017-07-23 18:25:00 | 1023 | 16.2282 | FALSE | <25mph | LAYC1 | 3.32 | 2015-01-23T14:29:00Z | 2.01 | 1 | < 25mph | LAYC1 | 3.32 | 2015-01-23T14:29:00Z | 2.01 | 1 | < 25mph | LAYC1 | 3.32 | 2015-01-23T15:29:00Z | 2.01 | 2 | < 25mph | LAYC1 | 3.32 | 2015-01-23T15:29:00Z | 2.01 | 2 | < 25mph
PG&E | 2015-04-30 00:26 | 2015-04-30 00:26 | 37.2401 | -122.2472 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 1145 VERDE R |  | 12000 | Conductor | Overhead | Yes | 42124.0181 | 2015-04-30 00:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0304 | 2015 | 4 | 30 | 0 | 26 | 15-0030607 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1256 | 5.7566 | 145_197 | <25mph | <15mph | HFTD - Distribution | 2015-04-30 00:26:00 | 50 | 15.5915 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.52 | 2017-02-19T16:07:00Z | 14 | 18 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.52 | 2017-02-19T17:07:00Z | 17 | 35 | < 25mph
PG&E | 2016-09-22 | 13:53 | 40.224 | -122.3417 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101539450 | None | 12000 | Conductor | Overhead | Yes | 42635 | 13:53 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0996 | 2016 | 9 | 22 | 13 | 53 | 16-0066692 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 14706 | 14.6017 | 143_362 | <25mph | <15mph | HFTD - Distribution | 2016-09-22 13:53:00 | 739 | 20.1469 | FALSE | <25mph | D6527 | 1.82 | 2015-04-15T13:39:00Z | 20 | 2 | < 25mph | D6527 | 1.82 | 2015-04-15T13:39:00Z | 20 | 2 | < 25mph | D6527 | 1.82 | 2015-04-15T13:39:00Z | 20 | 2 | < 25mph | KRBL | 6.93 | 2015-04-15T14:54:00Z | 21.85 | 3 | < 25mph
PG&E | 2019-06-17 | 10:25 | 38.511 | -122.2134 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 43051101 |  | 12000 | Conductor | Overhead | Yes | 43633 | 10:25 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-84 | 2019 | 6 | 17 | 10 | 25 | 19-0068579 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 306900 | 10.2943 | 147_267 | <25mph | <15mph | HFTD - Distribution | 2019-06-17 10:25:00 | 1843 | 15.8677 | FALSE | <25mph | ATLC1 | 3.74 | 2017-09-01T22:29:00Z | 11.01 | 1 | < 25mph | ATLC1 | 3.74 | 2017-09-01T22:29:00Z | 11.01 | 1 | < 25mph | ATLC1 | 3.74 | 2017-09-01T23:29:00Z | 11.01 | 2 | < 25mph | ATLC1 | 3.74 | 2017-09-01T23:29:00Z | 11.01 | 2 | < 25mph
PG&E | 2019-09-22 | 11:56 | 37.5168 | -119.9159 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103967994 |  | 21000 | Pole | Overhead | Yes | 43730 | 11:56 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-452 | 2019 | 9 | 22 | 11 | 56 | 19-0102232 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 133232 | 11.5782 | 247_213 | <25mph | <15mph | HFTD - Distribution | 2019-09-22 11:56:00 | 2051 | 13.905 | FALSE | <25mph | PG189 | 1.46 | 2019-02-06T05:10:00Z | 8.12 | 8 | < 25mph | PG189 | 1.46 | 2019-02-06T05:10:00Z | 8.12 | 18 | < 25mph | PG189 | 1.46 | 2019-02-06T05:10:00Z | 8.12 | 15 | < 25mph | PG189 | 1.46 | 2019-02-06T05:10:00Z | 8.12 | 34 | < 25mph
PG&E | 2017-07-01 | 12:02 | 39.8209 | -121.6418 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 003/039 | Unknown | 60000 | Conductor | Overhead | Yes | 42917 | 12:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1212 | 2017 | 7 | 1 | 12 | 2 | INT-09792 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.6345 | 172_339 | <25mph | <15mph | HFTD - Transmission | 2017-07-01 12:02:00 | 954 | 9.664 | FALSE | <25mph | PG075 | 3.12 | 2019-03-14T18:30:00Z | 7.67 | 28 | < 25mph | PG134 | 5.37 | 2019-03-14T18:00:00Z | 8.99 | 36 | < 25mph | PG075 | 3.12 | 2019-03-14T18:30:00Z | 7.67 | 56 | < 25mph | PG134 | 5.37 | 2019-03-14T18:00:00Z | 8.99 | 72 | < 25mph
PG&E | 2017-07-05 12:11 | 11:58 | 39.2105 | -121.2266 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVE ROBERTSON 530 906 4892 | 100010286 | Unknown | 21000 | Conductor | Overhead | Yes | 42921.5077 | 11:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1223 | 2017 | 7 | 5 | 11 | 58 | 17-0060605 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 10231 | 9.71 | 190_306 | <25mph | <15mph | HFTD - Distribution | 2017-07-05 11:58:00 | 962 | 14.0848 | FALSE | <25mph | E2572 | 2.49 | 2016-03-05T01:45:00Z | 4.99 | 12 | < 25mph | E1789 | 6.76 | 2016-03-05T01:42:00Z | 8.01 | 34 | < 25mph | E2572 | 2.49 | 2016-03-05T02:40:00Z | 8.01 | 24 | < 25mph | E1789 | 6.76 | 2016-03-05T02:42:00Z | 12.01 | 67 | < 25mph
PG&E | 2018-10-24 | 7:08 | 37.9475 | -120.2671 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SCOTT PITTMAN 209-768-8182 TCU INCIDENT# 012528 | 101047865 | Unknown | 17000 | Conductor | Overhead | Yes | 43397 | 7:08 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1949 | 2018 | 10 | 24 | 7 | 8 | 18-0093599 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 13433 | 8.6394 | 231_236 | <25mph | <15mph | HFTD - Distribution | 2018-10-24 07:08:00 | 1688 | 12.0171 | FALSE | <25mph | C3161 | 2.32 | 2017-08-27T17:40:00Z | 4.99 | 4 | < 25mph | C3161 | 2.32 | 2017-08-27T17:40:00Z | 4.99 | 4 | < 25mph | C3161 | 2.32 | 2017-08-27T18:40:00Z | 8.99 | 8 | < 25mph | C3161 | 2.32 | 2017-08-27T18:40:00Z | 8.99 | 8 | < 25mph
PG&E | 2018-07-30 | 14:36 | 38.1987 | -120.3638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NICK WEBB ( 209) 532-7424 | 103336176 | Unknown | 17000 | Conductor | Overhead | Yes | 43311 | 14:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1800 | 2018 | 7 | 30 | 14 | 36 | 18-0065131 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18530 | 10.5817 | 227_250 | <25mph | <15mph | HFTD - Distribution | 2018-07-30 14:36:00 | 1540 | 14.4256 | FALSE | <25mph | AR738 | 3.05 | 2015-11-09T14:15:00Z | 1.01 | 16 | < 25mph | AR738 | 3.05 | 2015-11-09T14:15:00Z | 1.01 | 20 | < 25mph | AR738 | 3.05 | 2015-11-09T15:30:00Z | 1.01 | 32 | < 25mph | AR738 | 3.05 | 2015-11-09T15:30:00Z | 1.01 | 40 | < 25mph
PG&E | 2018-12-14 | 10:32 | 40.4379 | -123.7834 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101009136 | Unknown | 12000 | Conductor | Overhead | Yes | 43448 | 10:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1985 | 2018 | 12 | 14 | 10 | 32 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 36.1442 | 82_375 | 25-40mph | 30-45mph | HFTD - Distribution | 2018-12-14 10:32:00 | 1725 | 36.1442 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E8593 | 4.88 | 2016-02-22T16:15:00Z | 12.01 | 12 | < 25mph |  |  |  | 0 | 0 | No data | E8593 | 4.88 | 2016-02-22T16:25:00Z | 12.01 | 24 | < 25mph
PG&E | 2015-04-11 17:16 | 2015-04-11 17:16 | 40.5462 | -122.2343 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101491414 |  | 12000 | Conductor | Overhead | Yes | 42105.7194 | 2015-04-11 17:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0286 | 2015 | 4 | 11 | 17 | 16 | 15-0026023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 11914 | 19.429 | 148_380 | <25mph | <15mph | HFTD - Distribution | 2015-04-11 17:16:00 | 32 | 19.429 | FALSE | <25mph | RRAC1 | 3.7 | 2019-03-21T21:24:00Z | 12.01 | 1 | < 25mph | RRAC1 | 3.7 | 2019-03-21T21:24:00Z | 12.01 | 7 | < 25mph | RRAC1 | 3.7 | 2019-03-21T21:24:00Z | 12.01 | 2 | < 25mph | RRAC1 | 3.7 | 2019-03-21T21:24:00Z | 12.01 | 14 | < 25mph
PG&E | 2018-06-15 | 9:51 | 37.1986 | -119.4709 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RANCHARIA ENGINE 4255 USFS ENG 52 | 101058060 | Unknown | 12000 | Conductor | Overhead | Yes | 43266 | 9:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1660 | 2018 | 6 | 15 | 9 | 51 | 18-0051354 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 35146 | 7.0865 | 267_195 | <25mph | <15mph | HFTD - Distribution | 2018-06-15 09:51:00 | 1402 | 16.2916 | FALSE | <25mph | NFRC1 | 3.06 | 2017-01-13T19:55:00Z | 5.99 | 4 | < 25mph | NFRC1 | 3.06 | 2017-01-13T19:55:00Z | 5.99 | 4 | < 25mph | C6459 | 3.69 | 2017-01-13T21:00:00Z | 5.99 | 8 | < 25mph | C6459 | 3.69 | 2017-01-13T21:00:00Z | 5.99 | 8 | < 25mph
PG&E | 2017-07-10 18:00 | 17:00 | 37.3768 | -122.3597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | David Hibdon 831-254-1763 | 100270370 | Unknown | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1240 | 2017 | 7 | 10 | 17 | 0 | 17-0061857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3322 | 11.4741 | 140_205 | <25mph | <15mph | HFTD - Distribution | 2017-07-10 17:00:00 | 979 | 11.9313 | FALSE | <25mph | E4551 | 0.89 | 2017-01-22T17:47:00Z | 0 | 7 | < 25mph | PUGC1 | 7.47 | 2017-01-22T17:18:00Z | 11.01 | 18 | < 25mph | E4551 | 0.89 | 2017-01-22T18:06:00Z | 2.01 | 11 | < 25mph | PUGC1 | 7.47 | 2017-01-22T17:18:00Z | 11.01 | 33 | < 25mph
PG&E | 2017-07-12 | 16:04 | 40.6531 | -122.3343 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 000/001 | Unknown | 60000 | Conductor | Overhead | Yes | 42928 | 16:04 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1245 | 2017 | 7 | 12 | 16 | 4 | INT-09837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 13.5069 | 143_386 | <25mph | <15mph | HFTD - Transmission | 2017-07-12 16:04:00 | 987 | 13.828 | FALSE | <25mph | C5599 | 3.4 | 2016-05-31T07:01:00Z | 0 | 3 | < 25mph | C5599 | 3.4 | 2016-05-31T07:01:00Z | 0 | 3 | < 25mph | C5599 | 3.4 | 2016-05-31T07:46:00Z | 0 | 6 | < 25mph | C5599 | 3.4 | 2016-05-31T07:46:00Z | 0 | 6 | < 25mph
PG&E | 2018-08-20 | 9:34 | 39.8014 | -121.5813 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100400441 | Unknown | 12000 | Conductor | Overhead | Yes | 43332 | 9:34 | Contact From Object | N.A. | Other | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1849 | 2018 | 8 | 20 | 9 | 34 | 18-0071596 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 394259 | 5.4464 | 175_338 | <25mph | <15mph | HFTD - Distribution | 2018-08-20 09:34:00 | 1588 | 11.8754 | FALSE | <25mph | C4565 | 3.06 | 2019-03-12T01:50:00Z | 2.01 | 4 | < 25mph | JBGC1 | 6.67 | 2019-03-12T01:13:00Z | 17 | 37 | < 25mph | C4565 | 3.06 | 2019-03-12T02:21:00Z | 2.01 | 8 | < 25mph | JBGC1 | 6.67 | 2019-03-12T02:13:00Z | 20 | 73 | < 25mph
PG&E | 2016-06-11 | 2016-06-11 19:45 | 39.3265 | -121.3921 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101292512 |  | 0 – 750 | Transformer | Overhead | Yes | 42532 | 2016-06-11 19:45 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0790 | 2016 | 6 | 11 | 19 | 45 | 16-0042611 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 642 | 8.1809 | 183_312 | <25mph | <15mph | HFTD - Distribution | 2016-06-11 19:45:00 | 533 | 16.0839 | FALSE | <25mph | BNGC1 | 3.76 | 2017-02-21T02:51:00Z | 18.99 | 1 | < 25mph | BNGC1 | 3.76 | 2017-02-21T02:51:00Z | 18.99 | 1 | < 25mph | BNGC1 | 3.76 | 2017-02-21T03:51:00Z | 22.01 | 2 | < 25mph | BNGC1 | 3.76 | 2017-02-21T03:51:00Z | 22.01 | 2 | < 25mph
PG&E | 2017-09-27 | 19:06 | 40.7592 | -123.995 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103660812 | Unknown | 12000 | Conductor | Overhead | Yes | 43005 | 19:06 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1437 | 2017 | 9 | 27 | 19 | 6 | 17-0082303 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 35394 | 10.6184 | 74_393 | <25mph | <15mph | HFTD - Distribution | 2017-09-27 19:06:00 | 1175 | 13.0154 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KNNC1 | 4.42 | 2015-09-20T15:55:00Z | 4.99 | 5 | < 25mph |  |  |  | 0 | 0 | No data | E6225 | 6.97 | 2015-09-20T17:30:00Z | 5.99 | 14 | < 25mph
PG&E | 2019-08-31 | 10:20 | 40.661 | -122.356 | Vehicle | Barren/Other | 3 meters - 0.25 Acres | Fire Dept | Shasta Lake FD | 103571671 | Yes | 12000 | Fuse | Overbuild | Yes | 43708 | 10:20 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-421 | 2019 | 8 | 31 | 10 | 20 | 19-0094332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3050 | 3.1396 | 143_386 | <25mph | <15mph | HFTD - Distribution | 2019-08-31 10:20:00 | 2007 | 12.9011 | FALSE | <25mph | F0355 | 3.02 | 2017-06-06T18:11:00Z | 3 | 6 | < 25mph | C5599 | 4.13 | 2017-06-06T18:01:00Z | 5.99 | 12 | < 25mph | F0355 | 3.02 | 2017-06-06T18:51:00Z | 4.99 | 12 | < 25mph | C5599 | 4.13 | 2017-06-06T18:47:00Z | 8.01 | 24 | < 25mph
PG&E | 2018-09-14 | 15:08 | 35.328 | -120.6982 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Sean Hernandez Cell # 805 903 3423 | 103400199 | Unknown | 12000 | Conductor | Overhead | Yes | 43357 | 15:08 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1898 | 2018 | 9 | 14 | 15 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 24.1105 | 213_92 | <25mph | <15mph | HFTD - Distribution | 2018-09-14 15:08:00 | 1637 | 24.1304 | FALSE | <25mph | PG119 | 3.27 | 2019-09-24T06:30:00Z | 24.11 | 7 | < 25mph | PG119 | 3.27 | 2019-09-24T06:30:00Z | 24.11 | 43 | < 25mph | PG119 | 3.27 | 2019-09-24T07:20:00Z | 25.95 | 14 | 25-40mph | PG119 | 3.27 | 2019-09-24T07:20:00Z | 25.95 | 84 | 25-40mph
PG&E | 2018-06-05 | 13:45 | 38.5432 | -122.7202 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 102031673 | Unknown | 12000 | Conductor | Overhead | Yes | 43256 | 13:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1633 | 2018 | 6 | 5 | 13 | 45 | 18-0047625 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 40599 | 7.3889 | 125_270 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 13:45:00 | 1375 | 15.9614 | FALSE | <25mph | PG005 | 2.46 | 2018-05-21T20:50:00Z | 13.15 | 26 | < 25mph | C3628 | 7 | 2018-05-21T20:31:00Z | 20 | 86 | < 25mph | PG005 | 2.46 | 2018-05-21T21:30:00Z | 15.12 | 52 | < 25mph | C3628 | 7 | 2018-05-21T20:31:00Z | 20 | 170 | < 25mph
PG&E | 2019-07-01 | 2:15 | 38.2955 | -120.8335 |  | Shrub | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-252 | 2019 | 7 | 1 | 2 | 15 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.9479 | 207_255 | <25mph | <15mph | HFTD - Distribution | 2019-07-01 02:15:00 | 1878 | 14.184 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.85 | 2016-01-29T08:05:00Z | 5.99 | 11 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.85 | 2016-01-29T09:05:00Z | 8.99 | 19 | < 25mph
PG&E | 2015-05-09 21:37 | 2015-05-09 21:37 | 39.2848 | -121.0219 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100004095 | Pacific Bell | 12000 | Fuse | Overhead | Yes | 42133.9007 | 2015-05-09 21:37 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0312 | 2015 | 5 | 9 | 21 | 37 | 15-0033109 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 11 | 9.2188 | 198_310 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 21:37:00 | 58 | 15.4234 | FALSE | <25mph | E9947 | 3.3 | 2016-11-24T19:46:00Z | 7 | 34 | < 25mph | E9947 | 3.3 | 2016-11-24T19:46:00Z | 7 | 59 | < 25mph | E5439 | 3.42 | 2016-11-24T21:15:00Z | 8.99 | 66 | < 25mph | E5439 | 3.42 | 2016-11-24T21:15:00Z | 8.99 | 116 | < 25mph
PG&E | 2017-07-30 09:47 | 09:46 | 38.9132 | -122.6179 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike wink | 102151066 | None | 0 – 750 | Conductor | Overhead | Yes | 42946.4075 | 09:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1302 | 2017 | 7 | 30 | 9 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.2785 | 130_290 | <25mph | <15mph | HFTD - Distribution | 2017-07-30 09:46:00 | 1040 | 13.7198 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 4.76 | 2017-08-14T19:57:00Z | 17 | 8 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 4.76 | 2017-08-14T19:57:00Z | 17 | 17 | < 25mph
PG&E | 2016-07-08 10:49 | 2016-07-08 10:49 | 38.3373 | -122.1211 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 102291118 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42559.4507 | 2016-07-08 10:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0842 | 2016 | 7 | 8 | 10 | 49 | 16-0048647 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 19469 | 8.3702 | 151_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-08 10:49:00 | 585 | 20.6133 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AT068 | 6.17 | 2016-04-02T05:00:00Z | 0 | 1 | < 25mph |  |  |  | 0 | 0 | No data | AT068 | 6.17 | 2016-04-02T06:00:00Z | 0 | 2 | < 25mph
PG&E | 2018-10-16 | 10:44 | 40.5097 | -124.1624 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101004106 | Unknown | 12000 | Conductor | Overhead | Yes | 43389 | 10:44 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1942 | 2018 | 10 | 16 | 10 | 44 | 18-0090952 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 2081 | 4.5851 | 67_380 | <25mph | <15mph | HFTD - Distribution | 2018-10-16 10:44:00 | 1681 | 13.3626 | FALSE | <25mph | PG287 | 3.28 | 2019-04-10T17:20:00Z | 25.66 | 8 | 25-40mph | PG287 | 3.28 | 2019-04-10T17:20:00Z | 25.66 | 37 | 25-40mph | PG287 | 3.28 | 2019-04-10T18:00:00Z | 28.27 | 16 | 25-40mph | PG287 | 3.28 | 2019-04-10T18:00:00Z | 28.27 | 72 | 25-40mph
PG&E | 2017-07-25 15:52 | 15:51 | 38.3779 | -122.5388 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102031447 | Unknown | 12000 | Conductor | Overhead | Yes | 42941.6609 | 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1290 | 2017 | 7 | 25 | 15 | 51 | 17-0065437 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 18584 | 12.338 | 133_260 | <25mph | <15mph | HFTD - Distribution | 2017-07-25 15:51:00 | 1029 | 16.6773 | FALSE | <25mph | PG177 | 3.11 | 2019-09-18T08:00:00Z | 17.76 | 20 | < 25mph | PG593 | 5.38 | 2019-09-18T07:20:00Z | 17.98 | 83 | < 25mph | PG177 | 3.11 | 2019-09-18T08:00:00Z | 17.76 | 40 | < 25mph | PG162 | 7.57 | 2019-09-18T09:10:00Z | 19.35 | 166 | < 25mph
PG&E | 2015-11-21 10:36 | 2015-11-21 10:36 | 38.0679 | -120.1872 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101045952 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42329.4417 | 2015-11-21 10:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0677 | 2015 | 11 | 21 | 10 | 36 | 15-0079868 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18350 | 7.816 | 235_243 | <25mph | <15mph | HFTD - Distribution | 2015-11-21 10:36:00 | 421 | 16.6927 | FALSE | <25mph | MOUC1 | 3.29 | 2017-05-09T15:02:00Z | 10 | 1 | < 25mph | MOUC1 | 3.29 | 2017-05-09T15:02:00Z | 10 | 1 | < 25mph | MOUC1 | 3.29 | 2017-05-09T15:02:00Z | 10 | 2 | < 25mph | MOUC1 | 3.29 | 2017-05-09T15:02:00Z | 10 | 2 | < 25mph
PG&E | 2018-08-20 | 9:34 | 39.8014 | -121.5813 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100400441 | Unknown | 12000 | Conductor | Overhead | Yes | 43332 | 9:34 | Contact From Object | N.A. | Other | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1849 | 2018 | 8 | 20 | 9 | 34 | 18-0071596 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 394259 | 5.4464 | 175_338 | <25mph | <15mph | HFTD - Distribution | 2018-08-20 09:34:00 | 1588 | 11.8754 | FALSE | <25mph | PG333 | 0.95 | 2019-06-04T09:20:00Z | 11.18 | 16 | < 25mph | JBGC1 | 6.67 | 2019-06-04T09:13:00Z | 21 | 78 | < 25mph | PG333 | 0.95 | 2019-06-04T09:20:00Z | 11.18 | 32 | < 25mph | JBGC1 | 6.67 | 2019-06-04T10:13:00Z | 27 | 156 | 25-40mph
PG&E | 2017-06-24 10:32 | 10:31 | 38.9438 | -121.0447 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100090318 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42910.439 | 10:31 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1193 | 2017 | 6 | 24 | 10 | 31 | 17-0058318 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 582 | 9.5424 | 198_291 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 10:31:00 | 932 | 10.7882 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8862 | 4.36 | 2015-04-27T11:22:00Z | 11.99 | 22 | < 25mph |  |  |  | 0 | 0 | No data | D8862 | 4.36 | 2015-04-27T11:22:00Z | 11.99 | 43 | < 25mph
PG&E | 2016-07-29 | 18:16 | 38.5769 | -122.6187 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Selma Fire Department |  |  | 12000 | Conductor | Overhead | Yes | 42580 | 18:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0890 | 2016 | 7 | 29 | 18 | 16 | 16-0053726 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 177834 | 13.7145 | 130_271 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 18:16:00 | 635 | 15.1116 | FALSE | <25mph | E1553 | 3.84 | 2018-04-14T15:14:00Z | 3 | 4 | < 25mph | E1553 | 3.84 | 2018-04-14T15:14:00Z | 3 | 18 | < 25mph | E1553 | 3.84 | 2018-04-14T16:29:00Z | 4 | 8 | < 25mph | C1766 | 4.56 | 2018-04-14T16:02:00Z | 4.99 | 36 | < 25mph
PG&E | 2018-04-27 | 12:48 | 39.1717 | -120.8652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | incident # 9960 ph # 530-8850111 | 100075314 | Unknown | 12000 | Conductor | Overhead | Yes | 43217 | 12:48 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Dead | 1577 | 2018 | 4 | 27 | 12 | 48 | 18-0036310 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 28650 | 12.9115 | 205_304 | <25mph | <15mph | HFTD - Distribution | 2018-04-27 12:48:00 | 1319 | 12.9115 | FALSE | <25mph | SETC1 | 1.33 | 2017-10-01T05:28:00Z | 8.01 | 1 | < 25mph | SETC1 | 1.33 | 2017-10-01T05:28:00Z | 8.01 | 9 | < 25mph | SETC1 | 1.33 | 2017-10-01T05:28:00Z | 8.01 | 2 | < 25mph | SETC1 | 1.33 | 2017-10-01T05:28:00Z | 8.01 | 21 | < 25mph
PG&E | 2019-06-03 | 14:47 | 40.4419 | -122.3036 |  | Herbaceous | 1 meter - < 3 meters | Fire Dept | Anderson FD | 101495889 |  | 12000 | Insulator | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-456 | 2019 | 6 | 3 | 14 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 9.9807 | 145_374 | <25mph | <15mph | HFTD - Distribution | 2019-06-03 14:47:00 | 1799 | 16.209 | FALSE | <25mph | AP525 | 3.17 | 2018-04-18T06:00:00Z | 0 | 6 | < 25mph | RRAC1 | 5.14 | 2018-04-18T05:24:00Z | 4 | 11 | < 25mph | AP525 | 3.17 | 2018-04-18T07:00:00Z | 0 | 12 | < 25mph | RRAC1 | 5.14 | 2018-04-18T06:24:00Z | 5.99 | 22 | < 25mph
PG&E | 2015-10-09 06:32 | 2015-10-09 06:32 | 38.364 | -122.9173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 320 Freestone St, Frestone | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0642 | 2015 | 10 | 9 | 6 | 32 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 2.6818 | 117_260 | <25mph | <15mph | HFTD - Distribution | 2015-10-09 06:32:00 | 386 | 15.5803 | FALSE | <25mph | E5234 | 0.7 | 2016-03-20T00:39:00Z | 10 | 22 | < 25mph | AR323 | 5.17 | 2016-03-20T00:20:00Z | 17 | 48 | < 25mph | E5234 | 0.7 | 2016-03-20T00:39:00Z | 10 | 44 | < 25mph | AR323 | 5.17 | 2016-03-20T00:20:00Z | 17 | 96 | < 25mph
PG&E | 2017-09-18 | 13:01 | 39.3889 | -121.4054 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 103795057 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42996 | 13:01 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1418 | 2017 | 9 | 18 | 13 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 17.7047 | 182_316 | <25mph | <15mph | HFTD - Distribution | 2017-09-18 13:01:00 | 1156 | 19.5678 | FALSE | <25mph | BNGC1 | 1.17 | 2015-07-29T22:51:00Z | 11.01 | 1 | < 25mph | TT309 | 5.6 | 2015-07-29T22:45:00Z | 12.01 | 2 | < 25mph | BNGC1 | 1.17 | 2015-07-29T23:51:00Z | 13 | 2 | < 25mph | TT309 | 5.6 | 2015-07-29T23:45:00Z | 13 | 4 | < 25mph
PG&E | 2019-04-28 | 12:36 | 39.6756 | -121.5677 |  | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 100404366 |  | 12000 | Conductor | Overhead | Yes | 43583 | 12:36 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-166 | 2019 | 4 | 28 | 12 | 36 | 19-0046853 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 79810 | 6.7497 | 175_331 | <25mph | <15mph | HFTD - Distribution | 2019-04-28 12:36:00 | 1752 | 11.2512 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JBGC1 | 5.9 | 2018-04-23T03:13:00Z | 5.99 | 3 | < 25mph |  |  |  | 0 | 0 | No data | JBGC1 | 5.9 | 2018-04-23T03:13:00Z | 5.99 | 6 | < 25mph
PG&E | 2017-06-25 02:47 | 0:23 | 39.4043 | -123.3869 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102193088 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42911.1159 | 0:23 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1197 | 2017 | 6 | 25 | 0 | 23 | 17-0058406 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 23100 | 15.6787 | 98_318 | <25mph | <15mph | HFTD - Distribution | 2017-06-25 00:23:00 | 935 | 19.8426 | FALSE | <25mph | E4027 | 2.16 | 2017-11-12T22:28:00Z | 10 | 24 | < 25mph | E4027 | 2.16 | 2017-11-12T22:28:00Z | 10 | 44 | < 25mph | E4027 | 2.16 | 2017-11-12T22:28:00Z | 10 | 48 | < 25mph | AU552 | 7.7 | 2017-11-12T23:26:00Z | 12.01 | 91 | < 25mph
PG&E | 2017-09-18 | 13:01 | 39.3889 | -121.4054 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 103795057 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42996 | 13:01 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1418 | 2017 | 9 | 18 | 13 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 17.7047 | 182_316 | <25mph | <15mph | HFTD - Distribution | 2017-09-18 13:01:00 | 1156 | 19.5678 | FALSE | <25mph | BNGC1 | 1.17 | 2017-05-22T20:51:00Z | 10 | 1 | < 25mph | BNGC1 | 1.17 | 2017-05-22T20:51:00Z | 10 | 1 | < 25mph | BNGC1 | 1.17 | 2017-05-22T21:51:00Z | 10 | 2 | < 25mph | BNGC1 | 1.17 | 2017-05-22T21:51:00Z | 10 | 2 | < 25mph
PG&E | 2016-08-22 | 2016-08-22 16:10 | 37.9666 | -120.2395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Toulumne City FD | 101043683 |  | 17000 | Conductor | Overhead | Yes | 42604 | 2016-08-22 16:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0941 | 2016 | 8 | 22 | 16 | 10 | 16-0059149 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 78534 | 13.4322 | 233_237 | <25mph | <15mph | HFTD - Distribution | 2016-08-22 16:10:00 | 684 | 13.7297 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.67 | 2015-10-10T11:02:00Z | 15.99 | 10 | < 25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.67 | 2015-10-10T12:02:00Z | 17 | 20 | < 25mph
PG&E | 2017-07-28 | 14:02 | 40.9997 | -121.9579 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101512624 | Unknown | 12000 | Conductor | Overhead | Yes | 42944 | 14:02 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1293 | 2017 | 7 | 28 | 14 | 2 | 17-0066367 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 46581 | 11.7167 | 159_405 | <25mph | <15mph | HFTD - Distribution | 2017-07-28 14:02:00 | 1031 | 11.7167 | FALSE | <25mph | OMTC1 | 1.45 | 2018-10-18T01:26:00Z | 5.99 | 1 | < 25mph | OMTC1 | 1.45 | 2018-10-18T01:26:00Z | 5.99 | 1 | < 25mph | OMTC1 | 1.45 | 2018-10-18T01:26:00Z | 5.99 | 2 | < 25mph | OMTC1 | 1.45 | 2018-10-18T01:26:00Z | 5.99 | 2 | < 25mph
PG&E | 2016-07-25 15:32 | 2016-07-25 15:32 | 38.3522 | -120.7107 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42576.6472 | 2016-07-25 15:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0878 | 2016 | 7 | 25 | 15 | 32 | 16-0052398 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 19951 | 10.4912 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-25 15:32:00 | 621 | 14.4675 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2015-05-16T11:56:00Z | 8.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2015-05-16T12:56:00Z | 10 | 2 | < 25mph
PG&E | 2018-07-28 | 6:51 | 38.7473 | -120.7866 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101418155 | AT&T | 21000 | Conductor | Overhead | Yes | 43309 | 6:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1794 | 2018 | 7 | 28 | 6 | 51 | 18-0064545 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 15429 | 14.6813 | 209_280 | <25mph | <15mph | HFTD - Distribution | 2018-07-28 06:51:00 | 1534 | 14.6813 | FALSE | <25mph | E5691 | 0.5 | 2015-07-02T15:37:00Z | 5.99 | 18 | < 25mph | C6129 | 4.92 | 2015-07-02T15:19:00Z | 7 | 43 | < 25mph | E5691 | 0.5 | 2015-07-02T16:37:00Z | 12.01 | 36 | < 25mph | C6129 | 4.92 | 2015-07-02T16:19:00Z | 14.99 | 85 | < 25mph
PG&E | 2015-09-10 16:24 | 2015-09-10 16:24 | 38.5049 | -122.3535 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103159970 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42257.6833 | 2015-09-10 16:24 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0589 | 2015 | 9 | 10 | 16 | 24 | 15-0060610 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 130124 | 14.3548 | 141_267 | <25mph | <15mph | HFTD - Distribution | 2015-09-10 16:24:00 | 334 | 16.5969 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.22 | 2015-06-06T02:29:00Z | 27 | 1 | 25-40mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.22 | 2015-06-06T02:29:00Z | 27 | 2 | 25-40mph
PG&E | 2015-02-07 18:38 | 2015-02-07 18:38 | 40.4674 | -123.6545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | mile marker 36.61, hwy 36, bridgeville |  | 12000 | Conductor | Overhead | Yes | 42042.7764 | 2015-02-07 18:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0262 | 2015 | 2 | 7 | 18 | 38 | 15-0011390 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 7691 | 20.9308 | 88_377 | <25mph | <15mph | HFTD - Distribution | 2015-02-07 18:38:00 | 9 | 24.639 | FALSE | <25mph | E8593 | 2.58 | 2018-09-29T21:05:00Z | 17 | 12 | < 25mph | E8593 | 2.58 | 2018-09-29T21:05:00Z | 17 | 13 | < 25mph | E8593 | 2.58 | 2018-09-29T21:05:00Z | 17 | 24 | < 25mph | E8593 | 2.58 | 2018-09-29T21:05:00Z | 17 | 26 | < 25mph
PG&E | 2018-01-16 | 14:25 | 34.5703 | -119.9645 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101921689 | Verizon | 12000 | Conductor | Overhead | Yes | 43116 | 14:25 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1556 | 2018 | 1 | 16 | 14 | 25 | 18-0006506 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 23519 | 5.0963 | 247_50 | <25mph | <15mph | HFTD - Distribution | 2018-01-16 14:25:00 | 1298 | 9.8389 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KIZA | 6.8 | 2015-05-08T22:55:00Z | 17.27 | 3 | < 25mph |  |  |  | 0 | 0 | No data | AP901 | 7.72 | 2015-05-08T23:40:00Z | 20 | 9 | < 25mph
PG&E | 2017-09-04 | 3:29 | 39.8317 | -121.8444 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102300100 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1392 | 2017 | 9 | 4 | 3 | 29 | 17-0075723 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 214974 | 9.8341 | 164_340 | <25mph | <15mph | HFTD - Distribution | 2017-09-04 03:29:00 | 1130 | 13.8789 | FALSE | <25mph | PG286 | 3.27 | 2019-06-03T11:20:00Z | 6.58 | 6 | < 25mph | PG339 | 7.74 | 2019-06-03T11:20:00Z | 10.29 | 23 | < 25mph | PG286 | 3.27 | 2019-06-03T11:20:00Z | 6.58 | 12 | < 25mph | PG339 | 7.74 | 2019-06-03T11:20:00Z | 10.29 | 46 | < 25mph
PG&E | 2019-06-10 | 13:29 | 38.8137 | -120.9433 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Other | Customer | 153652109 |  | 21000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-243 | 2019 | 6 | 10 | 13 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.2437 | 202_284 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 13:29:00 | 1823 | 9.9566 | FALSE | <25mph | PLTC1 | 3.76 | 2016-07-25T17:56:00Z | 7 | 1 | < 25mph | PLTC1 | 3.76 | 2016-07-25T17:56:00Z | 7 | 32 | < 25mph | PLTC1 | 3.76 | 2016-07-25T18:56:00Z | 10 | 2 | < 25mph | PLTC1 | 3.76 | 2016-07-25T18:56:00Z | 10 | 63 | < 25mph
PG&E | 2018-10-08 | 11:03 | 38.2621 | -122.7881 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101987186 | AT&T | 12000 | Conductor | Overhead | No | N.A. | N.A. | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1933 | 2018 | 10 | 8 | 11 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 15.6859 | 122_254 | <25mph | <15mph | HFTD - Distribution | 2018-10-08 11:03:00 | 1672 | 17.3485 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E8654 | 6.76 | 2018-04-22T12:11:00Z | 2.01 | 10 | < 25mph |  |  |  | 0 | 0 | No data | E8654 | 6.76 | 2018-04-22T13:21:00Z | 2.01 | 20 | < 25mph
PG&E | 2015-02-23 02:05 | 2015-02-23 02:05 | 39.3027 | -121.0175 | Vegetation | Rural | < 3 meters | Fire Agency | NEVADA CITY FIRE | 100086316 |  | 12000 | Conductor | Overhead | Yes | 42058.0868 | 2015-02-23 02:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0267 | 2015 | 2 | 23 | 2 | 5 | 15-0014910 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 93279 | 24.5459 | 199_311 | <25mph | <15mph | HFTD - Distribution | 2015-02-23 02:05:00 | 14 | 25.6662 | FALSE | 25-40mph | E3651 | 2.92 | 2015-01-16T18:15:00Z | 8.01 | 12 | < 25mph | E5439 | 4.63 | 2015-01-16T18:35:00Z | 14 | 66 | < 25mph | E3651 | 2.92 | 2015-01-16T18:15:00Z | 8.01 | 24 | < 25mph | E5439 | 4.63 | 2015-01-16T18:35:00Z | 14 | 131 | < 25mph
PG&E | 2018-07-18 | 1:14 | 38.3671 | -120.5578 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101247987 | Unknown | 12000 | Conductor | Overhead | Yes | 43299 | 1:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1761 | 2018 | 7 | 18 | 1 | 14 | 18-0060882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6420 | 6.6576 | 219_259 | <25mph | <15mph | HFTD - Distribution | 2018-07-18 01:14:00 | 1501 | 11.9385 | FALSE | <25mph | PG095 | 1.67 | 2018-11-30T17:40:00Z | 3.51 | 22 | < 25mph | PG108 | 5.25 | 2018-11-30T18:00:00Z | 5.7 | 67 | < 25mph | AT450 | 3.1 | 2018-11-30T19:33:00Z | 5.99 | 44 | < 25mph | AT450 | 3.1 | 2018-11-30T19:33:00Z | 5.99 | 133 | < 25mph
PG&E | 2017-05-15 | 3:05 | 35.6261 | -120.8962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101873299 | Unknown | 21000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1097 | 2017 | 5 | 15 | 3 | 5 | 17-0047837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 337188 | 4.016 | 204_108 | <25mph | <15mph | HFTD - Distribution | 2017-05-15 03:05:00 | 837 | 18.5139 | FALSE | <25mph | TABC1 | 2.62 | 2016-02-21T16:07:00Z | 2.01 | 1 | < 25mph | TABC1 | 2.62 | 2016-02-21T16:07:00Z | 2.01 | 1 | < 25mph | TABC1 | 2.62 | 2016-02-21T17:07:00Z | 3 | 2 | < 25mph | TABC1 | 2.62 | 2016-02-21T17:07:00Z | 3 | 2 | < 25mph
PG&E | 2016-06-20 | 2016-06-20 16:45 | 41.0697 | -123.6789 | Vegetation | RURAL | < 3 meters | Fire Agency | Hoopa FD | 101011420 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42541 | 2016-06-20 16:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0811 | 2016 | 6 | 20 | 16 | 45 | 16-0044577 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7361 | 15.1157 | 88_410 | <25mph | <15mph | HFTD - Distribution | 2016-06-20 16:45:00 | 554 | 15.1157 | FALSE | <25mph | BIIC1 | 2.95 | 2019-01-01T19:40:00Z | 10 | 2 | < 25mph | BIIC1 | 2.95 | 2019-01-01T19:40:00Z | 10 | 2 | < 25mph | BIIC1 | 2.95 | 2019-01-01T20:40:00Z | 14.99 | 4 | < 25mph | BIIC1 | 2.95 | 2019-01-01T20:40:00Z | 14.99 | 4 | < 25mph
PG&E | 2019-04-09 | 14:07 | 34.6311 | -119.9813 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Fire Dept | Santa Barbra County FD | 101863014 |  | 12000 | Conductor | Overhead | Yes | 43564 | 14:07 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-263 | 2019 | 4 | 9 | 14 | 7 | 19-0040969 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 70756 | 38.5369 | 246_53 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-09 14:07:00 | 1737 | 43.1384 | FALSE | 40-55mph |  |  |  | 0 | 0 | No data | FGMC1 | 7.28 | 2017-03-09T08:35:00Z | 18.01 | 19 | < 25mph |  |  |  | 0 | 0 | No data | FGMC1 | 7.28 | 2017-03-09T08:35:00Z | 18.01 | 35 | < 25mph
PG&E | 2017-06-22 17:54 | 18:07 | 38.7583 | -120.7176 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101401088 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.7461 | 18:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1188 | 2017 | 6 | 22 | 18 | 7 | 17-0057857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 8517 | 11.5365 | 212_281 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 18:07:00 | 927 | 16.1873 | FALSE | <25mph | PG104 | 2.74 | 2019-01-25T07:30:00Z | 10.51 | 35 | < 25mph | PG104 | 2.74 | 2019-01-25T07:30:00Z | 10.51 | 64 | < 25mph | PG104 | 2.74 | 2019-01-25T08:30:00Z | 14.25 | 70 | < 25mph | PG104 | 2.74 | 2019-01-25T08:30:00Z | 14.25 | 128 | < 25mph
PG&E | 2015-08-22 20:38 | 2015-08-22 20:38 | 38.7748 | -120.8564 | Vegetation | Rural | < 3 meters | Self Extinguished |  | at base of co pole 21721 - 720 Woodridge Rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42238.8597 | 2015-08-22 20:38 | Contact From Object | N.A. | Vegetation | Communication Facility | Unknown | tree hit phone lines | Fell into (Moderate-Severe defect) | 0549 | 2015 | 8 | 22 | 20 | 38 | 15-0056766 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26513 | 9.2929 | 206_282 | <25mph | <15mph | HFTD - Distribution | 2015-08-22 20:38:00 | 293 | 10.7008 | FALSE | <25mph | E5691 | 3.87 | 2016-11-08T19:00:00Z | 0 | 12 | < 25mph | C6129 | 5.5 | 2016-11-08T18:09:00Z | 7 | 59 | < 25mph | E5691 | 3.87 | 2016-11-08T20:00:00Z | 0 | 24 | < 25mph | C6129 | 5.5 | 2016-11-08T19:09:00Z | 8.01 | 119 | < 25mph
PG&E | 2017-10-11 | 11:57 | 38.5015 | -123.0237 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101974930 | Unknown | 12000 | Conductor | Overhead | Yes | 43019 | 11:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1484 | 2017 | 10 | 11 | 11 | 57 | 17-0086350 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 226925 | 16.5068 | 112_268 | <25mph | <15mph | HFTD - Distribution | 2017-10-11 11:57:00 | 1227 | 19.0479 | FALSE | <25mph | AR798 | 1.52 | 2015-11-07T00:00:00Z | 7 | 28 | < 25mph | AR798 | 1.52 | 2015-11-07T00:00:00Z | 7 | 28 | < 25mph | AR798 | 1.52 | 2015-11-07T00:00:00Z | 7 | 55 | < 25mph | AR798 | 1.52 | 2015-11-07T00:00:00Z | 7 | 55 | < 25mph
7. Camp Fire | 2018-11-08 | 6:33 | 39.8134 | -121.4347 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 60000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1993 | 2018 | 11 | 8 | 6 | 33 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Conductor | 826291590 | 33.1236 | 181_339 | 25-40mph | 30-45mph | HFTD - Transmission | 2018-11-08 06:33:00 | 1699 | 39.0185 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | JBGC1 | 6.08 | 2018-02-14T23:13:00Z | 11.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | JBGC1 | 6.08 | 2018-02-15T00:13:00Z | 11.01 | 2 | < 25mph
PG&E | 2017-07-23 18:25 | 18:25 | 39.6723 | -123.5336 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103823226 | Unknown | 12000 | Conductor | Overhead | Yes | 42939.7676 | 18:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1284 | 2017 | 7 | 23 | 18 | 25 | 17-0064854 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 12864 | 11.8402 | 92_333 | <25mph | <15mph | HFTD - Distribution | 2017-07-23 18:25:00 | 1023 | 16.2282 | FALSE | <25mph | LAYC1 | 3.32 | 2019-03-05T19:29:00Z | 8.01 | 1 | < 25mph | UCAC | 6.93 | 2019-03-05T19:40:00Z | 8.5 | 7 | < 25mph | LAYC1 | 3.32 | 2019-03-05T20:29:00Z | 12.01 | 2 | < 25mph | LAYC1 | 3.32 | 2019-03-05T20:29:00Z | 12.01 | 14 | < 25mph
PG&E | 2019-04-09 | 14:07 | 34.6311 | -119.9813 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Fire Dept | Santa Barbra County FD | 101863014 |  | 12000 | Conductor | Overhead | Yes | 43564 | 14:07 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-263 | 2019 | 4 | 9 | 14 | 7 | 19-0040969 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 70756 | 38.5369 | 246_53 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-09 14:07:00 | 1737 | 43.1384 | FALSE | 40-55mph |  |  |  | 0 | 0 | No data | SXWC1 | 5.08 | 2019-04-03T03:09:00Z | 18.99 | 11 | < 25mph |  |  |  | 0 | 0 | No data | SXWC1 | 5.08 | 2019-04-03T03:09:00Z | 18.99 | 26 | < 25mph
PG&E | 2017-09-27 | 12:12 | 39.4845 | -121.3545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | bill lopez cell 530 521-8052 | 100429924 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 43005 | 12:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1436 | 2017 | 9 | 27 | 12 | 12 | 17-0082180 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 6370 | 7.6613 | 184_321 | <25mph | <15mph | HFTD - Distribution | 2017-09-27 12:12:00 | 1174 | 27.61 | FALSE | 25-40mph | TT309 | 3.08 | 2015-12-17T19:45:00Z | 10 | 1 | < 25mph | TT309 | 3.08 | 2015-12-17T19:45:00Z | 10 | 2 | < 25mph | TT309 | 3.08 | 2015-12-17T20:45:00Z | 11.01 | 2 | < 25mph | TT309 | 3.08 | 2015-12-17T20:45:00Z | 11.01 | 4 | < 25mph
PG&E | 2018-11-13 | 15:41 | 37.0644 | -121.9578 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101680441 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43417 | 15:41 | Other | N.A. | N.A. | N.A. | Human Error | Grow house | Other/Unknown | 1973 | 2018 | 11 | 13 | 15 | 41 | 18-0099492 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 21484 | 1.9347 | 157_188 | <25mph | <15mph | HFTD - Distribution | 2018-11-13 15:41:00 | 1713 | 13.1257 | FALSE | <25mph | D8700 | 0.73 | 2015-10-08T09:53:00Z | 4 | 36 | < 25mph | E5038 | 6.81 | 2015-10-08T09:59:00Z | 7 | 130 | < 25mph | D8700 | 0.73 | 2015-10-08T09:53:00Z | 4 | 71 | < 25mph | E5038 | 6.81 | 2015-10-08T11:14:00Z | 8.01 | 249 | < 25mph
PG&E | 2015-08-03 00:07 | 2015-08-03 00:07 | 40.5056 | -122.347 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | COTTONWOOD FIRE DEPT | 101503428 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42219.0049 | 2015-08-03 00:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0509 | 2015 | 8 | 3 | 0 | 7 | 15-0052184 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 10427 | 9.7241 | 143_378 | <25mph | <15mph | HFTD - Distribution | 2015-08-03 00:07:00 | 254 | 13.2206 | FALSE | <25mph | RRAC1 | 2.97 | 2016-05-12T23:24:00Z | 12.01 | 1 | < 25mph | RRAC1 | 2.97 | 2016-05-12T23:24:00Z | 12.01 | 15 | < 25mph | RRAC1 | 2.97 | 2016-05-12T23:24:00Z | 12.01 | 2 | < 25mph | RRAC1 | 2.97 | 2016-05-12T23:24:00Z | 12.01 | 29 | < 25mph
PG&E | 2017-08-28 | 10:07 | 39.0472 | -120.7859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | FORESTHILL | 100019525 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 10:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1357 | 2017 | 8 | 28 | 10 | 7 | 17-0073379 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 10077 | 5.9792 | 209_297 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 10:07:00 | 1095 | 13.4783 | FALSE | <25mph | AU268 | 3.78 | 2016-02-14T05:28:00Z | 1.01 | 5 | < 25mph | FSHC1 | 4.22 | 2016-02-14T05:33:00Z | 3 | 6 | < 25mph | AU268 | 3.78 | 2016-02-14T05:28:00Z | 1.01 | 8 | < 25mph | FSHC1 | 4.22 | 2016-02-14T06:33:00Z | 5.99 | 10 | < 25mph
PG&E | 2017-07-22 12:26 | 12:25 | 40.8795 | -123.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Josh , comander chief of forest service. | 100980577 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.518 | 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1279 | 2017 | 7 | 22 | 12 | 25 | 17-0064721 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 23227 | 10.7493 | 84_399 | <25mph | <15mph | HFTD - Distribution | 2017-07-22 12:25:00 | 1018 | 13.5476 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BHTC1 | 5.5 | 2017-06-26T04:46:00Z | 8.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | BHTC1 | 5.5 | 2017-06-26T04:46:00Z | 8.99 | 2 | < 25mph
PG&E | 2016-05-18 | 18:24 | 39.7381 | -123.1587 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42508 | 18:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0735 | 2016 | 5 | 18 | 18 | 24 | 16-0036911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1482 | 13.4862 | 108_336 | <25mph | <15mph | HFTD - Distribution | 2016-05-18 18:24:00 | 480 | 21.4181 | FALSE | <25mph | C3111 | 2.79 | 2018-01-28T15:00:00Z | 2.01 | 2 | < 25mph | EELC1 | 7.26 | 2018-01-28T14:45:00Z | 3 | 3 | < 25mph | C3111 | 2.79 | 2018-01-28T16:00:00Z | 2.01 | 4 | < 25mph | EELC1 | 7.26 | 2018-01-28T15:45:00Z | 3 | 6 | < 25mph
PG&E | 2015-08-17 08:37 | 2015-08-17 08:37 | 37.0757 | -122.023 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101800237 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0537 | 2015 | 8 | 17 | 8 | 37 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 1.4249 | 154_188 | <25mph | <15mph | HFTD - Distribution | 2015-08-17 08:37:00 | 281 | 11.7495 | FALSE | <25mph | E5965 | 3.61 | 2016-04-27T14:39:00Z | 2.01 | 38 | < 25mph | E6085 | 7.55 | 2016-04-27T14:51:00Z | 8.99 | 165 | < 25mph | E5965 | 3.61 | 2016-04-27T15:54:00Z | 4.99 | 77 | < 25mph | E6085 | 7.55 | 2016-04-27T14:51:00Z | 8.99 | 328 | < 25mph
PG&E | 2019-08-22 | 22:23 | 39.139 | -121.0194 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 152481106 |  | 12000 | Conductor | Overhead | Yes | 43699 | 22:23 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-346 | 2019 | 8 | 22 | 22 | 23 | 19-0091224 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38628 | 9.4944 | 199_302 | <25mph | <15mph | HFTD - Distribution | 2019-08-22 22:23:00 | 1993 | 12.3163 | FALSE | <25mph | AT999 | 3.14 | 2018-01-16T18:08:00Z | 3 | 16 | < 25mph | E1789 | 6.14 | 2018-01-16T18:30:00Z | 8.01 | 81 | < 25mph | AT999 | 3.14 | 2018-01-16T19:23:00Z | 3 | 32 | < 25mph | E1789 | 6.14 | 2018-01-16T18:30:00Z | 8.01 | 162 | < 25mph
PG&E | 2018-10-07 | 1:44 | 37.178 | -122.0267 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Mike Mathiesen 408-472-1613 Incident # SCU7096 | 100518363 | Unknown | 12000 | Conductor | Overhead | Yes | 43380 | 1:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1929 | 2018 | 10 | 7 | 1 | 44 | 18-0087807 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 224444 | 25.0906 | 154_194 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-07 01:44:00 | 1668 | 25.864 | FALSE | 25-40mph | AV005 | 3.71 | 2017-12-08T01:02:00Z | 0 | 4 | < 25mph | D8979 | 5.36 | 2017-12-08T00:18:00Z | 7 | 111 | < 25mph | AV005 | 3.71 | 2017-12-08T02:02:00Z | 0 | 8 | < 25mph | D8979 | 5.36 | 2017-12-08T02:00:00Z | 10 | 223 | < 25mph
PG&E | 2015-05-09 13:10 | 2015-05-09 13:10 | 39.2343 | -121.2468 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100000103 | None | 21000 | Conductor | Overhead | Yes | 42133.5486 | 2015-05-09 13:10 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0311 | 2015 | 5 | 9 | 13 | 10 | 15-0033085 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 382926 | 12.172 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 13:10:00 | 57 | 17.071 | FALSE | <25mph | E2572 | 3.27 | 2016-10-31T07:28:00Z | 4.99 | 12 | < 25mph | E6355 | 7.8 | 2016-10-31T08:00:00Z | 13 | 18 | < 25mph | E2572 | 3.27 | 2016-10-31T07:28:00Z | 4.99 | 23 | < 25mph | E6355 | 7.8 | 2016-10-31T09:00:00Z | 13 | 35 | < 25mph
PG&E | 2015-09-24 13:56 | 2015-09-24 13:56 | 39.3508 | -121.2454 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 9692 Rices-Texas Hill rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42271.5806 | 2015-09-24 13:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0614 | 2015 | 9 | 24 | 13 | 56 | 15-0063159 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 51917 | 10.3419 | 189_313 | <25mph | <15mph | HFTD - Distribution | 2015-09-24 13:56:00 | 359 | 13.3743 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RRRC1 | 7.59 | 2015-10-06T03:13:00Z | 4 | 2 | < 25mph |  |  |  | 0 | 0 | No data | RRRC1 | 7.59 | 2015-10-06T03:13:00Z | 4 | 4 | < 25mph
PG&E | 2017-07-23 09:22 | 09:22 | 40.642 | -122.2302 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT? | 101459708 | FRONTIER COMMUNICATI | 12000 | Conductor | Overhead | Yes | 42939.3906 | 09:22 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1282 | 2017 | 7 | 23 | 9 | 22 | 17-0064801 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 184712 | 3.9314 | 148_385 | <25mph | <15mph | HFTD - Distribution | 2017-07-23 09:22:00 | 1021 | 13.6933 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C5599 | 5.97 | 2016-10-29T08:16:00Z | 0 | 3 | < 25mph |  |  |  | 0 | 0 | No data | C5599 | 5.97 | 2016-10-29T09:16:00Z | 0 | 7 | < 25mph
PG&E | 2016-07-27 17:05 | 2016-07-27 17:05 | 38.5392 | -122.7656 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102029945 |  | 60000 | Conductor | Overhead | Yes | 42578.7118 | 2016-07-27 17:05 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0882 | 2016 | 7 | 27 | 17 | 5 | FU-2016-047 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 18.1446 | 123_269 | <25mph | <15mph | HFTD - Transmission | 2016-07-27 17:05:00 | 625 | 18.1446 | FALSE | <25mph | E6724 | 1.55 | 2019-02-11T04:00:00Z | 2.01 | 6 | < 25mph | RSAC1 | 5.1 | 2019-02-11T03:29:00Z | 11.01 | 47 | < 25mph | E6724 | 1.55 | 2019-02-11T04:30:00Z | 2.01 | 12 | < 25mph | RSAC1 | 5.1 | 2019-02-11T04:29:00Z | 11.01 | 94 | < 25mph
PG&E | 2015-09-10 05:42 | 2015-09-10 05:42 | 37.4609 | -121.8434 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100619766 | None | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0588 | 2015 | 9 | 10 | 5 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 1.7354 | 163_209 | <25mph | <15mph | HFTD - Distribution | 2015-09-10 05:42:00 | 333 | 13.8129 | FALSE | <25mph | E3968 | 2.89 | 2017-10-31T09:39:00Z | 0 | 4 | < 25mph | RSPC1 | 6.56 | 2017-10-31T09:28:00Z | 13 | 32 | < 25mph | E3968 | 2.89 | 2017-10-31T10:39:00Z | 0 | 8 | < 25mph | RSPC1 | 6.56 | 2017-10-31T09:28:00Z | 13 | 64 | < 25mph
PG&E | 2018-09-29 | 16:16 | 41.0219 | -123.655 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Hoopa Fire Dept | 100962165 | Unknown | 12000 | Conductor | Overhead | Yes | 43372 | 16:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1923 | 2018 | 9 | 29 | 16 | 16 | 18-0084877 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 16028 | 7.8421 | 89_407 | <25mph | <15mph | HFTD - Distribution | 2018-09-29 16:16:00 | 1662 | 11.5265 | FALSE | <25mph | HOAC1 | 1.98 | 2018-06-10T09:40:00Z | 4.99 | 1 | < 25mph | BHTC1 | 7.5 | 2018-06-10T09:46:00Z | 7 | 7 | < 25mph | HOAC1 | 1.98 | 2018-06-10T10:40:00Z | 4.99 | 2 | < 25mph | BHTC1 | 7.5 | 2018-06-10T10:46:00Z | 7 | 14 | < 25mph
[49 empty] | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0
[49 empty] | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0
[49 empty] | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0
[49 empty] | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0
[49 empty] | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0
[49 empty] | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0
[49 empty] | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0
[49 empty] | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0
[49 empty] | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0
[49 empty] | 0 | 0 |  |  |  | 0 | 0 |  |  |  |  | 0 | 0 |  |  |  |  | 0 | 0
Note on AP4: Based on the max wind gust speed in the hour of ignition. used wind gust speed factor of 1.6.
Note on AW4: Based on the max wind gust speed +/- 12 hours of ignition. Used wind gust speed factor of 1.6.
Note on AY4: based on mph_day_max

## SignifAnalysis
| Count of 8m/2h Category |  |  | Ignition data | Exp | P>25(chi-squared) | phat25 mc | 0.067929
< 25mph | 2264 | 2264 | 0.93207 | 520 | 534.0766 | 0.019437 | phat25 ig | 0.092496
25-40mph | 139 | 165 | 0.067929 | 53 | 38.9234 |  | phat25 pl | 0.072618
40-55mph | 20 | 2429 | 1 | 573 |  |  | phat25 dt | 0.024566
55mph+ | 6 | [5 empty] | SE pooled | 0.012052
No data | 71 | 0.0284 |  |  |  |  | z-score | 2.0383
Grand Total | 2500 | [5 empty] | p-value | 0.020758
| Count of 8m/1h Category |  |  | Ignition data | Exp | P>25(chi-squared) | phat25 mc | 0.055189
< 25mph | 2294 | 2294 | 0.94481 | 526 | 540.4316 | 0.0082294 | phat25 ig | 0.08042
25-40mph | 116 | 134 | 0.055189 | 46 | 31.5684 |  | phat25 pl | 0.06
40-55mph | 13 | 2428 | 1 | 572 |  |  | phat25 dt | 0.02523
55mph+ | 5 | [5 empty] | SE pooled | 0.011038
No data | 72 | 0.0288 |  |  |  |  | z-score | 2.2858
Grand Total | 2500 | [5 empty] | p-value | 0.011132
| Count of 4m/2h Category |  |  | Ignition data | Exp | P>25(chi-squared) | phat25 mc | 0.0375
< 25mph | 1617 | 1617 | 0.9625 | 374 | 378.2625 | 0.25774 | phat25 ig | 0.048346
25-40mph | 55 | 63 | 0.0375 | 19 | 14.7375 |  | phat25 pl | 0.039556
40-55mph | 6 | 1680 | 1 | 393 |  |  | phat25 dt | 0.010846
55mph+ | 2 | [5 empty] | SE pooled | 0.010922
No data | 820 | 0.328 |  |  |  |  | z-score | 0.99307
Grand Total | 2500 | [5 empty] | p-value | 0.16034
Row Labels | Count of 4m/1h Category |  |  | Ignition data | Exp | P>25(chi-squared) | phat25 mc | 0.02806
< 25mph | 1628 | 1628 | 0.97194 | 374 | 381.9725 | 0.014883 | phat25 ig | 0.048346
25-40mph | 42 | 47 | 0.02806 | 19 | 11.0275 |  | phat25 pl | 0.031915
40-55mph | 3 | 1675 | 1 | 393 |  |  | phat25 dt | 0.020286
55mph+ | 2 | [5 empty] | SE pooled | 0.009852
No data | 825 | 0.33 |  |  |  |  | z-score | 2.0591
Grand Total | 2500 | [5 empty] | p-value | 0.019742

## AnalysisMbar
Correlation Analysis
[7 empty] | R: | 0.44012
[7 empty] | N: | 573
[7 empty] | t: | 11.7125
[7 empty] | P: | 1.5136e-28
POMMS gusts | Column
| RFW |  |  |  |  | RFW Total | No RFW |  |  |  |  | No RFW Total | Grand Total
Row Labels | 2015 | 2016 | 2017 | 2018 | 2019 |  | 2015 | 2016 | 2017 | 2018 | 2019
<25mph | 2 | 2 | 9 | 11 | 7 | 31 | 105 | 91 | 127 | 103 | 85 | 511 | 542
25-40mph |  | 1 | 5 | 5 |  | 11 | 1 | 4 | 4 | 4 | 5 | 18 | 29 |  | POMMS (PG&E) | [5 empty] | Measured (MGRA)
40-55mph |  |  | 1 |  |  | 1 |  |  |  | 1 |  | 1 | 2 | Gust (mph) | Vegetation |  | Equipment |  | Agent |  | Vegetation |  | Equipment |  | Agent
Grand Total | 2 | 3 | 15 | 16 | 7 | 43 | 106 | 95 | 131 | 108 | 90 | 530 | 573 | < 25mph | 241 | 92.34% | 146 | 94.81% | 123 | 98.4% | 229 | 87.74% | 139 | 90.26% | 122 | 97.6%
[14 empty] | 25-40mph | 19 | 7.28% | 7 | 4.545% | 2 | 1.6% | 22 | 8.429% | 13 | 8.442% | 2 | 1.6%
Measured Gusts | [13 empty] | 40-55mph | 1 | 0.3831% | 1 | 0.6494% |  | 0% | 6 | 2.299% | 2 | 1.299% | 1 | 0.8%
| RFW |  |  |  |  | RFW Total | No RFW |  |  |  |  | No RFW Total | Grand Total | 55mph+ | [6 empty] | 4 | 1.533%
| 2015 | 2016 | 2017 | 2018 | 2019 |  | 2015 | 2016 | 2017 | 2018 | 2019 |  |  | Total | 261 |  | 154 |  | 125 |  | 261 |  | 154 |  | 125
< 25mph | 2 | 2 | 13 | 14 | 4 | 35 | 94 | 87 | 121 | 102 | 81 | 485 | 520
25-40mph |  | 1 | 1 |  | 3 | 5 | 9 | 5 | 10 | 5 | 6 | 35 | 40
40-55mph |  |  | 1 | 2 |  | 3 | 1 | 1 |  | 1 | 3 | 6 | 9
55mph+ | [6 empty] | 2 | 2 |  |  |  | 4 | 4
Grand Total | 2 | 3 | 15 | 16 | 7 | 43 | 106 | 95 | 131 | 108 | 90 | 530 | 573
Measured | [7 empty] | POMMS (PG&E) |  |  | Measured (MGRA)
Row Labels | Vegetation | Row Labels | Equipment | Row Labels | Agent |  | Gust (mph) | Vegetation | Equipment | Agent | Vegetation | Equipment | Agent
< 25mph | 229 | < 25mph | 139 | < 25mph | 122 |  | < 25mph | 241 | 146 | 123 | 229 | 139 | 122
25-40mph | 22 | 25-40mph | 13 | 25-40mph | 2 |  | 25-40mph | 19 | 7 | 2 | 22 | 13 | 2
40-55mph | 6 | 40-55mph | 2 | 40-55mph | 1 |  | 40-55mph | 1 | 1 |  | 6 | 2 | 1
55mph+ | 4 | Grand Total | 154 | Grand Total | 125 |  | 55mph+ |  |  |  | 4
Grand Total | 261
PG&E
Row Labels | Vegetation | Row Labels | Equipment | Row Labels | Agent
<25mph | 241 | <25mph | 146 | <25mph | 123
25-40mph | 19 | 25-40mph | 7 | 25-40mph | 2
40-55mph | 1 | 40-55mph | 1 | Grand Total | 125
Grand Total | 261 | Grand Total | 154
Count of 8m/1h
| RFW |  |  |  |  | RFW Total | No RFW |  |  |  |  | No RFW Total | Grand Total
Row Labels | 2015 | 2016 | 2017 | 2018 | 2019 |  | 2015 | 2016 | 2017 | 2018 | 2019
< 25mph | 2 | 2 | 13 | 14 | 4 | 35 | 95 | 89 | 123 | 102 | 82 | 491 | 526
25-40mph |  | 1 | 2 |  | 3 | 6 | 7 | 4 | 8 | 5 | 6 | 30 | 36
40-55mph |  |  |  | 2 |  | 2 | 2 | 2 |  | 1 | 2 | 7 | 9
55mph+ | [6 empty] | 1 |  |  |  |  | 1 | 1
No data | [6 empty] | 1 |  |  |  |  | 1 | 1
Grand Total | 2 | 3 | 15 | 16 | 7 | 43 | 106 | 95 | 131 | 108 | 90 | 530 | 573
Count of 4m/2h
| RFW |  |  |  |  | RFW Total | No RFW |  |  |  |  | No RFW Total | Grand Total
Row Labels | 2015 | 2016 | 2017 | 2018 | 2019 |  | 2015 | 2016 | 2017 | 2018 | 2019
< 25mph | 2 | 1 | 11 | 13 | 3 | 30 | 63 | 53 | 78 | 75 | 75 | 344 | 374
25-40mph |  |  |  |  | 3 | 3 | 2 |  | 3 | 1 | 1 | 7 | 10
40-55mph |  |  | 1 |  |  | 1 | 1 | 2 |  | 1 | 2 | 6 | 7
55mph+ | [6 empty] | 1 | 1 |  |  |  | 2 | 2
No data |  | 2 | 3 | 3 | 1 | 9 | 39 | 39 | 50 | 31 | 12 | 171 | 180
Grand Total | 2 | 3 | 15 | 16 | 7 | 43 | 106 | 95 | 131 | 108 | 90 | 530 | 573
Count of 4m/1h
| RFW |  |  |  |  | RFW Total | No RFW |  |  |  |  | No RFW Total | Grand Total
Row Labels | 2015 | 2016 | 2017 | 2018 | 2019 |  | 2015 | 2016 | 2017 | 2018 | 2019
< 25mph | 2 | 1 | 11 | 13 | 3 | 30 | 63 | 53 | 78 | 75 | 75 | 344 | 374
25-40mph |  |  | 1 |  | 3 | 4 | 2 | 1 | 3 | 1 | 1 | 8 | 12
40-55mph | [6 empty] | 2 | 2 |  | 1 | 2 | 7 | 7
No data |  | 2 | 3 | 3 | 1 | 9 | 39 | 39 | 50 | 31 | 12 | 171 | 180
Grand Total | 2 | 3 | 15 | 16 | 7 | 43 | 106 | 95 | 131 | 108 | 90 | 530 | 573