## Index
Table of Contents for Wildfire Bowtie Analysis file
| Tab # | Tab Name | Tab Description
| 1 | Index | Tab with Table of Contents
| 2 | All Ignition Data Set | CPUC Reportable Ignitions from 2015-2019 + 7 fires
| 3 | Risk Input Sheet | Pivot Tables based on tab 'All Ignition Dataset' from 2015 - 2019
| 4 | HFTD-Distribution Pivots | Pivot Tables based on tab 'All Ignition Dataset' from 2015 - 2019 for HFTD-Distribution Tranche
| 5 | LookUps | Lookup Tables used in tab 'All Ignition Dataset'
| 6 | Large Fires (PGETerritory) | CalFire wildfires that were greater than 300 acres that occurred in PG&E territory (2015 - 2019)
| 7 | EventTree | Large Fires Summary by HFTD / Red Flag Warning / Destructive
| 8 | Fire-driven Outages | Non-restorable Outages for 2015-2018
| 9 | Fire Names & ILIS | Mapping of Outage (ILIS) IDs to Fire Name

## All Ignition Data Set
CPUC Reportable Ignitions from 2015-2019 + 7 fires
Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations | [7 empty] | Used in the pivot | [7 empty] | Used in Pivot | Used for Tranche | Used in the Risk Input Sheet | Used in Pivot | Used in the Risk Input Sheet | Used in the Risk Input | Used in EO-WF-14 | [7 empty] | 0
Utility Name | Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | Notes (Optional): | Veg Subdriver | 0_Ignition ID | 0_Year | 0_Month | 0_Day | 0_Hour | 0_Minute | 0_Outage ID | 0_HFTD Zone | 0_HFTD | 0_RFW Applicable | 0_Transmission/Distribution | 0_Tranche | 0_Fire Greater than 300 Acres | 0_Driver | 0_Subdriver | 0_Customer Minutes Interrupted | 1_wg_mph | 1_we_sn | 1_Wind Categorization | 1_Wind Category | 1_Tranche | 2_dt_local | 2_wg_row | 2_wg_mph_day_max | 1_same date and time as other ignition | 2_Wind Category
PG&E | 2015-01-08 15:18 | 42012.6375 | 37.3663 | -121.8832 | Other | Rural | < 0.25 Acres | Fire Agency | SJFD | 100566657 | None | 12000 | Conductor | Subsurface | Yes | 42012.6375 | 2015-01-08 15:18 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error |  | Other/Unknown | 0255 | 2015 | 1 | 8 | 15 | 18 | 15-0003437 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 2186 | 0 | NA | <25mph | <15mph | #REF! | 2015-01-08 15:18:00 | #REF! | 0 |  | <25mph
PG&E | 2015-01-10 13:07 | 42014.5465 | 38.089 | -122.2087 | Vegetation | Urban | < 0.25 Acres | Utility: PG&E |  | 102217759 |  | 12000 | Conductor | Overhead | Yes | 42014.5465 | 2015-01-10 13:07 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0256 | 2015 | 1 | 10 | 13 | 7 | 15-0003725 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 488264 | 0 | NA | <25mph | <15mph | #REF! | 2015-01-10 13:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-01-16 07:07 | 42020.2965 | 38.7753 | -122.7004 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 102167494 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0257 | 2015 | 1 | 16 | 7 | 7 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-01-16 07:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-01-26 03:51 | 42030.1604 | 37.0539 | -122.1587 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42030.1604 | 2015-01-26 03:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0258 | 2015 | 1 | 26 | 3 | 51 | 15-0007000 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7602 | 0 | NA | <25mph | <15mph | #REF! | 2015-01-26 03:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-02-06 06:01 | 42041.2507 | 38.6059 | -121.0221 | Vegetation | Rural | < 3 meters | Fire Agency |  | 6661 Ryan Ranch Road, El Dorado Hills |  | 21000 | Conductor | Overhead | Yes | 42041.2507 | 2015-02-06 06:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0259 | 2015 | 2 | 6 | 6 | 1 | 15-0009876 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 51996 | 0 | NA | <25mph | <15mph | #REF! | 2015-02-06 06:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-02-06 14:08 | 42041.5889 | 36.4032 | -121.9109 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | loadside of 40283 |  | 12000 | Conductor | Overhead | Yes | 42041.5889 | 2015-02-06 14:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 0260 | 2015 | 2 | 6 | 14 | 8 | 15-0010258 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 30620 | 0 | NA | <25mph | <15mph | #REF! | 2015-02-06 14:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-02-07 15:13 | 42042.634 | 38.0871 | -122.5496 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NOVATO FIRE DEPARTMENT | 103598139 |  | 12000 | Conductor | Overhead | Yes | 42042.634 | 2015-02-07 15:13 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0261 | 2015 | 2 | 7 | 15 | 13 | 15-0011288 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 8601 | 0 | NA | <25mph | <15mph | #REF! | 2015-02-07 15:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-02-07 18:38 | 42042.7764 | 40.4674 | -123.6545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | mile marker 36.61, hwy 36, bridgeville |  | 12000 | Conductor | Overhead | Yes | 42042.7764 | 2015-02-07 18:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0262 | 2015 | 2 | 7 | 18 | 38 | 15-0011390 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 7691 | 0 | NA | <25mph | <15mph | #REF! | 2015-02-07 18:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-02-13 16:01 | 42048.6674 | 35.3628 | -118.9661 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Bakersfield FD | 512 Wilma Street, Bakersfield |  | 0 – 750 | Conductor | Overhead | Yes | 42048.6674 | 2015-02-13 16:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0263 | 2015 | 2 | 13 | 16 | 1 | 15-0013276 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 2292 | 0 | NA | <25mph | <15mph | #REF! | 2015-02-13 16:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-02-16 11:08 | 42051.4639 | 37.36 | -120.8523 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101206051 |  | 12000 | Conductor | Overhead | Yes | 42051.4639 | 2015-02-16 11:08 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0264 | 2015 | 2 | 16 | 11 | 8 | 15-0013522 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 29219 | 0 | NA | <25mph | <15mph | #REF! | 2015-02-16 11:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-02-17 16:46 | 42052.6986 | 39.7628 | -121.5827 | Vegetation | Urban | < 3 meters | Fire Agency | butte county | 100324934 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42052.6986 | 2015-02-17 16:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0265 | 2015 | 2 | 17 | 16 | 46 | 15-0013811 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6405 | 0 | NA | <25mph | <15mph | #REF! | 2015-02-17 16:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-02-22 14:20 | 42057.5972 | 38.816 | -122.1832 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Capay | 101592201 |  | 21000 | Conductor | Overhead | Yes | 42057.5972 | 2015-02-22 14:20 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0266 | 2015 | 2 | 22 | 14 | 20 | 15-0014860 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 705 | 0 | NA | <25mph | <15mph | #REF! | 2015-02-22 14:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-02-23 02:05 | 42058.0868 | 39.3027 | -121.0175 | Vegetation | Rural | < 3 meters | Fire Agency | NEVADA CITY FIRE | 100086316 |  | 12000 | Conductor | Overhead | Yes | 42058.0868 | 2015-02-23 02:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0267 | 2015 | 2 | 23 | 2 | 5 | 15-0014910 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 93279 | 0 | NA | <25mph | <15mph | #REF! | 2015-02-23 02:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-02-23 13:25 | 42058.559 | 38.5046 | -122.7408 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RINCON VALLEY | BEHIND 4870 CARRIAGE LN SANTA ROSA |  | 12000 | Conductor | Overhead | Yes | 42058.559 | 2015-02-23 13:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0268 | 2015 | 2 | 23 | 13 | 25 | 15-0015168 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 85762 | 0 | NA | <25mph | <15mph | #REF! | 2015-02-23 13:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-02-25 02:34 | 42060.1069 | 36.7562 | -119.78 | Vegetation | Urban | < 3 meters | Fire Agency | CITY OF FRESNO | 100869017 | Pacific Bell | 12000 | Fuse | Overhead | Yes | 42060.1069 | 2015-02-25 02:34 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0269 | 2015 | 2 | 25 | 2 | 34 | 15-0015530 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2695 | 0 | NA | <25mph | <15mph | #REF! | 2015-02-25 02:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-02-25 16:42 | 42060.6958 | 34.8921 | -120.504 | Vegetation | Rural | < 3 meters | Customer |  |  |  | 0 – 750 | Conductor | Overhead | Yes | 42060.6958 | 2015-02-25 16:42 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0270 | 2015 | 2 | 25 | 16 | 42 | 15-0015784 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 234 | 0 | NA | <25mph | <15mph | #REF! | 2015-02-25 16:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-03-04 18:44 | 42067.7806 | 38.9995 | -122.7545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kelseyville FD | 102156367 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42067.7806 | 2015-03-04 18:44 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0271 | 2015 | 3 | 4 | 18 | 44 | 15-0017374 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 29532 | 0 | NA | <25mph | <15mph | #REF! | 2015-03-04 18:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-03-07 13:35 | 42070.566 | 38.7091 | -122.6484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 14417 western mine rd, Middletown |  | 12000 | Conductor | Overhead | Yes | 42070.566 | 2015-03-07 13:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0272 | 2015 | 3 | 7 | 13 | 35 | 15-0018003 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2263 | 0 | NA | <25mph | <15mph | #REF! | 2015-03-07 13:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-03-09 09:36 | 42072.4 | 38.7328 | -120.7524 | Building | Urban | Structure Only | Unknown |  | 101399208 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42072.4 | 2015-03-09 09:36 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0273 | 2015 | 3 | 9 | 9 | 36 | 15-0018212 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 35991 | 0 | NA | <25mph | <15mph | #REF! | 2015-03-09 09:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-03-14 02:30 | 42077.1042 | 38.9038 | -122.7579 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 9210 Wildcat Road, Kelseyville |  | 12000 | Conductor | Overhead | Yes | 42077.1042 | 2015-03-14 02:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0274 | 2015 | 3 | 14 | 2 | 30 | 15-0019556 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2280 | 0 | NA | <25mph | <15mph | #REF! | 2015-03-14 02:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-03-14 14:17 | 42077.5951 | 38.8253 | -121.1363 | Vegetation | Rural | < 3 meters | Fire Agency | LOOMIS FIRE | 100051369 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | no-match | 0275 | 2015 | 3 | 14 | 14 | 17 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-03-14 14:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-03-14 22:09 | 42077.9229 | 36.8915 | -121.7119 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103525395 |  | 21000 | Conductor | Overhead | Yes | 42077.9229 | 2015-03-14 22:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0276 | 2015 | 3 | 14 | 22 | 9 | 15-0019640 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 8840 | 0 | NA | <25mph | <15mph | #REF! | 2015-03-14 22:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-03-15 03:26 | 42078.1431 | 35.3693 | -118.928 | Vegetation | Urban | < 0.25 Acres | Fire Agency | KERN COUNTY FIRE DEPT | 100216241 | Pacific Bell | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0277 | 2015 | 3 | 15 | 3 | 26 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-03-15 03:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-03-15 03:38 | 42078.1514 | 36.934 | -119.7802 | Vegetation | Rural | < 3 meters | Unknown |  | 101121519 | None | 21000 | Conductor | Overhead | Yes | 42078.1514 | 2015-03-15 03:38 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0278 | 2015 | 3 | 15 | 3 | 38 | 15-0019646 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1336 | 0 | NA | <25mph | <15mph | #REF! | 2015-03-15 03:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-03-15 22:47 | 42078.9493 | 38.3346 | -120.5325 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 103106530 |  | 12000 | Conductor | Overhead | Yes | 42078.9493 | 2015-03-15 22:47 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0279 | 2015 | 3 | 15 | 22 | 47 | 15-0019709 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 14520 | 0 | NA | <25mph | <15mph | #REF! | 2015-03-15 22:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-03-19 20:11 | 42082.841 | 37.8416 | -122.1218 | Vegetation | Urban | < 3 meters | Fire Agency | moraga fire | 100498544 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42082.841 | 2015-03-19 20:11 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0280 | 2015 | 3 | 19 | 20 | 11 | 15-0020838 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 441574 | 0 | NA | <25mph | <15mph | #REF! | 2015-03-19 20:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-03-21 10:46 | 42084.4486 | 40.1645 | -122.2894 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101546309 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42084.4486 | 2015-03-21 10:46 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0281 | 2015 | 3 | 21 | 10 | 46 | 15-0021120 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 10355 | 0 | NA | <25mph | <15mph | #REF! | 2015-03-21 10:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-03-21 11:03 | 42084.4604 | 36.5666 | -121.5143 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Monterey Regonal | 101758338 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42084.4604 | 2015-03-21 11:03 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0282 | 2015 | 3 | 21 | 11 | 3 | 15-0021118 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 114923 | 0 | NA | <25mph | <15mph | #REF! | 2015-03-21 11:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-03-31 13:33 | 42094.5646 | 37.1125 | -120.9433 | Vegetation | Rural | < 3 meters | Fire Agency | COUNTY FIRE | 101199839 |  | 0 – 750 | Conductor | Overhead | Yes | 42094.5646 | 2015-03-31 13:33 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0283 | 2015 | 3 | 31 | 13 | 33 | 15-0023303 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 14 | 0 | NA | <25mph | <15mph | #REF! | 2015-03-31 13:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-02 09:44 | 42096.4056 | 39.6772 | -121.492 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100338726 |  | 12000 | Conductor | Overhead | Yes | 42096.4056 | 2015-04-02 09:44 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0284 | 2015 | 4 | 2 | 9 | 44 | 15-0023747 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 100204 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-02 09:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-04 16:49 | 42098.7007 | 38.8824 | -122.5914 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 20748 Jerusalem Grade Road, Middletown |  | 12000 | Other | Overhead | Yes | 42098.7007 | 2015-04-04 16:49 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0285 | 2015 | 4 | 4 | 16 | 49 | 15-0024208 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 20448 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-04 16:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-11 17:16 | 42105.7194 | 40.5462 | -122.2343 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101491414 |  | 12000 | Conductor | Overhead | Yes | 42105.7194 | 2015-04-11 17:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0286 | 2015 | 4 | 11 | 17 | 16 | 15-0026023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 11914 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-11 17:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-12 12:35 | 42106.5243 | 40.1861 | -122.2138 | Vegetation | Rural | < 0.25 Acres | Fire Agency | NOT SURE 2ND ON SITE (1ST LXMX) | 101544984 |  | 12000 | Conductor | Overhead | Yes | 42106.5243 | 2015-04-12 12:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0287 | 2015 | 4 | 12 | 12 | 35 | 15-0026084 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 28316 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-12 12:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-14 11:09 | 42108.4646 | 38.0215 | -121.61 | Vegetation | Rural | < 3 meters | Fire Agency | EAST CONTRA COSTA | 100505773 | Pacific Bell | 0 – 750 | Conductor | Overhead | Yes | 42108.4646 | 2015-04-14 11:09 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0288 | 2015 | 4 | 14 | 11 | 9 | 15-0026599 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 384 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-14 11:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-14 12:35 | 42108.5243 | 38.1789 | -121.6938 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | AIRPORT RD BTW 2CD & 3RD P/S/O CHURCH RD |  | 21000 | Conductor | Overhead | Yes | 42108.5243 | 2015-04-14 12:35 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0289 | 2015 | 4 | 14 | 12 | 35 | 15-0026607 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 101522 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-14 12:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-15 12:35 | 42109.5243 | 39.1152 | -121.5711 | Vegetation | Urban | < 3 meters | Unknown |  | 101319105 | Pacific Bell | 0 – 750 | Conductor | Overhead | Yes | 42109.5243 | 2015-04-15 12:35 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 0290 | 2015 | 4 | 15 | 12 | 35 | 15-0026892 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1660 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-15 12:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-16 17:35 | 42110.7326 | 38.2054 | -122.1475 | Vegetation | Rural | < 3 meters | Fire Agency | FAIRFIELD FD | SB 17513 |  | 12000 | Conductor | Overhead | Yes | 42110.7326 | 2015-04-16 17:35 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0291 | 2015 | 4 | 16 | 17 | 35 | 15-0027307 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 128448 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-16 17:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-17 14:34 | 42111.6069 | 37.0041 | -119.7293 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MADERA COUNTY | 101118401 |  | 21000 | Conductor | Overhead | Yes | 42111.6069 | 2015-04-17 14:34 | Other | N.A. | N.A. | N.A. | Other | bird nest caught fire | Other/Unknown | 0292 | 2015 | 4 | 17 | 14 | 34 | 15-0027497 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 22011 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-17 14:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-18 03:07 | 42112.1299 | 38.6858 | -121.0084 | Vegetation | Urban | < 3 meters | Fire Agency | carmeron park F.D. | around t-7464 |  | 21000 | Conductor | Overhead | Yes | 42112.1299 | 2015-04-18 03:07 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0293 | 2015 | 4 | 18 | 3 | 7 | 15-0027556 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 49438 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-18 03:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-19 09:18 | 42113.3875 | 36.5764 | -119.669 | Vegetation | Rural | < 0.25 Acres | Self Extinguished |  | 100826688 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42113.3875 | 2015-04-19 09:18 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0294 | 2015 | 4 | 19 | 9 | 18 | 15-0027657 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 29732 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-19 09:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-19 13:01 | 42113.5424 | 37.1571 | -120.4145 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101013878 |  | 12000 | Conductor | Overhead | Yes | 42113.5424 | 2015-04-19 13:01 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0295 | 2015 | 4 | 19 | 13 | 1 | 15-0027671 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 11924 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-19 13:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-20 18:18 | 42114.7625 | 36.9743 | -120.0176 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MFD | 101211344 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42114.7625 | 2015-04-20 18:18 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0296 | 2015 | 4 | 20 | 18 | 18 | 15-0028023 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 58006 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-20 18:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-21 17:01 | 42115.709 | 34.9313 | -120.4405 | Vegetation | Urban | < 3 meters | Self Extinguished |  | 101919414 | Verizon | 12000 | Conductor | Overhead | Yes | 42115.709 | 2015-04-21 17:01 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0297 | 2015 | 4 | 21 | 17 | 1 | 15-0028372 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 133051 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-21 17:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-24 06:06 | 42118.2542 | 38.0501 | -121.4966 | Vegetation | Rural | < 3 meters | Fire Agency | unknown | levee rd s/o herman and helans resort |  | 21000 | Conductor | Overhead | Yes | 42118.2542 | 2015-04-24 06:06 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0298 | 2015 | 4 | 24 | 6 | 6 | 15-0029121 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 23770 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-24 06:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-24 17:47 | 42118.741 | 37.5586 | -121.9196 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Alameda County | Base of C/O pole 9435 |  | 12000 | Unknown | Overhead | Yes | 42118.741 | 2015-04-24 17:47 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0299 | 2015 | 4 | 24 | 17 | 47 | 15-0029398 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 5096 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-24 17:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-26 16:50 | 42120.7014 | 34.8547 | -120.524 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Santa Barbara County Fire Dept | 2 poles load side 7455 | None | 12000 | Conductor | Overhead | Yes | 42120.7014 | 2015-04-26 16:50 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0300 | 2015 | 4 | 26 | 16 | 50 | 15-0029655 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1125 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-26 16:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-27 12:54 | 42121.5375 | 35.4871 | -120.6756 | Vegetation | Rural | < 3 meters | Unknown |  | 103310601 |  | 21000 | Conductor | Overhead | Yes | 42121.5375 | 2015-04-27 12:54 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0301 | 2015 | 4 | 27 | 12 | 54 | 15-0029875 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 5836 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-27 12:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-28 13:57 | 42122.5813 | 36.7504 | -119.7483 | Vegetation | Urban | < 3 meters | Fire Agency | FRESNO CITY FIRE | 100842188 |  | 12000 | Conductor | Overhead | Yes | 42122.5813 | 2015-04-28 13:57 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0302 | 2015 | 4 | 28 | 13 | 57 | 15-0030226 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 88469 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-28 13:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-28 14:20 | 42122.5972 | 39.7972 | -121.8907 | Vegetation | Rural | < 3 meters | Unknown |  | 100435592 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42122.5972 | 2015-04-28 14:20 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0303 | 2015 | 4 | 28 | 14 | 20 | 15-0030236 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 410 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-28 14:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-04-30 00:26 | 42124.0181 | 37.2401 | -122.2472 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 1145 VERDE R |  | 12000 | Conductor | Overhead | Yes | 42124.0181 | 2015-04-30 00:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0304 | 2015 | 4 | 30 | 0 | 26 | 15-0030607 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1256 | 0 | NA | <25mph | <15mph | #REF! | 2015-04-30 00:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-02 16:51 | 42126.7021 | 37.3284 | -119.643 | Vegetation | Rural | < 0.25 Acres | Fire Agency | MADERA COUNTY | 103768995 |  | 12000 | Conductor | Overhead | Yes | 42126.7021 | 2015-05-02 16:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0305 | 2015 | 5 | 2 | 16 | 51 | 15-0031285 | Zone 1 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 79805 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-02 16:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-02 17:30 | 42126.7292 | 38.2038 | -121.2644 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 103765745 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42126.7292 | 2015-05-02 17:30 | Contact From Object | N.A. | Other | Electric Facility | Human Error | Sky diver hit line | Other/Unknown | 0306 | 2015 | 5 | 2 | 17 | 30 | 15-0031286 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 39030 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-02 17:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-06 17:17 | 42130.7201 | 37.4273 | -119.8803 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | BOOSTER 8179 INDIAN PEEK N/O MIWUK | None | 21000 | Other | Overhead | Yes | 42130.7201 | 2015-05-06 17:17 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0307 | 2015 | 5 | 6 | 17 | 17 | 15-0032311 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 81600 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-06 17:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-06 23:10 | 42130.9653 | 39.8104 | -122.3292 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | BLACK BUTTE |  | 12000 | Lightning Arrestor | Overhead | Yes | 42130.9653 | 2015-05-06 23:10 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | Other/Unknown | 0308 | 2015 | 5 | 6 | 23 | 10 | 15-0032339 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 720 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-06 23:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-07 08:06 | 42131.3375 | 39.238 | -121.5875 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101331086 |  | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0309 | 2015 | 5 | 7 | 8 | 6 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-05-07 08:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-08 05:55 | 42132.2465 | 38.7755 | -121.5064 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | fire dept | mtr # 03650R |  | 0 – 750 | Fuse | Overhead | Yes | 42132.2465 | 2015-05-08 05:55 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0310 | 2015 | 5 | 8 | 5 | 55 | 15-0032846 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 492 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-08 05:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-09 13:10 | 42133.5486 | 39.2343 | -121.2468 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100000103 | None | 21000 | Conductor | Overhead | Yes | 42133.5486 | 2015-05-09 13:10 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0311 | 2015 | 5 | 9 | 13 | 10 | 15-0033085 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 382926 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-09 13:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-09 21:37 | 42133.9007 | 39.2848 | -121.0219 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100004095 | Pacific Bell | 12000 | Fuse | Overhead | Yes | 42133.9007 | 2015-05-09 21:37 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0312 | 2015 | 5 | 9 | 21 | 37 | 15-0033109 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 11 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-09 21:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-10 15:03 | 42134.6271 | 37.6649 | -122.4322 | Vegetation | Urban | < 0.25 Acres | Fire Agency | San Mateo FD | 100282481 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42134.6271 | 2015-05-10 15:03 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0313 | 2015 | 5 | 10 | 15 | 3 | 15-0033163 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 81774 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-10 15:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-10 16:07 | 42134.6715 | 37.7832 | -120.7933 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Oakdale | 9956 Dillwood rd. |  | 17000 | Conductor | Overhead | Yes | 42134.6715 | 2015-05-10 16:07 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0314 | 2015 | 5 | 10 | 16 | 7 | 15-0033168 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-05-10 16:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-11 07:19 | 42135.3049 | 38.1233 | -121.3708 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | woodbridge fd | 102075242 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42135.3049 | 2015-05-11 07:19 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0315 | 2015 | 5 | 11 | 7 | 19 | 15-0033213 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4492 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-11 07:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-11 16:07 | 42135.6715 | 35.9253 | -120.8669 | Vegetation | Rural | < 3 meters | Unknown |  | LR 7064 JUMP |  | 12000 | Conductor | Overhead | Yes | 42135.6715 | 2015-05-11 16:07 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0316 | 2015 | 5 | 11 | 16 | 7 | 15-0033385 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 73491 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-11 16:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-11 16:18 | 42135.6792 | 39.2804 | -123.2067 | Vegetation | Rural | < 0.25 Acres | Fire Agency | REDWOOD VALLEY FIRE | 9502 EAST RD., REDWOOD VALLEY |  | 0 – 750 | Conductor | Overhead | Yes | 42135.6792 | 2015-05-11 16:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0317 | 2015 | 5 | 11 | 16 | 18 | 15-0033419 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 489 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-11 16:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-12 23:57 | 42136.9979 | 39.1851 | -121.6804 | Vegetation | Rural | < 3 meters | Fire Agency | YUBA CITY | 101303383 | Pacific Bell | 0 – 750 | Transformer | Overhead | Yes | 42136.9979 | 2015-05-12 23:57 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0318 | 2015 | 5 | 12 | 23 | 57 | 15-0033691 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 940 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-12 23:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-13 21:57 | 42137.9146 | 37.4942 | -122.368 | Vegetation | Rural | < 3 meters | Fire Agency | sm county cal fire | 103492873 |  | 12000 | Conductor | Overhead | Yes | 42137.9146 | 2015-05-13 21:57 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0319 | 2015 | 5 | 13 | 21 | 57 | 15-0033936 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 42892 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-13 21:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-14 11:03 | 42138.4604 | 37.0551 | -120.317 | Vegetation | Rural | < 0.25 Acres | Self Extinguished |  | S/O 10696 AVE. 19 1/2 |  | 12000 | Conductor | Overhead | Yes | 42138.4604 | 2015-05-14 11:03 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0320 | 2015 | 5 | 14 | 11 | 3 | 15-0034056 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 35639 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-14 11:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-17 23:41 | 42141.9868 | 39.4317 | -121.7259 | Vegetation | Rural | < 0.25 Acres | Self Extinguished |  | 100414389 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42141.9868 | 2015-05-17 23:41 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0321 | 2015 | 5 | 17 | 23 | 41 | 15-0034777 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 13223 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-17 23:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-19 13:31 | 42143.5632 | 37.9273 | -122.0863 | Vegetation | Urban | < 3 meters | Fire Agency | CONTRA COSTA FIRE | 100476269 | Pacific Bell | 21000 | Switch | Overhead | Yes | 42143.5632 | 2015-05-19 13:31 | Equipment/ Facility Failure | Switch | N.A. | N.A. | Unknown |  | Other/Unknown | 0322 | 2015 | 5 | 19 | 13 | 31 | 15-0035210 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 16695 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-19 13:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-21 06:02 | 42145.2514 | 36.2152 | -121.1646 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 3 pole structure east side 101 south of central |  | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0323 | 2015 | 5 | 21 | 6 | 2 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-05-21 06:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-21 09:23 | 42145.391 | 38.5996 | -122.9935 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 4 SPANS LOAD SIDE 2993 |  | 12000 | Conductor | Overhead | Yes | 42145.391 | 2015-05-21 09:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0324 | 2015 | 5 | 21 | 9 | 23 | 15-0035686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2850 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-21 09:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-24 10:59 | 42148.4576 | 36.2013 | -121.1612 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | king city fire department | 101734774 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42148.4576 | 2015-05-24 10:59 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0325 | 2015 | 5 | 24 | 10 | 59 | 15-0036228 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 4089 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-24 10:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-25 02:42 | 42149.1125 | 38.7027 | -121.9001 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  | Str. 029/177 |  | 115000 | Unknown | Overhead | Yes | 42149.1125 | 2015-05-25 02:42 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0326 | 2015 | 5 | 25 | 2 | 42 | VD-2015-049 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 0 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-25 02:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-26 05:44 | 42150.2389 | 36.1661 | -120.2535 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FRESNO COUNTY FIRE DEPT. | OFF PHELPS 2 MILES E/O CALAVERAS |  | 0 – 750 | Conductor | Overhead | No |  |  | Other | N.A. | N.A. | N.A. | Other | Crow's nest caught fire | no-match | 0327 | 2015 | 5 | 26 | 5 | 44 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-05-26 05:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-27 01:02 | 42151.0431 | 36.5986 | -119.4219 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Reedley Fire /dept | Open field by Riser 7465, Zumwalt Ave S/O Manning Ave, Reedley | Verizon | 12000 | Conductor | Overhead | Yes | 42151.0431 | 2015-05-27 01:02 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown | UG cable | Other/Unknown | 0328 | 2015 | 5 | 27 | 1 | 2 | 15-0036578 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 54594 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-27 01:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-27 21:44 | 42151.9056 | 39.169 | -120.9612 | Vegetation | Rural | < 0.25 Acres | Fire Agency | PEARDALE F.D. | 100077687 |  | 12000 | Conductor | Overhead | Yes | 42151.9056 | 2015-05-27 21:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0329 | 2015 | 5 | 27 | 21 | 44 | 15-0036850 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10828 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-27 21:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-28 17:09 | 42152.7146 | 40.3942 | -122.2891 | Vegetation | Urban | < 0.25 Acres | Unknown |  | 101492440 | Pacific Bell | 0 – 750 | Transformer | Overhead | Yes | 42152.7146 | 2015-05-28 17:09 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0330 | 2015 | 5 | 28 | 17 | 9 | 15-0037102 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 582 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-28 17:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-29 11:31 | 42153.4799 | 36.964 | -121.5335 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100616133 |  | 21000 | Conductor | Overhead | Yes | 42153.4799 | 2015-05-29 11:31 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0331 | 2015 | 5 | 29 | 11 | 31 | 15-0037249 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 4852 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-29 11:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-30 09:06 | 42154.3792 | 39.4743 | -121.6981 | Vegetation | Rural | < 0.25 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42154.3792 | 2015-05-30 09:06 | Contact From Object | N.A. | Other | Electric Facility | Human Error | helicopter hit line | Other/Unknown | 0332 | 2015 | 5 | 30 | 9 | 6 | 15-0037391 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 2310 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-30 09:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-30 11:04 | 42154.4611 | 36.9023 | -119.7737 | Vegetation | Rural | .26 - 9.99 Acres | Self Extinguished |  | 100643725 |  | 12000 | Conductor | Overhead | Yes | 42154.4611 | 2015-05-30 11:04 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0333 | 2015 | 5 | 30 | 11 | 4 | 15-0037404 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 9139 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-30 11:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-30 12:52 | 42154.5361 | 38.7371 | -120.8122 | Vegetation | Urban | < 3 meters | Fire Agency | el dorado co fire district | across from 2669 hwy 49 |  | 12000 | Fuse | Overhead | Yes | 42154.5361 | 2015-05-30 12:52 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0334 | 2015 | 5 | 30 | 12 | 52 | 15-0037405 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 115 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-30 12:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-30 17:35 | 42154.7326 | 38.7254 | -120.8326 | Vegetation | Rural | < 3 meters | Fire Agency | el dorado co fire | 100 placerville dr behind maint shop, Placerville |  | 12000 | Conductor | Overhead | Yes | 42154.7326 | 2015-05-30 17:35 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0335 | 2015 | 5 | 30 | 17 | 35 | 15-0037426 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 350 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-30 17:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-31 00:23 | 42155.016 | 37.2966 | -120.4682 | Vegetation | Urban | < 3 meters | Fire Agency | HAD LEFT SCENE BEFORE ARRIVAL | 101157239 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0336 | 2015 | 5 | 31 | 0 | 23 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-05-31 00:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-31 07:07 | 42155.2965 | 38.7824 | -121.4802 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Pleasnt Grove Fire Dept Station # | 3700 Sankey Rd, Pleasant Grove |  | 12000 | Unknown | Overhead | Yes | 42155.2965 | 2015-05-31 07:07 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0337 | 2015 | 5 | 31 | 7 | 7 | 15-0037465 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 2944 | 0 | NA | <25mph | <15mph | #REF! | 2015-05-31 07:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-31 09:27 | 42155.3938 | 37.9774 | -121.3267 | Vegetation | Urban | < 0.25 Acres | Customer |  | 102057703 | Pacific Bell | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | no-match | 0338 | 2015 | 5 | 31 | 9 | 27 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-05-31 09:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-31 11:31 | 42155.4799 | 37.2732 | -120.471 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101152842 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | no-match | 0339 | 2015 | 5 | 31 | 11 | 31 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-05-31 11:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-05-31 11:55 | 42155.4965 | 37.7218 | -120.7931 | Vegetation | Rural | < 3 meters | Customer | NONE | 102340604 | None | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0340 | 2015 | 5 | 31 | 11 | 55 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-05-31 11:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-03 09:33 | 42158.3979 | 39.6896 | -121.6216 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42158.3979 | 2015-06-03 09:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0341 | 2015 | 6 | 3 | 9 | 33 | 15-0038091 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 28146 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-03 09:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-03 13:44 | 42158.5722 | 38.627 | -121.0766 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103035299 |  | 21000 | Conductor | Overhead | Yes | 42158.5722 | 2015-06-03 13:44 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0342 | 2015 | 6 | 3 | 13 | 44 | 15-0038125 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 4654 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-03 13:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-03 17:09 | 42158.7146 | 35.3612 | -119.0062 | Vegetation | Urban | < 0.25 Acres | Fire Agency | KCFD AND BCFD | 100150055 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0343 | 2015 | 6 | 3 | 17 | 9 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-03 17:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-04 13:17 | 42159.5535 | 39.2694 | -123.7841 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42159.5535 | 2015-06-04 13:17 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0344 | 2015 | 6 | 4 | 13 | 17 | 15-0038501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 20525 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-04 13:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-04 15:44 | 42159.6556 | 39.4684 | -121.5613 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | powerhouse hill rd 2spans e on ophir rd |  | 12000 | Conductor | Overhead | Yes | 42159.6556 | 2015-06-04 15:44 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0345 | 2015 | 6 | 4 | 15 | 44 | 15-0038556 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 17573 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-04 15:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-04 16:38 | 42159.6931 | 38.588 | -121.5171 | Vegetation | Urban | < 3 meters | Fire Agency | west sacramento FD | 101565849 | Pacific Bell | 12000 | Unknown | Overhead | Yes | 42159.6931 | 2015-06-04 16:38 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0346 | 2015 | 6 | 4 | 16 | 38 | 15-0038570 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 7670 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-04 16:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-04 20:00 | 42159.8333 | 38.6916 | -120.8606 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101412760 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42159.8333 | 2015-06-04 20:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0347 | 2015 | 6 | 4 | 20 | 0 | 15-0038597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 9640 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-04 20:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-05 01:25 | 42160.059 | 38.3461 | -122.3998 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | 4870 REDWOOD |  | 21000 | Conductor | Overhead | Yes | 42160.059 | 2015-06-05 01:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0348 | 2015 | 6 | 5 | 1 | 25 | 15-0038607 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 53842 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-05 01:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-05 09:58 | 42160.4153 | 40.107 | -123.7142 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100986799 |  | 12000 | Conductor | Overhead | Yes | 42160.4153 | 2015-06-05 09:58 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | tie wire | Other/Unknown | 0349 | 2015 | 6 | 5 | 9 | 58 | 15-0038700 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-05 09:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-05 14:40 | 42160.6111 | 37.9578 | -120.4519 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101012484 |  | 17000 | Conductor | Overhead | Yes | 42160.6111 | 2015-06-05 14:40 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0350 | 2015 | 6 | 5 | 14 | 40 | 15-0038686 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 14319 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-05 14:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-05 15:15 | 42160.6354 | 36.7759 | -119.7703 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CITY OF FRESNO | 100857009 | Pacific Bell | 0 – 750 | Transformer | Overhead | Yes | 42160.6354 | 2015-06-05 15:15 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0351 | 2015 | 6 | 5 | 15 | 15 | 15-0038875 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4806 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-05 15:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-05 22:13 | 42160.9257 | 38.7729 | -121.4699 | Vegetation | Rural | < 3 meters | Fire Agency | WATER | 100064053 |  | 12000 | Capacitor Bank | Overhead | Yes | 42160.9257 | 2015-06-05 22:13 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | Other/Unknown | 0352 | 2015 | 6 | 5 | 22 | 13 | 15-0038964 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2996 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-05 22:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-06 11:24 | 42161.475 | 39.8029 | -121.9064 | Vegetation | Rural | < 3 meters | Unknown |  | 100433862 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42161.475 | 2015-06-06 11:24 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0353 | 2015 | 6 | 6 | 11 | 24 | 15-0039038 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-06 11:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-06 12:00 | 42161.5 | 36.9828 | -120.0332 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101015092 |  | 12000 | Lightning Arrestor | Overhead | Yes | 42161.5 | 2015-06-06 12:00 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | Other/Unknown | 0354 | 2015 | 6 | 6 | 12 | 0 | 15-0039033 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 232368 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-06 12:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-06 15:38 | 42161.6514 | 39.0409 | -123.4019 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 11480 ANDERSON VALLEY WAY @ BRIDGE |  | 12000 | Conductor | Overhead | Yes | 42161.6514 | 2015-06-06 15:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0355 | 2015 | 6 | 6 | 15 | 38 | 15-0039056 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 1748 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-06 15:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-06 21:17 | 42161.8868 | 38.0057 | -121.2382 | Vegetation | Rural | < 0.25 Acres | Fire Agency | COUNTY FIRE | 102135759 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42161.8868 | 2015-06-06 21:17 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0356 | 2015 | 6 | 6 | 21 | 17 | 15-0039081 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 61586 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-06 21:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-07 05:05 | 42162.2118 | 36.6906 | -119.7488 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | FRESNO FIRE | 103339346 |  | 12000 | Conductor | Overhead | Yes | 42162.2118 | 2015-06-07 05:05 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0357 | 2015 | 6 | 7 | 5 | 5 | 15-0039099 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 46829 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-07 05:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-07 14:53 | 42162.6201 | 36.3216 | -121.2836 | Vegetation | Rural | < 0.25 Acres | Fire Agency | monterey county | peach and thorne greenfield | Pacific Bell | 12000 | Unknown | Overhead | Yes | 42162.6201 | 2015-06-07 14:53 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0358 | 2015 | 6 | 7 | 14 | 53 | 15-0039129 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 196 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-07 14:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-07 17:48 | 42162.7417 | 38.2179 | -121.9752 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Suisun fire protection district. | c/o's 278361 |  | 21000 | Conductor | Overhead | Yes | 42162.7417 | 2015-06-07 17:48 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | Other/Unknown | 0359 | 2015 | 6 | 7 | 17 | 48 | 15-0039148 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1626 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-07 17:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-08 14:18 | 42163.5958 | 38.1796 | -120.959 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 102048579 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42163.5958 | 2015-06-08 14:18 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0360 | 2015 | 6 | 8 | 14 | 18 | 15-0039368 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 65168 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-08 14:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-08 16:12 | 42163.675 | 38.1155 | -122.5562 | Vegetation | Rural | < 3 meters | Fire Agency | novato fire | front yard 9 equestrian ct |  | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0361 | 2015 | 6 | 8 | 16 | 12 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-08 16:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-08 16:15 | 42163.6771 | 39.8236 | -123.6093 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 2 spans loadside 1741 |  | 12000 | Conductor | Overhead | Yes | 42163.6771 | 2015-06-08 16:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0362 | 2015 | 6 | 8 | 16 | 15 | 15-0039481 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1740 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-08 16:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-08 17:38 | 42163.7347 | 37.9582 | -121.9441 | Vegetation | Urban | < 3 meters | Unknown |  | T7325 |  | 0 – 750 | Conductor | Overhead | Yes | 42163.7347 | 2015-06-08 17:38 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0363 | 2015 | 6 | 8 | 17 | 38 | 15-0039473 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 5292 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-08 17:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-08 18:32 | 42163.7722 | 37.9404 | -122.0795 | Vegetation | Urban | < 3 meters | Fire Agency | CONTRA COSTA FIRE | 100462348 | Pacific Bell | 0 – 750 | Fuse | Overhead | Yes | 42163.7722 | 2015-06-08 18:32 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0364 | 2015 | 6 | 8 | 18 | 32 | 15-0039513 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1836 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-08 18:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-09 01:19 | 42164.0549 | 40.5424 | -122.2391 | Vegetation | Rural | < 3 meters | Customer |  | 101490096 | Frontier | 12000 | Transformer | Overhead | Yes | 42164.0549 | 2015-06-09 01:19 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0365 | 2015 | 6 | 9 | 1 | 19 | 15-0039581 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1653 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-09 01:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-09 11:51 | 42164.4938 | 36.4887 | -119.5824 | Building | Rural | Structure Only | Fire Agency | tulare county fire | 4390 ave 352 |  | 12000 | Conductor | Overhead | Yes | 42164.4938 | 2015-06-09 11:51 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0366 | 2015 | 6 | 9 | 11 | 51 | 15-0039726 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 92757 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-09 11:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-09 13:10 | 42164.5486 | 38.1176 | -121.1509 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | WATERLOO MORADA FIRE DISTRICT | 102076487 |  | 21000 | Conductor | Overhead | Yes | 42164.5486 | 2015-06-09 13:10 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0367 | 2015 | 6 | 9 | 13 | 10 | 15-0039758 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 169899 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-09 13:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-09 15:24 | 42164.6417 | 38.3651 | -122.2541 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | load side 2987 | Yes | 21000 | Conductor | Overhead | Yes | 42164.6417 | 2015-06-09 15:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0368 | 2015 | 6 | 9 | 15 | 24 | 15-0039825 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 651298 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-09 15:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-09 16:20 | 42164.6806 | 38.3822 | -122.4316 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102269716 | Pacific Bell | 21000 | Unknown | Overhead | Yes | 42164.6806 | 2015-06-09 16:20 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0369 | 2015 | 6 | 9 | 16 | 20 | 15-0039860 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 4184 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-09 16:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-09 21:21 | 42164.8896 | 38.9394 | -121.2467 | Vegetation | Rural | < 3 meters | Unknown |  | 100035304 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42164.8896 | 2015-06-09 21:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0370 | 2015 | 6 | 9 | 21 | 21 | 15-0039888 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 64672 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-09 21:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-10 12:00 | 42165.5 | 39.1376 | -121.6315 | Vegetation | Urban | < 0.25 Acres | Fire Agency | YUBA CITY | 101320887 |  | 12000 | Conductor | Overhead | Yes | 42165.5 | 2015-06-10 12:00 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0371 | 2015 | 6 | 10 | 12 | 0 | 15-0040075 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 210 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-10 12:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-10 17:02 | 42165.7097 | 36.9671 | -120.0305 | Vegetation | Rural | < 3 meters | Unknown |  | 101216691 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0372 | 2015 | 6 | 10 | 17 | 2 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-10 17:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-10 21:43 | 42165.9049 | 37.6381 | -121.8943 | Vegetation | Rural | < 3 meters | Fire Agency | PLEASANTON FIRE DEPT | 100927124 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42165.9049 | 2015-06-10 21:43 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0373 | 2015 | 6 | 10 | 21 | 43 | 15-0040240 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 41250 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-10 21:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-11 18:32 | 42166.7722 | 38.8221 | -121.306 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CITY OF ROCKLIN/ CAL FIRE | 103661493 |  | 21000 | Switch | Overhead | Yes | 42166.7722 | 2015-06-11 18:32 | Equipment/ Facility Failure | Switch | N.A. | N.A. | Unknown |  | Other/Unknown | 0374 | 2015 | 6 | 11 | 18 | 32 | 15-0040519 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 536220 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-11 18:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-12 09:04 | 42167.3778 | 39.394 | -122.2299 | Vegetation | Rural | < 0.25 Acres | Fire Agency | WILLOWS FIRE DEPT. | 100326792 |  | 21000 | Conductor | Overhead | Yes | 42167.3778 | 2015-06-12 09:04 | Contact From Object | N.A. | Other | Electric Facility | Human Error | crop duster hit line | Other/Unknown | 0375 | 2015 | 6 | 12 | 9 | 4 | 15-0040626 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 924 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-12 09:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-12 09:24 | 42167.3917 | 37.0761 | -120.2003 | Vegetation | Rural | < 3 meters | Self Extinguished |  | 103204949 |  | 0 – 750 | Conductor | Overhead | Yes | 42167.3917 | 2015-06-12 09:24 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0376 | 2015 | 6 | 12 | 9 | 24 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-12 09:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-12 10:48 | 42167.45 | 38.4273 | -122.859 | Vegetation | Rural | < 0.25 Acres | Fire Agency | GRATON FIRE DEP. | 102023459 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42167.45 | 2015-06-12 10:48 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0377 | 2015 | 6 | 12 | 10 | 48 | 15-0040663 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1530 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-12 10:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-12 13:07 | 42167.5465 | 40.4077 | -122.4104 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS STREET FROM 4139 OLD HAPPY VALLEY RD |  | 12000 | Lightning Arrestor | Overhead | No |  |  | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | no-match | 0378 | 2015 | 6 | 12 | 13 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-12 13:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-12 16:01 | 42167.6674 | 37.9252 | -122.0782 | Vegetation | Urban | < 3 meters | Fire Agency | WALNUT CREEK FIRE | 100478251 | Pacific Bell | 0 – 750 | Transformer | Overhead | Yes | 42167.6674 | 2015-06-12 16:01 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0379 | 2015 | 6 | 12 | 16 | 1 | 15-0040749 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1476 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-12 16:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-12 23:32 | 42167.9806 | 39.2308 | -121.1559 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 10903 PROSPECTOR RD ROUGH AND READY | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42167.9806 | 2015-06-12 23:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0380 | 2015 | 6 | 12 | 23 | 32 | 15-0040789 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 20 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-12 23:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-13 12:50 | 42168.5347 | 35.2722 | -118.9122 | Vegetation | Rural | < 3 meters | Fire Agency | Kern Co Fire Dept | 103779942 |  | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0381 | 2015 | 6 | 13 | 12 | 50 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-13 12:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-14 12:19 | 42169.5132 | 39.7432 | -121.8425 | Vegetation | Urban | < 3 meters | Fire Agency | CHICO FIRE DEPT | 100426666 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0382 | 2015 | 6 | 14 | 12 | 19 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-14 12:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-14 13:50 | 42169.5764 | 36.9363 | -119.8703 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 12915 mesa, madera |  | 21000 | Conductor | Overhead | Yes | 42169.5764 | 2015-06-14 13:50 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0383 | 2015 | 6 | 14 | 13 | 50 | 15-0040928 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 14245 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-14 13:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-15 15:35 | 42170.6493 | 37.1852 | -121.7595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Jose city | 100618215 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42170.6493 | 2015-06-15 15:35 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0384 | 2015 | 6 | 15 | 15 | 35 | 15-0041178 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 345 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-15 15:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-16 10:40 | 42171.4444 | 38.0062 | -122.1092 | Vegetation | Urban | .26 - 9.99 Acres | Unknown |  | Twr 008/058 |  | 115000 | Conductor | Overhead | Yes | 42171.4444 | 2015-06-16 10:40 | Contact From Object | N.A. | Other | Electric Facility | Unknown | bird-dropped material | no-match | 0385 | 2015 | 6 | 16 | 10 | 40 | PS-2015-013 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-16 10:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-16 11:27 | 42171.4771 | 39.0382 | -122.9264 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LAKEPORT FIRE | 102165174 | Pacific Bell | 0 – 750 | Conductor | Overhead | Yes | 42171.4771 | 2015-06-16 11:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0386 | 2015 | 6 | 16 | 11 | 27 | 15-0041440 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 972 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-16 11:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-17 10:32 | 42172.4389 | 37.7688 | -120.9078 | Vegetation | Rural | < 3 meters | Fire Agency | Escalon fire dept. |  |  | 17000 | Conductor | Overhead | Yes | 42172.4389 | 2015-06-17 10:32 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0387 | 2015 | 6 | 17 | 10 | 32 | 15-0041589 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 219629 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-17 10:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-17 15:49 | 42172.659 | 37.3516 | -120.642 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 8503 LONGVIEW ATWATER |  | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0388 | 2015 | 6 | 17 | 15 | 49 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-17 15:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-17 18:35 | 42172.7743 | 35.3302 | -119.0116 | Vegetation | Urban | < 3 meters | Fire Agency | BCFD | 100155778 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42172.7743 | 2015-06-17 18:35 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0389 | 2015 | 6 | 17 | 18 | 35 | 15-0041752 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 18144 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-17 18:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-19 12:14 | 42174.5097 | 34.8356 | -120.3843 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | SANTA BARBRA COUNTY FIRE DEPT | 103015189 |  | 12000 | Conductor | Overhead | Yes | 42174.5097 | 2015-06-19 12:14 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0390 | 2015 | 6 | 19 | 12 | 14 | 15-0042163 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 1500 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-19 12:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-19 20:09 | 42174.8396 | 39.1597 | -121.4865 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101308410 | Pacific Bell | 0 – 750 | Conductor | Overhead | Yes | 42174.8396 | 2015-06-19 20:09 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0391 | 2015 | 6 | 19 | 20 | 9 | 15-0042237 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 780 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-19 20:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-20 01:28 | 42175.0611 | 36.2548 | -119.6435 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42175.0611 | 2015-06-20 01:28 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0392 | 2015 | 6 | 20 | 1 | 28 | 15-0042245 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 43464 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-20 01:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-21 01:32 | 42176.0639 | 39.008 | -121.344 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100021218 |  | 12000 | Conductor | Overhead | Yes | 42176.0639 | 2015-06-21 01:32 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0393 | 2015 | 6 | 21 | 1 | 32 | 15-0042321 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-21 01:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-21 03:17 | 42176.1368 | 39.0956 | -121.5421 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Wheatland fire dept | Transmission Sw 159 on the Pease - Rio-Oso 115kv line |  | 115000 | Transformer | Overhead | Yes | 42176.1368 | 2015-06-21 03:17 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown | Potential transformer | no-match | 0394 | 2015 | 6 | 21 | 3 | 17 | TM-2015-054 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 0 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-21 03:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-21 12:07 | 42176.5049 | 36.7225 | -121.7667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NORTH COUNTY FIRE DEPARTMENT #1428 |  | None | 21000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0395 | 2015 | 6 | 21 | 12 | 7 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-21 12:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-21 12:10 | 42176.5069 | 37.9273 | -122.3182 | Vegetation | Urban | < 0.25 Acres | Fire Agency | RICHMOND | KEY BLVD. |  | 4000 | Conductor | Overhead | Yes | 42176.5069 | 2015-06-21 12:10 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0396 | 2015 | 6 | 21 | 12 | 10 | 15-0042347 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 50768 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-21 12:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-21 12:31 | 42176.5215 | 38.8317 | -121.1642 | Vegetation | Rural | < 3 meters | Fire Agency | penryn fire dept | 100050933 | Pacific Bell | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0397 | 2015 | 6 | 21 | 12 | 31 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-21 12:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-21 12:46 | 42176.5319 | 38.0017 | -121.2977 | Vegetation | Urban | < 0.25 Acres | Fire Agency | STOCKTON F.D | 102138737 |  | 12000 | Conductor | Overhead | Yes | 42176.5319 | 2015-06-21 12:46 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0398 | 2015 | 6 | 21 | 12 | 46 | 15-0042350 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 34849 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-21 12:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-21 13:31 | 42176.5632 | 37.375 | -119.6116 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103204866 |  | 0 – 750 | Conductor | Overhead | No |  |  | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0399 | 2015 | 6 | 21 | 13 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-21 13:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-22 11:58 | 42177.4986 | 39.1737 | -121.0667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | SENTINAL WY |  | 12000 | Conductor | Overhead | Yes | 42177.4986 | 2015-06-22 11:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0400 | 2015 | 6 | 22 | 11 | 58 | 15-0042502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 148438 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-22 11:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-22 18:56 | 42177.7889 | 36.987 | -121.5381 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Gilroy city fire |  |  | 21000 | Conductor | Overhead | Yes | 42177.7889 | 2015-06-22 18:56 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0401 | 2015 | 6 | 22 | 18 | 56 | 15-0042617 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 49963 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-22 18:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-23 15:23 | 42178.641 | 39.0551 | -121.561 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LINDA FIRE DEPT | 102354046 |  | 12000 | Conductor | Overhead | Yes | 42178.641 | 2015-06-23 15:23 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0402 | 2015 | 6 | 23 | 15 | 23 | 15-0042906 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 148680 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-23 15:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-23 19:06 | 42178.7958 | 37.9453 | -120.8237 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102344528 |  | 17000 | Conductor | Overhead | Yes | 42178.7958 | 2015-06-23 19:06 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0403 | 2015 | 6 | 23 | 19 | 6 | 15-0042932 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 1633 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-23 19:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-23 20:34 | 42178.8569 | 38.9086 | -121.5249 | Vegetation | Rural | < 0.25 Acres | Fire Agency | EAST NICOLAUS F.D. | 101300582 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42178.8569 | 2015-06-23 20:34 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0404 | 2015 | 6 | 23 | 20 | 34 | 15-0042939 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 25253 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-23 20:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-23 20:57 | 42178.8729 | 39.0439 | -123.1536 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102192356 |  | 12000 | Conductor | Overhead | Yes | 42178.8729 | 2015-06-23 20:57 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0405 | 2015 | 6 | 23 | 20 | 57 | 15-0042941 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 53476 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-23 20:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-24 19:05 | 42179.7951 | 39.9921 | -123.9258 | Vegetation | Rural | < 3 meters | Customer |  | 4 spans load side 8207 |  | 12000 | Conductor | Overhead | Yes | 42179.7951 | 2015-06-24 19:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0406 | 2015 | 6 | 24 | 19 | 5 | 15-0043176 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1080 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-24 19:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-25 08:43 | 42180.3632 | 39.6472 | -121.6079 | Vegetation | Rural | < 0.25 Acres | Customer |  | 100398087 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42180.3632 | 2015-06-25 08:43 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0407 | 2015 | 6 | 25 | 8 | 43 | 15-0043257 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 6384 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-25 08:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-25 11:22 | 42180.4736 | 37.9302 | -120.9707 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Farmington Fire Department | 103223594 | None | 0 – 750 | Conductor | Overhead | Yes | 42180.4736 | 2015-06-25 11:22 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0408 | 2015 | 6 | 25 | 11 | 22 | 15-0043296 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 472 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-25 11:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-25 18:05 | 42180.7535 | 37.9092 | -122.0572 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Walnut Creek FIRE | 511 LAWRENCE W C |  | 21000 | Conductor | Overhead | Yes | 42180.7535 | 2015-06-25 18:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0409 | 2015 | 6 | 25 | 18 | 5 | 15-0043446 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 145726 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-25 18:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-25 18:29 | 42180.7701 | 36.3639 | -119.8591 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | COUNTY FIRE | East of 22403 Fremont Ave, Lemoore | None | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0410 | 2015 | 6 | 25 | 18 | 29 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-25 18:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-25 19:44 | 42180.8222 | 38.6707 | -121.9686 | Vegetation | Rural | < 0.25 Acres | Unknown |  | R2226 |  | 21000 | Other | Overhead | Yes | 42180.8222 | 2015-06-25 19:44 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0411 | 2015 | 6 | 25 | 19 | 44 | 15-0043464 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 141960 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-25 19:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-26 02:51 | 42181.1188 | 35.1584 | -120.6763 | Vegetation | Urban | < 3 meters | Fire Agency | CAL FIRE | 101929266 | Pacific Bell | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0412 | 2015 | 6 | 26 | 2 | 51 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-26 02:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-26 17:20 | 42181.7222 | 37.9356 | -122.0145 | Vegetation | Urban | < 3 meters | Fire Agency | wc fire | 100481136 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0413 | 2015 | 6 | 26 | 17 | 20 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-26 17:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-27 12:48 | 42182.5333 | 37.9474 | -120.4274 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101034512 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.5333 | 2015-06-27 12:48 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0414 | 2015 | 6 | 27 | 12 | 48 | 15-0043755 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 150075 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-27 12:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-27 18:51 | 42182.7854 | 37.9911 | -120.438 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | MORMON CREEK 100' FROM S/OF HWY 49 |  | 17000 | Conductor | Overhead | Yes | 42182.7854 | 2015-06-27 18:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0415 | 2015 | 6 | 27 | 18 | 51 | 15-0043784 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 5249 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-27 18:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-27 21:15 | 42182.8854 | 39.2699 | -121.0403 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 16151 INDAIN FLAT RD |  | 12000 | Conductor | Overhead | Yes | 42182.8854 | 2015-06-27 21:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0416 | 2015 | 6 | 27 | 21 | 15 | 15-0043789 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4210 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-27 21:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-27 22:28 | 42182.9361 | 38.1194 | -120.6218 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 101281699 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.9361 | 2015-06-27 22:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0417 | 2015 | 6 | 27 | 22 | 28 | 15-0043798 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 517 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-27 22:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-28 02:50 | 42183.1181 | 35.491 | -120.731 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 13505 Santa Lucia Rd. Atascadero |  | 12000 | Conductor | Overhead | Yes | 42183.1181 | 2015-06-28 02:50 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0418 | 2015 | 6 | 28 | 2 | 50 | 15-0043807 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 12323 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-28 02:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-28 02:54 | 42183.1208 | 38.9704 | -123.1437 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | HOPLAND FIRE | MTR # 100971 |  | 12000 | Conductor | Overhead | Yes | 42183.1208 | 2015-06-28 02:54 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0419 | 2015 | 6 | 28 | 2 | 54 | 15-0043804 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 4653 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-28 02:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-28 14:39 | 42183.6104 | 38.2684 | -122.4296 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 102005422 |  | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0420 | 2015 | 6 | 28 | 14 | 39 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-28 14:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-28 14:47 | 42183.616 | 38.2214 | -122.2427 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102278099 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42183.616 | 2015-06-28 14:47 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0421 | 2015 | 6 | 28 | 14 | 47 | 15-0043853 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 16017 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-28 14:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-28 17:15 | 42183.7188 | 35.5527 | -120.7314 | Vegetation | Rural | < 0.25 Acres | Fire Agency | tempelton fire | 347 puffin |  | 21000 | Conductor | Overhead | Yes | 42183.7188 | 2015-06-28 17:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0422 | 2015 | 6 | 28 | 17 | 15 | 15-0043858 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2800 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-28 17:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-28 20:40 | 42183.8611 | 37.9376 | -120.6091 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101282825 |  | 17000 | Conductor | Overhead | Yes | 42183.8611 | 2015-06-28 20:40 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0423 | 2015 | 6 | 28 | 20 | 40 | 15-0043868 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 127930 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-28 20:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-28 21:07 | 42183.8799 | 39.7405 | -121.4974 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | DEADWOOD RD, JARBO GAP |  | 12000 | Conductor | Overhead | Yes | 42183.8799 | 2015-06-28 21:07 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0424 | 2015 | 6 | 28 | 21 | 7 | 15-0043869 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 45683 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-28 21:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-29 01:06 | 42184.0458 | 35.3516 | -119.0323 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Bakersfield FD | 100145659 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42184.0458 | 2015-06-29 01:06 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0425 | 2015 | 6 | 29 | 1 | 6 | 15-0043880 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 18722 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-29 01:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-29 06:26 | 42184.2681 | 37.5646 | -122.393 | Vegetation | Rural | < 3 meters | Fire Agency | burlingame fire | 100311342 | Pacific Bell | 4000 | Conductor | Overhead | Yes | 42184.2681 | 2015-06-29 06:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0426 | 2015 | 6 | 29 | 6 | 26 | 15-0043887 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2270 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-29 06:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-29 07:43 | 42184.3215 | 36.9343 | -119.9389 | Vegetation | Rural | < 0.25 Acres | Self Extinguished |  | rd 33 1/2 n/o ave 12 at 5451 |  | 12000 | Conductor | Overhead | Yes | 42184.3215 | 2015-06-29 07:43 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0427 | 2015 | 6 | 29 | 7 | 43 | 15-0043890 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 6125 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-29 07:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-29 18:45 | 42184.7812 | 39.1171 | -121.5725 | Vegetation | Urban | < 3 meters | Fire Agency | OLIVEHURST FIRE | 101319193 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | no-match | 0428 | 2015 | 6 | 29 | 18 | 45 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-06-29 18:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-30 00:05 | 42185.0035 | 35.4012 | -120.6222 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | santa margarita rch SS c/o 6631 |  | 12000 | Conductor | Overhead | Yes | 42185.0035 | 2015-06-30 00:05 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0429 | 2015 | 6 | 30 | 0 | 5 | 15-0044117 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 210493 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-30 00:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-30 05:40 | 42185.2361 | 35.2086 | -119.008 | Vegetation | Rural | < 3 meters | Fire Agency | KC Fire | 100127938 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42185.2361 | 2015-06-30 05:40 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0430 | 2015 | 6 | 30 | 5 | 40 | 15-0044123 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 60568 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-30 05:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-30 17:54 | 42185.7458 | 37.734 | -121.9381 | Vegetation | Urban | < 3 meters | Fire Agency | SRFD | 100901822 | Pacific Bell | 21000 | Transformer | Overhead | Yes | 42185.7458 | 2015-06-30 17:54 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0431 | 2015 | 6 | 30 | 17 | 54 | 15-0044387 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 9641 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-30 17:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-06-30 18:18 | 42185.7625 | 36.2199 | -121.7534 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | loadside of 88973 | unknown | 12000 | Conductor | Overhead | Yes | 42185.7625 | 2015-06-30 18:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0432 | 2015 | 6 | 30 | 18 | 18 | 15-0044405 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 158 | 0 | NA | <25mph | <15mph | #REF! | 2015-06-30 18:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-01 09:17 | 42186.3868 | 38.5715 | -122.5443 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42186.3868 | 2015-07-01 09:17 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0433 | 2015 | 7 | 1 | 9 | 17 | 15-0044529 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 85168 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-01 09:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-01 12:57 | 42186.5396 | 39.4146 | -121.379 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42186.5396 | 2015-07-01 12:57 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0434 | 2015 | 7 | 1 | 12 | 57 | 15-0044609 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-01 12:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-02 12:59 | 42187.541 | 37.0168 | -120.6358 | Vegetation | Rural | < 0.25 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42187.541 | 2015-07-02 12:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0435 | 2015 | 7 | 2 | 12 | 59 | 15-0045089 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 63960 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-02 12:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-02 14:06 | 42187.5875 | 38.7926 | -121.5015 | Vegetation | Rural | < 0.25 Acres | Fire Agency | unknown | 101299516 | None | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0436 | 2015 | 7 | 2 | 14 | 6 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-02 14:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-02 22:52 | 42187.9528 | 37.8561 | -120.9446 | Vegetation | Rural | < 0.25 Acres | Fire Agency | OAKDALE F.D. | W/SIDE VALLEY HOME RD @ LAMBUTH RD OAKDALE | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42187.9528 | 2015-07-02 22:52 | Contamination | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0437 | 2015 | 7 | 2 | 22 | 52 | 15-0045225 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 71577 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-02 22:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-03 03:23 | 42188.141 | 35.6785 | -120.9567 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 1 soan 1 conducter 1 span loade side transformer formtr 1008493290 |  | 21000 | Conductor | Overhead | Yes | 42188.141 | 2015-07-03 03:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0438 | 2015 | 7 | 3 | 3 | 23 | 15-0045239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 978 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-03 03:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-03 12:12 | 42188.5083 | 35.386 | -120.8571 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Morro Bay city | 101848318 |  | 12000 | Conductor | Overhead | Yes | 42188.5083 | 2015-07-03 12:12 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0439 | 2015 | 7 | 3 | 12 | 12 | 15-0045349 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-03 12:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-03 19:21 | 42188.8063 | 36.535 | -119.5004 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | County, CDF | 40952 Road 32 Kingsburg |  | 12000 | Conductor | Overhead | Yes | 42188.8063 | 2015-07-03 19:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0440 | 2015 | 7 | 3 | 19 | 21 | 15-0045424 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1980 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-03 19:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-04 01:14 | 42189.0514 | 38.9566 | -121.0434 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100037226 |  | 12000 | Other | Overhead | Yes | 42189.0514 | 2015-07-04 01:14 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0441 | 2015 | 7 | 4 | 1 | 14 | 15-0045440 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 53865 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-04 01:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-04 07:37 | 42189.3174 | 36.8314 | -119.8926 | Vegetation | Urban | < 0.25 Acres | Unknown |  | 103291813 |  | 115000 | Conductor | Overhead | Yes | 42189.3174 | 2015-07-04 07:37 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | no-match | 0442 | 2015 | 7 | 4 | 7 | 37 | FR-2015-042 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 0 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-04 07:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-04 14:14 | 42189.5931 | 37.8892 | -121.6135 | Vegetation | Rural | < 3 meters | Fire Agency | FIRE DEPARTMENT | 15001 HWY 4 2W/O DISCOVERY BAY | None | 21000 | Conductor | Overhead | Yes | 42189.5931 | 2015-07-04 14:14 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0443 | 2015 | 7 | 4 | 14 | 14 | 15-0045498 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 79283 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-04 14:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-05 09:42 | 42190.4042 | 35.5323 | -120.7371 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 0 – 750 | Conductor | Overhead | No |  |  | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0444 | 2015 | 7 | 5 | 9 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-05 09:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-05 21:21 | 42190.8896 | 38.6524 | -120.6278 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | one span east of c/o 1055 |  | 21000 | Conductor | Overhead | Yes | 42190.8896 | 2015-07-05 21:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0445 | 2015 | 7 | 5 | 21 | 21 | 15-0045605 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 22374 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-05 21:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-07 03:02 | 42192.1264 | 36.0218 | -120.1998 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FRESNO CAL FIRE | 1 POLE E/O 9716F OFF SUTTER AVE |  | 21000 | Conductor | Overhead | Yes | 42192.1264 | 2015-07-07 03:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0446 | 2015 | 7 | 7 | 3 | 2 | 15-0045876 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 591 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-07 03:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-07 05:52 | 42192.2444 | 36.7593 | -121.2954 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Hollister City | .25 Mile south of Bolado Park on Airline Hwy |  | 21000 | Conductor | Overhead | Yes | 42192.2444 | 2015-07-07 05:52 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0447 | 2015 | 7 | 7 | 5 | 52 | 15-0045883 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 156626 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-07 05:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-07 10:42 | 42192.4458 | 39.1138 | -121.0655 | Vegetation | Rural | < 0.25 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42192.4458 | 2015-07-07 10:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0448 | 2015 | 7 | 7 | 10 | 42 | 15-0045985 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 46738 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-07 10:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-07 15:27 | 42192.6438 | 35.155 | -120.5442 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 303corraltos cyn rd | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42192.6438 | 2015-07-07 15:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0449 | 2015 | 7 | 7 | 15 | 27 | 15-0046127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 98566 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-07 15:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-07 22:02 | 42192.9181 | 37.0033 | -121.5644 | Vegetation | Urban | < 0.25 Acres | Self Extinguished |  | 100614011 | Verizon | 21000 | Conductor | Overhead | Yes | 42192.9181 | 2015-07-07 22:02 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0450 | 2015 | 7 | 7 | 22 | 2 | 15-0046170 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 91036 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-07 22:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-08 11:23 | 42193.4743 | 39.224 | -121.0635 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 100094468 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42193.4743 | 2015-07-08 11:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0451 | 2015 | 7 | 8 | 11 | 23 | 15-0046274 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 22064 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-08 11:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-11 08:57 | 42196.3729 | 38.2188 | -122.2333 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | mid span from 5267 |  | 12000 | Conductor | Overhead | Yes | 42196.3729 | 2015-07-11 08:57 | Equipment/ Facility Failure | Guy/Span Wire | N.A. | N.A. | Unknown |  | Other/Unknown | 0452 | 2015 | 7 | 11 | 8 | 57 | 15-0046944 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 364 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-11 08:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-11 15:38 | 42196.6514 | 38.1839 | -121.8836 | Vegetation | Rural | < 0.25 Acres | Fire Agency | unknown | FUSE C/O 10313 LITTLE HONKER BAY RD & 20 SPANS E/O 10313 |  | 21000 | Conductor | Overhead | Yes | 42196.6514 | 2015-07-11 15:38 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0453 | 2015 | 7 | 11 | 15 | 38 | 15-0046967 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 862 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-11 15:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-12 01:32 | 42197.0639 | 39.952 | -122.2303 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101528676 | None | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0454 | 2015 | 7 | 12 | 1 | 32 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-12 01:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-12 15:27 | 42197.6438 | 35.2562 | -120.6839 | Vegetation | Urban | < 3 meters | Customer |  | 101936544 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0455 | 2015 | 7 | 12 | 15 | 27 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-12 15:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-12 17:04 | 42197.7111 | 37.4713 | -122.4256 | Vegetation | Rural | < 0.25 Acres | Fire Agency | COUNTY FIRE | 1 s w c509 |  | 12000 | Conductor | Overhead | Yes | 42197.7111 | 2015-07-12 17:04 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown | Jumper | Other/Unknown | 0456 | 2015 | 7 | 12 | 17 | 4 | 15-0047023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 117853 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-12 17:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-12 19:47 | 42197.8243 | 39.5118 | -122.1984 | Vegetation | Rural | < 3 meters | Fire Agency | WILLOWS FIRE DEPT. | 100403587 |  | 0 – 750 | Conductor | Overhead | Yes | 42197.8243 | 2015-07-12 19:47 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0457 | 2015 | 7 | 12 | 19 | 47 | 15-0047039 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 1029 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-12 19:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-13 14:16 | 42198.5944 | 37.2655 | -121.9804 | Vegetation | Urban | < 3 meters | Fire Agency | campbell | 100523574 | Pacific Bell | 12000 | Capacitor Bank | Overhead | Yes | 42198.5944 | 2015-07-13 14:16 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | Other/Unknown | 0458 | 2015 | 7 | 13 | 14 | 16 | 15-0047167 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 36960 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-13 14:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-13 17:04 | 42198.7111 | 37.968 | -122.3591 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RICHMOND FIRE DEPT & CCC FIRE FEPT | 101435021 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42198.7111 | 2015-07-13 17:04 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0459 | 2015 | 7 | 13 | 17 | 4 | 15-0047238 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 119 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-13 17:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-14 12:37 | 42199.5257 | 39.027 | -122.1353 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | arbuckle fire demp | Pole 010/189 - SAND CREEK RD CORTINA SCHOOL RD |  | 60000 | Conductor | Overhead | Yes | 42199.5257 | 2015-07-14 12:37 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0460 | 2015 | 7 | 14 | 12 | 37 | TM-2015-059 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-14 12:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-14 17:25 | 42199.7257 | 37.3631 | -122.021 | Vegetation | Urban | < 3 meters | Fire Agency | fd | 100530398 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42199.7257 | 2015-07-14 17:25 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0461 | 2015 | 7 | 14 | 17 | 25 | 15-0047489 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 161736 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-14 17:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-14 20:38 | 42199.8597 | 38.2439 | -122.5405 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101997187 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42199.8597 | 2015-07-14 20:38 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0462 | 2015 | 7 | 14 | 20 | 38 | 15-0047509 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 12268 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-14 20:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-15 09:00 | 42200.375 | 36.997 | -121.7381 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101795728 |  | 21000 | Conductor | Overhead | Yes | 42200.375 | 2015-07-15 09:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0463 | 2015 | 7 | 15 | 9 | 0 | 15-0047650 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3800 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-15 09:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-15 19:14 | 42200.8014 | 36.8985 | -121.6905 | Vegetation | Rural | < 0.25 Acres | Fire Agency | city | 101710538 |  | 21000 | Conductor | Overhead | Yes | 42200.8014 | 2015-07-15 19:14 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0464 | 2015 | 7 | 15 | 19 | 14 | 15-0047764 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 76058 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-15 19:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-16 19:11 | 42201.7993 | 37.1989 | -119.7712 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 20334 ROAD 400 |  | 12000 | Conductor | Overhead | Yes | 42201.7993 | 2015-07-16 19:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0465 | 2015 | 7 | 16 | 19 | 11 | 15-0048064 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-16 19:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-16 19:27 | 42201.8104 | 37.7619 | -120.8213 | Vegetation | Urban | < 3 meters | Self Extinguished |  | 102333491 | Pacific Bell | 0 – 750 | Conductor | Overhead | Yes | 42201.8104 | 2015-07-16 19:27 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0466 | 2015 | 7 | 16 | 19 | 27 | 15-0048066 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 297 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-16 19:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-17 00:20 | 42202.0139 | 36.9672 | -119.6436 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100651276 |  | 0 – 750 | Conductor | Overhead | Yes | 42202.0139 | 2015-07-17 00:20 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0467 | 2015 | 7 | 17 | 0 | 20 | 15-0048087 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | 154 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-17 00:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-17 00:53 | 42202.0368 | 34.8682 | -120.323 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SANTA BARBRA COUNTY FIRE DEPT | EAST OF SISQUOC SUB |  | 12000 | Conductor | Overhead | Yes | 42202.0368 | 2015-07-17 00:53 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0468 | 2015 | 7 | 17 | 0 | 53 | 15-0048084 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 46571 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-17 00:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-17 17:18 | 42202.7208 | 38.5596 | -121.6435 | Vegetation | Rural | < 3 meters | Unknown |  | in mid span between 2 poles. @ 46735 co. rd. 32B davis |  | 12000 | Conductor | Overhead | Yes | 42202.7208 | 2015-07-17 17:18 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0469 | 2015 | 7 | 17 | 17 | 18 | 15-0048287 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 13932 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-17 17:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-18 17:00 | 42203.7083 | 38.8383 | -123.6297 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | off HWY 1 PA |  | 12000 | Conductor | Overhead | Yes | 42203.7083 | 2015-07-18 17:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0470 | 2015 | 7 | 18 | 17 | 0 | 15-0048394 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 51806 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-18 17:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-18 18:59 | 42203.791 | 39.712 | -123.3284 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42203.791 | 2015-07-18 18:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0471 | 2015 | 7 | 18 | 18 | 59 | 15-0048410 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 2466 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-18 18:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-19 09:44 | 42204.4056 | 35.215 | -120.6144 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101930875 |  | 12000 | Conductor | Overhead | Yes | 42204.4056 | 2015-07-19 09:44 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 0472 | 2015 | 7 | 19 | 9 | 44 | 15-0048659 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 113118 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-19 09:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-19 19:36 | 42204.8167 | 38.6563 | -121.7935 | Vegetation | Urban | < 3 meters | Fire Agency | WOODLAND FIRE DEPT. | BASE OF TRANSMISSION / DISTRIBUITION POLE = 1/P/S/O FUSES # 8973 |  | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0473 | 2015 | 7 | 19 | 19 | 36 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-19 19:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-20 15:15 | 42205.6354 | 37.762 | -120.8654 | Vegetation | Urban | < 0.25 Acres | Fire Agency | OAKDALE CITY FIRE |  |  | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0474 | 2015 | 7 | 20 | 15 | 15 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-20 15:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-21 08:44 | 42206.3639 | 39.1181 | -123.2011 | Vegetation | Rural | < 0.25 Acres | Fire Agency | UKIAH FIRE | 102178810 | Pacific Bell | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0475 | 2015 | 7 | 21 | 8 | 44 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-21 08:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-21 10:46 | 42206.4486 | 37.1806 | -121.0625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | e/o dmc s/o cottenwood |  | 12000 | Conductor | Overhead | Yes | 42206.4486 | 2015-07-21 10:46 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0476 | 2015 | 7 | 21 | 10 | 46 | 15-0049524 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 5171 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-21 10:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-22 11:03 | 42207.4604 | 38.1206 | -122.2481 | Vegetation | Urban | < 3 meters | Fire Agency | VALLEJO FD | 102308149 |  | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0477 | 2015 | 7 | 22 | 11 | 3 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-22 11:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-22 14:21 | 42207.5979 | 38.7935 | -120.714 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | s\ 3204 stope dr |  | 12000 | Conductor | Overhead | Yes | 42207.5979 | 2015-07-22 14:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0478 | 2015 | 7 | 22 | 14 | 21 | 15-0049908 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 149206 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-22 14:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-23 13:14 | 42208.5514 | 36.2398 | -119.7767 | Vegetation | Rural | < 0.25 Acres | Fire Agency | KINGS COUNTY | 103242492 | YES | 12000 | Conductor | Overhead | Yes | 42208.5514 | 2015-07-23 13:14 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0479 | 2015 | 7 | 23 | 13 | 14 | 15-0050086 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 14270 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-23 13:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-23 20:04 | 42208.8361 | 38.0075 | -121.8482 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Tower 006/081 |  | 60000 | Unknown | Overhead | Yes | 42208.8361 | 2015-07-23 20:04 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0480 | 2015 | 7 | 23 | 20 | 4 | PS-2015-015 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 0 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-23 20:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-24 04:10 | 42209.1736 | 38.4523 | -121.7182 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Dixon fire dept | 101575623 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42209.1736 | 2015-07-24 04:10 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0481 | 2015 | 7 | 24 | 4 | 10 | 15-0050202 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 810 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-24 04:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-24 14:30 | 42209.6042 | 36.6913 | -119.0312 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46970 DUNLAP RD | YES | 0 – 750 | Transformer | Overhead | Yes | 42209.6042 | 2015-07-24 14:30 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0482 | 2015 | 7 | 24 | 14 | 30 | 15-0050401 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 281 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-24 14:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-25 14:52 | 42210.6194 | 38.9264 | -121.2946 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | wise rd west of gladding lincoln | None | 12000 | Conductor | Overhead | Yes | 42210.6194 | 2015-07-25 14:52 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0483 | 2015 | 7 | 25 | 14 | 52 | 15-0050487 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1525 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-25 14:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-25 19:34 | 42210.8153 | 39.7848 | -121.8608 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 3668 hicks lane, Chico |  | 12000 | Conductor | Overhead | Yes | 42210.8153 | 2015-07-25 19:34 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0484 | 2015 | 7 | 25 | 19 | 34 | 15-0050509 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 6525 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-25 19:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-26 12:25 | 42211.5174 | 39.1586 | -121.0634 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 15499 ALLISON RANCH RD |  | 12000 | Conductor | Overhead | Yes | 42211.5174 | 2015-07-26 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0485 | 2015 | 7 | 26 | 12 | 25 | 15-0050558 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2224 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-26 12:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-27 09:41 | 42212.4035 | 37.6565 | -121.757 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LPFD | 100926006 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0486 | 2015 | 7 | 27 | 9 | 41 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-27 09:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-27 13:07 | 42212.5465 | 37.7673 | -121.42 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TRACY FIRE DEPT | AT C258; S/S ARBOR W/ MACARTHUR | None | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0487 | 2015 | 7 | 27 | 13 | 7 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-27 13:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-27 15:33 | 42212.6479 | 38.4183 | -122.7167 | Building | Urban | .26 - 9.99 Acres | Fire Agency |  | 2180 Corby Ave, Santa Rosa | None | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0488 | 2015 | 7 | 27 | 15 | 33 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-27 15:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-27 15:57 | 42212.6646 | 39.0711 | -121.4728 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Wheatland fire dept | 101324044 |  | 12000 | Other | Overhead | Yes | 42212.6646 | 2015-07-27 15:57 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0489 | 2015 | 7 | 27 | 15 | 57 | 15-0050786 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 16898 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-27 15:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-28 12:15 | 42213.5104 | 40.9086 | -124.0716 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100973761 | Pacific Bell | 12000 | Lightning Arrestor | Overhead | Yes | 42213.5104 | 2015-07-28 12:15 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | Other/Unknown | 0490 | 2015 | 7 | 28 | 12 | 15 | 15-0050964 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-28 12:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-28 12:19 | 42213.5132 | 37.7643 | -121.3442 | Vegetation | Rural | < 3 meters | Fire Agency | tracy fire dept | w/ berry ave on canal blvd | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42213.5132 | 2015-07-28 12:19 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0491 | 2015 | 7 | 28 | 12 | 19 | 15-0050969 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 12649 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-28 12:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-28 12:32 | 42213.5222 | 37.9429 | -120.944 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | Waverly Road and HWY 4, Farmington |  | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0492 | 2015 | 7 | 28 | 12 | 32 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-28 12:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-29 13:30 | 42214.5625 | 38.5549 | -122.8303 | Vegetation | Urban | < 3 meters | Unknown |  | 1031 Starr View Drive, Windsor |  | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Other | Electric Facility | Human Error | hit by boom of bucket truck | no-match | 0493 | 2015 | 7 | 29 | 13 | 30 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-29 13:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-29 23:34 | 42214.9819 | 37.3662 | -121.8438 | Vegetation | Urban | < 3 meters | Fire Agency | SJFD | IRO 751 FLEMING AVE IN FIELD NEAR DRY CREEK BED |  | 12000 | Conductor | Overhead | Yes | 42214.9819 | 2015-07-29 23:34 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0494 | 2015 | 7 | 29 | 23 | 34 | 15-0051483 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 100542 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-29 23:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-30 14:26 | 42215.6014 | 38.3459 | -122.3105 | Vegetation | Urban | < 0.25 Acres | Unknown | unknown | In ditch at base of pole. 12 by 60 | Pacific Bell | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0495 | 2015 | 7 | 30 | 14 | 26 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-30 14:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-30 14:55 | 42215.6215 | 38.4448 | -121.8269 | Building | Urban | Structure Only | Fire Agency | dixon fire dept | 103309947 |  | 12000 | Transformer | Overhead | Yes | 42215.6215 | 2015-07-30 14:55 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0496 | 2015 | 7 | 30 | 14 | 55 | 15-0051715 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 24065 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-30 14:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-30 15:19 | 42215.6382 | 39.2321 | -121.0567 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | GRASS VALLEY FIRE DEPT | BEHIND 272 HUGHES RD, GRASS VALLEY |  | 12000 | Conductor | Overhead | Yes | 42215.6382 | 2015-07-30 15:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0497 | 2015 | 7 | 30 | 15 | 19 | 15-0051726 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 2988 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-30 15:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-30 17:38 | 42215.7347 | 40.5203 | -122.2326 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | MTR 10061916 |  | 12000 | Conductor | Overhead | Yes | 42215.7347 | 2015-07-30 17:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0498 | 2015 | 7 | 30 | 17 | 38 | 15-0051755 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 30139 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-30 17:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-30 17:56 | 42215.7472 | 37.9021 | -120.4739 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101019808 |  | 17000 | Conductor | Overhead | Yes | 42215.7472 | 2015-07-30 17:56 | Contact From Object | N.A. | Other | Electric Facility | Unknown | osprey nest | Other/Unknown | 0499 | 2015 | 7 | 30 | 17 | 56 | 15-0051764 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 615 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-30 17:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-30 19:11 | 42215.7993 | 37.8102 | -120.1287 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE |  |  | 17000 | Conductor | Overhead | Yes | 42215.7993 | 2015-07-30 19:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0500 | 2015 | 7 | 30 | 19 | 11 | 15-0051772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26776 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-30 19:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-31 15:57 | 42216.6646 | 36.7974 | -119.8189 | Vegetation | Urban | < 3 meters | Fire Agency | fresno fire dept | 100856564 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0501 | 2015 | 7 | 31 | 15 | 57 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-31 15:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-31 19:36 | 42216.8167 | 35.3986 | -118.99 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CITY OF BAKERSFIELD | 100164905 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0502 | 2015 | 7 | 31 | 19 | 36 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-07-31 19:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-07-31 22:45 | 42216.9479 | 38.3805 | -120.5628 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS FROM 1958 QUAIL LN WEST POINT | None | 12000 | Conductor | Overhead | Yes | 42216.9479 | 2015-07-31 22:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0503 | 2015 | 7 | 31 | 22 | 45 | 15-0052033 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 33559 | 0 | NA | <25mph | <15mph | #REF! | 2015-07-31 22:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-01 07:15 | 42217.3021 | 36.4029 | -121.9094 | Vegetation | Rural | < 0.25 Acres | Fire Agency | fire com | 3spans loadside of 40283 |  | 12000 | Conductor | Overhead | Yes | 42217.3021 | 2015-08-01 07:15 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 0504 | 2015 | 8 | 1 | 7 | 15 | 15-0052054 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4650 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-01 07:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-01 14:30 | 42217.6042 | 34.9524 | -120.2952 | Vegetation | Rural | 10 - 99 Acres | Unknown |  | 101868639 |  | 12000 | Conductor | Overhead | Yes | 42217.6042 | 2015-08-01 14:30 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0505 | 2015 | 8 | 1 | 14 | 30 | 15-0052506 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 1528 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-01 14:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-02 08:08 | 42218.3389 | 37.5338 | -120.3277 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Pole 013/002 |  | 70000 | Conductor | Overhead | Yes | 42218.3389 | 2015-08-02 08:08 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0506 | 2015 | 8 | 2 | 8 | 8 | LB-2015-026 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-02 08:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-02 13:48 | 42218.575 | 37.88 | -122.5268 | Vegetation | Urban | < 0.25 Acres | Fire Agency | mill valley FD | 102276049 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0507 | 2015 | 8 | 2 | 13 | 48 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-08-02 13:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-02 16:24 | 42218.6833 | 37.6317 | -120.1547 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101076992 |  | 21000 | Conductor | Overhead | Yes | 42218.6833 | 2015-08-02 16:24 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0508 | 2015 | 8 | 2 | 16 | 24 | 15-0064792 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-08-02 16:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-03 00:07 | 42219.0049 | 40.5056 | -122.347 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | COTTONWOOD FIRE DEPT | 101503428 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42219.0049 | 2015-08-03 00:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0509 | 2015 | 8 | 3 | 0 | 7 | 15-0052184 | Zone 1 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 10427 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-03 00:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-03 17:53 | 42219.7451 | 39.3361 | -121.1894 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Pole 000/008 |  | 60000 | Conductor | Overhead | Yes | 42219.7451 | 2015-08-03 17:53 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0510 | 2015 | 8 | 3 | 17 | 53 | TM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-03 17:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-04 16:05 | 42220.6701 | 40.0822 | -121.1538 | Vegetation | Rural | < 0.25 Acres | Fire Agency | USFS | 100441220 | None | 0 – 750 | Fuse | Overhead | Yes | 42220.6701 | 2015-08-04 16:05 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0511 | 2015 | 8 | 4 | 16 | 5 | 15-0052743 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4591 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-04 16:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-04 17:57 | 42220.7479 | 37.5879 | -120.229 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Str. 007/019 |  | 70000 | Conductor | Overhead | Yes | 42220.7479 | 2015-08-04 17:57 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0512 | 2015 | 8 | 4 | 17 | 57 | LB-2015-028 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-04 17:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-05 15:13 | 42221.634 | 37.32 | -120.5051 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 101162540 |  | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0513 | 2015 | 8 | 5 | 15 | 13 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-08-05 15:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-06 12:10 | 42222.5069 | 38.2269 | -121.0261 | Vegetation | Rural | < 0.25 Acres | Fire Agency | city of ione fire dept | 103194904 | Verizon | 21000 | Conductor | Overhead | Yes | 42222.5069 | 2015-08-06 12:10 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0514 | 2015 | 8 | 6 | 12 | 10 | 15-0053232 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 540 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-06 12:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-06 16:18 | 42222.6792 | 39.2754 | -122.0758 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 6 POLES E/LR 3036 |  | 12000 | Conductor | Overhead | Yes | 42222.6792 | 2015-08-06 16:18 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0515 | 2015 | 8 | 6 | 16 | 18 | 15-0053318 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 41180 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-06 16:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-07 06:24 | 42223.2667 | 37.5024 | -122.1057 | Vegetation | Rural | < 0.25 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42223.2667 | 2015-08-07 06:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0516 | 2015 | 8 | 7 | 6 | 24 | 15-0053461 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14784 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-07 06:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-07 06:32 | 42223.2722 | 37.84 | -122.1823 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100498058 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42223.2722 | 2015-08-07 06:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0517 | 2015 | 8 | 7 | 6 | 32 | 15-0053493 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-08-07 06:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-07 16:59 | 42223.7076 | 39.8918 | -122.1694 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | EVERY BODY | 101500955 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42223.7076 | 2015-08-07 16:59 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0518 | 2015 | 8 | 7 | 16 | 59 | 15-0053713 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 117811 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-07 16:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-08 07:42 | 42224.3208 | 39.2007 | -121.2137 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100076217 | Pacific Bell | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0519 | 2015 | 8 | 8 | 7 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-08-08 07:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-08 16:03 | 42224.6687 | 41.2844 | -124.0757 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | PARKS SERVICE | 100978185 | Verizon | 12000 | Conductor | Overhead | Yes | 42224.6687 | 2015-08-08 16:03 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0520 | 2015 | 8 | 8 | 16 | 3 | 15-0053872 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 3928 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-08 16:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-10 11:30 | 42226.4792 | 37.9446 | -121.9698 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CONTRA COSTA FIRE | 1 pole west of c/o 7069 | None | 21000 | Conductor | Overhead | Yes | 42226.4792 | 2015-08-10 11:30 | Contact From Object | N.A. | Other | Electric Facility | Human Error | third-party cut into riser | Other/Unknown | 0521 | 2015 | 8 | 10 | 11 | 30 | 15-0054066 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 136665 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-10 11:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-10 12:41 | 42226.5285 | 36.8877 | -121.8158 | Vegetation | Rural | < 3 meters | Self Extinguished |  |  | None | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0522 | 2015 | 8 | 10 | 12 | 41 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-08-10 12:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-10 21:58 | 42226.9153 | 38.5296 | -120.8164 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101235918 |  | 0 – 750 | Conductor | Overhead | Yes | 42226.9153 | 2015-08-10 21:58 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0523 | 2015 | 8 | 10 | 21 | 58 | 15-0054201 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 532 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-10 21:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-11 04:26 | 42227.1847 | 36.1289 | -121.0147 | Vegetation | Rural | < 0.25 Acres | Fire Agency | unknown | 101728045 |  | 12000 | Conductor | Overhead | Yes | 42227.1847 | 2015-08-11 04:26 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0524 | 2015 | 8 | 11 | 4 | 26 | 15-0054211 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 25678 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-11 04:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-12 17:38 | 42228.7347 | 40.2153 | -123.8681 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 1 SP LD SD METER 1007960761 |  | 12000 | Conductor | Overhead | Yes | 42228.7347 | 2015-08-12 17:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0525 | 2015 | 8 | 12 | 17 | 38 | 15-0054643 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 14640 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-12 17:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-13 03:46 | 42229.1569 | 37.2072 | -119.7343 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 44365 SAVAGE RD COARSEGOLD |  | 21000 | Conductor | Overhead | Yes | 42229.1569 | 2015-08-13 03:46 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0526 | 2015 | 8 | 13 | 3 | 46 | 15-0054655 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 7600 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-13 03:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-13 03:57 | 42229.1646 | 38.7757 | -121.8585 | Vegetation | Rural | < 3 meters | Fire Agency | DON'T KNOW - COUNTY? THEY WERE GONE | LINE & BUCK PG&E POLE AT FUSES 79079. | None | 12000 | Conductor | Overhead | Yes | 42229.1646 | 2015-08-13 03:57 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0527 | 2015 | 8 | 13 | 3 | 57 | 15-0054657 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 56178 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-13 03:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-13 23:55 | 42229.9965 | 37.4077 | -121.8538 | Vegetation | Urban | < 0.25 Acres | Fire Agency | MILPITAS FD | 100558502 | Pacific Bell | 12000 | Fuse | Overhead | Yes | 42229.9965 | 2015-08-13 23:55 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0528 | 2015 | 8 | 13 | 23 | 55 | 15-0054932 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 22872 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-13 23:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-14 10:22 | 42230.4319 | 39.8288 | -122.0851 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ORLAND FD(FIRE DEPT) | 4 TH AVE N/O 1/4 MI. CLARK RD |  | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0529 | 2015 | 8 | 14 | 10 | 22 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-08-14 10:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-14 15:09 | 42230.6312 | 40.9829 | -121.7802 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101514540 |  | 21000 | Conductor | Overhead | Yes | 42230.6312 | 2015-08-14 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0530 | 2015 | 8 | 14 | 15 | 9 | 15-0055136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3072 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-14 15:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-14 17:44 | 42230.7389 | 37.8894 | -120.4933 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | ENTRANCE TO 14650 HWY 108, JAMESTOWN |  | 17000 | Conductor | Overhead | Yes | 42230.7389 | 2015-08-14 17:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0531 | 2015 | 8 | 14 | 17 | 44 | 15-0055160 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 1726 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-14 17:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-15 12:26 | 42231.5181 | 36.8344 | -121.6614 | Vegetation | Rural | < 3 meters | Customer |  | 101713223 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42231.5181 | 2015-08-15 12:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0532 | 2015 | 8 | 15 | 12 | 26 | 15-0055208 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 58780 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-15 12:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-15 13:41 | 42231.5701 | 37.9607 | -122.5709 | Vegetation | Urban | < 0.25 Acres | Fire Agency | COUNTY FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42231.5701 | 2015-08-15 13:41 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0533 | 2015 | 8 | 15 | 13 | 41 | 15-0055217 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 5973 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-15 13:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-16 07:35 | 42232.316 | 35.4572 | -120.6567 | Vegetation | Rural | < 3 meters | Utility: PG&E |  | 8932 SAN GABRIEL RD. SW C/O OF LOT, Atascadero | None | 0 – 750 | Conductor | Overhead | Yes | 42232.316 | 2015-08-16 07:35 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0534 | 2015 | 8 | 16 | 7 | 35 | 15-0055284 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-08-16 07:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-16 12:04 | 42232.5028 | 37.5939 | -122.0066 | Vegetation | Urban | < 0.25 Acres | Fire Agency | ALCO FIRE/UNION CITY |  |  | 12000 | Conductor | Overhead | Yes | 42232.5028 | 2015-08-16 12:04 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0535 | 2015 | 8 | 16 | 12 | 4 | 15-0055307 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 108351 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-16 12:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-16 20:59 | 42232.8743 | 38.5963 | -121.5266 | Vegetation | Urban | < 3 meters | Fire Agency | west sacramento FD | 101606084 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42232.8743 | 2015-08-16 20:59 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0536 | 2015 | 8 | 16 | 20 | 59 | 15-0055402 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 68623 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-16 20:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-17 08:37 | 42233.359 | 37.0757 | -122.023 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101800237 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0537 | 2015 | 8 | 17 | 8 | 37 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-08-17 08:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-17 14:29 | 42233.6035 | 36.7216 | -119.8315 | Vegetation | Rural | < 3 meters | Fire Agency | FRESNO FD |  |  | 12000 | Conductor | Overhead | Yes | 42233.6035 | 2015-08-17 14:29 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0538 | 2015 | 8 | 17 | 14 | 29 | 15-0055602 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-08-17 14:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-17 17:33 | 42233.7312 | 38.8337 | -123.5533 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 14 spans load side 2345 |  | 12000 | Conductor | Overhead | Yes | 42233.7312 | 2015-08-17 17:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0539 | 2015 | 8 | 17 | 17 | 33 | 15-0055664 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 676 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-17 17:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-17 20:57 | 42233.8729 | 36.6867 | -119.0612 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46371 ORCHARD DRIVE |  | 12000 | Conductor | Overhead | Yes | 42233.8729 | 2015-08-17 20:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0540 | 2015 | 8 | 17 | 20 | 57 | 15-0055696 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 34398 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-17 20:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-18 08:03 | 42234.3354 | 39.0867 | -122.9236 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | at base of pole across from 3838 Hill rd Lakeport |  | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0541 | 2015 | 8 | 18 | 8 | 3 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-08-18 08:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-18 20:36 | 42234.8583 | 39.202 | -121.0784 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CO. & CDF | 3 LOC HIDDEN VALLEY ; OLD AUBURN RD 1 |  | 12000 | Conductor | Overhead | Yes | 42234.8583 | 2015-08-18 20:36 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0542 | 2015 | 8 | 18 | 20 | 36 | 15-0055958 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 160480 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-18 20:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-19 00:07 | 42235.0049 | 38.8862 | -121.0745 | Vegetation | Urban | < 0.25 Acres | Unknown |  |  |  | 12000 | Capacitor Bank | Overhead | Yes | 42235.0049 | 2015-08-19 00:07 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | Other/Unknown | 0543 | 2015 | 8 | 19 | 0 | 7 | 15-0055968 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-08-19 00:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-19 02:10 | 42235.0903 | 39.3848 | -122.5514 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STONYFORD FIRE DEPT | @ MTR # 1008056130 |  | 12000 | Conductor | Overhead | Yes | 42235.0903 | 2015-08-19 02:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0544 | 2015 | 8 | 19 | 2 | 10 | 15-0055976 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 211970 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-19 02:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-19 06:20 | 42235.2639 | 39.2831 | -123.2931 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | MTR#50001225 | None | 12000 | Conductor | Overhead | Yes | 42235.2639 | 2015-08-19 06:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0545 | 2015 | 8 | 19 | 6 | 20 | 15-0055982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5403 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-19 06:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-19 13:42 | 42235.5708 | 37.7926 | -120.7748 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Stanislaus Consolidated fire . | 102334306 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42235.5708 | 2015-08-19 13:42 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0546 | 2015 | 8 | 19 | 13 | 42 | 15-0056116 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 62632 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-19 13:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-20 14:08 | 42236.5889 | 36.8989 | -119.5213 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100725569 | None | 12000 | Conductor | Overhead | Yes | 42236.5889 | 2015-08-20 14:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0547 | 2015 | 8 | 20 | 14 | 8 | 15-0056381 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 75567 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-20 14:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-21 13:54 | 42237.5792 | 37.4295 | -121.9142 | Vegetation | Urban | < 3 meters | Customer |  | BACK YARD OF 296 ABBOTT |  | 21000 | Conductor | Overhead | Yes | 42237.5792 | 2015-08-21 13:54 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 0548 | 2015 | 8 | 21 | 13 | 54 | 15-0056672 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 19316 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-21 13:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-22 20:38 | 42238.8597 | 38.7748 | -120.8564 | Vegetation | Rural | < 3 meters | Self Extinguished |  | at base of co pole 21721 - 720 Woodridge Rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42238.8597 | 2015-08-22 20:38 | Contact From Object | N.A. | Vegetation | Communication Facility | Unknown | tree hit phone lines | Fell into (Moderate-Severe defect) | 0549 | 2015 | 8 | 22 | 20 | 38 | 15-0056766 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26513 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-22 20:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-23 14:04 | 42239.5861 | 38.9334 | -122.62 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CL fire dept | 7200 so. center dr | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42239.5861 | 2015-08-23 14:04 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0550 | 2015 | 8 | 23 | 14 | 4 | 15-0056827 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 16815 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-23 14:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-23 14:15 | 42239.5938 | 37.3394 | -120.4378 | Vegetation | Rural | < 0.25 Acres | Utility: PG&E |  | AT INTERSECTION OF HARBOR & DUNN |  | 12000 | Lightning Arrestor | Overhead | Yes | 42239.5938 | 2015-08-23 14:15 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | Other/Unknown | 0551 | 2015 | 8 | 23 | 14 | 15 | 15-0056830 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1743 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-23 14:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-24 22:48 | 42240.95 | 37.896 | -122.6011 | Vegetation | Rural | < 3 meters | Fire Agency | marin county fire | 200' east of pan toll rd 50' north of panoramic hwy |  | 12000 | Unknown | Overhead | Yes | 42240.95 | 2015-08-24 22:48 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0552 | 2015 | 8 | 24 | 22 | 48 | 15-0057082 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 1128 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-24 22:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-25 09:12 | 42241.3833 | 38.3351 | -123.0449 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Bodega bay fire dept | 101974695 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42241.3833 | 2015-08-25 09:12 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0553 | 2015 | 8 | 25 | 9 | 12 | 15-0057152 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 15200 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-25 09:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-25 14:01 | 42241.584 | 39.1491 | -121.5971 | Vegetation | Urban | < 0.25 Acres | Customer |  | 101338374 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0554 | 2015 | 8 | 25 | 14 | 1 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-08-25 14:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-26 12:04 | 42242.5028 | 37.9638 | -122.5243 | Vegetation | Urban | < 0.25 Acres | Fire Agency | srfd | 102242504 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42242.5028 | 2015-08-26 12:04 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0555 | 2015 | 8 | 26 | 12 | 4 | 15-0057475 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 28873 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-26 12:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-26 15:36 | 42242.65 | 36.6245 | -121.5289 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MONTEREY COUNTY FIRE DEPT. | 101770699 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42242.65 | 2015-08-26 15:36 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0556 | 2015 | 8 | 26 | 15 | 36 | 15-0057543 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-08-26 15:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-26 23:49 | 42242.9924 | 36.3897 | -121.3653 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101756678 | None | 21000 | Conductor | Overhead | Yes | 42242.9924 | 2015-08-26 23:49 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0557 | 2015 | 8 | 26 | 23 | 49 | 15-0057613 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 8445 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-26 23:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-27 03:30 | 42243.1458 | 37.8448 | -122.1992 | Vegetation | Urban | < 0.25 Acres | Unknown |  | 100487196 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42243.1458 | 2015-08-27 03:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0558 | 2015 | 8 | 27 | 3 | 30 | 15-0057619 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 176351 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-27 03:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-27 18:00 | 42243.75 | 37.403 | -121.9056 | Vegetation | Urban | < 3 meters | Fire Agency | Milpitas F.D | switches 1238 and 1114 |  | 21000 | Switch | Overhead | Yes | 42243.75 | 2015-08-27 18:00 | Equipment/ Facility Failure | Switch | N.A. | N.A. | Unknown |  | Other/Unknown | 0559 | 2015 | 8 | 27 | 18 | 0 | 15-0057830 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 360531 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-27 18:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-28 03:14 | 42244.1347 | 36.6067 | -119.8807 | Vegetation | Rural | < 3 meters | Fire Agency | COUNTY FIRE | 100710466 |  | 12000 | Conductor | Overhead | Yes | 42244.1347 | 2015-08-28 03:14 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0560 | 2015 | 8 | 28 | 3 | 14 | 15-0057861 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 71695 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-28 03:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-28 07:08 | 42244.2972 | 38.8839 | -121.303 | Vegetation | Urban | < 0.25 Acres | Fire Agency | lincoln fire | 100068928 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42244.2972 | 2015-08-28 07:08 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0561 | 2015 | 8 | 28 | 7 | 8 | 15-0057874 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 178276 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-28 07:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-28 11:48 | 42244.4917 | 38.8513 | -121.1469 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100055373 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0562 | 2015 | 8 | 28 | 11 | 48 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-08-28 11:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-28 12:02 | 42244.5014 | 37.9047 | -122.2058 | Vegetation | Rural | < 0.25 Acres | Fire Agency | EB MUD | 103623279 |  | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0563 | 2015 | 8 | 28 | 12 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-08-28 12:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-28 21:45 | 42244.9062 | 38.0198 | -122.0614 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CONTRA COSTA FIRE | HWY 4 PORT CHICAGO WILLOW PASS |  | 21000 | Conductor | Overhead | Yes | 42244.9062 | 2015-08-28 21:45 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | pole cut with chainsaw | Other/Unknown | 0564 | 2015 | 8 | 28 | 21 | 45 | 15-0058108 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 79108 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-28 21:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-28 22:05 | 42244.9201 | 37.8039 | -121.2076 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Manteca Fire | 102084916 | Verizon | 17000 | Conductor | Overhead | Yes | 42244.9201 | 2015-08-28 22:05 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0565 | 2015 | 8 | 28 | 22 | 5 | 15-0058113 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 21350 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-28 22:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-29 03:30 | 42245.1458 | 38.6302 | -122.8327 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Dirt road across from 3204 Rio Lindo Rd, Healdsburg |  | 12000 | Conductor | Overhead | Yes | 42245.1458 | 2015-08-29 03:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0566 | 2015 | 8 | 29 | 3 | 30 | 15-0058127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4780 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-29 03:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-30 17:05 | 42246.7118 | 38.4039 | -120.5559 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | centennial mine rd |  | 12000 | Conductor | Overhead | Yes | 42246.7118 | 2015-08-30 17:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0567 | 2015 | 8 | 30 | 17 | 5 | 15-0058273 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 40298 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-30 17:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-31 14:28 | 42247.6028 | 36.5325 | -121.1462 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 29401 Hwy 25 |  | 21000 | Conductor | Overhead | Yes | 42247.6028 | 2015-08-31 14:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0568 | 2015 | 8 | 31 | 14 | 28 | 15-0058455 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25668 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-31 14:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-31 16:06 | 42247.6708 | 40.4915 | -122.2835 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101467437 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42247.6708 | 2015-08-31 16:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0569 | 2015 | 8 | 31 | 16 | 6 | 15-0058470 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 87466 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-31 16:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-08-31 20:19 | 42247.8465 | 37.9885 | -122.5778 | Vegetation | Urban | < 0.25 Acres | Fire Agency | marin county fire | 102222106 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42247.8465 | 2015-08-31 20:19 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0570 | 2015 | 8 | 31 | 20 | 19 | 15-0058488 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 63957 | 0 | NA | <25mph | <15mph | #REF! | 2015-08-31 20:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-01 01:29 | 42248.0618 | 38.1594 | -121.6128 | Other | Rural | Structure Only | Fire Agency | ISELTON FIRE DEPT | 16393 JACKSON BL ISLETON |  | 21000 | Conductor | Overhead | Yes | 42248.0618 | 2015-09-01 01:29 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0571 | 2015 | 9 | 1 | 1 | 29 | 15-0058496 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 100322 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-01 01:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-01 10:34 | 42248.4403 | 39.4054 | -122.0011 | Vegetation | Rural | < 0.25 Acres | Fire Agency | BUTTE CITY | 101638382 |  | 0 – 750 | Conductor | Overhead | Yes | 42248.4403 | 2015-09-01 10:34 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | Other/Unknown | 0572 | 2015 | 9 | 1 | 10 | 34 | 15-0058663 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 209 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-01 10:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-01 18:48 | 42248.7833 | 35.3821 | -118.9301 | Other | Urban | Structure Only | Fire Agency | KCFD | 100120045 |  | 0 – 750 | Conductor | Overhead | Yes | 42248.7833 | 2015-09-01 18:48 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0573 | 2015 | 9 | 1 | 18 | 48 | 15-0058757 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 4168 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-01 18:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-01 22:15 | 42248.9271 | 35.6443 | -120.7067 | Vegetation | Rural | < 3 meters | Utility: PG&E |  | 101939126 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42248.9271 | 2015-09-01 22:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0574 | 2015 | 9 | 1 | 22 | 15 | 15-0058762 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 73610 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-01 22:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-02 19:07 | 42249.7965 | 39.7251 | -122.0871 | Vegetation | Rural | < 3 meters | Fire Agency | ORLAND FIRE DEPT |  |  | 0 – 750 | Conductor | Overhead | No |  |  | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 0575 | 2015 | 9 | 2 | 19 | 7 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-09-02 19:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-03 19:51 | 42250.8271 | 37.6022 | -122.0395 | Vegetation | Urban | < 3 meters | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42250.8271 | 2015-09-03 19:51 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0576 | 2015 | 9 | 3 | 19 | 51 | 15-0059243 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 45428 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-03 19:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-04 07:49 | 42251.3257 | 40.2318 | -122.3643 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | E/O FRONTIER RD & N/O WAGON WAY |  | 12000 | Conductor | Overhead | Yes | 42251.3257 | 2015-09-04 07:49 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0577 | 2015 | 9 | 4 | 7 | 49 | 15-0059323 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 9563 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-04 07:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-04 08:47 | 42251.366 | 36.7925 | -121.6629 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE DEPT | 101722853 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42251.366 | 2015-09-04 08:47 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0578 | 2015 | 9 | 4 | 8 | 47 | 15-0059316 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 50078 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-04 08:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-05 05:36 | 42252.2333 | 39.9275 | -122.1915 | Building | Urban | Structure Only | Fire Agency | city fire | 101533501 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0579 | 2015 | 9 | 5 | 5 | 36 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-09-05 05:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-05 16:47 | 42252.6993 | 37.6911 | -122.0578 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CASTRO VALLEY | 100914170 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | no-match | 0580 | 2015 | 9 | 5 | 16 | 47 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-09-05 16:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-06 13:37 | 42253.5674 | 40.1692 | -122.2569 | Vegetation | Urban | < 3 meters | Fire Agency | Red Bluff fire dept | at switch 3571 |  | 0 – 750 | Conductor | Overhead | Yes | 42253.5674 | 2015-09-06 13:37 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0581 | 2015 | 9 | 6 | 13 | 37 | 15-0059595 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-09-06 13:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-06 19:27 | 42253.8104 | 34.6195 | -120.2534 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Santa Barbara County Fire | meter# 1008400678 | Verizon | 12000 | Conductor | Overhead | Yes | 42253.8104 | 2015-09-06 19:27 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0582 | 2015 | 9 | 6 | 19 | 27 | 15-0059612 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 863 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-06 19:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-06 19:40 | 42253.8194 | 37.5133 | -121.9469 | Vegetation | Urban | < 3 meters | Customer |  | 100943889 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0583 | 2015 | 9 | 6 | 19 | 40 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-09-06 19:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-07 00:05 | 42254.0035 | 37.6913 | -122.1388 | Vegetation | Urban | < 0.25 Acres | Fire Agency | SAN LEANDRO |  |  | 12000 | Conductor | Overhead | Yes | 42254.0035 | 2015-09-07 00:05 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0584 | 2015 | 9 | 7 | 0 | 5 | 15-0059621 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 924229 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-07 00:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-08 08:19 | 42255.3465 | 37.4132 | -121.882 | Vegetation | Urban | < 3 meters | Fire Agency | MILPITAS FD | 100561024 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0585 | 2015 | 9 | 8 | 8 | 19 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-09-08 08:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-09 06:44 | 42256.2806 | 38.8269 | -123.0158 | Vegetation | Rural | < 3 meters | Fire Agency | CLOVERDALE FIRE | 102039036 |  | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0586 | 2015 | 9 | 9 | 6 | 44 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-09-09 06:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-09 10:47 | 42256.4493 | 37.1041 | -121.8853 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100520291 |  | 12000 | Conductor | Overhead | Yes | 42256.4493 | 2015-09-09 10:47 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0587 | 2015 | 9 | 9 | 10 | 47 | 15-0060074 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 142401 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-09 10:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-10 05:42 | 42257.2375 | 37.4609 | -121.8434 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100619766 | None | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0588 | 2015 | 9 | 10 | 5 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-09-10 05:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-10 16:24 | 42257.6833 | 38.5049 | -122.3535 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103159970 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42257.6833 | 2015-09-10 16:24 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0589 | 2015 | 9 | 10 | 16 | 24 | 15-0060610 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 130124 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-10 16:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-10 18:39 | 42257.7771 | 40.7569 | -123.7958 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 096/004 |  | 115000 | Conductor | Overhead | Yes | 42257.7771 | 2015-09-10 18:39 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0590 | 2015 | 9 | 10 | 18 | 39 | RM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-10 18:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-11 06:38 | 42258.2764 | 37.5232 | -122.2654 | Other | Urban | Structure Only | Fire Agency | sc |  |  | 12000 | Conductor | Overhead | Yes | 42258.2764 | 2015-09-11 06:38 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0591 | 2015 | 9 | 11 | 6 | 38 | 15-0060646 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 461108 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-11 06:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-11 08:15 | 42258.3438 | 38.1094 | -122.87 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102293992 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42258.3438 | 2015-09-11 08:15 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0592 | 2015 | 9 | 11 | 8 | 15 | 15-0060698 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 32419 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-11 08:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-11 17:28 | 42258.7278 | 37.7972 | -121.2747 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MANTECA/LATHROP FIRE DEPT | 102105463 | Verizon | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0593 | 2015 | 9 | 11 | 17 | 28 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-09-11 17:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-12 09:51 | 42259.4104 | 39.1164 | -121.0693 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | TOP OF AVALON PLACE, GRASS VALLEY TOWER NUMBER 19/152 40689729 |  | 115000 | Conductor | Overhead | Yes | 42259.4104 | 2015-09-12 09:51 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0594 | 2015 | 9 | 12 | 9 | 51 | VD-2015-079 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-12 09:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-12 11:09 | 42259.4646 | 38.603 | -120.6741 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101394996 |  | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0595 | 2015 | 9 | 12 | 11 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-09-12 11:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-12 11:36 | 42259.4833 | 35.3558 | -119.046 | Vegetation | Urban | < 3 meters | Fire Agency | Bakersfield FD | 100194486 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | no-match | 0596 | 2015 | 9 | 12 | 11 | 36 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-09-12 11:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-13 08:48 | 42260.3667 | 37.7245 | -121.3259 | Vegetation | Rural | < 3 meters | Fire Agency | TRACY FIRE DEPT | CRNR OF KASSON AND LORENZEN |  | 12000 | Conductor | Overhead | Yes | 42260.3667 | 2015-09-13 08:48 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0597 | 2015 | 9 | 13 | 8 | 48 | 15-0061074 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 23790 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-13 08:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-13 18:24 | 42260.7667 | 39.2673 | -121.8831 | Vegetation | Rural | < 0.25 Acres | Customer |  |  | None | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0598 | 2015 | 9 | 13 | 18 | 24 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-09-13 18:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-15 22:05 | 42262.9201 | 36.5874 | -119.5687 | Vegetation | Rural | < 0.25 Acres | Fire Agency | COUNTY FIRE | 100878350 | Pacific Bell | 0 – 750 | Conductor | Overhead | Yes | 42262.9201 | 2015-09-15 22:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0599 | 2015 | 9 | 15 | 22 | 5 | 15-0061618 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 72 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-15 22:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-16 00:18 | 42263.0125 | 37.9914 | -121.6682 | Vegetation | Rural | < 3 meters | Fire Agency | EAST COUNTY FIRE | 100457468 |  | 21000 | Conductor | Overhead | Yes | 42263.0125 | 2015-09-16 00:18 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0600 | 2015 | 9 | 16 | 0 | 18 | 15-0061626 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 44007 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-16 00:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-18 16:23 | 42265.6826 | 37.8691 | -121.2063 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FRENCH CAMP FIRE | IN CANAL AT 5027 FRENCH CAMP RD |  | 12000 | Conductor | Overhead | Yes | 42265.6826 | 2015-09-18 16:23 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0601 | 2015 | 9 | 18 | 16 | 23 | 15-0062194 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 408 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-18 16:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-18 17:05 | 42265.7118 | 37.8992 | -120.4551 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101019893 |  | 17000 | Conductor | Overhead | Yes | 42265.7118 | 2015-09-18 17:05 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0602 | 2015 | 9 | 18 | 17 | 5 | 15-0062207 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 35222 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-18 17:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-19 09:51 | 42266.4104 | 38.4755 | -122.9069 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FORESTVILLE | 103334444 |  | 12000 | Conductor | Overhead | Yes | 42266.4104 | 2015-09-19 09:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0603 | 2015 | 9 | 19 | 9 | 51 | 15-0062267 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 488 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-19 09:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-20 18:53 | 42267.7868 | 39.8638 | -121.6599 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42267.7868 | 2015-09-20 18:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0604 | 2015 | 9 | 20 | 18 | 53 | 15-0062407 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 3479 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-20 18:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-21 04:06 | 42268.1708 | 38.6587 | -121.0404 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 1of3@13833 |  | 21000 | Conductor | Overhead | Yes | 42268.1708 | 2015-09-21 04:06 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0605 | 2015 | 9 | 21 | 4 | 6 | 15-0062450 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | 162824 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-21 04:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-21 14:23 | 42268.5993 | 40.4786 | -123.771 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | mile marker 29.1, e of hairpin turn |  | 12000 | Conductor | Overhead | Yes | 42268.5993 | 2015-09-21 14:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0606 | 2015 | 9 | 21 | 14 | 23 | 15-0062556 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 13197 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-21 14:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-21 16:33 | 42268.6896 | 38.2452 | -122.0412 | Vegetation | Urban | < 0.25 Acres | Fire Agency | FAIRFIELD FIRE DEPT | REAR OF 900 TAFT |  | 12000 | Conductor | Overhead | Yes | 42268.6896 | 2015-09-21 16:33 | Contact From Object | N.A. | Balloons | Electric Facility | Unknown |  | Other/Unknown | 0607 | 2015 | 9 | 21 | 16 | 33 | 15-0062576 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 999493 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-21 16:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-22 00:44 | 42269.0306 | 39.0078 | -122.8938 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LAKEPORT FIRE | 102159765 |  | 12000 | Conductor | Overhead | Yes | 42269.0306 | 2015-09-22 00:44 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0608 | 2015 | 9 | 22 | 0 | 44 | 15-0062608 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 164896 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-22 00:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-22 15:55 | 42269.6632 | 39.1224 | -121.6392 | Vegetation | Urban | < 0.25 Acres | Fire Agency | YUBA CITY | 101300036 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42269.6632 | 2015-09-22 15:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0609 | 2015 | 9 | 22 | 15 | 55 | 15-0062773 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 57520 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-22 15:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-22 20:07 | 42269.8382 | 38.4779 | -121.9895 | Vegetation | Rural | < 0.25 Acres | Fire Agency | WINTERS? | 101577611 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42269.8382 | 2015-09-22 20:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0610 | 2015 | 9 | 22 | 20 | 7 | 15-0062807 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 6632 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-22 20:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-24 01:40 | 42271.0694 | 37.9936 | -122.3337 | Vegetation | Urban | < 0.25 Acres | Unknown |  | 101426065 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42271.0694 | 2015-09-24 01:40 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0611 | 2015 | 9 | 24 | 1 | 40 | 15-0063006 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 160539 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-24 01:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-24 03:58 | 42271.1653 | 39.9203 | -122.3859 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103132877 |  | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0612 | 2015 | 9 | 24 | 3 | 58 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-09-24 03:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-24 04:30 | 42271.1875 | 38.6769 | -123.314 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Str. 041/007 |  | 60000 | Conductor | Overhead | Yes | 42271.1875 | 2015-09-24 04:30 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0613 | 2015 | 9 | 24 | 4 | 30 | FU-2015-057 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 22680 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-24 04:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-24 13:56 | 42271.5806 | 39.3508 | -121.2454 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 9692 Rices-Texas Hill rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42271.5806 | 2015-09-24 13:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0614 | 2015 | 9 | 24 | 13 | 56 | 15-0063159 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 51917 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-24 13:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-25 13:31 | 42272.5632 | 37.261 | -120.7311 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 2 POLES EAST OF MTR#1009626581 |  | 12000 | Conductor | Overhead | Yes | 42272.5632 | 2015-09-25 13:31 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | Other/Unknown | 0615 | 2015 | 9 | 25 | 13 | 31 | 15-0063629 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6784 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-25 13:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-25 17:28 | 42272.7278 | 38.7169 | -120.7693 | Vegetation | Rural | < 0.25 Acres | Fire Agency | el dorado F D | 101405928 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42272.7278 | 2015-09-25 17:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0616 | 2015 | 9 | 25 | 17 | 28 | 15-0063666 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 111180 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-25 17:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-26 14:24 | 42273.6 | 37.986 | -121.2301 | Vegetation | Rural | < 0.25 Acres | Fire Agency | waterloo/morada | 102135315 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0617 | 2015 | 9 | 26 | 14 | 24 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-09-26 14:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-28 04:42 | 42275.1958 | 38.7877 | -121.2083 | Vegetation | Urban | < 3 meters | Fire Agency | n/a | 100058887 | Pacific Bell | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0618 | 2015 | 9 | 28 | 4 | 42 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-09-28 04:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-28 09:42 | 42275.4042 | 37.9623 | -122.1765 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100458692 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42275.4042 | 2015-09-28 09:42 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0619 | 2015 | 9 | 28 | 9 | 42 | 15-0066062 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 2125 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-28 09:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-28 18:10 | 42275.7569 | 38.135 | -122.477 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 1 mile north of 37 on lakeville |  | 12000 | Conductor | Overhead | Yes | 42275.7569 | 2015-09-28 18:10 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0620 | 2015 | 9 | 28 | 18 | 10 | 15-0066175 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 49410 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-28 18:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-29 02:52 | 42276.1194 | 38.337 | -121.8601 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | VACAVILLE FD | FRY RD @ CLARK |  | 21000 | Conductor | Overhead | Yes | 42276.1194 | 2015-09-29 02:52 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0621 | 2015 | 9 | 29 | 2 | 52 | 15-0066199 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 54144 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-29 02:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-29 19:05 | 42276.7951 | 35.4198 | -118.9499 | Vegetation | Urban | < 0.25 Acres | Fire Agency | KERN COUNTY FIRE DEPARTMENT | 100193545 |  | 12000 | Conductor | Overhead | Yes | 42276.7951 | 2015-09-29 19:05 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | Other/Unknown | 0622 | 2015 | 9 | 29 | 19 | 5 | 15-0066487 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6124 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-29 19:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-29 19:46 | 42276.8236 | 37.9779 | -121.7195 | Vegetation | Urban | < 0.25 Acres | Fire Agency | OAKLEY FIRE DEPARTMENT | 100470700 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0623 | 2015 | 9 | 29 | 19 | 46 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-09-29 19:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-30 16:41 | 42277.6951 | 37.3542 | -122.1592 | Vegetation | Rural | < 3 meters | Utility: PG&E |  | 100520776 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42277.6951 | 2015-09-30 16:41 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0624 | 2015 | 9 | 30 | 16 | 41 | 15-0066923 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 12718 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-30 16:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-30 17:25 | 42277.7257 | 38.5747 | -120.682 | Vegetation | Rural | < 0.25 Acres | Fire Agency | el dorado county | 7901 shenandoah ln |  | 21000 | Conductor | Overhead | Yes | 42277.7257 | 2015-09-30 17:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0625 | 2015 | 9 | 30 | 17 | 25 | 15-0066934 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 28912 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-30 17:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-09-30 19:38 | 42277.8181 | 39.2188 | -122.2464 | Vegetation | Rural | < 0.25 Acres | Fire Agency | willams fire demp | 101641855 | None | 12000 | Conductor | Overhead | Yes | 42277.8181 | 2015-09-30 19:38 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0626 | 2015 | 9 | 30 | 19 | 38 | 15-0066941 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 31194 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-30 19:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-01 02:43 | 42278.1132 | 39.6666 | -121.7742 | Vegetation | Rural | < 3 meters | Fire Agency | NOT KNOWN-GONE ON ARRIVAL | 100345398 | Pacific Bell | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0627 | 2015 | 10 | 1 | 2 | 43 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-10-01 02:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-01 11:28 | 42278.4778 | 37.5088 | -120.3446 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Pole 019/007 |  | 70000 | Conductor | Overhead | Yes | 42278.4778 | 2015-10-01 11:28 | Contamination | N.A. | N.A. | N.A. | Weather |  | no-match | 0628 | 2015 | 10 | 1 | 11 | 28 | LB-2015-038 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 0 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-01 11:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-01 13:13 | 42278.5507 | 37.6291 | -122.1153 | Vegetation | Rural | < 0.25 Acres | Fire Agency | HAYWARD | X ST FROM 25920 EDEN LANDING RD |  | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0629 | 2015 | 10 | 1 | 13 | 13 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-10-01 13:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-02 19:16 | 42279.8028 | 36.9454 | -119.8302 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101121403 | None | 21000 | Conductor | Overhead | Yes | 42279.8028 | 2015-10-02 19:16 | Contact From Object | N.A. | Other | Electric Facility | Human Error | Kite on line | Other/Unknown | 0630 | 2015 | 10 | 2 | 19 | 16 | 15-0067533 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 69317 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-02 19:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-03 07:27 | 42280.3104 | 39.0633 | -122.6237 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 2323 new long valley rd | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0631 | 2015 | 10 | 3 | 7 | 27 | No ILIS or TOTL available | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-10-03 07:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-03 21:11 | 42280.8826 | 39.7358 | -121.6855 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | honey run rd at cutouts 16015 |  | 12000 | Conductor | Overhead | Yes | 42280.8826 | 2015-10-03 21:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0632 | 2015 | 10 | 3 | 21 | 11 | 15-0067708 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 10499 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-03 21:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-03 22:51 | 42280.9521 | 39.1158 | -122.8879 | Vegetation | Rural | < 0.25 Acres | Fire Agency | north shore fire department, | 102164828 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42280.9521 | 2015-10-03 22:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0633 | 2015 | 10 | 3 | 22 | 51 | 15-0067693 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 61335 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-03 22:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-04 01:03 | 42281.0437 | 39.7923 | -121.5803 | Vegetation | Urban | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42281.0437 | 2015-10-04 01:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0634 | 2015 | 10 | 4 | 1 | 3 | 15-0067711 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2697 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-04 01:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-04 01:32 | 42281.0639 | 39.2279 | -121.3774 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | in field at 6275 sandstonel ln |  | 12000 | Conductor | Overhead | Yes | 42281.0639 | 2015-10-04 01:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0635 | 2015 | 10 | 4 | 1 | 32 | 15-0067743 | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 4021 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-04 01:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-04 08:26 | 42281.3514 | 38.8127 | -121.2046 | Vegetation | Urban | < 3 meters | Fire Agency | LOOMIS FIRE | C-126 TAYLOR RD AND SIERRA COLLEGE |  | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0636 | 2015 | 10 | 4 | 8 | 26 | No ILIS or TOTL available | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-10-04 08:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-04 14:35 | 42281.6076 | 39.4704 | -121.6887 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | NORTH SIDE OF HWY 162, 1500' EAST OF RICETON HWY |  | 12000 | Lightning Arrestor | Overhead | Yes | 42281.6076 | 2015-10-04 14:35 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | Other/Unknown | 0637 | 2015 | 10 | 4 | 14 | 35 | 15-0067833 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 15669 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-04 14:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-04 17:42 | 42281.7375 | 39.1165 | -122.8951 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | robin hll |  | 12000 | Conductor | Overhead | Yes | 42281.7375 | 2015-10-04 17:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0638 | 2015 | 10 | 4 | 17 | 42 | 15-0067856 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 54392 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-04 17:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-06 18:48 | 42283.7833 | 40.5106 | -122.2241 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  | 101468974 | Frontier | 12000 | Conductor | Overhead | Yes | 42283.7833 | 2015-10-06 18:48 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0639 | 2015 | 10 | 6 | 18 | 48 | 15-0068454 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 22417 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-06 18:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-07 15:04 | 42284.6277 | 35.3079 | -120.8328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101924901 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42284.6277 | 2015-10-07 15:04 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0640 | 2015 | 10 | 7 | 15 | 3 | 15-0068730 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 77896 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-07 15:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-08 13:47 | 42285.5743 | 35.5473 | -120.7701 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | DEERFIELD RD S/O HIDDEN VALEY RD. |  | 21000 | Conductor | Overhead | Yes | 42285.5743 | 2015-10-08 13:47 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0641 | 2015 | 10 | 8 | 13 | 47 | 15-0069017 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10899 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-08 13:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-09 06:32 | 42286.2722 | 38.364 | -122.9173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 320 Freestone St, Frestone | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0642 | 2015 | 10 | 9 | 6 | 32 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-10-09 06:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-09 19:03 | 42286.7937 | 38.3856 | -122.5303 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101988271 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42286.7937 | 2015-10-09 19:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0643 | 2015 | 10 | 9 | 19 | 3 | 15-0069325 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 868 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-09 19:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-09 22:16 | 42286.9278 | 37.5908 | -122.3502 | Vegetation | Urban | < 3 meters | Fire Agency | central county fire, engine 34 | at base of pole c0708 |  | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0644 | 2015 | 10 | 9 | 22 | 16 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-10-09 22:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-10 00:20 | 42287.0139 | 40.8862 | -124.0883 | Building | Urban | Structure Only | Fire Agency | CAL FIRE | 100966524 | Pacific Bell | 0 – 750 | Conductor | Overhead | Yes | 42287.0139 | 2015-10-10 00:20 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0645 | 2015 | 10 | 10 | 0 | 20 | 15-0069353 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 11590 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-10 00:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-12 09:13 | 42289.384 | 38.2919 | -122.2706 | Vegetation | Urban | < 3 meters | Customer |  | 1111 Terrace Drive, Napa |  | 0 – 750 | Conductor | Overhead | Yes | 42289.384 | 2015-10-12 09:13 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0646 | 2015 | 10 | 12 | 9 | 13 | 15-0069574 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-10-12 09:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-12 15:16 | 42289.6361 | 38.9021 | -121.3011 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 1800 HWY 65 LINCOLN | None | 21000 | Conductor | Overhead | Yes | 42289.6361 | 2015-10-12 15:16 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0647 | 2015 | 10 | 12 | 15 | 16 | 15-0069723 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 669 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-12 15:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-12 17:25 | 42289.7257 | 36.7074 | -121.3282 | Vegetation | Rural | 300 - 999 Acres | Fire Agency | CAL FIRE | Cienega Road X Limekiln Road, San Benito Co. |  | 21000 | Conductor | Overhead | Yes | 2015-10-12 17:25 | 2015-10-12 17:25 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0648 | 2015 | 10 | 12 | 17 | 25 | 15-0069756 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | Equip Failure | #REF! | 2328 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-12 17:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-13 14:38 | 42290.6097 | 37.7935 | -120.9284 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Escalon Fire | 102335307 | None | 17000 | Conductor | Overhead | Yes | 42290.6097 | 2015-10-13 14:38 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0649 | 2015 | 10 | 13 | 14 | 38 | 15-0070003 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 148700 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-13 14:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-13 18:32 | 42290.7722 | 37.7421 | -121.9439 | Building | Urban | Structure Only | Fire Agency | SAN RAMON FD | 100902269 | None | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0650 | 2015 | 10 | 13 | 18 | 32 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-10-13 18:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-14 14:17 | 42291.5951 | 37.333 | -120.5057 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 3537 N HWY 59 MERCED |  | 0 – 750 | Conductor | Overhead | Yes | 42291.5951 | 2015-10-14 14:17 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0651 | 2015 | 10 | 14 | 14 | 17 | 15-0070304 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 582 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-14 14:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-15 18:51 | 42292.7854 | 36.5082 | -119.7908 | Building | Rural | Structure Only | Fire Agency | FRESNO COUNTY | 100803812 |  | 12000 | Conductor | Overhead | Yes | 42292.7854 | 2015-10-15 18:51 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 0652 | 2015 | 10 | 15 | 18 | 51 | 15-0070808 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 40479 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-15 18:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-16 09:43 | 42293.4049 | 39.187 | -123.2015 | Vegetation | Rural | < 3 meters | Unknown |  | 102196855 |  | 12000 | Conductor | Overhead | Yes | 42293.4049 | 2015-10-16 09:43 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0653 | 2015 | 10 | 16 | 9 | 43 | 15-0070948 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 65228 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-16 09:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-17 07:04 | 42294.2944 | 37.6574 | -121.6197 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 13900 TESLA RD LIVERMORE |  | 12000 | Conductor | Overhead | Yes | 42294.2944 | 2015-10-17 07:04 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0654 | 2015 | 10 | 17 | 7 | 4 | 15-0071191 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 30728 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-17 07:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-18 20:06 | 42295.8375 | 37.5514 | -122.2928 | Vegetation | Urban | < 3 meters | Fire Agency | SAN MATEO |  |  | 12000 | Conductor | Overhead | Yes | 42295.8375 | 2015-10-18 20:06 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0655 | 2015 | 10 | 18 | 20 | 6 | 15-0071561 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 136854 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-18 20:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-20 05:59 | 42297.2493 | 38.7571 | -121.2079 | Vegetation | Rural | < 0.25 Acres | Fire Agency | South Placer fire dist | 5062 Whisper Way |  | 12000 | Conductor | Overhead | Yes | 42297.2493 | 2015-10-20 05:59 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0656 | 2015 | 10 | 20 | 5 | 59 | 15-0072051 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1206 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-20 05:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-25 05:50 | 42302.2431 | 37.7843 | -121.7683 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | cutouts 9504 |  | 21000 | Conductor | Overhead | Yes | 42302.2431 | 2015-10-25 05:50 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0657 | 2015 | 10 | 25 | 5 | 50 | 15-0073203 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 10710 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-25 05:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-27 16:15 | 42304.6771 | 38.6154 | -121.0586 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal FIRE | 101375211 | Pacific Bell | 0 – 750 | Transformer | Overhead | Yes | 42304.6771 | 2015-10-27 16:15 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0658 | 2015 | 10 | 27 | 16 | 15 | 15-0073716 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-10-27 16:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-27 19:27 | 42304.8104 | 39.0729 | -121.6899 | Vegetation | Rural | < 3 meters | Fire Agency | sutter county | 101329222 |  | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0659 | 2015 | 10 | 27 | 19 | 27 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-10-27 19:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-28 01:05 | 42305.0451 | 37.6398 | -122.1155 | Vegetation | Urban | < 3 meters | Fire Agency | Hayward Fire Dept | 100928934 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0660 | 2015 | 10 | 28 | 1 | 5 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-10-28 01:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-30 04:29 | 42307.1868 | 39.5059 | -123.7672 | Vegetation | Rural | < 3 meters | Fire Agency | local fire | in field next to hwy / 1 span SS of Fuse 4617 |  | 12000 | Conductor | Overhead | Yes | 42307.1868 | 2015-10-30 04:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0661 | 2015 | 10 | 30 | 4 | 29 | 15-0074188 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 273183 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-30 04:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-30 17:13 | 42307.7174 | 38.3166 | -120.7226 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 7600 HWY 49, Jackson | None | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0662 | 2015 | 10 | 30 | 17 | 13 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-10-30 17:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-31 07:45 | 42308.3229 | 38.1157 | -120.8931 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal FIRE | 103763040 |  | 12000 | Conductor | Overhead | Yes | 42308.3229 | 2015-10-31 07:45 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0663 | 2015 | 10 | 31 | 7 | 45 | 15-0074424 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 314565 | 0 | NA | <25mph | <15mph | #REF! | 2015-10-31 07:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-10-31 19:11 | 42308.7993 | 37.3698 | -120.7234 | Vegetation | Urban | < 3 meters | Fire Agency | CAL FIRE | 5686 LINCOLN BLVD LIVINGSTON |  | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0664 | 2015 | 10 | 31 | 19 | 11 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-10-31 19:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-11-01 04:22 | 42309.1819 | 40.4391 | -122.3977 | Vegetation | Rural | < 0.25 Acres | Fire Agency | HAPPY VALLEY FIRE FIRST RESPONDER, | 101490990 | TDS HAPPY VALLEY | 12000 | Conductor | Overhead | Yes | 42309.1819 | 2015-11-01 04:22 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0665 | 2015 | 11 | 1 | 4 | 22 | 15-0074508 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 48911 | 0 | NA | <25mph | <15mph | #REF! | 2015-11-01 04:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-11-02 09:53 | 42310.4118 | 36.7778 | -119.9312 | Building | Rural | Structure Only | Fire Agency | FRESNO COUNTY FIRE | 7777 W SHIELDS |  | 12000 | Conductor | Overhead | Yes | 42310.4118 | 2015-11-02 09:53 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0666 | 2015 | 11 | 2 | 9 | 53 | 15-0074805 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 14175 | 0 | NA | <25mph | <15mph | #REF! | 2015-11-02 09:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-11-04 17:30 | 42312.7292 | 36.8215 | -120.5081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FRESNO COUNTY FD | SMART METER RELAY # 16704 |  | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0667 | 2015 | 11 | 4 | 17 | 30 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-11-04 17:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-11-04 19:21 | 42312.8063 | 37.5524 | -122.3304 | Vegetation | Urban | < 3 meters | Fire Agency | smfd | 103376789 |  | 4000 | Conductor | Overhead | Yes | 42312.8063 | 2015-11-04 19:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0668 | 2015 | 11 | 4 | 19 | 21 | 15-0075662 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 22986 | 0 | NA | <25mph | <15mph | #REF! | 2015-11-04 19:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-11-05 10:39 | 42313.4437 | 36.4092 | -119.797 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FRESNO COUNTY | 100871818 |  | 12000 | Conductor | Overhead | Yes | 42313.4437 | 2015-11-05 10:39 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0669 | 2015 | 11 | 5 | 10 | 39 | 15-0075816 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 1108 | 0 | NA | <25mph | <15mph | #REF! | 2015-11-05 10:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-11-05 12:11 | 42313.5076 | 35.3755 | -118.9463 | Vegetation | Urban | < 3 meters | Fire Agency | CITY | 100254768 | Pacific Bell | 0 – 750 | Conductor | Overhead | Yes | 42313.5076 | 2015-11-05 12:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0670 | 2015 | 11 | 5 | 12 | 11 | 15-0075858 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 10272 | 0 | NA | <25mph | <15mph | #REF! | 2015-11-05 12:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-11-07 01:15 | 42315.0521 | 37.7153 | -122.0647 | Vegetation | Urban | < 3 meters | Customer |  | 100909751 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0671 | 2015 | 11 | 7 | 1 | 15 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-11-07 01:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-11-07 10:16 | 42315.4278 | 39.1054 | -121.5607 | Vegetation | Rural | < 0.25 Acres | Fire Agency | OLIVEHURST | 101319679 |  | 12000 | Conductor | Overhead | Yes | 42315.4278 | 2015-11-07 10:16 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0672 | 2015 | 11 | 7 | 10 | 16 | 15-0076332 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 28612 | 0 | NA | <25mph | <15mph | #REF! | 2015-11-07 10:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-11-09 05:55 | 42317.2465 | 34.9984 | -120.3634 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42317.2465 | 2015-11-09 05:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0673 | 2015 | 11 | 9 | 5 | 55 | 15-0076534 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 205393 | 0 | NA | <25mph | <15mph | #REF! | 2015-11-09 05:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-11-13 12:03 | 42321.5021 | 40.5923 | -124.14 | Vegetation | Urban | < 3 meters | Fire Agency | CITY | 100993131 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42321.5021 | 2015-11-13 12:03 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0674 | 2015 | 11 | 13 | 12 | 3 | 15-0077620 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 88992 | 0 | NA | <25mph | <15mph | #REF! | 2015-11-13 12:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-11-15 13:47 | 42323.5743 | 37.2494 | -121.9134 | Other | Urban | Structure Only | Fire Agency |  | 4879 Harwood Road, San Jose | None | 12000 | Conductor | Overhead | Yes | 42323.5743 | 2015-11-15 13:47 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0675 | 2015 | 11 | 15 | 13 | 47 | 15-0077919 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 231394 | 0 | NA | <25mph | <15mph | #REF! | 2015-11-15 13:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-11-15 16:30 | 42323.6875 | 37.0007 | -121.885 | Vegetation | Rural | < 3 meters | Customer |  | 101691004 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42323.6875 | 2015-11-15 16:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0676 | 2015 | 11 | 15 | 16 | 30 | 15-0077978 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 25920 | 0 | NA | <25mph | <15mph | #REF! | 2015-11-15 16:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-11-21 10:36 | 42329.4417 | 38.0679 | -120.1872 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101045952 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42329.4417 | 2015-11-21 10:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0677 | 2015 | 11 | 21 | 10 | 36 | 15-0079868 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18350 | 0 | NA | <25mph | <15mph | #REF! | 2015-11-21 10:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-11-26 15:32 | 42334.6472 | 38.4876 | -122.0021 | Vegetation | Rural | < 3 meters | Customer |  | 101648676 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42334.6472 | 2015-11-26 15:32 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0678 | 2015 | 11 | 26 | 15 | 32 | 15-0081290 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 2540 | 0 | NA | <25mph | <15mph | #REF! | 2015-11-26 15:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-12-01 09:26 | 42339.3931 | 39.6315 | -121.9302 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | ORD FERRY RD WEST OF 126147 |  | 12000 | Conductor | Overhead | Yes | 42339.3931 | 2015-12-01 09:26 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0679 | 2015 | 12 | 1 | 9 | 26 | 15-0081935 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 10594 | 0 | NA | <25mph | <15mph | #REF! | 2015-12-01 09:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-12-01 12:03 | 42339.5021 | 35.6744 | -120.9932 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal FIRE | 101860660 |  | 21000 | Conductor | Overhead | Yes | 42339.5021 | 2015-12-01 12:03 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0680 | 2015 | 12 | 1 | 12 | 3 | 15-0081983 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 42427 | 0 | NA | <25mph | <15mph | #REF! | 2015-12-01 12:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-12-02 09:40 | 42340.4028 | 39.1743 | -122.1603 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Lr 30332 |  | 12000 | Conductor | Overhead | Yes | 42340.4028 | 2015-12-02 09:40 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0681 | 2015 | 12 | 2 | 9 | 40 | 15-0082983 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2015-12-02 09:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-12-03 09:12 | 42341.3833 | 37.3044 | -122.0202 | Vegetation | Urban | Structure Only | Fire Agency | san jose fire dept | 100522714 | Pacific Bell | 0 – 750 | Conductor | Overhead | Yes | 42341.3833 | 2015-12-03 09:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0682 | 2015 | 12 | 3 | 9 | 12 | 15-0082471 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 5590 | 0 | NA | <25mph | <15mph | #REF! | 2015-12-03 09:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-12-03 12:10 | 42341.5069 | 40.0277 | -120.9652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | usfs | spanish creek campground |  | 12000 | Conductor | Overhead | Yes | 42341.5069 | 2015-12-03 12:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0683 | 2015 | 12 | 3 | 12 | 10 | 15-0082505 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 196854 | 0 | NA | <25mph | <15mph | #REF! | 2015-12-03 12:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-12-08 12:41 | 42346.5285 | 38.2489 | -120.5228 | Other | Rural | Structure Only | Unknown |  | 7026 Railroad Flat Road, Mountain Ranch |  | 12000 | Conductor | Overhead | Yes | 42346.5285 | 2015-12-08 12:41 | Contact From Object | N.A. | Other | Electric Facility | Human Error | AT&T work error | Other/Unknown | 0684 | 2015 | 12 | 8 | 12 | 41 | 15-0083435 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1120 | 0 | NA | <25mph | <15mph | #REF! | 2015-12-08 12:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-12-10 11:19 | 42348.4715 | 36.2183 | -119.9951 | Other | Rural | Structure Only | Fire Agency | CAL FIRE | 100694631 |  | 12000 | Conductor | Overhead | Yes | 42348.4715 | 2015-12-10 11:19 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0685 | 2015 | 12 | 10 | 11 | 19 | 15-0083962 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 2528 | 0 | NA | <25mph | <15mph | #REF! | 2015-12-10 11:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-12-11 07:27 | 42349.3104 | 34.8788 | -120.3308 | Vegetation | Rural | < 3 meters | Customer |  | 4 POLES LOAD SIDE OF SW 7807 |  | 12000 | Conductor | Overhead | Yes | 42349.3104 | 2015-12-11 07:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0686 | 2015 | 12 | 11 | 7 | 27 | 15-0084199 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 35942 | 0 | NA | <25mph | <15mph | #REF! | 2015-12-11 07:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-12-22 02:44 | 42360.1139 | 38.2767 | -122.5036 | Building | Rural | Structure Only | Fire Agency | sonoma | 102005111 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42360.1139 | 2015-12-22 02:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0687 | 2015 | 12 | 22 | 2 | 44 | 15-0086634 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 42700 | 0 | NA | <25mph | <15mph | #REF! | 2015-12-22 02:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-12-28 19:29 | 42366.8118 | 34.9679 | -120.4529 | Vegetation | Urban | < 3 meters | Fire Agency | SANTA MARIA FIRE DEPT. | 103158996 |  | 12000 | Conductor | Overhead | Yes | 42366.8118 | 2015-12-28 19:29 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0688 | 2015 | 12 | 28 | 19 | 29 | 15-0087677 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 202827 | 0 | NA | <25mph | <15mph | #REF! | 2015-12-28 19:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2015-12-31 19:12 | 42369.8 | 37.1568 | -121.9868 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LOS GATOS MONTE SERENO SARATOGA | 100518215 | Verizon | 21000 | Conductor | Overhead | Yes | 42369.8 | 2015-12-31 19:12 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0689 | 2015 | 12 | 31 | 19 | 12 | 15-0087962 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 7979 | 0 | NA | <25mph | <15mph | #REF! | 2015-12-31 19:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-01-21 21:32 | 42390.8972 | 40.553 | -124.1116 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100994021 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42390.8972 | 2016-01-21 21:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0690 | 2016 | 1 | 21 | 21 | 32 | 16-0007239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 6468 | 0 | NA | <25mph | <15mph | #REF! | 2016-01-21 21:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-01-23 15:41 | 42392.6535 | 39.9486 | -122.3728 | Vegetation | RURAL | < 0.25 Acres | Self Extinguished | N.A. | 101524077 |  | 12000 | Conductor | Overhead | Yes | 42392.6535 | 2016-01-23 15:41 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0691 | 2016 | 1 | 23 | 15 | 41 | 16-0007778 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 133520 | 0 | NA | <25mph | <15mph | #REF! | 2016-01-23 15:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-02-02 06:01 | 42402.2507 | 37.7755 | -122.4411 | Building | URBAN | Structure Only | Fire Agency | SFFD | 101817610 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42402.2507 | 2016-02-02 06:01 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | no-match | 0692 | 2016 | 2 | 2 | 6 | 1 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-02-02 06:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-02-05 20:50 | 42405.8681 | 40.0156 | -122.4333 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | TEHAMA COUNTY & LOCAL VOLUNTEER | 101529688 | None | 12000 | Conductor | Overhead | Yes | 42405.8681 | 2016-02-05 20:50 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0693 | 2016 | 2 | 5 | 20 | 50 | 16-0011034 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 11424 | 0 | NA | <25mph | <15mph | #REF! | 2016-02-05 20:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-02-08 03:55 | 42408.1632 | 39.7852 | -121.5056 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100337507 |  | 12000 | Conductor | Overhead | Yes | 42408.1632 | 2016-02-08 03:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0694 | 2016 | 2 | 8 | 3 | 55 | 16-0011201 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 87046 | 0 | NA | <25mph | <15mph | #REF! | 2016-02-08 03:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-02-17 21:16 | 42417.8861 | 40.6677 | -124.2273 | Building | RURAL | Structure Only | Fire Agency | Cal Fire | 101002728 |  | 0 – 750 | Conductor | Overhead | Yes | 42417.8861 | 2016-02-17 21:16 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 0695 | 2016 | 2 | 17 | 21 | 16 | 16-0013542 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 1336 | 0 | NA | <25mph | <15mph | #REF! | 2016-02-17 21:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-02-26 15:40 | 42426.6528 | 36.8396 | -119.7975 | Building | URBAN | Structure Only | Self Extinguished | N.A. | 100640781 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42426.6528 | 2016-02-26 15:40 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0696 | 2016 | 2 | 26 | 15 | 40 | 16-0015914 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 14883 | 0 | NA | <25mph | <15mph | #REF! | 2016-02-26 15:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-03-28 12:16 | 42457.5111 | 39.7428 | -121.8202 | Vegetation | URBAN | < 3 meters | Fire Agency | Chico FD | 100338028 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42457.5111 | 2016-03-28 12:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0697 | 2016 | 3 | 28 | 12 | 16 | 16-0024413 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 71190 | 0 | NA | <25mph | <15mph | #REF! | 2016-03-28 12:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-01 04:25 | 42461.184 | 35.0164 | -118.8921 | Vegetation | RURAL | < 3 meters | Fire Agency | Kern County FD | 100194594 | None | 12000 | Other | Overhead | Yes | 42461.184 | 2016-04-01 04:25 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0698 | 2016 | 4 | 1 | 4 | 25 | 16-0025465 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 24025 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-01 04:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-02 03:48 | 42462.1583 | 35.3703 | -118.9752 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | KCFD | 100244829 |  | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0699 | 2016 | 4 | 2 | 3 | 48 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-04-02 03:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-02 07:06 | 42462.2958 | 35.0307 | -120.5279 | Vegetation | RURAL | < 3 meters | Fire Agency | SAN LUIS CO FIRE | 101892796 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42462.2958 | 2016-04-02 07:06 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0700 | 2016 | 4 | 2 | 7 | 6 | 16-0025694 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 75976 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-02 07:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-03 06:54 | 42463.2875 | 40.4175 | -122.2109 | Other | RURAL | Structure Only | Fire Agency | COTTONWOOD FIRE DEPT | 101488627 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42463.2875 | 2016-04-03 06:54 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0701 | 2016 | 4 | 3 | 6 | 54 | 16-0025760 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 33084 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-03 06:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-03 12:01 | 42463.5007 | 38.6804 | -123.125 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101968191 |  | 12000 | Conductor | Overhead | Yes | 42463.5007 | 2016-04-03 12:01 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0702 | 2016 | 4 | 3 | 12 | 1 | 16-0025794 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 3528 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-03 12:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-04 00:08 | 42464.0056 | 37.7567 | -121.4193 | Vegetation | URBAN | < 3 meters | Fire Agency | Tracy FD | 102119421 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42464.0056 | 2016-04-04 00:08 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0703 | 2016 | 4 | 4 | 0 | 8 | 16-0025844 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 150033 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-04 00:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-07 17:07 | 42467.7132 | 35.342 | -119.0175 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Bakersfield FD | 100245953 |  | 0 – 750 | Conductor | Overhead | Yes | 42467.7132 | 2016-04-07 17:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0704 | 2016 | 4 | 7 | 17 | 7 | 16-0026980 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 10253 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-07 17:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-08 13:14 | 42468.5514 | 39.0429 | -121.1002 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100086751 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42468.5514 | 2016-04-08 13:14 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0705 | 2016 | 4 | 8 | 13 | 14 | 16-0027237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 11817 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-08 13:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-13 19:28 | 42473.8111 | 40.4954 | -124.1219 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103659313 |  | 12000 | Conductor | Overhead | Yes | 42473.8111 | 2016-04-13 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0706 | 2016 | 4 | 13 | 19 | 28 | 16-0028421 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 688 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-13 19:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-14 14:16 | 42474.5944 | 36.1584 | -119.565 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Kings County FD | 100766367 |  | 12000 | Other | Overhead | Yes | 42474.5944 | 2016-04-14 14:16 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0707 | 2016 | 4 | 14 | 14 | 16 | 16-0028680 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1632 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-14 14:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-18 18:14 | 42478.7597 | 37.7938 | -120.9842 | Vegetation | URBAN | < 3 meters | Fire Agency | Escalon Fire | 102332958 | None | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0708 | 2016 | 4 | 18 | 18 | 14 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-04-18 18:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-20 16:39 | 42480.6937 | 39.4024 | -122.0141 | Vegetation | RURAL | < 3 meters | Unknown | Unknown | 101641171 |  | 12000 | Conductor | Overhead | Yes | 42480.6937 | 2016-04-20 16:39 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0709 | 2016 | 4 | 20 | 16 | 39 | 16-0030087 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 26283 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-20 16:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-21 03:20 | 42481.1389 | 38.1907 | -122.2472 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | American Canyon FD | 102295263 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42481.1389 | 2016-04-21 03:20 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0710 | 2016 | 4 | 21 | 3 | 20 | 16-0030121 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 13969 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-21 03:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-21 09:25 | 42481.3924 | 39.293 | -123.769 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 103312287 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0711 | 2016 | 4 | 21 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-04-21 09:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-22 17:10 | 42482.7153 | 37.8875 | -121.6965 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Brentwood FD | 100506567 | None | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0712 | 2016 | 4 | 22 | 17 | 10 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-04-22 17:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-22 22:02 | 42482.9181 | 35.3492 | -119.0537 | Vegetation | URBAN | < 3 meters | Customer | N.A. | 100156969 | Yes | 0 – 750 | Conductor | Overhead | Yes | 42482.9181 | 2016-04-22 22:02 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, 4-12ft) | 0713 | 2016 | 4 | 22 | 22 | 2 | 16-0030861 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, 4-12ft) | 1912 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-22 22:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-23 18:32 | 42483.7722 | 36.4906 | -119.6292 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | city of selma | 100818205 |  | 12000 | Conductor | Overhead | Yes | 42483.7722 | 2016-04-23 18:32 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0714 | 2016 | 4 | 23 | 18 | 32 | 16-0030960 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 111253 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-23 18:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-24 11:10 | 42484.4653 | 34.709 | -120.4612 | Vegetation | URBAN | .26 - 9.99 Acres | Fire Agency | Santa Barbara County FD | 101898989 |  | 12000 | Conductor | Overhead | Yes | 42484.4653 | 2016-04-24 11:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0715 | 2016 | 4 | 24 | 11 | 10 | 16-0031023 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 154288 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-24 11:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-25 12:34 | 42485.5236 | 36.4761 | -119.7904 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100875278 |  | 12000 | Conductor | Overhead | Yes | 42485.5236 | 2016-04-25 12:34 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0716 | 2016 | 4 | 25 | 12 | 34 | 16-0031324 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4169 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-25 12:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-25 14:50 | 42485.6181 | 35.5444 | -119.0869 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Kern County FD | 100207184 | None | 12000 | Conductor | Overhead | Yes | 42485.6181 | 2016-04-25 14:50 | Other | N.A. | N.A. | N.A. | Human Error |  | Other/Unknown | 0717 | 2016 | 4 | 25 | 14 | 50 | 16-0031366 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-04-25 14:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-27 14:02 | 42487.5847 | 36.5161 | -119.2597 | Vegetation | RURAL | < 3 meters | Unknown | Unknown | 100755216 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42487.5847 | 2016-04-27 14:02 | Contact From Object | N.A. | Other | Electric Facility | Unknown | bird nest | Other/Unknown | 0718 | 2016 | 4 | 27 | 14 | 2 | 16-0032003 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 276 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-27 14:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-30 | 17:59 | 38.3142 | -120.9015 | Vegetation | RURAL | < 3 meters | Fire Agency | Kern County FD |  |  | 12000 | Conductor | Overhead | Yes | 42490 | 0.74931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0719 | 2016 | 4 | 30 | 17 | 59 | 16-0032910 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 722 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-30 17:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-30 | 42490.6944 | 37.0066 | -120.6378 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Merced County FD | 103083239 |  | 12000 | Conductor | Overhead | Yes | 42490 | 2016-04-30 16:40 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0720 | 2016 | 4 | 30 | 16 | 40 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-04-30 16:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-04-30 13:41 | 42490.5701 | 38.2588 | -122.0255 | Vegetation | URBAN | < 3 meters | Fire Agency | Fairfield FD | 101560133 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42490.5701 | 2016-04-30 13:41 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0721 | 2016 | 4 | 30 | 13 | 41 | 16-0032869 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 2145 | 0 | NA | <25mph | <15mph | #REF! | 2016-04-30 13:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-02 10:05 | 42492.4201 | 37.9148 | -120.6178 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101283625 | CALAVERAS TELEPHONE | 17000 | Conductor | Overhead | Yes | 42492.4201 | 2016-05-02 10:05 | Contact From Object | N.A. | Other | Electric Facility | Unknown | bird dropped snake | Other/Unknown | 0722 | 2016 | 5 | 2 | 10 | 5 | 16-0033214 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 31898 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-02 10:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-09 17:05 | 42499.7118 | 35.986 | -119.4294 | Vegetation | RURAL | < 3 meters | Unknown | Unknown | 100663426 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0723 | 2016 | 5 | 9 | 17 | 5 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-05-09 17:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-11 12:15 | 42501.5104 | 37.6781 | -122.4788 | Vegetation | URBAN | < 3 meters | Fire Agency | DALY CITY | 103565907 |  | 0 – 750 | Conductor | Overhead | Yes | 42501.5104 | 2016-05-11 12:15 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0724 | 2016 | 5 | 11 | 12 | 15 | 16-0035355 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 900 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-11 12:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-12 10:47 | 42502.4493 | 35.3024 | -120.7159 | Vegetation | RURAL | < 3 meters | Self Extinguished | N.A. | 101937429 |  | 12000 | Conductor | Overhead | Yes | 42502.4493 | 2016-05-12 10:47 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0725 | 2016 | 5 | 12 | 10 | 47 | 16-0035574 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 7616 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-12 10:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-12 13:35 | 42502.566 | 40.4538 | -124.0477 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101006413 |  | 12000 | Conductor | Overhead | Yes | 42502.566 | 2016-05-12 13:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0726 | 2016 | 5 | 12 | 13 | 35 | 16-0035614 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25974 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-12 13:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-12 20:15 | 42502.8438 | 35.1922 | -120.4563 | Vegetation | RURAL | < 3 meters | Self Extinguished | N.A. | 101857280 |  | 12000 | Conductor | Overhead | Yes | 42502.8438 | 2016-05-12 20:15 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0727 | 2016 | 5 | 12 | 20 | 15 | 16-0035728 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 54088 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-12 20:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-14 15:06 | 42504.6292 | 37.9688 | -121.6704 | Vegetation | RURAL | < 0.25 Acres | Unknown | Unknown | 100472239 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42504.6292 | 2016-05-14 15:06 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0728 | 2016 | 5 | 14 | 15 | 6 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-05-14 15:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-14 22:06 | 42504.9208 | 39.1636 | -121.5613 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Marysville FD | 101312807 |  | 12000 | Switch | Overhead | Yes | 42504.9208 | 2016-05-14 22:06 | Equipment/ Facility Failure | Switch | N.A. | N.A. | Unknown |  | Other/Unknown | 0729 | 2016 | 5 | 14 | 22 | 6 | 16-0036073 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 48140 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-14 22:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-15 15:54 | 42505.6625 | 36.7948 | -119.3966 | Vegetation | RURAL | 100 - 299 Acres | Fire Agency | Cal Fire | 100729685 | None | 12000 | Conductor | Overhead | Yes | 42505.6625 | 2016-05-15 15:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0730 | 2016 | 5 | 15 | 15 | 54 | 16-0036136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 180310 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-15 15:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-16 08:59 | 42506.3743 | 37.9283 | -121.2164 | Vegetation | RURAL | < 3 meters | Fire Agency | Unknown | 102130215 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42506.3743 | 2016-05-16 08:59 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0731 | 2016 | 5 | 16 | 8 | 59 | 16-0036212 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 26400 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-16 08:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-16 11:34 | 42506.4819 | 38.7734 | -121.4692 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103323287 |  | 12000 | Conductor | Overhead | Yes | 42506.4819 | 2016-05-16 11:34 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error |  | Other/Unknown | 0732 | 2016 | 5 | 16 | 11 | 34 | 16-0036256 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 15240 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-16 11:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-17 10:01 | 42507.4174 | 35.2379 | -118.9639 | Vegetation | RURAL | < 3 meters | Fire Agency | KCFD | 100135809 |  | 0 – 750 | Transformer | Overhead | Yes | 42507.4174 | 2016-05-17 10:01 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0733 | 2016 | 5 | 17 | 10 | 1 | 16-0036479 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 376 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-17 10:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-17 16:03 | 42507.6687 | 35.3856 | -119.0075 | Vegetation | URBAN | < 3 meters | Fire Agency | Bakersfield FD | 100246655 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42507.6687 | 2016-05-17 16:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Grow Into | 0734 | 2016 | 5 | 17 | 16 | 3 | 16-0036617 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Grow Into | 6150 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-17 16:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-18 | 18:24 | 39.7381 | -123.1587 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42508 | 0.76667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0735 | 2016 | 5 | 18 | 18 | 24 | 16-0036911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1482 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-18 18:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-18 15:45 | 42508.6562 | 35.555 | -120.6803 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Atascadero FD | 101901773 |  | 21000 | Conductor | Overhead | Yes | 42508.6562 | 2016-05-18 15:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 0736 | 2016 | 5 | 18 | 15 | 45 | 16-0036852 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 409654 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-18 15:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-18 20:04 | 42508.8361 | 40.4779 | -122.4031 | Vegetation | RURAL | < 3 meters | Fire Agency | County | 102307139 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42508.8361 | 2016-05-18 20:04 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0737 | 2016 | 5 | 18 | 20 | 4 | 16-0036905 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 114822 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-18 20:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-19 01:42 | 42509.0708 | 34.6645 | -120.4 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Santa Barbara County FD | 101916587 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42509.0708 | 2016-05-19 01:42 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | no-match | 0738 | 2016 | 5 | 19 | 1 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-05-19 01:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-19 18:33 | 42509.7729 | 37.74 | -120.8034 | Vegetation | RURAL | < 3 meters | Fire Agency | OAKDALE F.D. | 102342932 |  | 17000 | Conductor | Overhead | Yes | 42509.7729 | 2016-05-19 18:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0739 | 2016 | 5 | 19 | 18 | 33 | 16-0037236 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 79702 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-19 18:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-19 18:54 | 42509.7875 | 38.8168 | -123.5843 | Vegetation | RURAL | < 3 meters | Fire Agency | Gualala Firw | 102183917 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42509.7875 | 2016-05-19 18:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0740 | 2016 | 5 | 19 | 18 | 54 | 16-0037247 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 4510 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-19 18:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-20 15:01 | 15:01 | 39.0559 | -123.4581 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102198323 |  | 12000 | Conductor | Overhead | Yes | 42510.6257 | 0.62569 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0741 | 2016 | 5 | 20 | 15 | 1 | 16-0037479 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2720 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-20 15:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-20 18:54 | 42510.7875 | 37.3035 | -121.8398 | Vegetation | URBAN | .26 - 9.99 Acres | Fire Agency | San Jose FD | 103457021 |  | 21000 | Unknown | Overhead | Yes | 42510.7875 | 2016-05-20 18:54 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0742 | 2016 | 5 | 20 | 18 | 54 | 16-0037507 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 48049 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-20 18:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-20 20:43 | 42510.8632 | 35.4965 | -120.6806 | Vegetation | URBAN | .26 - 9.99 Acres | Fire Agency | Atascadero FD | 101897769 | PACIFIC BELL | 0 – 750 | Unknown | Overhead | No |  |  | Other | N.A. | N.A. | N.A. | Unknown |  | no-match | 0743 | 2016 | 5 | 20 | 20 | 43 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-05-20 20:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-21 17:44 | 42511.7389 | 37.369 | -120.6772 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101162897 |  | 12000 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0744 | 2016 | 5 | 21 | 17 | 44 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-05-21 17:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-23 12:52 | 42513.5361 | 38.5529 | -121.629 | Vegetation | RURAL | < 3 meters | Utility: PG&E | N.A. | 101593014 |  | 12000 | Conductor | Overhead | Yes | 42513.5361 | 2016-05-23 12:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0745 | 2016 | 5 | 23 | 12 | 52 | 16-0037850 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 28160 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-23 12:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-23 16:08 | 42513.6722 | 37.9537 | -121.6593 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Contra Costa County FD | 100472785 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42513.6722 | 2016-05-23 16:08 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0746 | 2016 | 5 | 23 | 16 | 8 | 16-0037909 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 22789 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-23 16:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-24 12:36 | 42514.525 | 38.0811 | -120.668 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101278239 |  | 12000 | Conductor | Overhead | Yes | 42514.525 | 2016-05-24 12:36 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0747 | 2016 | 5 | 24 | 12 | 36 | 16-0038096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 10678 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-24 12:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-26 17:42 | 42516.7375 | 35.5467 | -119.0935 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | BCFD/KCFD | 100207252 |  | 12000 | Conductor | Overhead | Yes | 42516.7375 | 2016-05-26 17:42 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 0748 | 2016 | 5 | 26 | 17 | 42 | 16-0038844 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-05-26 17:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-27 03:01 | 42517.1257 | 38.0935 | -122.2344 | Vegetation | URBAN | < 3 meters | Fire Agency | Vallejo FD | 102217012 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42517.1257 | 2016-05-27 03:01 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0749 | 2016 | 5 | 27 | 3 | 1 | 16-0038874 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 173663 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-27 03:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-28 15:53 | 42518.6618 | 36.7202 | -119.7134 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Fresno FD | 103297542 |  | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0750 | 2016 | 5 | 28 | 15 | 53 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-05-28 15:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-29 14:19 | 42519.5965 | 40.5795 | -122.4694 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103156596 | Yes | 12000 | Conductor | Overhead | Yes | 42519.5965 | 2016-05-29 14:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0751 | 2016 | 5 | 29 | 14 | 19 | 16-0039619 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3860 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-29 14:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-29 18:28 | 42519.7694 | 36.795 | -119.7716 | Vegetation | URBAN | < 3 meters | Customer | N.A. | 100839020 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42519.7694 | 2016-05-29 18:28 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0752 | 2016 | 5 | 29 | 18 | 28 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-05-29 18:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-30 20:37 | 42520.859 | 35.4562 | -118.9327 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | County | 100118357 |  | 0 – 750 | Conductor | Overhead | Yes | 42520.859 | 2016-05-30 20:37 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0753 | 2016 | 5 | 30 | 20 | 37 | 16-0039739 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1152 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-30 20:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-31 04:02 | 42521.1681 | 35.7984 | -120.9743 | Vegetation | RURAL | < 0.25 Acres | Utility: PG&E | N.A. | 101863413 |  | 12000 | Conductor | Overhead | Yes | 42521.1681 | 2016-05-31 04:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0754 | 2016 | 5 | 31 | 4 | 2 | 16-0039748 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 51888 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-31 04:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-31 08:24 | 42521.35 | 35.7308 | -119.8972 | Vegetation | RURAL | < 0.25 Acres | Unknown | Unknown | 100170377 |  | 12000 | Conductor | Overhead | Yes | 42521.35 | 2016-05-31 08:24 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0755 | 2016 | 5 | 31 | 8 | 24 | 16-0039786 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 12896 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-31 08:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-31 09:51 | 42521.4104 | 35.7314 | -119.8677 | Vegetation | RURAL | < 0.25 Acres | Self Extinguished | N.A. | 100168140 |  | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0756 | 2016 | 5 | 31 | 9 | 51 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-05-31 09:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-05-31 10:20 | 42521.4306 | 39.1939 | -122.0974 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Williams FD | 101642880 |  | 12000 | Conductor | Overhead | Yes | 42521.4306 | 2016-05-31 10:20 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0757 | 2016 | 5 | 31 | 10 | 20 | 16-0039857 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 316 | 0 | NA | <25mph | <15mph | #REF! | 2016-05-31 10:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-01 14:00 | 42522.5833 | 36.7977 | -121.7316 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire and north county | 101712734 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42522.5833 | 2016-06-01 14:00 | Contact From Object | N.A. | Other | Electric Facility | Human Error | third-party caused | no-match | 0758 | 2016 | 6 | 1 | 14 | 0 | 16-0040266 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | Substation | non-HFTD - Substation | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 0 | NA | <25mph | <15mph | non-HFTD - Substation | 2016-06-01 14:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-01 22:31 | 42522.9382 | 37.9281 | -120.7538 | Vegetation | RURAL | .26 - 9.99 Acres | Unknown | Unknown | 102343418 |  | 115000 | Conductor | Overhead | Yes | 42522.9382 | 2016-06-01 22:31 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0759 | 2016 | 6 | 1 | 22 | 31 | TE-2016-036 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-01 22:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-02 | 42523.5993 | 38.5901 | -121.8042 | Vegetation | RURAL | < 3 meters | Unknown | Unknown | 101557874 |  | 12000 | Transformer | Overhead | Yes | 42523 | 2016-06-02 14:23 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0760 | 2016 | 6 | 2 | 14 | 23 | 16-0040616 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 3060 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-02 14:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-02 | 42523.6229 | 37.0652 | -121.5654 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100607860 | VERIZON CALIFORNIA I | 0 – 750 | Conductor | Overhead | Yes | 42523 | 2016-06-02 14:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0761 | 2016 | 6 | 2 | 14 | 57 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-02 14:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-02 | 42523.6354 | 34.5887 | -120.1065 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Santa Barbara County FD | 101918537 |  | 12000 | Conductor | Overhead | Yes | 42523 | 2016-06-02 15:15 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0762 | 2016 | 6 | 2 | 15 | 15 | 16-0040636 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 21290 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-02 15:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-02 | 42523.7069 | 36.5857 | -121.6052 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | County | 101746812 |  | 0 – 750 | Conductor | Overhead | Yes | 42523 | 2016-06-02 16:58 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0763 | 2016 | 6 | 2 | 16 | 58 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-02 16:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-03 | 42524.5111 | 38.6435 | -120.6959 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | cal-fire and usfs | 103119737 |  | 21000 | Conductor | Overhead | Yes | 42524 | 2016-06-03 12:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0764 | 2016 | 6 | 3 | 12 | 16 | 16-0040808 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 101354 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-03 12:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-03 | 42524.6979 | 35.4046 | -119.0314 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Kern County FD | 100242571 | PACIFIC BELL | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0765 | 2016 | 6 | 3 | 16 | 45 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-03 16:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-03 | 42524.7799 | 39.7482 | -121.8232 | Vegetation | URBAN | < 3 meters | Fire Agency | Chico FD | 100344305 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42524 | 2016-06-03 18:43 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0766 | 2016 | 6 | 3 | 18 | 43 | 16-0040924 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 12330 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-03 18:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-03 | 42525.8701 | 37.4346 | -121.8772 | Vegetation | URBAN | < 3 meters | Fire Agency | Milpitas FD | 100559460 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0767 | 2016 | 6 | 3 | 20 | 53 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-03 20:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-04 | 22:15 | 38.5117 | -122.9373 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42525 | 0.92708 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0768 | 2016 | 6 | 4 | 22 | 15 | 16-0041119 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7220 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-04 22:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-04 | 42525.6326 | 36.8049 | -119.7871 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Fresno County FD | 100828880 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42525 | 2016-06-04 15:11 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0769 | 2016 | 6 | 4 | 15 | 11 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-04 15:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-04 | 42525.6604 | 38.309 | -121.7605 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Dixon FD | 101568694 |  | 21000 | Conductor | Overhead | Yes | 42525 | 2016-06-04 15:51 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0770 | 2016 | 6 | 4 | 15 | 51 | 16-0041087 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 15076 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-04 15:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-04 | 42525.8597 | 37.4346 | -121.8772 | Vegetation | URBAN | < 3 meters | Fire Agency | Milpitas FD | 100559460 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0771 | 2016 | 6 | 4 | 20 | 38 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-04 20:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-05 | 16:57 | 36.5868 | -119.6114 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42526 | 0.70625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0772 | 2016 | 6 | 5 | 16 | 57 | 16-0041171 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 231467 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-05 16:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-05 | 42526.4208 | 36.7504 | -119.6686 | Vegetation | RURAL | < 0.25 Acres | Utility: PG&E | N.A. | 100780354 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42526 | 2016-06-05 10:06 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0773 | 2016 | 6 | 5 | 10 | 6 | 16-0041152 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 264 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-05 10:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-05 15:44 | 42526.6556 | 40.3441 | -123.71 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101009790 |  | 60000 | Conductor | Overhead | Yes | 42526.6556 | 2016-06-05 15:44 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0774 | 2016 | 6 | 5 | 15 | 44 | HM-2016-016 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-05 15:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-06 | 42527.825 | 38.9129 | -121.1192 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire/placer fire | 100050264 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42527 | 2016-06-06 19:48 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0775 | 2016 | 6 | 6 | 19 | 48 | 16-0041497 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2039 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-06 19:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-07 | 42528.5799 | 36.9315 | -119.8658 | Vegetation | RURAL | < 3 meters | Utility: PG&E | N.A. | 101215609 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42528 | 2016-06-07 13:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0776 | 2016 | 6 | 7 | 13 | 55 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-07 13:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-07 | 42528.7632 | 36.9887 | -120.6377 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Cal Fire | 103214859 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0777 | 2016 | 6 | 7 | 18 | 19 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-07 18:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-07 | 42528.8194 | 35.5852 | -120.5829 | Vegetation | RURAL | < 0.25 Acres | Unknown | Unknown | 101943517 |  | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0778 | 2016 | 6 | 7 | 19 | 40 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-07 19:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-07 00:45 | 42528.0312 | 37.2856 | -120.4517 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Cal Fire | 103333060 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42528.0312 | 2016-06-07 00:45 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0779 | 2016 | 6 | 7 | 0 | 45 | 16-0041541 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 68746 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-07 00:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-07 09:12 | 42528.3833 | 39.3629 | -121.7723 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100378551 | None | 12000 | Conductor | Overhead | Yes | 42528.3833 | 2016-06-07 09:12 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0780 | 2016 | 6 | 7 | 9 | 12 | 16-0042534 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-07 09:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-08 | 42529.4722 | 39.3032 | -121.5207 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 101331693 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42529 | 2016-06-08 11:20 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0781 | 2016 | 6 | 8 | 11 | 20 | 16-0041897 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 6031 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-08 11:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-08 00:21 | 42529.0146 | 36.7567 | -119.797 | Vegetation | URBAN | Structure Only | Fire Agency | Fresno FD | 100864822 |  | 12000 | Conductor | Overhead | Yes | 42529.0146 | 2016-06-08 00:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, 4-12ft) | 0782 | 2016 | 6 | 8 | 0 | 21 | 16-0041800 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, 4-12ft) | 163032 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-08 00:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-08 16:50 | 42529.7014 | 35.6716 | -120.598 | Building | RURAL | Structure Only | Fire Agency | Cal Fire | 101867293 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42529.7014 | 2016-06-08 16:50 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error |  | no-match | 0783 | 2016 | 6 | 8 | 16 | 50 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-08 16:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-09 | 42530.6014 | 38.7003 | -120.847 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101390214 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42530 | 2016-06-09 14:26 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0784 | 2016 | 6 | 9 | 14 | 26 | 16-0042273 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 208224 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-09 14:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-09 10:52 | 42530.4528 | 36.8058 | -119.7103 | Vegetation | URBAN | < 3 meters | Unknown | Unknown | 100794383 |  | 21000 | Conductor | Overhead | Yes | 42530.4528 | 2016-06-09 10:52 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0785 | 2016 | 6 | 9 | 10 | 52 | 16-0042171 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 13704 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-09 10:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-09 23:39 | 42530.9854 | 39.0148 | -122.857 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102143661 |  | 12000 | Conductor | Overhead | Yes | 42530.9854 | 2016-06-09 23:39 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0786 | 2016 | 6 | 9 | 23 | 39 | 16-0042334 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 179342 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-09 23:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-10 | 42531.3507 | 36.7296 | -119.6997 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Fresno FD | 102309139 |  | 12000 | Conductor | Overhead | Yes | 42531 | 2016-06-10 08:25 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0787 | 2016 | 6 | 10 | 8 | 25 | 16-0042388 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 1078 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-10 08:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-10 15:51 | 42531.6604 | 39.9934 | -123.7883 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100992291 |  | 12000 | Conductor | Overhead | Yes | 42531.6604 | 2016-06-10 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0788 | 2016 | 6 | 10 | 15 | 51 | 16-0042501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-10 15:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-10 15:57 | 42531.6646 | 38.1792 | -120.6657 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103809655 |  | 12000 | Conductor | Overhead | Yes | 42531.6646 | 2016-06-10 15:57 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0789 | 2016 | 6 | 10 | 15 | 57 | 16-0042508 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-10 15:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-11 | 42532.8229 | 39.3265 | -121.3921 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101292512 |  | 0 – 750 | Transformer | Overhead | Yes | 42532 | 2016-06-11 19:45 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0790 | 2016 | 6 | 11 | 19 | 45 | 16-0042611 | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 642 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-11 19:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-12 | 42533.334 | 36.5936 | -119.9887 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100668862 |  | 12000 | Conductor | Overhead | Yes | 42533 | 2016-06-12 08:01 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0791 | 2016 | 6 | 12 | 8 | 1 | 16-0042672 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 31269 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-12 08:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-12 | 42533.4319 | 38.0491 | -120.3976 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101042514 |  | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0792 | 2016 | 6 | 12 | 10 | 22 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-12 10:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-12 | 42533.4944 | 39.6799 | -122.3217 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire/ORLAND | 100405660 |  | 21000 | Conductor | Overhead | Yes | 42533 | 2016-06-12 11:52 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0793 | 2016 | 6 | 12 | 11 | 52 | 16-0042724 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1612 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-12 11:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-12 | 42533.5486 | 38.2535 | -122.0628 | Vegetation | URBAN | < 3 meters | Fire Agency | Fairfield FD | 101557178 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42533 | 2016-06-12 13:10 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0794 | 2016 | 6 | 12 | 13 | 10 | 16-0042721 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 17542 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-12 13:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-12 | 42533.5514 | 37.5096 | -120.0462 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101083986 |  | 0 – 750 | Conductor | Overhead | Yes | 42533 | 2016-06-12 13:14 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0795 | 2016 | 6 | 12 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-12 13:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-12 01:45 | 1:45 | 37.4643 | -122.3459 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Unknown | 100265854 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42533.0729 | 0.072917 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0796 | 2016 | 6 | 12 | 1 | 45 | 16-0042637 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 19836 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-12 01:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-12 19:19 | 42533.8049 | 39.1591 | -121.5886 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Marysville FD | 101312163 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42533.8049 | 2016-06-12 19:19 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0797 | 2016 | 6 | 12 | 19 | 19 | 16-0042737 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 56738 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-12 19:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-12 20:00 | 42533.8333 | 37.2694 | -121.7893 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | San Jose FD | 103434547 | None | 115000 | Conductor | Overhead | Yes | 42533.8333 | 2016-06-12 20:00 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | no-match | 0798 | 2016 | 6 | 12 | 20 | 0 | ME-2016-005 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 0 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-12 20:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-13 | 42534.2438 | 39.4641 | -121.8858 | Vegetation | RURAL | < 3 meters | Fire Agency | COLUSA GLENN FIRE | 101617882 |  | 12000 | Transformer | Overhead | Yes | 42534 | 2016-06-13 05:51 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0799 | 2016 | 6 | 13 | 5 | 51 | 16-0042781 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2745 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-13 05:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-15 | 14:40 | 38.3079 | -122.6553 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire |  |  | 0 – 750 | Conductor | Overhead | Yes | 42536 | 0.61111 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Grow Into | 0800 | 2016 | 6 | 15 | 14 | 40 | 16-0043512 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Grow Into | 195 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-15 14:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-15 | 42536.5479 | 38.4433 | -120.7568 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103169620 |  | 12000 | Conductor | Overhead | Yes | 42536 | 2016-06-15 13:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0801 | 2016 | 6 | 15 | 13 | 9 | 16-0043476 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 23963 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-15 13:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-15 | 42536.5722 | 38.4375 | -122.6771 | Vegetation | URBAN | < 3 meters | Customer | N.A. | 102024321 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42536 | 2016-06-15 13:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0802 | 2016 | 6 | 15 | 13 | 44 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-15 13:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-16 | 17:41 | 37.3406 | -121.7823 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | San Jose FD | 100576793 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42537 | 0.73681 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Fell into (No defect) | 0803 | 2016 | 6 | 16 | 17 | 41 | 16-0043850 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 2890 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-16 17:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-16 07:22 | 42537.3069 | 37.8678 | -121.6382 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Contra Costa County FD | 100497743 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42537.3069 | 2016-06-16 07:22 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0804 | 2016 | 6 | 16 | 7 | 22 | 16-0043642 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 56505 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-16 07:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-16 13:07 | 42537.5465 | 39.0681 | -121.6605 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Yuba City FD | 101329181 |  | 12000 | Lightning Arrestor | Overhead | Yes | 42537.5465 | 2016-06-16 13:07 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | Other/Unknown | 0805 | 2016 | 6 | 16 | 13 | 7 | 16-0044374 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-16 13:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-17 | 42538.4701 | 36.7325 | -120.4049 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102312507 |  | 0 – 750 | Capacitor Bank | Overhead | Yes | 42538 | 2016-06-17 11:17 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0806 | 2016 | 6 | 17 | 11 | 17 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-17 11:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-19 | 42540.5049 | 39.3811 | -123.7737 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102187888 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 12:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0807 | 2016 | 6 | 19 | 12 | 7 | 16-0044317 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6100 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-19 12:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-19 | 42540.7215 | 38.4508 | -122.3546 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire--napa fire | 102256859 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 17:19 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0808 | 2016 | 6 | 19 | 17 | 19 | 16-0044337 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 672 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-19 17:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-19 15:50 | 42540.6597 | 38.2425 | -121.8535 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | RIO VISTA MONTEZHUMA FIRE | 101582754 |  | 21000 | Conductor | Overhead | Yes | 42540.6597 | 2016-06-19 15:50 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0809 | 2016 | 6 | 19 | 15 | 50 | 16-0044329 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 21329 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-19 15:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-20 | 42541.5813 | 36.5356 | -119.379 | Vegetation | URBAN | < 3 meters | Customer | N.A. | 103238848 |  | 0 – 750 | Conductor | Overhead | Yes | 42541 | 2016-06-20 13:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0810 | 2016 | 6 | 20 | 13 | 57 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-20 13:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-20 | 42541.6979 | 41.0697 | -123.6789 | Vegetation | RURAL | < 3 meters | Fire Agency | Hoopa FD | 101011420 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42541 | 2016-06-20 16:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0811 | 2016 | 6 | 20 | 16 | 45 | 16-0044577 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7361 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-20 16:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-21 | 20:49 | 35.5352 | -120.8457 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101900832 |  | 12000 | Conductor | Overhead | Yes | 42542 | 0.86736 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0812 | 2016 | 6 | 21 | 20 | 49 | 16-0044904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7806 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-21 20:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-21 | 42542.4229 | 39.0294 | -121.2927 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100024816 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | no-match | 0813 | 2016 | 6 | 21 | 10 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-21 10:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-21 | 42542.7035 | 38.4233 | -122.5448 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | KENWOOD FIRE XST | 102036904 | Yes | 0 – 750 | Conductor | Overhead | Yes | 42542 | 2016-06-21 16:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0814 | 2016 | 6 | 21 | 16 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-21 16:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-21 18:01 | 42542.7507 | 39.2852 | -123.2053 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire/Redwood Valley FD | 102176908 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42542.7507 | 2016-06-21 18:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0815 | 2016 | 6 | 21 | 18 | 1 | 16-0044889 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 136782 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-21 18:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-22 | 42543.8007 | 36.3875 | -119.835 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Kings County FD | 100848643 |  | 0 – 750 | Conductor | Overhead | Yes | 42543 | 2016-06-22 19:13 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0816 | 2016 | 6 | 22 | 19 | 13 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-22 19:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-23 | 42544.4236 | 36.7243 | -120.0583 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Fresno FD | 100637712 | KERMAN TELEPHONE CO. | 0 – 750 | Conductor | Overhead | Yes | 42544 | 2016-06-23 10:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0817 | 2016 | 6 | 23 | 10 | 10 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-23 10:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-23 | 42544.8049 | 35.6212 | -120.3562 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101937184 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42544 | 2016-06-23 19:19 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0818 | 2016 | 6 | 23 | 19 | 19 | 16-0045476 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 1296 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-23 19:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-23 | 42544.8979 | 38.1206 | -121.9545 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Suisun Fire Protection District. | 101558702 |  | 0 – 750 | Conductor | Overhead | Yes | 42544 | 2016-06-23 21:33 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0819 | 2016 | 6 | 23 | 21 | 33 | 16-0045210 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4517 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-23 21:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-24 | 42545.1299 | 38.7192 | -121.0546 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire/EDH FIRE DEPT | 101376553 |  | 21000 | Conductor | Overhead | Yes | 42545 | 2016-06-24 03:07 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Fell into (No defect) | 0820 | 2016 | 6 | 24 | 3 | 7 | 16-0045498 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 54027 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-24 03:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-24 | 42545.6097 | 40.22 | -122.283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101526647 | PACIFIC BELL | 0 – 750 | Unknown | Overhead | Yes | 42545 | 2016-06-24 14:38 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0821 | 2016 | 6 | 24 | 14 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-24 14:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-25 17:07 | 42546.7132 | 39.7603 | -121.6188 | Vegetation | URBAN | < 3 meters | Fire Agency | CAL FIRE/ PARADISE | 100327279 |  | 12000 | Conductor | Overhead | Yes | 42546.7132 | 2016-06-25 17:07 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0822 | 2016 | 6 | 25 | 17 | 7 | 16-0045792 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 282305 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-25 17:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-26 | 42547.6931 | 39.5042 | -121.4475 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100375810 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42547 | 2016-06-26 16:38 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0823 | 2016 | 6 | 26 | 16 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-26 16:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-26 | 42547.7014 | 35.6772 | -120.684 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | County | 101869974 | None | 0 – 750 | Conductor | Overhead | No |  |  | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gunshot | no-match | 0824 | 2016 | 6 | 26 | 16 | 50 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-26 16:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-26 | 42547.7493 | 38.8087 | -121.5159 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | PLEASANT GROVE F D - SUTTER COUNTY | 101340542 |  | 12000 | Conductor | Overhead | Yes | 42547 | 2016-06-26 17:59 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0825 | 2016 | 6 | 26 | 17 | 59 | 16-0045869 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 72562 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-26 17:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-26 11:06 | 42547.4625 | 40.4832 | -122.0466 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101483777 | FRONTIER | 12000 | Conductor | Overhead | Yes | 42547.4625 | 2016-06-26 11:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0826 | 2016 | 6 | 26 | 11 | 6 | 16-0045846 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 15520 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-26 11:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-27 | 42548.4667 | 36.9089 | -119.5224 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100726035 | None | 12000 | Lightning Arrestor | Overhead | Yes | 42548 | 2016-06-27 11:12 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | Other/Unknown | 0827 | 2016 | 6 | 27 | 11 | 12 | 16-0045997 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 29408 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-27 11:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-28 | 42549.4861 | 37.2998 | -121.9766 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Unknown | 100593023 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42549 | 2016-06-28 11:40 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0828 | 2016 | 6 | 28 | 11 | 40 | 16-0046303 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 307901 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-28 11:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-28 | 42549.5667 | 38.0961 | -122.2304 | Building | URBAN | Structure Only | Fire Agency | vall fire | 102278744 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42549 | 2016-06-28 13:36 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0829 | 2016 | 6 | 28 | 13 | 36 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-28 13:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-28 09:11 | 42549.3826 | 37.1005 | -120.2249 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Chowchilla FD | 103810794 | None | 12000 | Conductor | Overhead | Yes | 42549.3826 | 2016-06-28 09:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0830 | 2016 | 6 | 28 | 9 | 11 | 16-0046243 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 5396 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-28 09:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-29 | 42550.5382 | 36.5004 | -121.4347 | Vegetation | URBAN | < 0.25 Acres | Customer | N.A. | 101754504 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0831 | 2016 | 6 | 29 | 12 | 55 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-06-29 12:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-30 | 0:03 | 39.8157 | -121.5994 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42551 | 0.0020833 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0832 | 2016 | 6 | 30 | 0 | 3 | 16-0046763 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 299100 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-30 00:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-30 | 42551.7181 | 40.0353 | -122.5694 | Vegetation | RURAL | 300 - 999 Acres | Fire Agency | Cal Fire | 101528146 |  | 12000 | Conductor | Overhead | Yes | 2016-06-30 | 2016-06-30 17:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0833 | 2016 | 6 | 30 | 17 | 14 | 16-0047210 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | Vegetation | Fell into (slight defect) | 4520 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-30 17:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-06-30 14:20 | 42551.5972 | 37.9927 | -120.3996 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Cal Fire | 102327111 | PACIFIC BELL | 17000 | Conductor | Overhead | Yes | 42551.5972 | 2016-06-30 14:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0834 | 2016 | 6 | 30 | 14 | 20 | 16-0047073 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 278 | 0 | NA | <25mph | <15mph | #REF! | 2016-06-30 14:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-01 22:03 | 42552.9187 | 37.9273 | -122.3181 | Vegetation | URBAN | .26 - 9.99 Acres | Fire Agency | CITY OF RICHMOND | 101444612 | PACIFIC BELL | 4000 | Conductor | Overhead | Yes | 42552.9187 | 2016-07-01 22:03 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0835 | 2016 | 7 | 1 | 22 | 3 | 16-0047525 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 26767 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-01 22:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-02 04:05 | 42553.1701 | 37.7805 | -121.4974 | Vegetation | RURAL | < 3 meters | Utility: PG&E | N.A. | 102094598 |  | 12000 | Conductor | Overhead | Yes | 42553.1701 | 2016-07-02 04:05 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0836 | 2016 | 7 | 2 | 4 | 5 | 16-0047533 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 2680 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-02 04:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-03 15:00 | 42554.625 | 38.0348 | -120.3809 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101050507 |  | 17000 | Conductor | Overhead | Yes | 42554.625 | 2016-07-03 15:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0837 | 2016 | 7 | 3 | 15 | 0 | 16-0047689 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38812 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-03 15:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-04 07:43 | 42555.3215 | 38.7623 | -121.2142 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | South Placer FD | 103810320 |  | 12000 | Conductor | Overhead | Yes | 42555.3215 | 2016-07-04 07:43 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0838 | 2016 | 7 | 4 | 7 | 43 | 16-0047731 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3933 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-04 07:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-05 08:35 | 8:35 | 36.239 | -120.3015 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100743822 |  | 12000 | Conductor | Overhead | Yes | 42556.3576 | 0.35764 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0839 | 2016 | 7 | 5 | 8 | 35 | 16-0047849 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 19757 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-05 08:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-05 10:36 | 42556.4417 | 36.2827 | -120.2617 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Fresno County FD | 100747232 |  | 0 – 750 | Conductor | Overhead | Yes | 42556.4417 | 2016-07-05 10:36 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0840 | 2016 | 7 | 5 | 10 | 36 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-05 10:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-07 10:56 | 42558.4556 | 39.2966 | -121.8263 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | LIVE OAK | 101315522 |  | 12000 | Fuse | Overhead | Yes | 42558.4556 | 2016-07-07 10:56 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0841 | 2016 | 7 | 7 | 10 | 56 | 16-0048407 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1086 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-07 10:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-08 10:49 | 42559.4507 | 38.3373 | -122.1211 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 102291118 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42559.4507 | 2016-07-08 10:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0842 | 2016 | 7 | 8 | 10 | 49 | 16-0048647 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 19469 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-08 10:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-08 15:13 | 42559.634 | 33.6143 | -117.111 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Unknown | 103070565 | None | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0843 | 2016 | 7 | 8 | 15 | 13 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-08 15:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-09 10:05 | 10:05 | 35.131 | -120.6069 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Unknown | 101924844 |  | 12000 | Conductor | Overhead | Yes | 42560.4201 | 0.42014 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0844 | 2016 | 7 | 9 | 10 | 5 | 16-0048770 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-09 10:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-09 14:57 | 42560.6229 | 38.5035 | -121.7826 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Dixon FD | 101599862 | None | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0845 | 2016 | 7 | 9 | 14 | 57 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-09 14:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-09 15:42 | 42560.6542 | 38.8928 | -121.9748 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | DUGGAGAN FIRE | 101602162 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42560.6542 | 2016-07-09 15:42 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0846 | 2016 | 7 | 9 | 15 | 42 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-09 15:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-09 19:22 | 42560.8069 | 37.3111 | -121.8313 | Vegetation | URBAN | < 3 meters | Fire Agency | San Jose FD | 100592926 | PACIFIC BELL | 0 – 750 | Unknown | Overhead | Yes | 42560.8069 | 2016-07-09 19:22 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0847 | 2016 | 7 | 9 | 19 | 22 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-09 19:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-12 14:18 | 42563.5958 | 35.3471 | -120.3813 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101879190 |  | 21000 | Conductor | Overhead | Yes | 42563.5958 | 2016-07-12 14:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0848 | 2016 | 7 | 12 | 14 | 18 | 16-0049403 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 18883 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-12 14:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-13 10:20 | 42564.4306 | 37.3277 | -122.0719 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire/scfd | 103510668 |  | 115000 | Conductor | Overhead | Yes | 42564.4306 | 2016-07-13 10:20 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0849 | 2016 | 7 | 13 | 10 | 20 | ME-2016-006 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-13 10:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-14 13:44 | 42565.5722 | 35.3833 | -118.9232 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Kern County FD | 100119861 |  | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0850 | 2016 | 7 | 14 | 13 | 44 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-14 13:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-15 05:19 | 42566.2215 | 35.1839 | -120.5018 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101846594 |  | 12000 | Conductor | Overhead | Yes | 42566.2215 | 2016-07-15 05:19 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0851 | 2016 | 7 | 15 | 5 | 19 | 16-0050086 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 62404 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-15 05:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-15 14:09 | 42566.5896 | 38.6965 | -120.8598 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412774 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.5896 | 2016-07-15 14:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0852 | 2016 | 7 | 15 | 14 | 9 | 16-0050274 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 11253 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-15 14:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-15 14:26 | 42566.6014 | 38.1366 | -122.7092 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | NOVATO FIRE AND OTHERS | 102013570 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.6014 | 2016-07-15 14:26 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0853 | 2016 | 7 | 15 | 14 | 26 | 16-0050269 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 758 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-15 14:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-15 17:09 | 42566.7146 | 35.3585 | -119.0409 | Vegetation | URBAN | < 3 meters | Fire Agency | CITY | 100194332 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42566.7146 | 2016-07-15 17:09 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0854 | 2016 | 7 | 15 | 17 | 9 | 16-0050306 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2086 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-15 17:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-16 00:58 | 42567.0403 | 36.4379 | -121.9198 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101669758 |  | 12000 | Other | Overhead | Yes | 42567.0403 | 2016-07-16 00:58 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0855 | 2016 | 7 | 16 | 0 | 58 | 16-0050335 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 8976 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-16 00:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-16 08:19 | 42567.3465 | 37.4828 | -119.87 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101079104 | None | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0856 | 2016 | 7 | 16 | 8 | 19 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-16 08:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-16 20:26 | 42567.8514 | 38.4944 | -122.4944 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Cal Fire | 102265740 | None | 12000 | Conductor | Overhead | Yes | 42567.8514 | 2016-07-16 20:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0857 | 2016 | 7 | 16 | 20 | 26 | 16-0050320 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 13240 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-16 20:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-18 07:39 | 42569.3187 | 36.7572 | -119.7807 | Vegetation | URBAN | < 3 meters | Self Extinguished | N.A. | 100869066 | PACIFIC BELL | 0 – 750 | Capacitor Bank | Overhead | Yes | 42569.3187 | 2016-07-18 07:39 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0858 | 2016 | 7 | 18 | 7 | 39 | 16-0050556 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 2799 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-18 07:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-18 09:11 | 42569.3826 | 36.9977 | -119.983 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101017131 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42569.3826 | 2016-07-18 09:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0859 | 2016 | 7 | 18 | 9 | 11 | 16-0050594 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 3434 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-18 09:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-18 15:56 | 42569.6639 | 37.3221 | -121.8055 | Vegetation | URBAN | .26 - 9.99 Acres | Fire Agency | San Jose FD | 100579940 |  | 21000 | Conductor | Overhead | Yes | 42569.6639 | 2016-07-18 15:56 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0860 | 2016 | 7 | 18 | 15 | 56 | 16-0050704 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 744476 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-18 15:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-18 17:14 | 42569.7181 | 36.912 | -121.7913 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101699685 | PACIFIC BELL | 21000 | Switch | Overhead | Yes | 42569.7181 | 2016-07-18 17:14 | Equipment/ Facility Failure | Sectionalizer | N.A. | N.A. | Unknown |  | Other/Unknown | 0861 | 2016 | 7 | 18 | 17 | 14 | 16-0050712 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 116709 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-18 17:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-19 01:53 | 42570.0785 | 38.0757 | -122.5396 | Vegetation | RURAL | < 3 meters | Fire Agency | NOVATO FIRE DEPT | 102305231 |  | 12000 | Other | Overhead | Yes | 42570.0785 | 2016-07-19 01:53 | Equipment/ Facility Failure | Recloser | N.A. | N.A. | Unknown |  | Other/Unknown | 0862 | 2016 | 7 | 19 | 1 | 53 | 16-0050759 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 137627 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-19 01:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-19 14:41 | 42570.6118 | 38.2535 | -122.0628 | Vegetation | URBAN | < 3 meters | Fire Agency | Fairfield FD | 101557178 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42570.6118 | 2016-07-19 14:41 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0863 | 2016 | 7 | 19 | 14 | 41 | 16-0050992 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 28206 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-19 14:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-20 06:25 | 42571.2674 | 34.8933 | -120.3513 | Vegetation | RURAL | < 3 meters | Fire Agency | Santa Barbara County FD | 101861585 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42571.2674 | 2016-07-20 06:25 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0864 | 2016 | 7 | 20 | 6 | 25 | 16-0051062 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 3579 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-20 06:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-20 19:15 | 42571.8021 | 37.7712 | -121.8104 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100898986 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42571.8021 | 2016-07-20 19:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0865 | 2016 | 7 | 20 | 19 | 15 | 16-0051308 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 3013 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-20 19:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-21 13:10 | 42572.5486 | 39.4965 | -121.6886 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100416773 |  | 12000 | Conductor | Overhead | Yes | 42572.5486 | 2016-07-21 13:10 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0866 | 2016 | 7 | 21 | 13 | 10 | 16-0051607 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 14701 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-21 13:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-21 13:30 | 42572.5625 | 39.1679 | -121.7165 | Vegetation | RURAL | < 0.25 Acres | Unknown | Unknown | 101302589 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | Yes | 42572.5625 | 2016-07-21 13:30 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0867 | 2016 | 7 | 21 | 13 | 30 | 16-0051576 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 21 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-21 13:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-21 17:38 | 42572.7347 | 38.4941 | -121.7874 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Dixon FD | 101599745 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42572.7347 | 2016-07-21 17:38 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0868 | 2016 | 7 | 21 | 17 | 38 | 16-0051689 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 8095 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-21 17:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-21 18:20 | 42572.7639 | 35.5922 | -120.6474 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103390807 |  | 21000 | Other | Overhead | Yes | 42572.7639 | 2016-07-21 18:20 | Equipment/ Facility Failure | Recloser | N.A. | N.A. | Unknown |  | Other/Unknown | 0869 | 2016 | 7 | 21 | 18 | 20 | 16-0051688 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 129207 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-21 18:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-21 21:45 | 42572.9062 | 40.8566 | -122.3387 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101455670 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0870 | 2016 | 7 | 21 | 21 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-21 21:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-22 04:46 | 42573.1986 | 37.3465 | -120.9329 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Merced County FD | 101207784 |  | 12000 | Conductor | Overhead | Yes | 42573.1986 | 2016-07-22 04:46 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0871 | 2016 | 7 | 22 | 4 | 46 | 16-0051731 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 2455 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-22 04:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-22 14:11 | 42573.591 | 39.7121 | -121.8136 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100346440 |  | 12000 | Conductor | Overhead | Yes | 42573.591 | 2016-07-22 14:11 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0872 | 2016 | 7 | 22 | 14 | 11 | 16-0051883 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 104176 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-22 14:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-23 12:45 | 42574.5312 | 38.0193 | -121.9021 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Contra Costa County FD | 102345455 |  | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0873 | 2016 | 7 | 23 | 12 | 45 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-23 12:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-23 16:12 | 42574.675 | 35.3431 | -119.043 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Bakersfield FD | 100256351 | Yes | 0 – 750 | Conductor | Overhead | Yes | 42574.675 | 2016-07-23 16:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0874 | 2016 | 7 | 23 | 16 | 12 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-23 16:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-23 19:12 | 42574.8 | 36.7409 | -119.7273 | Vegetation | URBAN | < 3 meters | Customer | N.A. | 100820603 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42574.8 | 2016-07-23 19:12 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 0875 | 2016 | 7 | 23 | 19 | 12 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-23 19:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-24 16:24 | 42575.6833 | 38.0105 | -122.1941 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | CCD | 103049639 |  | 115000 | Conductor | Overhead | Yes | 42575.6833 | 2016-07-24 16:24 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0876 | 2016 | 7 | 24 | 16 | 24 | PS-2016-013 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 0 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-24 16:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-25 10:14 | 42576.4264 | 37.476 | -120.574 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | CAL FIRE MERCED | 101195552 |  | 21000 | Conductor | Overhead | Yes | 42576.4264 | 2016-07-25 10:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0877 | 2016 | 7 | 25 | 10 | 14 | 16-0052265 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3382 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-25 10:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-25 15:32 | 42576.6472 | 38.3522 | -120.7107 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42576.6472 | 2016-07-25 15:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0878 | 2016 | 7 | 25 | 15 | 32 | 16-0052398 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 19951 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-25 15:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-27 | 15:29 | 38.8308 | -122.1899 | Vegetation | RURAL | < 0.25 Acres | Unknown | Unknown |  |  | 21000 | Conductor | Overhead | Yes | 42578 | 0.64514 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0879 | 2016 | 7 | 27 | 15 | 29 | 16-0053024 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 12144 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-27 15:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-27 11:53 | 42578.4951 | 37.8649 | -120.5134 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101041792 |  | 17000 | Conductor | Overhead | Yes | 42578.4951 | 2016-07-27 11:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0880 | 2016 | 7 | 27 | 11 | 53 | 16-0052942 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 14734 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-27 11:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-27 15:04 | 42578.6278 | 40.8207 | -124.1825 | Vegetation | RURAL | < 3 meters | Fire Agency | SAMOA PENNISUL;A FIRE DEPT | 100968543 |  | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0881 | 2016 | 7 | 27 | 15 | 4 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-27 15:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-27 17:05 | 42578.7118 | 38.5392 | -122.7656 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102029945 |  | 60000 | Conductor | Overhead | Yes | 42578.7118 | 2016-07-27 17:05 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0882 | 2016 | 7 | 27 | 17 | 5 | FU-2016-047 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-27 17:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-28 02:41 | 42579.1118 | 35.3674 | -120.3977 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101849904 |  | 21000 | Conductor | Overhead | Yes | 42579.1118 | 2016-07-28 02:41 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0883 | 2016 | 7 | 28 | 2 | 41 | 16-0053127 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 22592 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-28 02:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-28 08:12 | 42579.3417 | 37.8207 | -120.1388 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101037043 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0884 | 2016 | 7 | 28 | 8 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-28 08:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-28 12:58 | 42579.5403 | 37.2371 | -119.8157 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103323932 |  | 21000 | Conductor | Overhead | Yes | 42579.5403 | 2016-07-28 12:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0885 | 2016 | 7 | 28 | 12 | 58 | 16-0053313 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 15215 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-28 12:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-28 13:19 | 42579.5549 | 39.7127 | -123.4973 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102195566 |  | 12000 | Conductor | Overhead | Yes | 42579.5549 | 2016-07-28 13:19 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0886 | 2016 | 7 | 28 | 13 | 19 | 16-0053369 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4447 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-28 13:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-28 14:07 | 42579.5882 | 39.6872 | -121.7185 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 103653216 |  | 60000 | Conductor | Overhead | Yes | 42579.5882 | 2016-07-28 14:07 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0887 | 2016 | 7 | 28 | 14 | 7 | TM-2016-041 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-28 14:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-28 14:24 | 42579.6 | 37.8232 | -120.1356 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101037045 |  | 17000 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Guy/Span Wire | N.A. | N.A. | Unknown |  | no-match | 0888 | 2016 | 7 | 28 | 14 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-28 14:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-28 16:16 | 42579.6778 | 36.75 | -119.7296 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Fresno FD | 100818516 | PACIFIC BELL | 0 – 750 | Other | Overhead | Yes | 42579.6778 | 2016-07-28 16:16 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0889 | 2016 | 7 | 28 | 16 | 16 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-28 16:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-29 | 18:16 | 38.5769 | -122.6187 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Selma Fire Department |  |  | 12000 | Conductor | Overhead | Yes | 42580 | 0.76111 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0890 | 2016 | 7 | 29 | 18 | 16 | 16-0053726 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 177834 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-29 18:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-29 01:31 | 42580.0632 | 41.0396 | -123.674 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Hoopa FD | 100962351 |  | 12000 | Conductor | Overhead | Yes | 42580.0632 | 2016-07-29 01:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0891 | 2016 | 7 | 29 | 1 | 31 | 16-0053478 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1418 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-29 01:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-29 15:47 | 42580.6576 | 39.0497 | -121.5153 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101334767 |  | 0 – 750 | Unknown | Overhead | Yes | 42580.6576 | 2016-07-29 15:47 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0892 | 2016 | 7 | 29 | 15 | 47 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-29 15:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-29 18:50 | 42580.7847 | 38.0204 | -122.0619 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Contra Costa County FD | 100446986 |  | 21000 | Conductor | Overhead | Yes | 42580.7847 | 2016-07-29 18:50 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0893 | 2016 | 7 | 29 | 18 | 50 | 16-0053741 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 132237 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-29 18:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-30 11:04 | 42581.4611 | 35.1941 | -118.9131 | Vegetation | RURAL | < 0.25 Acres | Utility: PG&E | N.A. | 100150295 |  | 12000 | Conductor | Overhead | Yes | 42581.4611 | 2016-07-30 11:04 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0894 | 2016 | 7 | 30 | 11 | 4 | 16-0053837 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 474 | 0 | NA | <25mph | <15mph | #REF! | 2016-07-30 11:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-07-31 12:11 | 42582.5076 | 38.7827 | -120.9168 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101417359 |  | 21000 | Conductor | Overhead | Yes | 42582.5076 | 2016-07-31 12:11 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0895 | 2016 | 7 | 31 | 12 | 11 | 16-0053949 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-07-31 12:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-01 | 42583.5347 | 38.9044 | -121.1274 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100078299 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42583 | 2016-08-01 12:50 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0896 | 2016 | 8 | 1 | 12 | 50 | 16-0054142 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 855 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-01 12:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-01 | 42583.6993 | 38.9319 | -121.4694 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Unknown | 101292397 |  | 0 – 750 | Transformer | Overhead | Yes | 42583 | 2016-08-01 16:47 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0897 | 2016 | 8 | 1 | 16 | 47 | 16-0054256 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 52 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-01 16:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-01 | 42583.7701 | 38.6956 | -120.9283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412720 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0898 | 2016 | 8 | 1 | 18 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-01 18:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-02 | 42584.2861 | 38.197 | -122.2757 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Napa/American Canyon FD | 103154739 |  | 12000 | Conductor | Overhead | Yes | 42584 | 2016-08-02 06:52 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0899 | 2016 | 8 | 2 | 6 | 52 | 16-0054326 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 7905 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-02 06:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-02 | 42584.6771 | 37.0312 | -119.4395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Fresno County FD | 100675986 |  | 12000 | Conductor | Overhead | Yes | 42584 | 2016-08-02 16:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0900 | 2016 | 8 | 2 | 16 | 15 | 16-0054552 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 265566 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-02 16:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-03 | 42585.1931 | 38.8474 | -120.812 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire garden valley fire | 103809676 |  | 21000 | Conductor | Overhead | Yes | 42585 | 2016-08-03 04:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0901 | 2016 | 8 | 3 | 4 | 38 | 16-0054597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2751 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-03 04:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-03 | 42585.5285 | 39.3269 | -120.6033 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100001032 |  | 12000 | Conductor | Overhead | Yes | 42585 | 2016-08-03 12:41 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0902 | 2016 | 8 | 3 | 12 | 41 | 16-0054769 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 20554 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-03 12:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-03 | 42585.8201 | 40.3868 | -122.2822 | Building | URBAN | Structure Only | Fire Agency | COTTONWOOD FIRE DEPT | 101492556 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42585 | 2016-08-03 19:41 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0903 | 2016 | 8 | 3 | 19 | 41 | 16-0054583 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 31093 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-03 19:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-04 | 42586.5132 | 35.9425 | -119.3844 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Tulare County Fire Dept. | 103074837 |  | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0904 | 2016 | 8 | 4 | 12 | 19 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-04 12:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-05 | 42587.5278 | 38.3407 | -122.2578 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 102284869 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42587 | 2016-08-05 12:40 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0905 | 2016 | 8 | 5 | 12 | 40 | 16-0055382 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 30041 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-05 12:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-05 | 42587.5292 | 38.4048 | -120.5292 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101244628 |  | 12000 | Conductor | Overhead | Yes | 42587 | 2016-08-05 12:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0906 | 2016 | 8 | 5 | 12 | 42 | 16-0055368 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 363 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-05 12:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-05 | 42587.6153 | 40.4797 | -123.7803 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103572261 |  | 12000 | Conductor | Overhead | Yes | 42587 | 2016-08-05 14:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0907 | 2016 | 8 | 5 | 14 | 46 | 16-0055425 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 7019 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-05 14:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-05 | 42587.8639 | 39.0249 | -122.6672 | Vegetation | RURAL | < 0.25 Acres | Customer | N.A. | 102154138 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42587 | 2016-08-05 20:44 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0908 | 2016 | 8 | 5 | 20 | 44 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-05 20:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-06 | 42588.7868 | 38.2819 | -122.3019 | Vegetation | RURAL | < 3 meters | Unknown | Unknown | 102277853 | PACIFIC BELL | 0 – 750 | Fuse | Overhead | No |  |  | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0909 | 2016 | 8 | 6 | 18 | 53 | 16-0055531 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-06 18:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-07 | 42589.5972 | 37.2316 | -122.1552 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire/woodside fire | 103413747 |  | 12000 | Conductor | Overhead | Yes | 42589 | 2016-08-07 14:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0910 | 2016 | 8 | 7 | 14 | 20 | 16-0055597 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29869 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-07 14:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-07 | 42589.9042 | 39.753 | -123.2362 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 102183401 | None | 12000 | Conductor | Overhead | Yes | 42589 | 2016-08-07 21:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0911 | 2016 | 8 | 7 | 21 | 42 | 16-0055617 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2556 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-07 21:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-08 | 42590.6556 | 37.1382 | -121.9672 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100519919 |  | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0912 | 2016 | 8 | 8 | 15 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-08 15:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-09 | 42591.4292 | 37.0575 | -119.9775 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101107871 |  | 0 – 750 | Conductor | Overhead | Yes | 42591 | 2016-08-09 10:18 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0913 | 2016 | 8 | 9 | 10 | 18 | 16-0055962 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 9928 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-09 10:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-09 | 42591.5875 | 37.3398 | -122.0111 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | sunnyvale fd | 100555160 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42591 | 2016-08-09 14:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | no-match | 0914 | 2016 | 8 | 9 | 14 | 6 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-09 14:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-09 | 42591.8063 | 38.9187 | -120.9525 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | El Dorado County FD | 100038028 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0915 | 2016 | 8 | 9 | 19 | 21 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-09 19:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-10 | 17:59 | 37.0856 | -121.0131 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Merced County FD | 103203955 |  | 12000 | Conductor | Overhead | Yes | 42592 | 0.74931 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0916 | 2016 | 8 | 10 | 17 | 59 | 16-0056395 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 20344 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-10 17:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-10 | 42592.3583 | 37.0575 | -121.9556 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 101680487 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0917 | 2016 | 8 | 10 | 8 | 36 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-10 08:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-10 | 42592.6431 | 36.8046 | -119.7687 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Fresno County FD | 100840914 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42592 | 2016-08-10 15:26 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0918 | 2016 | 8 | 10 | 15 | 26 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-10 15:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-11 | 42593.1736 | 38.9803 | -121.4147 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100021159 |  | 12000 | Conductor | Overhead | Yes | 42593 | 2016-08-11 04:10 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0919 | 2016 | 8 | 11 | 4 | 10 | 16-0056422 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 21353 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-11 04:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-11 | 42593.8319 | 36.737 | -119.4482 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Fresno County FD | 100774692 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42593 | 2016-08-11 19:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0920 | 2016 | 8 | 11 | 19 | 58 | 16-0056775 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 22712 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-11 19:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-11 | 42593.9132 | 39.7175 | -123.3369 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102180749 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42593 | 2016-08-11 21:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0921 | 2016 | 8 | 11 | 21 | 55 | 16-0056781 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1320 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-11 21:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-12 | 42594.4222 | 38.8751 | -122.4223 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 102168360 |  | 12000 | Conductor | Overhead | Yes | 42594 | 2016-08-12 10:08 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0922 | 2016 | 8 | 12 | 10 | 8 | 16-0056982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 1368 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-12 10:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-13 | 14:31 | 37.4642 | -119.8589 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire |  |  | 21000 | Conductor | Overhead | Yes | 42595 | 0.60486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0923 | 2016 | 8 | 13 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-13 14:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-13 | 42595.5833 | 39.2009 | -121.213 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100011376 | PACIFIC BELL | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0924 | 2016 | 8 | 13 | 14 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-13 14:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-14 | 42596.9514 | 37.4977 | -122.3701 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100307761 |  | 12000 | Conductor | Overhead | Yes | 42596 | 2016-08-14 22:50 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0925 | 2016 | 8 | 14 | 22 | 50 | 16-0057219 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4664 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-14 22:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-15 | 42597.0076 | 38.1974 | -121.1338 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | clements fire dept | 102075968 |  | 21000 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0926 | 2016 | 8 | 15 | 0 | 11 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-15 00:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-15 | 42597.4785 | 37.2773 | -121.809 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | San Jose FD | 100588534 | PACIFIC BELL | 21000 | Other | Overhead | Yes | 42597 | 2016-08-15 11:29 | Equipment/ Facility Failure | Recloser | N.A. | N.A. | Unknown |  | Other/Unknown | 0927 | 2016 | 8 | 15 | 11 | 29 | 16-0057375 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 49256 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-15 11:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-15 | 42597.6549 | 37.8784 | -120.4488 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101020079 |  | 17000 | Conductor | Overhead | Yes | 42597 | 2016-08-15 15:43 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0928 | 2016 | 8 | 15 | 15 | 43 | 16-0057465 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 122905 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-15 15:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-16 | 42598.5542 | 40.3417 | -123.8803 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | miranda/fruitland vol, calfire | 100990019 | None | 12000 | Conductor | Overhead | Yes | 42598 | 2016-08-16 13:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0929 | 2016 | 8 | 16 | 13 | 18 | 16-0057668 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 137 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-16 13:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-16 | 42598.9285 | 36.787 | -119.6957 | Vegetation | URBAN | < 3 meters | Fire Agency | CLOVIS FIRE DEPT | 100887618 |  | 12000 | Conductor | Overhead | Yes | 42598 | 2016-08-16 22:17 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0930 | 2016 | 8 | 16 | 22 | 17 | 16-0057751 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 18980 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-16 22:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-17 | 42599.4035 | 35.3709 | -118.9684 | Building | URBAN | Structure Only | Fire Agency | Kern County FD | 100162417 |  | 21000 | Transformer | Overhead | Yes | 42599 | 2016-08-17 09:41 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0931 | 2016 | 8 | 17 | 9 | 41 | 16-0057860 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 9889 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-17 09:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-17 | 42599.516 | 41.2495 | -123.7671 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103315791 |  | 12000 | Conductor | Overhead | Yes | 42599 | 2016-08-17 12:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0932 | 2016 | 8 | 17 | 12 | 23 | 16-0058002 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 16544 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-17 12:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-17 | 42599.5847 | 39.6361 | -121.7479 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 100437069 |  | 60000 | Conductor | Overhead | Yes | 42599 | 2016-08-17 14:02 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | no-match | 0933 | 2016 | 8 | 17 | 14 | 2 | INT-08353 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-17 14:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-17 | 42599.7757 | 37.3078 | -119.6511 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101020932 |  | 21000 | Conductor | Overhead | Yes | 42599 | 2016-08-17 18:37 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0934 | 2016 | 8 | 17 | 18 | 37 | 16-0058019 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 59379 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-17 18:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-18 | 42600.6403 | 36.6187 | -119.4439 | Vegetation | RURAL | < 3 meters | Self Extinguished | N.A. | 100826791 | VERIZON CALIFORNIA I | 0 – 750 | Conductor | Overhead | Yes | 42600 | 2016-08-18 15:22 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0935 | 2016 | 8 | 18 | 15 | 22 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-18 15:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-18 | 42600.7583 | 37.5956 | -122.0865 | Vegetation | URBAN | < 3 meters | Fire Agency | union city fd | 100935109 | PACIFIC BELL | 0 – 750 | Fuse | Overhead | No |  |  | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 0936 | 2016 | 8 | 18 | 18 | 12 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-18 18:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-18 | 42600.775 | 36.9701 | -121.546 | Vegetation | RURAL | < 3 meters | Fire Agency | Santa Clara county fire | 103553473 |  | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0937 | 2016 | 8 | 18 | 18 | 36 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-18 18:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-19 | 42601.6826 | 39.2235 | -123.755 | Vegetation | RURAL | < 3 meters | Fire Agency | Albion-Little River FD | 102206661 |  | 12000 | Conductor | Overhead | Yes | 42601 | 2016-08-19 16:23 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0938 | 2016 | 8 | 19 | 16 | 23 | 16-0058677 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 95106 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-19 16:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-20 18:51 | 42602.7854 | 36.458 | -119.3472 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Merced County FD | 100729153 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42602.7854 | 2016-08-20 18:51 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0939 | 2016 | 8 | 20 | 18 | 51 | 16-0058782 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 53146 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-20 18:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-21 | 42603.5431 | 38.4445 | -122.2496 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102291451 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42603 | 2016-08-21 13:02 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0940 | 2016 | 8 | 21 | 13 | 2 | 16-0058847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 12780 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-21 13:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-22 | 42604.6736 | 37.9666 | -120.2395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Toulumne City FD | 101043683 |  | 17000 | Conductor | Overhead | Yes | 42604 | 2016-08-22 16:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0941 | 2016 | 8 | 22 | 16 | 10 | 16-0059149 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 78534 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-22 16:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-23 | 42605.6687 | 36.8741 | -119.6865 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 100731257 | None | 0 – 750 | Conductor | Overhead | Yes | 42605 | 2016-08-23 16:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0942 | 2016 | 8 | 23 | 16 | 3 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-23 16:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-24 | 42606.5076 | 36.4633 | -121.712 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101750810 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42606 | 2016-08-24 12:11 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0943 | 2016 | 8 | 24 | 12 | 11 | 16-0059702 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 232770 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-24 12:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-24 | 42606.5965 | 36.8457 | -119.8793 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Fresno FD | 103277500 |  | 21000 | Conductor | Overhead | Yes | 42606 | 2016-08-24 14:19 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0944 | 2016 | 8 | 24 | 14 | 19 | 16-0059751 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 40792 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-24 14:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-25 | 42607.5028 | 36.9726 | -119.3816 | Vegetation | RURAL | < 3 meters | Utility: PG&E | N.A. | 100651318 | PONDEROSA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0945 | 2016 | 8 | 25 | 12 | 4 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-25 12:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-25 11:31 | 11:31 | 37.3734 | -122.087 | Vegetation | URBAN | < 3 meters | Self Extinguished | N.A. | 100516445 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42607.4799 | 0.47986 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0946 | 2016 | 8 | 25 | 11 | 31 | 16-0059987 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-08-25 11:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-27 | 42609.234 | 36.0439 | -120.1117 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Kings County FD | 103246130 |  | 70000 | Conductor | Overhead | Yes | 42609 | 2016-08-27 05:37 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0947 | 2016 | 8 | 27 | 5 | 37 | FR-2016-057 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 0 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-27 05:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-27 | 42609.8146 | 36.9646 | -122.0529 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | SC FIRE DEPT & CDF | 101677596 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42609 | 2016-08-27 19:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0948 | 2016 | 8 | 27 | 19 | 33 | 16-0060408 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 845830 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-27 19:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-28 | 42610.7007 | 36.5619 | -119.7186 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100683911 |  | 12000 | Conductor | Overhead | Yes | 42610 | 2016-08-28 16:49 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0949 | 2016 | 8 | 28 | 16 | 49 | 16-0060527 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 56167 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-28 16:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-29 | 42611.684 | 38.2693 | -121.6029 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | SAC FIRE | 101583637 | FRONTIER | 21000 | Conductor | Overhead | Yes | 42611 | 2016-08-29 16:25 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error |  | Other/Unknown | 0950 | 2016 | 8 | 29 | 16 | 25 | 16-0060839 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 38936 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-29 16:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-30 | 42612.6674 | 36.5941 | -121.9212 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Unknown | 101734977 |  | 21000 | Conductor | Overhead | Yes | 42612 | 2016-08-30 16:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0951 | 2016 | 8 | 30 | 16 | 1 | 16-0061130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 199327 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-30 16:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-30 | 42612.6764 | 38.0575 | -122.1639 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Benicia FD | 102264159 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42612 | 2016-08-30 16:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0952 | 2016 | 8 | 30 | 16 | 14 | 16-0061132 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 42301 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-30 16:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-30 | 42612.8104 | 39.9288 | -122.1277 | Vegetation | RURAL | < 0.25 Acres | Unknown | Unknown | 103165395 | Yes | 12000 | Conductor | Overhead | Yes | 42612 | 2016-08-30 19:27 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0953 | 2016 | 8 | 30 | 19 | 27 | 16-0061164 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 153120 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-30 19:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-31 | 42613.4701 | 37.3721 | -120.4504 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Merced County FD | 101147802 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42613 | 2016-08-31 11:17 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0954 | 2016 | 8 | 31 | 11 | 17 | 16-0061199 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 44460 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-31 11:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-31 | 42613.6194 | 35.1918 | -120.4697 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101942860 |  | 12000 | Conductor | Overhead | Yes | 42613 | 2016-08-31 14:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0955 | 2016 | 8 | 31 | 14 | 52 | 16-0061423 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 156294 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-31 14:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-08-31 | 42613.8215 | 38.151 | -121.6804 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | ISLETON | 101665829 | FRONTIER | 21000 | Conductor | Overhead | Yes | 42613 | 2016-08-31 19:43 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0956 | 2016 | 8 | 31 | 19 | 43 | 16-0061468 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 31771 | 0 | NA | <25mph | <15mph | #REF! | 2016-08-31 19:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-01 | 9:30 | 37.2814 | -121.8603 | Vegetation | URBAN | < 3 meters | Customer | N.A. | 100617565 | None | 21000 | Conductor | Overhead | Yes | 42614 | 0.39583 | Contact from Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0957 | 2016 | 9 | 1 | 9 | 30 | 16-0061639 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 419257 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-01 09:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-01 | 13:08 | 38.4633 | -122.8162 | Vegetation | RURAL | < 3 meters | Fire Agency | WINDSOR AND SANTA ROSA FIRE | 101956270 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42614 | 0.54722 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0958 | 2016 | 9 | 1 | 13 | 8 | 16-0061732 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 16115 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-01 13:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-02 | 12:42 | 38.3868 | -122.7555 | Vegetation | RURAL | < 3 meters | Fire Agency | Santa Rosa FD | 101969369 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42615 | 0.52917 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0959 | 2016 | 9 | 2 | 12 | 42 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-09-02 12:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-02 | 13:50 | 37.6681 | -121.7681 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | LPFD | 100954399 |  | 21000 | Conductor | Overhead | Yes | 42615 | 0.57639 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | no-match | 0960 | 2016 | 9 | 2 | 13 | 50 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-09-02 13:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-03 | 20:12 | 39.3223 | -121.9849 | Vegetation | RURAL | < 3 meters | Unknown | Unknown | 101614478 |  | 12000 | Conductor | Overhead | Yes | 42616 | 0.84167 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0961 | 2016 | 9 | 3 | 20 | 12 | 16-0062160 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 29255 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-03 20:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-03 | 20:58 | 36.8081 | -119.6279 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Unknown | 103269240 |  | 12000 | Conductor | Overhead | Yes | 42616 | 0.87361 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0962 | 2016 | 9 | 3 | 20 | 58 | 16-0062289 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 1872 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-03 20:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-05 | 8:26 | 39.5233 | -122.1462 | Vegetation | RURAL | < 0.25 Acres | Unknown | Unknown | 100430821 |  | 21000 | Conductor | Overhead | Yes | 42618 | 0.35139 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0963 | 2016 | 9 | 5 | 8 | 26 | 16-0062379 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1844 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-05 08:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-07 | 19:37 | 37.9921 | -122.5445 | Vegetation | URBAN | < 3 meters | Fire Agency | San Rafael FD | 102249944 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42620 | 0.81736 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0964 | 2016 | 9 | 7 | 19 | 37 | 16-0063035 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 185 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-07 19:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-07 09:56 | 42620.4139 | 39.5528 | -121.6416 | Vegetation | RURAL | .26 - 9.99 Acres | Unknown | Unknown | 103653028 |  | 60000 | Conductor | Overhead | Yes | 42620.4139 | 2016-09-07 09:56 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0965 | 2016 | 9 | 7 | 9 | 56 | INT-08510 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 51660 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-07 09:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-08 | 14:39 | 38.0013 | -122.329 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | PINOLE FIRE DEPT | 101426911 |  | 12000 | Conductor | Overhead | Yes | 42621 | 0.61042 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0966 | 2016 | 9 | 8 | 14 | 39 | 16-0063300 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2670 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-08 14:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-08 | 22:04 | 37.2918 | -121.8711 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | San Jose FD | 100598024 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42621 | 0.91944 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0967 | 2016 | 9 | 8 | 22 | 4 | 16-0063340 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-09-08 22:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-09 | 10:57 | 36.8517 | -119.6225 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Fresno County FD | 100746408 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42622 | 0.45625 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0968 | 2016 | 9 | 9 | 10 | 57 | 16-0063497 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 338 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-09 10:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-09 | 13:22 | 37.2837 | -120.4741 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Cal Fire | 101018780 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42622 | 0.55694 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0969 | 2016 | 9 | 9 | 13 | 22 | 16-0063538 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 528 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-09 13:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-09 | 15:25 | 38.9202 | -121.0859 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Cal Fire | 100036304 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | Yes | 42622 | 0.64236 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0970 | 2016 | 9 | 9 | 15 | 25 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-09-09 15:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-10 | 2:09 | 37.1862 | -120.6775 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Merced County FD | 101072400 |  | 12000 | Conductor | Overhead | Yes | 42623 | 0.089583 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0971 | 2016 | 9 | 10 | 2 | 9 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-09-10 02:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-11 21:24 | 21:24 | 36.9526 | -119.7263 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Unknown | 100652942 |  | 21000 | Unknown | Overhead | Yes | 42624.8917 | 0.89167 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0972 | 2016 | 9 | 11 | 21 | 24 | 16-0063814 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 192 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-11 21:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-12 | 4:24 | 36.3999 | -121.902 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire Hwy 1 Carmel Hill | 101669614 |  | 12000 | Conductor | Overhead | Yes | 42625 | 0.18333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0973 | 2016 | 9 | 12 | 4 | 24 | 16-0063826 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 130604 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-12 04:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-12 | 12:38 | 38.7832 | -120.6006 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101421708 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42625 | 0.52639 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0974 | 2016 | 9 | 12 | 12 | 38 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-09-12 12:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-12 | 18:47 | 36.5303 | -119.3056 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CUTLER FIRE | 100807630 | None | 12000 | Conductor | Overhead | Yes | 42625 | 0.78264 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0975 | 2016 | 9 | 12 | 18 | 47 | 16-0064064 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 66571 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-12 18:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-12 | 20:42 | 37.355 | -121.9355 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Santa Clara county fire | 100608192 |  | 12000 | Conductor | Overhead | Yes | 42625 | 0.8625 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0976 | 2016 | 9 | 12 | 20 | 42 | 16-0064074 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 11743 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-12 20:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-12 15:08 | 42625.6306 | 39.5256 | -123.7655 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102185070 |  | 12000 | Conductor | Overhead | Yes | 42625.6306 | 2016-09-12 15:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0977 | 2016 | 9 | 12 | 15 | 8 | 16-0064050 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 428 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-12 15:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-13 | 10:26 | 39.1913 | -121.1819 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100082849 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42626 | 0.43472 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0978 | 2016 | 9 | 13 | 10 | 26 | 16-0064270 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 4114 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-13 10:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-13 10:45 | 42626.4479 | 40.2958 | -122.1318 | Vegetation | RURAL | 300 - 999 Acres | Fire Agency | Cal Fire | 103702175 |  | 60000 | Conductor | Overhead | Yes | 2016-09-13 10:45 | 2016-09-13 10:45 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0979 | 2016 | 9 | 13 | 10 | 45 | INT-08528 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-13 10:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-14 | 21:16 | 37.3447 | -121.0765 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | STANISLUAS COUNTY | 101228545 | None | 12000 | Conductor | Overhead | Yes | 42627 | 0.88611 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gunshot | Other/Unknown | 0980 | 2016 | 9 | 14 | 21 | 16 | 16-0064782 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6428 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-14 21:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-14 | 23:25 | 39.4796 | -121.8575 | Vegetation | RURAL | < 0.25 Acres | Unknown | Unknown | 101618097 |  | 12000 | Conductor | Overhead | Yes | 42627 | 0.97569 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0981 | 2016 | 9 | 14 | 23 | 25 | 16-0064404 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1080 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-14 23:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-15 | 15:56 | 37.1102 | -121.9509 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100520198 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42628 | 0.66389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0982 | 2016 | 9 | 15 | 15 | 56 | 16-0065001 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 28900 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-15 15:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-16 20:56 | 42629.8722 | 39.8387 | -121.7023 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 100441760 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42629.8722 | 2016-09-16 20:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0983 | 2016 | 9 | 16 | 20 | 56 | 16-0065273 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 314427 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-16 20:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-17 10:03 | 10:03 | 38.0495 | -121.0143 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Unknown | 102123492 |  | 12000 | Fuse | Overhead | Yes | 42630.4187 | 0.41875 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0984 | 2016 | 9 | 17 | 10 | 3 | 16-0065332 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 368 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-17 10:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-17 17:47 | 17:47 | 37.1012 | -120.1289 | Vegetation | RURAL | < 3 meters | Fire Agency | Unknown | 101062487 |  | 12000 | Conductor | Overhead | Yes | 42630.741 | 0.74097 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0985 | 2016 | 9 | 17 | 17 | 47 | 16-0065353 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 50747 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-17 17:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-18 | 14:33 | 37.1619 | -122.1347 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire & Boulder Creek Fire Dept. | 103410909 | Yes | 12000 | Conductor | Overhead | Yes | 42631 | 0.60625 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0986 | 2016 | 9 | 18 | 14 | 33 | 16-0065437 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 54983 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-18 14:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-19 | 14:09 | 37.9459 | -122.372 | Vegetation | RURAL | < 3 meters | Fire Agency | Unknown | 101433385 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42632 | 0.58958 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0987 | 2016 | 9 | 19 | 14 | 9 | 16-0065738 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 199082 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-19 14:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-19 | 22:10 | 37.9653 | -121.2579 | Vegetation | URBAN | < 3 meters | Fire Agency | STOCKTON FIRE | 102057961 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42632 | 0.92361 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0988 | 2016 | 9 | 19 | 22 | 10 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-09-19 22:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-19 08:51 | 42632.3688 | 35.4459 | -119.0919 | Vegetation | RURAL | < 0.25 Acres | Self Extinguished | N.A. | 103239256 |  | 115000 | Conductor | Overhead | Yes | 42632.3688 | 2016-09-19 08:51 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0989 | 2016 | 9 | 19 | 8 | 51 | INT-08547 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-19 08:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-20 | 8:25 | 40.0044 | -123.7871 | Vegetation | RURAL | < 3 meters | Self Extinguished | N.A. | 100992643 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42633 | 0.35069 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0990 | 2016 | 9 | 20 | 8 | 25 | 16-0065910 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 798 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-20 08:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-21 | 10:01 | 39.1173 | -121.071 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100014315 | PACIFIC BELL | 115000 | Conductor | Overhead | Yes | 42634 | 0.41736 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0991 | 2016 | 9 | 21 | 10 | 1 | INT-08560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-21 10:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-21 | 19:11 | 38.7872 | -123.5577 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire Point Arena & Gualala Fir | 103325552 |  | 12000 | Conductor | Overhead | Yes | 42634 | 0.79931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0992 | 2016 | 9 | 21 | 19 | 11 | 16-0066397 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 11655 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-21 19:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-21 | 21:00 | 38.8234 | -122.2045 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 101591523 |  | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0993 | 2016 | 9 | 21 | 21 | 0 | 16-0066437 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 473 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-21 21:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-21 | 42634.275 | 38.2313 | -122.0635 | Vegetation | RURAL | < 0.25 Acres | Unknown | Unknown | 101563903 | PACIFIC BELL | 12000 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0994 | 2016 | 9 | 21 | 6 | 36 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-09-21 06:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-22 | 8:27 | 38.9498 | -121.0817 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100036441 |  | 0 – 750 | Capacitor Bank | Overhead | Yes | 42635 | 0.35208 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0995 | 2016 | 9 | 22 | 8 | 27 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-09-22 08:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-22 | 13:53 | 40.224 | -122.3417 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101539450 | None | 12000 | Conductor | Overhead | Yes | 42635 | 0.57847 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0996 | 2016 | 9 | 22 | 13 | 53 | 16-0066692 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 14706 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-22 13:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-22 11:06 | 42635.4625 | 38.6353 | -122.8509 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103142538 |  | 12000 | Conductor | Overhead | Yes | 42635.4625 | 2016-09-22 11:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0997 | 2016 | 9 | 22 | 11 | 6 | 16-0066640 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1875 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-22 11:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-23 | 15:13 | 36.8498 | -119.8613 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Fresno FD | 100633830 | None | 12000 | Conductor | Overhead | Yes | 42636 | 0.63403 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0998 | 2016 | 9 | 23 | 15 | 13 | 16-0067099 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-09-23 15:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-23 05:23 | 15:23 | 39.3784 | -121.0922 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100091491 | None | 12000 | Conductor | Overhead | Yes | 42636.2243 | 0.64097 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0999 | 2016 | 9 | 23 | 15 | 23 | 16-0067089 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 80185 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-23 15:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-24 | 14:32 | 36.9115 | -121.3668 | Vegetation | RURAL | < 3 meters | Fire Agency | Hollister Fire | 101703542 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42637 | 0.60556 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1000 | 2016 | 9 | 24 | 14 | 32 | 16-0067228 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-09-24 14:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-25 | 12:13 | 39.34 | -121.9144 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | GLENN COLUSA FIRE | 101640793 |  | 12000 | Conductor | Overhead | Yes | 42638 | 0.50903 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1001 | 2016 | 9 | 25 | 12 | 13 | 16-0067326 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 10944 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-25 12:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-25 | 16:29 | 36.7231 | -119.7184 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | FFD #8 | 100815478 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42638 | 0.68681 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 1002 | 2016 | 9 | 25 | 16 | 29 | 16-0067334 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 96586 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-25 16:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-25 | 19:19 | 37.0993 | -122.1155 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire ben lomond fire | 101670837 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42638 | 0.80486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1003 | 2016 | 9 | 25 | 19 | 19 | 16-0067346 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1497 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-25 19:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-25 10:35 | 42638.441 | 38.8019 | -122.8176 | Vegetation | RURAL | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103613996 |  | 115000 | Other | Overhead | Yes | 2016-09-25 10:35 | 2016-09-25 10:35 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1004 | 2016 | 9 | 25 | 10 | 35 | INT-08572 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | Equip Failure | #REF! | 0 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-25 10:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-26 | 10:40 | 38.0157 | -122.6889 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | marin county fire | 102252082 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42639 | 0.44444 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1005 | 2016 | 9 | 26 | 10 | 40 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-09-26 10:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-27 | 12:28 | 37.8764 | -122.5264 | Vegetation | URBAN | < 3 meters | Fire Agency | Sounth Marin | 102277447 |  | 12000 | Conductor | Overhead | Yes | 42640 | 0.51944 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1006 | 2016 | 9 | 27 | 12 | 28 | 16-0067841 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 4920 | 0 | NA | <25mph | <15mph | #REF! | 2016-09-27 12:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-28 | 5:30 | 38.0972 | -121.3178 | Vegetation | RURAL | < 3 meters | Fire Agency | LODI FIRE | 102107151 |  | 0 – 750 | Capacitor Bank | Overhead | Yes | 42641 | 0.22917 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | Other/Unknown | 1007 | 2016 | 9 | 28 | 5 | 30 | 16-0068010 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-09-28 05:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-28 | 14:00 | 35.2145 | -118.5625 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire |  |  | 0 – 750 | Conductor | Overhead | Yes | 42641 | 0.58333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1008 | 2016 | 9 | 28 | 14 | 0 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-09-28 14:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-28 | 16:21 | 37.1465 | -121.6673 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Cal Fire | 100601627 |  | 21000 | Conductor | Overhead | Yes | 42641 | 0.68125 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 1009 | 2016 | 9 | 28 | 16 | 21 | 16-0068262 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-09-28 16:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-09-29 | 11:17 | 38.0178 | -121.6484 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Contra Costa County FD | 100457240 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42642 | 0.47014 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1010 | 2016 | 9 | 29 | 11 | 17 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-09-29 11:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-01 15:29 | 15:19 | 39.4384 | -120.816 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | State goverment forestry | 100112411 |  | 12000 | Conductor | Overhead | Yes | 42644.6455 | 0.63819 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1011 | 2016 | 10 | 1 | 15 | 19 | 16-0068934 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6157 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-01 15:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-02 15:51 | 15:51 | 38.2131 | -122.1338 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Fairfield FD | 101563172 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 42645.6605 | 0.66042 | Contamination | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1012 | 2016 | 10 | 2 | 15 | 51 | 16-0069049 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 6611 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-02 15:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-02 16:41 | 16:41 | 39.8888 | -121.6648 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103358082 |  | 12000 | Other | Overhead | Yes | 42645.6954 | 0.69514 | Other | N.A. | N.A. | N.A. | Weather | lightning strike | Other/Unknown | 1013 | 2016 | 10 | 2 | 16 | 41 | 16-0069050 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 339550 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-02 16:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-03 17:39 | 18:23 | 34.5967 | -120.0921 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Santa Barbara County FD | 101895043 |  | 12000 | Conductor | Overhead | Yes | 42646.7356 | 0.76597 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1014 | 2016 | 10 | 3 | 18 | 23 | 16-0069410 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3231 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-03 18:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-04 02:04 | 2:04 | 38.0665 | -122.1961 | Vegetation | URBAN | .26 - 9.99 Acres | Unknown | Unknown | 103773890 |  | 21000 | Conductor | Overhead | Yes | 42647.0861 | 0.086111 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1015 | 2016 | 10 | 4 | 2 | 4 | 16-0069438 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 454368 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-04 02:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-04 12:50 | 12:50 | 35.2089 | -119.2352 | Vegetation | RURAL | < 3 meters | Fire Agency | County | 103261612 |  | 12000 | Conductor | Overhead | Yes | 42647.5347 | 0.53472 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 1016 | 2016 | 10 | 4 | 12 | 50 | 16-0069605 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 2619 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-04 12:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-05 16:24 | 16:23 | 35.2964 | -118.7765 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Kern County FD | 100187871 |  | 12000 | Conductor | Overhead | Yes | 42648.6831 | 0.68264 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1017 | 2016 | 10 | 5 | 16 | 23 | 16-0069972 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1344 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-05 16:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-06 22:07 | 22:06 | 35.4378 | -119.6873 | Vegetation | RURAL | < 0.25 Acres | Utility: PG&E | N.A. | 100162148 |  | 21000 | Conductor | Overhead | Yes | 42649.9215 | 0.92083 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1018 | 2016 | 10 | 6 | 22 | 6 | 16-0070260 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 10243 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-06 22:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-07 08:17 | 8:17 | 37.9891 | -121.045 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Linden- Peters Fire Department | 102119967 |  | 0 – 750 | Transformer | Overhead | Yes | 42650.3453 | 0.34514 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1019 | 2016 | 10 | 7 | 8 | 17 | 16-0070296 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 441 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-07 08:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-08 06:52 | 6:52 | 39.5717 | -121.7296 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100396647 |  | 12000 | Conductor | Overhead | Yes | 42651.2861 | 0.28611 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1020 | 2016 | 10 | 8 | 6 | 52 | 16-0070518 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 26123 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-08 06:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-08 15:05 | 15:04 | 38.6686 | -120.9091 | Vegetation | RURAL | < 0.25 Acres | Customer | N.A. | 101380856 |  | 0 – 750 | Capacitor Bank | Overhead | Yes | 42651.6284 | 0.62778 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1021 | 2016 | 10 | 8 | 15 | 4 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-10-08 15:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-08 16:31 | 16:31 | 39.0099 | -122.6145 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102152342 |  | 0 – 750 | Transformer | Overhead | Yes | 42651.6884 | 0.68819 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1022 | 2016 | 10 | 8 | 16 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-10-08 16:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-09 07:44 | 7:43 | 37.5362 | -120.4669 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 101197077 |  | 0 – 750 | Conductor | Overhead | Yes | 42652.322 | 0.32153 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1023 | 2016 | 10 | 9 | 7 | 43 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-10-09 07:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-09 18:52 | 18:52 | 38.656 | -120.9725 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101376768 |  | 12000 | Conductor | Overhead | Yes | 42652.7862 | 0.78611 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1024 | 2016 | 10 | 9 | 18 | 52 | 16-0070676 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 98361 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-09 18:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-09 22:48 | 22:47 | 38.2059 | -121.8889 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | MONTEZUMA FIRE DISTRICT | 101662848 |  | 21000 | Conductor | Overhead | Yes | 42652.9499 | 0.94931 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1025 | 2016 | 10 | 9 | 22 | 47 | 16-0070703 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 40275 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-09 22:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-10 10:07 | 10:06 | 38.4756 | -122.9079 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103002919 |  | 12000 | Conductor | Overhead | Yes | 42653.4212 | 0.42083 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1026 | 2016 | 10 | 10 | 10 | 6 | 16-0070811 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 672 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-10 10:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-11 11:30 | 11:30 | 36.8024 | -119.8102 | Vegetation | URBAN | < 3 meters | Fire Agency | Unknown | 100857712 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42654.4794 | 0.47917 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1027 | 2016 | 10 | 11 | 11 | 30 | 16-0071132 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 5772 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-11 11:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-11 23:17 | 23:16 | 39.0201 | -120.8294 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire.foresthill fire | 100025501 |  | 60000 | Conductor | Overhead | Yes | 42654.9701 | 0.96944 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error |  | no-match | 1028 | 2016 | 10 | 11 | 23 | 16 | INT-08640 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 0 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-11 23:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-13 23:23 | 23:14 | 40.4901 | -122.3729 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | SHASTA COUNTY FIRE | 101502366 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42656.9745 | 0.96806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1029 | 2016 | 10 | 13 | 23 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-10-13 23:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-13 23:52 | 23:52 | 39.7545 | -122.2008 | Building | URBAN | Structure Only | Fire Agency | CITY OF ORLAND | 100361735 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42656.9945 | 0.99444 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1030 | 2016 | 10 | 13 | 23 | 52 | 16-0071806 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | 52128 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-13 23:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-14 01:33 | 1:32 | 40.5007 | -121.9162 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101489328 |  | 12000 | Conductor | Overhead | Yes | 42657.0644 | 0.063889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1031 | 2016 | 10 | 14 | 1 | 32 | 16-0071832 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 213622 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-14 01:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-14 04:33 | 4:32 | 40.5228 | -121.6813 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101513661 |  | 12000 | Conductor | Overhead | Yes | 42657.1893 | 0.18889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1032 | 2016 | 10 | 14 | 4 | 32 | 16-0071897 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 38950 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-14 04:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-14 10:24 | 10:24 | 37.7449 | -121.9368 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Contra Costa County FD | 100902256 |  | 21000 | Other | Overhead | Yes | 42657.4335 | 0.43333 | Contamination | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1033 | 2016 | 10 | 14 | 10 | 24 | 16-0072155 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 1116505 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-14 10:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-14 10:36 | 10:36 | 37.7438 | -121.934 | Vegetation | URBAN | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100902265 |  | 0 – 750 | Conductor | Overhead | Yes | 42657.4418 | 0.44167 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | no-match | 1034 | 2016 | 10 | 14 | 10 | 36 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-10-14 10:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-14 11:00 | 11:00 | 38.8962 | -121.5892 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | placer | 101334896 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 42657.4584 | 0.45833 | Contamination | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1035 | 2016 | 10 | 14 | 11 | 0 | 16-0072081 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 1464 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-14 11:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-14 19:45 | 19:44 | 39.6245 | -121.5382 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100435570 |  | 0 – 750 | Conductor | Overhead | Yes | 42657.8228 | 0.82222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1036 | 2016 | 10 | 14 | 19 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-10-14 19:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-15 15:35 | 15:34 | 37.3255 | -120.311 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101142010 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42658.649 | 0.64861 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1037 | 2016 | 10 | 15 | 15 | 34 | 16-0072586 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4298 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-15 15:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-18 10:50 | 10:50 | 37.2999 | -120.7294 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Unknown | 101166039 |  | 12000 | Conductor | Overhead | Yes | 42661.4514 | 0.45139 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1038 | 2016 | 10 | 18 | 10 | 50 | 16-0073608 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 558 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-18 10:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-18 16:21 | 16:20 | 38.4712 | -122.6569 | Vegetation | URBAN | < 3 meters | Fire Agency | CITY OF SANTA ROSA | 101966406 |  | 0 – 750 | Conductor | Overhead | Yes | 42661.6812 | 0.68056 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | no-match | 1039 | 2016 | 10 | 18 | 16 | 20 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-10-18 16:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-19 10:42 | 10:42 | 38.5098 | -122.45 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | st helena | 102242552 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42662.4459 | 0.44583 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1040 | 2016 | 10 | 19 | 10 | 42 | 16-0073955 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 693 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-19 10:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-23 10:55 | 10:54 | 35.5545 | -120.6708 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101901785 |  | 21000 | Conductor | Overhead | Yes | 42666.4548 | 0.45417 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1041 | 2016 | 10 | 23 | 10 | 54 | 16-0074816 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-10-23 10:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-23 14:16 | 14:16 | 38.2271 | -121.0495 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 102074335 | VERIZON CALIFORNIA I | 21000 | Conductor | Overhead | Yes | 42666.5947 | 0.59444 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 1042 | 2016 | 10 | 23 | 14 | 16 | 16-0074827 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 8664 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-23 14:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-23 18:44 | 18:10 | 38.021 | -120.5991 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101272943 |  | 115000 | Conductor | Overhead | Yes | 42666.7804 | 0.75694 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1043 | 2016 | 10 | 23 | 18 | 10 | INT-08709 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 0 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-23 18:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-26 10:17 | 10:16 | 37.1199 | -120.3113 | Vegetation | RURAL | < 3 meters | Fire Agency | Chowchilla FD | 101129171 |  | 12000 | Conductor | Overhead | Yes | 42669.4284 | 0.42778 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1044 | 2016 | 10 | 26 | 10 | 16 | 16-0075606 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 600 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-26 10:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-10-31 17:04 | 17:04 | 36.6638 | -119.7463 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Fresno County FD | 100808306 |  | 12000 | Conductor | Overhead | Yes | 42674.7114 | 0.71111 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1045 | 2016 | 10 | 31 | 17 | 4 | 16-0077078 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1430 | 0 | NA | <25mph | <15mph | #REF! | 2016-10-31 17:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-11-09 | 9:06 | 37.4532 | -119.6413 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | US FOREST SERVICE | 101017062 |  | 12000 | Conductor | Overhead | Yes | 42683 | 0.37917 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1046 | 2016 | 11 | 9 | 9 | 6 | 16-0078863 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1586 | 0 | NA | <25mph | <15mph | #REF! | 2016-11-09 09:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-11-14 | 3:25 | 35.4397 | -120.8902 | Vegetation | URBAN | < 3 meters | Fire Agency | Cayucos fire | 101853338 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42688 | 0.14236 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1047 | 2016 | 11 | 14 | 3 | 25 | 16-0079568 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2016-11-14 03:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-11-14 | 13:15 | 35.4577 | -120.4619 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101895511 |  | 21000 | Conductor | Overhead | Yes | 42688 | 0.55208 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1048 | 2016 | 11 | 14 | 13 | 15 | 16-0079725 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 19590 | 0 | NA | <25mph | <15mph | #REF! | 2016-11-14 13:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-11-15 | 17:27 | 39.7275 | -121.6557 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100327525 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42689 | 0.72708 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 1049 | 2016 | 11 | 15 | 17 | 27 | 16-0080083 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 69231 | 0 | NA | <25mph | <15mph | #REF! | 2016-11-15 17:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-11-20 | 11:04 | 39.6326 | -123.7823 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102200173 |  | 12000 | Conductor | Overhead | Yes | 42694 | 0.46111 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1050 | 2016 | 11 | 20 | 11 | 4 | 16-0081252 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 87261 | 0 | NA | <25mph | <15mph | #REF! | 2016-11-20 11:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2016-11-26 | 12:10 | 35.3221 | -118.7808 | Vegetation | RURAL | < 0.25 Acres | Utility: PG&E | N.A. | 102300399 |  | 12000 | Conductor | Overhead | Yes | 42700 | 0.50694 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1051 | 2016 | 11 | 26 | 12 | 10 | 16-0082281 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 56819 | 0 | NA | <25mph | <15mph | #REF! | 2016-11-26 12:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-01-01 15:59 | 15:57 | 38.6629 | -121.748 | Vegetation | Urban | < 3 Meters | Fire Agency | Woodland fire dept 530-666-8920 | 101589774 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42736.6661 | 0.66458 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1052 | 2017 | 1 | 1 | 15 | 57 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-01-01 15:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-01-10 | 15:55 | 38.7538 | -121.1564 | Building | Urban | Structure Only | Unknown | N.A. | 100065079 | Unknown | 12000 | Conductor | Overhead | Yes | 42745 | 0.66319 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1053 | 2017 | 1 | 10 | 15 | 55 | 17-0006950 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 334100 | 0 | NA | <25mph | <15mph | #REF! | 2017-01-10 15:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-01-18 | 15:34 | 37.3839 | -121.8088 | Building | Urban | Structure Only | Unknown | N.A. | 100564835 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42753 | 0.64861 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1054 | 2017 | 1 | 18 | 15 | 34 | 17-0010936 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 13560 | 0 | NA | <25mph | <15mph | #REF! | 2017-01-18 15:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-01-29 09:46 | 09:45 | 38.3616 | -121.9509 | Building | Urban | Structure Only | Fire Agency | Unknown | T8550 | Unknown | 12000 | Transformer | Subsurface | Yes | 42764.4067 | 09:45 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1055 | 2017 | 1 | 29 | 9 | 45 | 17-0015899 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 10815 | 0 | NA | <25mph | <15mph | #REF! | 2017-01-29 09:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-02-03 10:01 | 10:00 | 37.5615 | -122.0277 | Vegetation | Urban | < 3 Meters | Fire Agency | jeff | 100938466 | Unknown | 12000 | Conductor | Overhead | Yes | 42769.4171 | 10:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1056 | 2017 | 2 | 3 | 10 | 0 | 17-0017171 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 120338 | 0 | NA | <25mph | <15mph | #REF! | 2017-02-03 10:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-02-07 04:50 | 04:50 | 38.4331 | -122.719 | Building | Urban | Structure Only | Fire Agency | Santa Rosa Fire Dept | 102014637 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42773.2017 | 04:50 | Other | N.A. | N.A. | N.A. | Unknown |  | Fell into (No defect) | 1057 | 2017 | 2 | 7 | 4 | 50 | 17-0018145 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 395582 | 0 | NA | <25mph | <15mph | #REF! | 2017-02-07 04:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-03-16 12:44 | 12:43 | 38.2718 | -122.0197 | Other | Urban | < 0.25 Acres | Fire Agency | Unknown | 101561532 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42810.5305 | 12:43 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1058 | 2017 | 3 | 16 | 12 | 43 | 17-0031293 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 394022 | 0 | NA | <25mph | <15mph | #REF! | 2017-03-16 12:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-03-17 09:37 | 09:37 | 38.1153 | -121.4222 | Other | Rural | Structure Only | Fire Agency | 911 | 102044732 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42811.4009 | 09:37 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1059 | 2017 | 3 | 17 | 9 | 37 | 17-0031464 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 48151 | 0 | NA | <25mph | <15mph | #REF! | 2017-03-17 09:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-03-19 17:06 | 17:06 | 39.7621 | -121.8525 | Vegetation | Urban | < 3 Meters | Fire Agency | CHICO FIRE DEPT 911 | 100441377 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42813.7128 | 17:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1060 | 2017 | 3 | 19 | 17 | 6 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-03-19 17:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-03-23 07:04 | 07:04 | 37.3697 | -121.8522 | Other | Urban | < 3 Meters | Fire Agency | SJFD disp 408-277-8950 Icident# F170829041 | 103485262 | Unknown | 12000 | Transformer | Subsurface | Yes | 42817.2945 | 07:04 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1061 | 2017 | 3 | 23 | 7 | 4 | 17-0033009 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 240914 | 0 | NA | <25mph | <15mph | #REF! | 2017-03-23 07:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-03-28 12:18 | 12:15 | 34.8809 | -120.4199 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 103397961 | YES | 12000 | Conductor | Overhead | Yes | 42822.5123 | 0.51042 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1062 | 2017 | 3 | 28 | 12 | 15 | 17-0034456 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 37191 | 0 | NA | <25mph | <15mph | #REF! | 2017-03-28 12:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-01 15:01 | 14:54 | 37.1882 | -120.9576 | Vegetation | Rural | < 0.25 Acres | Fire Agency | engine 74 mrced fire agency | 102318665 | Unknown | 12000 | Conductor | Overhead | Yes | 42826.6256 | 0.62083 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1063 | 2017 | 4 | 1 | 14 | 54 | 17-0035778 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 11617 | 0 | NA | <25mph | <15mph | #REF! | 2017-04-01 14:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-04 13:36 | 13:29 | 35.6885 | -120.7653 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101945026 | None | 12000 | Conductor | Overhead | Yes | 42829.567 | 0.56181 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1064 | 2017 | 4 | 4 | 13 | 29 | 17-0036460 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 167151 | 0 | NA | <25mph | <15mph | #REF! | 2017-04-04 13:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-04 18:18 | 14:54 | 37.2958 | -121.933 | Vegetation | Urban | < 3 Meters | Customer | N.A. | 100591136 | None | 12000 | Conductor | Overhead | Yes | 42829.7628 | 0.62083 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1065 | 2017 | 4 | 4 | 14 | 54 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-04-04 14:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-10 16:38 | 16:35 | 35.6175 | -119.743 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 100128630 | Unknown | 21000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1066 | 2017 | 4 | 10 | 16 | 35 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-04-10 16:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-13 14:07 | 14:21 | 37.7967 | -121.2521 | Other | Urban | Structure Only | Fire Agency | MANTECA CITY | 102104500 | VERIZON CALIFORNIA | 17000 | Conductor | Overhead | Yes | 42838.5885 | 0.59792 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1067 | 2017 | 4 | 13 | 14 | 21 | 17-0040005 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 35910 | 0 | NA | <25mph | <15mph | #REF! | 2017-04-13 14:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-16 15:33 | 15:14 | 35.5805 | -119.1423 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103833904 | Unknown | 12000 | Conductor | Overhead | Yes | 42841.6482 | 0.63472 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1068 | 2017 | 4 | 16 | 15 | 14 | 17-0040619 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 23993 | 0 | NA | <25mph | <15mph | #REF! | 2017-04-16 15:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-20 20:19 | 20:14 | 37.3741 | -120.7169 | Vegetation | Urban | < 3 Meters | Fire Agency | 209-966-3621 | 101205903 | Unknown | 12000 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1069 | 2017 | 4 | 20 | 20 | 14 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-04-20 20:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-23 07:32 | 7:10 | 36.0735 | -120.9345 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101726333 | Unknown | 12000 | Conductor | Overhead | Yes | 42848.3136 | 0.29861 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1070 | 2017 | 4 | 23 | 7 | 10 | 17-0042183 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 38538 | 0 | NA | <25mph | <15mph | #REF! | 2017-04-23 07:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-24 11:57 | 11:52 | 36.1899 | -121.1513 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101718856 | None | 12000 | Conductor | Overhead | Yes | 42849.4981 | 0.49444 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | tie wire | Other/Unknown | 1071 | 2017 | 4 | 24 | 11 | 52 | 17-0042463 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 3870 | 0 | NA | <25mph | <15mph | #REF! | 2017-04-24 11:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-25 12:39 | 12:38 | 38.6583 | -120.9762 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101376746 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 42850.5271 | 0.52639 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1072 | 2017 | 4 | 25 | 12 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-04-25 12:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-25 18:26 | 18:26 | 36.2373 | -119.7807 | Other | Rural | Structure Only | Self Extinguished | N.A. | 100716676 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42850.7682 | 18:26 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1073 | 2017 | 4 | 25 | 18 | 26 | 17-0042888 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 1808 | 0 | NA | <25mph | <15mph | #REF! | 2017-04-25 18:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-26 16:17 | 15:55 | 38.1561 | -121.6789 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT KENNY WILLIAMS (707)374-2233 | 103826165 | Unknown | 21000 | Conductor | Overhead | Yes | 42851.6787 | 0.66319 | Contact From Object | N.A. | Other | Electric Facility | Other | bird's nest | Other/Unknown | 1074 | 2017 | 4 | 26 | 15 | 55 | 17-0043172 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 31402 | 0 | NA | <25mph | <15mph | #REF! | 2017-04-26 15:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-28 07:18 | 5:55 | 34.5885 | -120.1057 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 805-683-2724 | 101900122 | Unknown | 12000 | Conductor | Overhead | Yes | 42853.3041 | 0.24653 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1075 | 2017 | 4 | 28 | 5 | 55 | 17-0043574 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 27164 | 0 | NA | <25mph | <15mph | #REF! | 2017-04-28 05:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-28 14:41 | 14:35 | 37.1247 | -121.6249 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Cal Fire | 103098414 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42853.6115 | 0.60764 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1076 | 2017 | 4 | 28 | 14 | 35 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-04-28 14:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-28 16:21 | 15:49 | 38.7679 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chris paper fire investigator, 530/677-1868. incident #caaeuo11821 | 101409833 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42853.6815 | 0.65903 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1077 | 2017 | 4 | 28 | 15 | 49 | 17-0043771 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 82614 | 0 | NA | <25mph | <15mph | #REF! | 2017-04-28 15:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-29 15:29 | 15:07 | 37.0349 | -119.5242 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100678661 | Unknown | 12000 | Conductor | Overhead | Yes | 42854.6453 | 0.62986 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1078 | 2017 | 4 | 29 | 15 | 7 | 17-0043911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-04-29 15:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-04-30 09:35 | 9:32 | 35.6349 | -118.9563 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 661-324-6551 | 100216308 | Unknown | 21000 | Conductor | Overhead | Yes | 42855.3995 | 0.39722 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1079 | 2017 | 4 | 30 | 9 | 32 | 17-0043980 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 3065 | 0 | NA | <25mph | <15mph | #REF! | 2017-04-30 09:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-01 | 14:20 | 36.0227 | -119.9584 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CORCORAN STATION 559-992-2156 | Pole 076/015 | Unknown | 70000 | Conductor | Overhead | Yes | 42856 | 0.59722 | Contact From Object | N.A. | Other | Electric Facility | Other | bird's nest | no-match | 1080 | 2017 | 5 | 1 | 14 | 20 | INT-09611 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-01 14:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-03 10:05 | 10:04 | 36.8161 | -119.632 | Vegetation | Rural | < 0.25 Acres | Fire Agency | eng 44 Eric connors 559-324-2294 | 100770906 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42858.4198 | 10:04 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1081 | 2017 | 5 | 3 | 10 | 4 | 17-0044998 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 770 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-03 10:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-03 13:06 | 12:51 | 38.1908 | -121.6615 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103834798 | None | 21000 | Conductor | Overhead | Yes | 42858.5456 | 0.53542 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1082 | 2017 | 5 | 3 | 12 | 51 | 17-0044911 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 37014 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-03 12:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-04 16:21 | 16:19 | 35.5573 | -120.7535 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101934476 | Unknown | 21000 | Conductor | Overhead | Yes | 42859.6812 | 0.67986 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1083 | 2017 | 5 | 4 | 16 | 19 | 17-0045385 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 18908 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-04 16:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-05 15:52 | 15:52 | 40.3776 | -123.0019 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101501566 | None | 12000 | Conductor | Overhead | Yes | 42860.6614 | 15:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1084 | 2017 | 5 | 5 | 15 | 52 | 17-0045707 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 56893 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-05 15:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-06 02:26 | 1:56 | 37.33 | -120.833 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103834182 | Unknown | 12000 | Conductor | Overhead | Yes | 42861.1012 | 0.080556 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1085 | 2017 | 5 | 6 | 1 | 56 | 17-0045735 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 4131 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-06 01:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-06 11:23 | 11:18 | 40.7951 | -124.029 | Vegetation | Rural | < 3 Meters | Fire Agency | chief rick harden 7074423352 | 103661154 | Unknown | 12000 | Conductor | Overhead | Yes | 42861.4744 | 0.47083 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1086 | 2017 | 5 | 6 | 11 | 18 | 17-0045785 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 113630 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-06 11:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-06 13:07 | 12:43 | 40.7623 | -124.162 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100998152 | Unknown | 12000 | Conductor | Overhead | Yes | 42861.5463 | 0.52986 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1087 | 2017 | 5 | 6 | 12 | 43 | 17-0045788 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 168540 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-06 12:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-06 15:37 | 15:00 | 39.2458 | -123.7785 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102185559 | Unknown | 12000 | Conductor | Overhead | Yes | 42861.651 | 0.625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1088 | 2017 | 5 | 6 | 15 | 0 | 17-0045831 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 79802 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-06 15:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-06 16:04 | 23:46 | 36.1654 | -120.3737 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 100741510 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42861.6693 | 0.99028 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1089 | 2017 | 5 | 6 | 23 | 46 | 17-0045905 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 254 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-06 23:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-09 11:18 | 11:15 | 40.0597 | -122.1889 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101531151 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42864.4711 | 0.46875 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1090 | 2017 | 5 | 9 | 11 | 15 | 17-0046509 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 71762 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-09 11:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-09 15:58 | 15:57 | 39.5465 | -121.8567 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100404826 | Unknown | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | no-match | 1091 | 2017 | 5 | 9 | 15 | 57 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-05-09 15:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-09 18:41 | 18:26 | 40.8689 | -123.5156 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | todd wright fire chief. 5307392493 | 103796045 | Unknown | 12000 | Conductor | Overhead | Yes | 42864.7782 | 0.76806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1092 | 2017 | 5 | 9 | 18 | 26 | 17-0046642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 108117 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-09 18:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-12 | 15:16 | 38.8507 | -121.3168 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102347828 | Unknown | 21000 | Conductor | Overhead | Yes | 42867 | 0.63611 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1093 | 2017 | 5 | 12 | 15 | 16 | 17-0047638 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 75635 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-12 15:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-13 | 21:49 | 39.6784 | -121.778 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 911 | 100355502 | Unknown | 12000 | Conductor | Overhead | Yes | 42868 | 0.90903 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1094 | 2017 | 5 | 13 | 21 | 49 | 17-0047670 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 150339 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-13 21:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-14 | 11:59 | 38.0798 | -122.8665 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102247059 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42869 | 0.49931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1095 | 2017 | 5 | 14 | 11 | 59 | 17-0047802 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 377483 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-14 11:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-14 | 16:09 | 35.6017 | -119.6566 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | 661-391-7000 | 100131572 | Unknown | 21000 | Conductor | Overhead | Yes | 42869 | 0.67292 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1096 | 2017 | 5 | 14 | 16 | 9 | 17-0047822 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 82407 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-14 16:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-15 | 3:05 | 35.6261 | -120.8962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101873299 | Unknown | 21000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1097 | 2017 | 5 | 15 | 3 | 5 | 17-0047837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 337188 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-15 03:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-15 13:05 | 13:05 | 38.1969 | -121.4095 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102071491 | Unknown | 12000 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1098 | 2017 | 5 | 15 | 13 | 5 | 17-0048042 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 5579 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-15 13:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-15 16:14 | 16:00 | 37.1766 | -119.8189 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SHAUN FAIRBANKS 559-683-4823 | 101108423 | SIERRA | 21000 | Conductor | Overhead | Yes | 42870.6767 | 0.66667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1099 | 2017 | 5 | 15 | 16 | 0 | 17-0048096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20007 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-15 16:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-15 21:06 | 20:57 | 38.6725 | -122.0456 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101589358 | Unknown | 21000 | Conductor | Overhead | Yes | 42870.8788 | 0.87292 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | no-match | 1100 | 2017 | 5 | 15 | 20 | 57 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-05-15 20:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-16 17:27 | 17:21 | 35.3759 | -119.1441 | Vegetation | Urban | < 0.25 Acres | Fire Agency | 324-6551 | 103264300 | Unknown | 12000 | Conductor | Overhead | Yes | 42871.7272 | 0.72292 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1101 | 2017 | 5 | 16 | 17 | 21 | 17-0048392 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 120785 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-16 17:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-17 | 14:49 | 37.225 | -120.4833 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101154662 | Unknown | 12000 | Transformer | Overhead | Yes | 42872 | 0.61736 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown | Transformer fuse | Other/Unknown | 1102 | 2017 | 5 | 17 | 14 | 49 | 17-0048612 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 124 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-17 14:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-17 | 15:13 | 36.2486 | -121.0383 | Other | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101764465 | None | 12000 | Conductor | Overhead | Yes | 42872 | 0.63403 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1103 | 2017 | 5 | 17 | 15 | 13 | 17-0048621 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-05-17 15:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-19 | 9:37 | 40.0334 | -122.0989 | Vegetation | Rural | < 0.25 Acres | Fire Agency | INCIDENT NUMBER 004751 | 101534483 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42874 | 0.40069 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown | secondary riser | no-match | 1104 | 2017 | 5 | 19 | 9 | 37 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-05-19 09:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-19 | 10:52 | 37.2086 | -121.0968 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 044/004 | Unknown | 115000 | Conductor | Overhead | Yes | 42874 | 0.45278 | Contamination | N.A. | N.A. | N.A. | Unknown |  | no-match | 1105 | 2017 | 5 | 19 | 10 | 52 | INT-09669 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-19 10:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-20 | 12:20 | 36.6528 | -119.8012 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100649202 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42875 | 0.51389 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown | secondary riser | no-match | 1106 | 2017 | 5 | 20 | 12 | 20 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-05-20 12:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-21 | 11:36 | 39.4277 | -121.698 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100379216 | Unknown | 12000 | Conductor | Overhead | Yes | 42876 | 0.48333 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1107 | 2017 | 5 | 21 | 11 | 36 | 17-0049454 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 8253 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-21 11:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-21 | 22:47 | 38.0645 | -122.5698 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 102238142 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42876 | 0.94931 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1108 | 2017 | 5 | 21 | 22 | 47 | 17-0050493 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-05-21 22:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-22 | 5:39 | 36.3753 | -121.048 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101770874 | Unknown | 21000 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | no-match | 1109 | 2017 | 5 | 22 | 5 | 39 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-05-22 05:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-22 | 17:52 | 37.7545 | -121.4193 | Vegetation | Urban | < 0.25 Acres | Fire Agency | TRACY | 102119359 | Unknown | 12000 | Conductor | Overhead | Yes | 42877 | 0.74444 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1110 | 2017 | 5 | 22 | 17 | 52 | 17-0049776 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 280778 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-22 17:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-24 16:25 | 16:24 | 38.834 | -121.1197 | Vegetation | Rural | < 3 Meters | Fire Agency | Fire Capt | 103838109 | None | 12000 | Conductor | Overhead | Yes | 42879.6837 | 16:24 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | no-match | 1111 | 2017 | 5 | 24 | 16 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-05-24 16:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-25 11:21 | 11:09 | 37.4526 | -121.889 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | ERIC EMMANUELE OFFICE (408)586-3365 DIRECT (408)586-3383 | 100557380 | Unknown | 12000 | Transformer | Overhead | Yes | 42880.4726 | 0.46458 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1112 | 2017 | 5 | 25 | 11 | 9 | 17-0050610 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 159410 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-25 11:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-25 15:05 | 15:05 | 36.5217 | -121.8473 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Buddy Bloxham 831-236-5659 | 101778611 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42880.6288 | 0.62847 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1113 | 2017 | 5 | 25 | 15 | 5 | 17-0050761 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 13965 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-25 15:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-25 17:36 | 16:55 | 38.3986 | -122.9876 | Vegetation | Rural | < 3 Meters | Utility: PG&E | N.A. | 101974034 | Unknown | 12000 | Conductor | Overhead | Yes | 42880.7334 | 0.70486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1114 | 2017 | 5 | 25 | 16 | 55 | 17-0050815 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 2644 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-25 16:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-29 18:30 | 18:29 | 39.2245 | -121.3753 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101304842 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1115 | 2017 | 5 | 29 | 18 | 29 | 17-0051324 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 616 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-29 18:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-30 | 11:40 | 36.8005 | -121.7702 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101707398 | Unknown | 12000 | Conductor | Overhead | Yes | 42885 | 0.48611 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1116 | 2017 | 5 | 30 | 11 | 40 | 17-0051473 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-05-30 11:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-31 02:15 | 2:06 | 38.754 | -121.2238 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Placer Co. fire | 100063341 | ROSEVILLE | 12000 | Conductor | Overhead | Yes | 42886.094 | 0.0875 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1117 | 2017 | 5 | 31 | 2 | 6 | 17-0051624 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 5463 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-31 02:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-05-31 05:52 | 5:24 | 37.0275 | -120.0707 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 101113852 | Unknown | 12000 | Conductor | Overhead | Yes | 42886.2446 | 0.225 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1118 | 2017 | 5 | 31 | 5 | 24 | 17-0051631 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 5072 | 0 | NA | <25mph | <15mph | #REF! | 2017-05-31 05:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-01 09:13 | 9:11 | 40.183 | -122.2665 | Vegetation | Rural | < 0.25 Acres | Fire Agency | MARK FRITZ | 101546068 | Unknown | 12000 | Conductor | Overhead | Yes | 42887.3843 | 0.38264 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1119 | 2017 | 6 | 1 | 9 | 11 | 17-0052002 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 5245 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-01 09:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-01 21:50 | 21:35 | 41.0557 | -121.3869 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101550337 | FRONTIER COMMUNICATI | 12000 | Conductor | Overhead | Yes | 42887.9101 | 0.89931 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1120 | 2017 | 6 | 1 | 21 | 35 | 17-0052160 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 265214 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-01 21:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-01 22:24 | 22:14 | 36.6539 | -121.6292 | Vegetation | Rural | < 3 Meters | Fire Agency | Salinas FD | 101732390 | Unknown | 12000 | Lightning Arrestor | Overhead | Yes | 42887.9336 | 0.92639 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | Other/Unknown | 1121 | 2017 | 6 | 1 | 22 | 14 | 17-0052182 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 5010 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-01 22:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-03 13:35 | 13:26 | 38.9017 | -121.2056 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100043664 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42889.5662 | 0.55972 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1122 | 2017 | 6 | 3 | 13 | 26 | 17-0052543 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 29512 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-03 13:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-03 20:52 | 20:52 | 36.8323 | -119.6333 | Vegetation | Rural | < 3 Meters | Fire Agency | CLOVIS F.D. CHIEF | 100768082 | Unknown | 12000 | Conductor | Overhead | Yes | 42889.8697 | 20:52 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1123 | 2017 | 6 | 3 | 20 | 52 | 17-0052562 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1686 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-03 20:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-04 00:08 | 00:08 | 36.982 | -120.0347 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Mike Gomez 559 906-1621 Incident #17cammu011185 | 103837406 | None | 12000 | Conductor | Overhead | Yes | 42890.0059 | 00:08 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1124 | 2017 | 6 | 4 | 0 | 8 | 17-0052593 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 80 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-04 00:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-04 13:13 | 13:12 | 36.7459 | -120.0602 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100645872 | Unknown | 12000 | Conductor | Overhead | Yes | 42890.5507 | 0.55 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1125 | 2017 | 6 | 4 | 13 | 12 | 17-0052623 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 1161 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-04 13:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-05 07:05 | 0:52 | 38.2342 | -121.2131 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 102083982 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42891.2954 | 0.036111 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1126 | 2017 | 6 | 5 | 0 | 52 | 17-0052666 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1468 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-05 00:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-05 08:01 | 7:56 | 37.8568 | -120.8815 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 209 5523911 | 102333651 | None | 17000 | Conductor | Overhead | Yes | 42891.334 | 0.33056 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1127 | 2017 | 6 | 5 | 7 | 56 | 17-0052694 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 28240 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-05 07:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-05 17:15 | 17:12 | 36.9424 | -121.4612 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Leo Alvarez 831-6364324 | 101717332 | Unknown | 21000 | Conductor | Overhead | Yes | 42891.719 | 0.71667 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1128 | 2017 | 6 | 5 | 17 | 12 | 17-0052872 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 25105 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-05 17:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-06 09:21 | 9:15 | 36.4543 | -119.1338 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TIM ROGERS, 559-358-7120 | 102306658 | Unknown | 12000 | Conductor | Overhead | Yes | 42892.3895 | 0.38542 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1129 | 2017 | 6 | 6 | 9 | 15 | 17-0053027 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 34417 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-06 09:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-06 09:49 | 09:48 | 36.9986 | -120.9369 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 101199765 | Unknown | 12000 | Conductor | Overhead | Yes | 42892.4089 | 09:48 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1130 | 2017 | 6 | 6 | 9 | 48 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-06 09:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-06 13:39 | 13:39 | 38.1711 | -121.6782 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101666656 | FRONTIER COMMUNICATI | 21000 | Fuse | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1131 | 2017 | 6 | 6 | 13 | 39 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-06 13:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-07 | 13:25 | 35.094 | -119.4161 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100192567 | Unknown | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1132 | 2017 | 6 | 7 | 13 | 25 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-07 13:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-07 10:39 | 10:13 | 39.5603 | -122.1077 | Vegetation | Rural | < 3 Meters | Utility: PG&E | N.A. | 103838281 | Unknown | 12000 | Conductor | Overhead | Yes | 42893.444 | 0.42569 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1133 | 2017 | 6 | 7 | 10 | 13 | 17-0053321 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 2033 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-07 10:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-08 | 5:33 | 36.2388 | -120.3016 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100743822 | Unknown | 12000 | Conductor | Overhead | Yes | 42894 | 0.23125 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1134 | 2017 | 6 | 8 | 5 | 33 | 17-0053512 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-08 05:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-08 00:40 | 0:26 | 37.1276 | -120.0193 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Jeff Mc Carroll (559) 806 - 8815 | 103205823 | Unknown | 12000 | Conductor | Overhead | Yes | 42894.0276 | 0.018056 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1135 | 2017 | 6 | 8 | 0 | 26 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-08 00:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-08 15:19 | 15:08 | 34.6058 | -120.0214 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SHAWN STEINER | 101947678 | Unknown | 12000 | Conductor | Overhead | Yes | 42894.6382 | 0.63056 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1136 | 2017 | 6 | 8 | 15 | 8 | 17-0053783 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 41311 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-08 15:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-09 10:41 | 10:40 | 36.6956 | -119.7186 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FRESNO COUNTY | 100793555 | Unknown | 12000 | Conductor | Overhead | Yes | 42895.4448 | 10:40 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1137 | 2017 | 6 | 9 | 10 | 40 | 17-0053984 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 458 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-09 10:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-09 13:30 | 13:27 | 36.7382 | -119.8204 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FFD INC # 703 4018 | 100895732 | Unknown | 12000 | Conductor | Overhead | Yes | 42895.5622 | 0.56042 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1138 | 2017 | 6 | 9 | 13 | 27 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-09 13:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-09 17:20 | 17:20 | 35.7974 | -120.5389 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 103406061 | Unknown | 12000 | Conductor | Overhead | Yes | 42895.7226 | 17:20 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1139 | 2017 | 6 | 9 | 17 | 20 | 17-0054121 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1006 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-09 17:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-10 07:38 | 07:37 | 35.4359 | -120.4957 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101890429 | Unknown | 21000 | Conductor | Overhead | Yes | 42896.3177 | 07:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1140 | 2017 | 6 | 10 | 7 | 37 | 17-0054182 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 34397 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-10 07:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-12 15:28 | 15:28 | 36.9672 | -120.0931 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101136946 | Unknown | 12000 | Conductor | Overhead | Yes | 42898.6448 | 15:28 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1141 | 2017 | 6 | 12 | 15 | 28 | 17-0054668 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 333725 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-12 15:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-12 18:04 | 18:04 | 35.3638 | -118.8256 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 103371824 | Unknown | 12000 | Transformer | Overhead | Yes | 42898.7529 | 18:04 | Contact From Object | N.A. | Other | Electric Facility | Other | bird's nest | no-match | 1142 | 2017 | 6 | 12 | 18 | 4 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-12 18:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-13 | 14:30 | 37.8526 | -122.1853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Tower 005/035c | Unknown | 115000 | Conductor | Overhead | Yes | 42899 | 0.60417 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1143 | 2017 | 6 | 13 | 14 | 30 | INT-09744 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-13 14:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-14 22:23 | 22:23 | 39.7559 | -121.5934 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100324481 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 42900.933 | 22:23 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1144 | 2017 | 6 | 14 | 22 | 23 | 17-0055350 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 176 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-14 22:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-15 04:31 | 2:58 | 40.299 | -122.4318 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101511631 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42901.1885 | 0.12361 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | Other/Unknown | 1145 | 2017 | 6 | 15 | 2 | 58 | 17-0055359 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1762 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-15 02:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-15 05:57 | 5:02 | 36.8261 | -121.6746 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101712958 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42901.2478 | 0.20972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1146 | 2017 | 6 | 15 | 5 | 2 | 17-0055368 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1329 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-15 05:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-15 08:08 | 7:39 | 39.2276 | -121.2348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE CHIEF | 103676075 | Unknown | 21000 | Conductor | Overhead | Yes | 42901.3391 | 0.31875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1147 | 2017 | 6 | 15 | 7 | 39 | 17-0055387 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 740 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-15 07:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-15 15:04 | 15:01 | 39.3913 | -123.3054 | Vegetation | Rural | < 0.25 Acres | Fire Agency | STEPHEN | 103838176 | YES | 12000 | Conductor | Overhead | Yes | 42901.6279 | 0.62569 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1148 | 2017 | 6 | 15 | 15 | 1 | 17-0055557 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 180469 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-15 15:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-15 16:22 | 16:21 | 38.7088 | -122.9016 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101957366 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42901.6817 | 16:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1149 | 2017 | 6 | 15 | 16 | 21 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-15 16:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-15 17:30 | 17:18 | 38.797 | -121.2069 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Cal Fire | 100058437 | Unknown | 21000 | Conductor | Overhead | Yes | 42901.7289 | 0.72083 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1150 | 2017 | 6 | 15 | 17 | 18 | 17-0055589 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1227 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-15 17:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-16 14:04 | 13:50 | 35.4505 | -120.6169 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101889864 | Unknown | 21000 | Conductor | Overhead | Yes | 42902.5864 | 0.57639 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1151 | 2017 | 6 | 16 | 13 | 50 | 17-0055812 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 1314 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-16 13:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-16 14:23 | 14:22 | 36.845 | -120.0192 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 101212782 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42902.599 | 14:22 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1152 | 2017 | 6 | 16 | 14 | 22 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-16 14:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-16 16:37 | 16:17 | 39.2226 | -121.0041 | Vegetation | Rural | < 3 Meters | Fire Agency | GVFIRE | 100036908 | Unknown | 12000 | Conductor | Overhead | Yes | 42902.692 | 0.67847 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1153 | 2017 | 6 | 16 | 16 | 17 | 17-0055836 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 18630 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-16 16:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-16 18:06 | 17:59 | 37.3094 | -122.0472 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100555441 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42902.7542 | 0.74931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1154 | 2017 | 6 | 16 | 17 | 59 | 17-0055843 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 3168 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-16 17:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-16 19:15 | 19:14 | 38.3443 | -122.7812 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101970801 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42902.8019 | 19:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1155 | 2017 | 6 | 16 | 19 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-16 19:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-16 22:30 | 22:30 | 38.0373 | -122.1847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101424286 | Unknown | 21000 | Conductor | Overhead | Yes | 42902.9378 | 22:30 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1156 | 2017 | 6 | 16 | 22 | 30 | 17-0055882 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 12000 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-16 22:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-17 02:53 | 02:53 | 37.3357 | -120.583 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101147424 | Unknown | 12000 | Conductor | Overhead | Yes | 42903.1204 | 02:53 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | no-match | 1157 | 2017 | 6 | 17 | 2 | 53 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-17 02:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-17 15:57 | 15:49 | 36.939 | -119.6846 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 103406061 | Unknown | 21000 | Conductor | Overhead | Yes | 42903.6648 | 0.65903 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1158 | 2017 | 6 | 17 | 15 | 49 | 17-0055960 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 33372 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-17 15:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-18 | 23:49 | 39.1949 | -122.9632 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102160857 | Unknown | 12000 | Conductor | Overhead | Yes | 42904 | 0.99236 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1159 | 2017 | 6 | 18 | 23 | 49 | 17-0056370 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 6763 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-18 23:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-18 12:22 | 12:22 | 36.7258 | -119.7907 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100894729 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42904.5154 | 12:22 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1160 | 2017 | 6 | 18 | 12 | 22 | 17-0056102 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2424 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-18 12:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-18 13:10 | 13:10 | 38.237 | -122.6702 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 102007208 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42904.5488 | 13:10 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1161 | 2017 | 6 | 18 | 13 | 10 | 17-0056142 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 690 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-18 13:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-18 18:09 | 18:09 | 37.5517 | -122.2925 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100309893 | Unknown | 21000 | Conductor | Overhead | Yes | 42904.7563 | 18:09 | Equipment/ Facility Failure | Guy/Span Wire | N.A. | N.A. | Unknown |  | Other/Unknown | 1162 | 2017 | 6 | 18 | 18 | 9 | 17-0056195 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 744538 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-18 18:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-18 20:17 | 20:16 | 38.8884 | -122.0204 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101650987 | None | 12000 | Lightning Arrestor | Overhead | Yes | 42904.8448 | 20:16 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | Other/Unknown | 1163 | 2017 | 6 | 18 | 20 | 16 | 17-0056353 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 178 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-18 20:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-18 21:39 | 21:07 | 37.8397 | -121.2864 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102085809 | Unknown | 12000 | Conductor | Overhead | Yes | 42904.9019 | 0.87986 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1164 | 2017 | 6 | 18 | 21 | 7 | 17-0056327 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 3843 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-18 21:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-18 22:12 | 22:12 | 38.539 | -122.792 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 102029435 | Unknown | 12000 | Other | Overhead | Yes | 42904.9253 | 22:12 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1165 | 2017 | 6 | 18 | 22 | 12 | 17-0056290 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 465423 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-18 22:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-18 23:13 | 23:12 | 36.7575 | -119.6646 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100780126 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1166 | 2017 | 6 | 18 | 23 | 12 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-18 23:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-18 23:31 | 23:31 | 38.8973 | -121.2947 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 103782395 | Unknown | 12000 | Conductor | Overhead | Yes | 42904.98 | 23:31 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1167 | 2017 | 6 | 18 | 23 | 31 | 17-0056369 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 81679 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-18 23:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-19 01:23 | 01:23 | 35.3676 | -118.9552 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100252360 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42905.0579 | 01:23 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1168 | 2017 | 6 | 19 | 1 | 23 | 17-0056407 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 3700 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-19 01:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-19 13:52 | 13:51 | 39.9063 | -122.1766 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 103841797 | YES | 12000 | Conductor | Overhead | Yes | 42905.5775 | 13:51 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1169 | 2017 | 6 | 19 | 13 | 51 | 17-0056601 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 27723 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-19 13:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-19 16:19 | 16:18 | 37.7927 | -121.2306 | Other | Urban | Structure Only | Utility: PG&E | N.A. | 103582825 | Unknown | 17000 | Transformer | Subsurface | Yes | 42905.6797 | 16:18 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1170 | 2017 | 6 | 19 | 16 | 18 | 17-0056687 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 15914 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-19 16:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-19 16:27 | 16:26 | 37.9378 | -120.609 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101282825 | Unknown | 17000 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Recloser | N.A. | N.A. | Unknown |  | no-match | 1171 | 2017 | 6 | 19 | 16 | 26 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-19 16:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-19 18:17 | 17:31 | 36.7627 | -120.3758 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 101094343 | Unknown | 12000 | Transformer | Overhead | Yes | 42905.762 | 0.72986 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1172 | 2017 | 6 | 19 | 17 | 31 | 17-0056755 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 19028 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-19 17:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-19 18:29 | 18:00 | 38.455 | -121.8242 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 101594910 | PACIFIC BELL | 12000 | Lightning Arrestor | Overhead | Yes | 42905.7704 | 0.75 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | Other/Unknown | 1173 | 2017 | 6 | 19 | 18 | 0 | 17-0056723 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 180 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-19 18:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-19 20:22 | 20:22 | 38.1012 | -120.8697 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101233468 | Unknown | 12000 | Transformer | Overhead | Yes | 42905.8488 | 20:22 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1174 | 2017 | 6 | 19 | 20 | 22 | 17-0056796 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 18380 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-19 20:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-20 00:50 | 00:49 | 39.749 | -121.8998 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 100437523 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42906.0344 | 00:49 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1175 | 2017 | 6 | 20 | 0 | 49 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-20 00:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-20 09:13 | 09:12 | 39.1975 | -121.495 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101306700 | Unknown | 12000 | Conductor | Overhead | Yes | 42906.3837 | 09:12 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1176 | 2017 | 6 | 20 | 9 | 12 | 17-0056925 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 37591 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-20 09:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-20 10:08 | 10:08 | 39.0367 | -121.0763 | Vegetation | Urban | < 3 Meters | Fire Agency | JERRY GOOD 530 268-0844 | 100023174 | None | 12000 | Conductor | Overhead | Yes | 42906.4224 | 10:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1177 | 2017 | 6 | 20 | 10 | 8 | 17-0056980 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 37968 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-20 10:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-20 13:38 | 13:37 | 37.9247 | -122.0895 | Vegetation | Urban | < 3 Meters | Fire Agency | contra costa fire | 100476159 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | Yes | 42906.5677 | 13:37 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | Other/Unknown | 1178 | 2017 | 6 | 20 | 13 | 37 | 17-0057040 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-20 13:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-20 15:18 | 15:17 | 40.1126 | -123.7677 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 100987107 | Unknown | 12000 | Conductor | Overhead | Yes | 42906.6372 | 15:17 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1179 | 2017 | 6 | 20 | 15 | 17 | 17-0057054 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6324 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-20 15:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-20 15:19 | 11:51 | 40.3156 | -124.0611 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101006039 | Unknown | 12000 | Conductor | Overhead | Yes | 42906.638 | 0.49375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1180 | 2017 | 6 | 20 | 11 | 51 | 17-0057001 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 9256 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-20 11:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-20 18:33 | 18:32 | 37.9281 | -121.2332 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 102132644 | Unknown | 12000 | Conductor | Overhead | Yes | 42906.7726 | 18:32 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1181 | 2017 | 6 | 20 | 18 | 32 | 17-0057106 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2055 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-20 18:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-20 22:18 | 20:46 | 38.9076 | -121.2603 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100085621 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42906.929 | 0.86528 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1182 | 2017 | 6 | 20 | 20 | 46 | 17-0057117 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 13777 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-20 20:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-20 23:17 | 23:16 | 35.6375 | -120.8566 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101873622 | Unknown | 12000 | Conductor | Overhead | Yes | 42906.9701 | 23:16 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1183 | 2017 | 6 | 20 | 23 | 16 | 17-0057167 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 3844 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-20 23:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-21 08:41 | 08:41 | 39.17 | -122.1573 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101637081 | Unknown | 12000 | Conductor | Overhead | Yes | 42907.362 | 08:41 | Contact From Object | N.A. | Other | Electric Facility | Human Error | helicopter | Other/Unknown | 1184 | 2017 | 6 | 21 | 8 | 41 | 17-0057228 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 207049 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-21 08:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-21 14:23 | 14:23 | 38.9921 | -121.3536 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100027499 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42907.5994 | 14:23 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1185 | 2017 | 6 | 21 | 14 | 23 | 17-0057402 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 520 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-21 14:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 0.4 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 22732 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-22 09:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-22 11:21 | 16:30 | 39.6131 | -121.6872 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 100347529 | None | 12000 | Conductor | Overhead | Yes | 42908.4727 | 0.6875 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1187 | 2017 | 6 | 22 | 16 | 30 | 17-0057661 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-22 16:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-22 17:54 | 18:07 | 38.7583 | -120.7176 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101401088 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.7461 | 0.75486 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1188 | 2017 | 6 | 22 | 18 | 7 | 17-0057857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 8517 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-22 18:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-22 19:02 | 19:29 | 35.5889 | -120.6691 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101912249 | Unknown | 21000 | Conductor | Overhead | Yes | 42908.7934 | 0.81181 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1189 | 2017 | 6 | 22 | 19 | 29 | 17-0057888 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 17715 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-22 19:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-23 13:01 | 13:00 | 39.3051 | -122.4862 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 100329817 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42909.5421 | 13:00 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | no-match | 1190 | 2017 | 6 | 23 | 13 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-23 13:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-23 19:20 | 20:09 | 40.3856 | -122.2841 | Vegetation | Urban | < 0.25 Acres | Fire Agency | kieth foster 530-347-4737 | 101505644 | Unknown | 12000 | Conductor | Overhead | Yes | 42909.8054 | 0.83958 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster bank | Other/Unknown | 1191 | 2017 | 6 | 23 | 20 | 9 | 17-0058223 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-23 20:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-23 19:39 | 19:23 | 39.7829 | -121.867 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100397376 | None | 12000 | Conductor | Overhead | Yes | 42909.8188 | 0.80764 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1192 | 2017 | 6 | 23 | 19 | 23 | 17-0058226 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 13027 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-23 19:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-24 10:32 | 10:31 | 38.9438 | -121.0447 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100090318 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42910.439 | 0.43819 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1193 | 2017 | 6 | 24 | 10 | 31 | 17-0058318 | Zone 1 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 582 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-24 10:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-24 15:06 | 14:51 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 42910.6292 | 0.61875 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1194 | 2017 | 6 | 24 | 14 | 51 | 17-0058332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 21296 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-24 14:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-24 22:27 | 22:27 | 38.2908 | -120.849 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CONTACT BOBBY BOWMAN | 101238865 | None | 12000 | Conductor | Overhead | Yes | 42910.9354 | 0.93542 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1195 | 2017 | 6 | 24 | 22 | 27 | 17-0058399 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 4529 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-24 22:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-25 | 18:18 | 37.3236 | -120.5591 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101159230 | Unknown | 12000 | Conductor | Overhead | Yes | 42911 | 0.7625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1196 | 2017 | 6 | 25 | 18 | 18 | 17-0058469 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 62065 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-25 18:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-25 02:47 | 0:23 | 39.4043 | -123.3869 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102193088 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42911.1159 | 0.015972 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1197 | 2017 | 6 | 25 | 0 | 23 | 17-0058406 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 23100 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-25 00:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-25 06:15 | 6:02 | 39.0774 | -121.5294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101314125 | Unknown | 12000 | Conductor | Overhead | Yes | 42911.2606 | 0.25139 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1198 | 2017 | 6 | 25 | 6 | 2 | 17-0058412 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 126896 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-25 06:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-25 15:38 | 15:37 | 34.9395 | -119.6925 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | 805-686-5074 | 100191652 | None | 12000 | Conductor | Overhead | Yes | 42911.6513 | 15:37 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1199 | 2017 | 6 | 25 | 15 | 37 | 17-0058466 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1318 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-25 15:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-25 22:15 | 22:14 | 39.025 | -121.5787 | Vegetation | Rural | < 3 Meters | Fire Agency | Olivehurst FD | 101314072 | Unknown | 21000 | Conductor | Overhead | Yes | 42911.9269 | 22:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1200 | 2017 | 6 | 25 | 22 | 14 | 17-0058514 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 27789 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-25 22:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-26 08:23 | 8:18 | 37.2733 | -120.5257 | Vegetation | Rural | < 0.25 Acres | Self Extinguished | N.A. | 103218794 | Unknown | 12000 | Conductor | Overhead | Yes | 42912.3491 | 0.34583 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1201 | 2017 | 6 | 26 | 8 | 18 | 17-0058557 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 17517 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-26 08:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-26 16:38 | 14:29 | 35.9782 | -120.1169 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | HENNAGIN 559 386 555 | 103243976 | Unknown | 21000 | Conductor | Overhead | Yes | 42912.6927 | 0.60347 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1202 | 2017 | 6 | 26 | 14 | 29 | 17-0058731 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 794 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-26 14:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-27 09:28 | 9:23 | 37.9559 | -122.6176 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | marin county fire | 102260068 | UNFILED | 12000 | Conductor | Overhead | Yes | 42913.3944 | 0.39097 | Other | N.A. | N.A. | N.A. | Unknown |  | Fell into (slight defect) | 1203 | 2017 | 6 | 27 | 9 | 23 | 17-0058882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 3920 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-27 09:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-27 18:25 | 17:47 | 39.5126 | -122.2033 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100341056 | None | 21000 | Conductor | Overhead | Yes | 42913.7672 | 0.74097 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1204 | 2017 | 6 | 27 | 17 | 47 | 17-0059004 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-27 17:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-28 09:58 | 09:57 | 35.9055 | -120.8421 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 101765453 | Unknown | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | no-match | 1205 | 2017 | 6 | 28 | 9 | 57 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-28 09:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-28 13:13 | 13:09 | 34.9276 | -119.6204 | Building | Rural | Structure Only | Fire Agency | (805)683-2724) | 100190548 | Unknown | 21000 | Conductor | Overhead | Yes | 42914.5505 | 0.54792 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1206 | 2017 | 6 | 28 | 13 | 9 | 17-0059232 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 12105 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-28 13:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-29 18:31 | 18:31 | 38.4445 | -122.8999 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 102021185 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42915.7718 | 18:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1207 | 2017 | 6 | 29 | 18 | 31 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-29 18:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-29 22:11 | 21:55 | 35.9804 | -121.0956 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 103312369 | Unknown | 12000 | Transformer | Overhead | Yes | 42915.924 | 0.91319 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1208 | 2017 | 6 | 29 | 21 | 55 | 17-0059645 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 702 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-29 21:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-30 | 10:24 | 39.0262 | -121.5432 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101341770 | Unknown | 21000 | Conductor | Overhead | Yes | 42916 | 0.43333 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1209 | 2017 | 6 | 30 | 10 | 24 | 17-0059728 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-06-30 10:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-30 01:20 | 01:20 | 39.821 | -121.5883 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103840463 | YES | 12000 | Conductor | Overhead | Yes | 42916.0559 | 01:20 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1210 | 2017 | 6 | 30 | 1 | 20 | 17-0059647 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 2888 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-30 01:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-06-30 23:55 | 23:54 | 38.5794 | -122.8835 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 101958804 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42916.9965 | 23:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1211 | 2017 | 6 | 30 | 23 | 54 | 17-0059922 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2025 | 0 | NA | <25mph | <15mph | #REF! | 2017-06-30 23:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-01 | 12:02 | 39.8209 | -121.6418 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 003/039 | Unknown | 60000 | Conductor | Overhead | Yes | 42917 | 0.50139 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1212 | 2017 | 7 | 1 | 12 | 2 | INT-09792 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-01 12:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-01 03:55 | 3:54 | 36.9995 | -119.9765 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 2099663621 | 101015895 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42917.1634 | 0.1625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1213 | 2017 | 7 | 1 | 3 | 54 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-01 03:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-01 04:43 | 3:12 | 38.1952 | -122.9197 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103855493 | Unknown | 12000 | Conductor | Overhead | Yes | 42917.1963 | 0.13333 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1214 | 2017 | 7 | 1 | 3 | 12 | 17-0059935 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 41370 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-01 03:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-01 10:44 | 10:41 | 39.2779 | -121.6875 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101294919 | Unknown | 12000 | Other | Overhead | Yes | 42917.4474 | 0.44514 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1215 | 2017 | 7 | 1 | 10 | 41 | 17-0059978 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 12221 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-01 10:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-02 | 13:28 | 39.8605 | -121.6274 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 000/017c | Unknown | 60000 | Conductor | Overhead | Yes | 42918 | 0.56111 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1216 | 2017 | 7 | 2 | 13 | 28 | INT-09794 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-02 13:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-02 03:55 | 3:49 | 36.9588 | -120.8927 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101205043 | Unknown | 12000 | Conductor | Overhead | Yes | 42918.1633 | 0.15903 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1217 | 2017 | 7 | 2 | 3 | 49 | 17-0060039 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 1728 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-02 03:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-03 20:28 | 20:26 | 38.7923 | -120.9438 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101388730 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42919.853 | 0.85139 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1218 | 2017 | 7 | 3 | 20 | 26 | 17-0060336 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 8134 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-03 20:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-04 13:59 | 13:56 | 40.383 | -122.315 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101506140 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42920.5826 | 0.58056 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1219 | 2017 | 7 | 4 | 13 | 56 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-04 13:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-04 16:25 | 16:16 | 38.8763 | -121.1318 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100050181 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42920.6838 | 0.67778 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1220 | 2017 | 7 | 4 | 16 | 16 | 17-0060422 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1518 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-04 16:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-04 20:17 | 20:16 | 40.4228 | -122.3975 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SCOTT CORN 530-448-2414 | 101481860 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42920.8451 | 20:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1221 | 2017 | 7 | 4 | 20 | 16 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-04 20:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-05 03:50 | 3:25 | 38.6845 | -121.0118 | Vegetation | Urban | < 0.25 Acres | Fire Agency | JUSTIN RHAMES | 101380157 | PACIFIC BELL | 21000 | Fuse | Overhead | Yes | 42921.1597 | 0.14236 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1222 | 2017 | 7 | 5 | 3 | 25 | 17-0060471 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-05 03:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-05 12:11 | 11:58 | 39.2105 | -121.2266 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVE ROBERTSON 530 906 4892 | 100010286 | Unknown | 21000 | Conductor | Overhead | Yes | 42921.5077 | 0.49861 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1223 | 2017 | 7 | 5 | 11 | 58 | 17-0060605 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 10231 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-05 11:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-05 20:56 | 20:54 | 35.6847 | -120.11 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 661-324-6551 LOG325962 | 100171224 | Unknown | 21000 | Capacitor Bank | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1224 | 2017 | 7 | 5 | 20 | 54 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-05 20:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-06 | 15:18 | 36.7402 | -119.7613 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 100864107 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42922 | 0.6375 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1225 | 2017 | 7 | 6 | 15 | 18 | 17-0060991 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 3798 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-06 15:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-06 14:04 | 14:02 | 39.3009 | -122.5173 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100414219 | Unknown | 12000 | Conductor | Overhead | Yes | 42922.5858 | 0.58472 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1226 | 2017 | 7 | 6 | 14 | 2 | 17-0061590 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-06 14:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-06 20:07 | 20:07 | 39.5987 | -121.9099 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100436921 | None | 12000 | Conductor | Overhead | Yes | 42922.8385 | 20:07 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1227 | 2017 | 7 | 6 | 20 | 7 | 17-0061025 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 14355 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-06 20:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-06 23:33 | 23:30 | 35.5562 | -120.7552 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101934472 | Unknown | 21000 | Conductor | Overhead | Yes | 42922.9815 | 0.97917 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1228 | 2017 | 7 | 6 | 23 | 30 | 17-0061026 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 272919 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-06 23:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-07 | 15:09 | 40.9054 | -122.3806 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101455950 | Unknown | 12000 | Conductor | Overhead | Yes | 42923 | 0.63125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1229 | 2017 | 7 | 7 | 15 | 9 | 17-0061903 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-07 15:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-07 20:49 | 14:31 | 37.499 | -119.799 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVEN WARD OFFICE 209-966-3542 CELL559-706-8811 | 103855637 | Unknown | 21000 | Conductor | Overhead | Yes | 42923.8675 | 0.60486 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1230 | 2017 | 7 | 7 | 14 | 31 | 17-0061288 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 554306 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-07 14:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-08 04:06 | 4:03 | 38.5535 | -121.5368 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101584938 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42924.1706 | 0.16875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1231 | 2017 | 7 | 8 | 4 | 3 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-08 04:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-08 16:02 | 15:59 | 37.2822 | -122.0189 | Other | Urban | < 0.25 Acres | Fire Agency | Unknown | 100540958 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42924.668 | 0.66597 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1232 | 2017 | 7 | 8 | 15 | 59 | 17-0061458 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 952 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-08 15:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-08 18:23 | 18:16 | 35.4653 | -120.6713 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 103392970 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42924.7662 | 0.76111 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1233 | 2017 | 7 | 8 | 18 | 16 | 17-0061464 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 175132 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-08 18:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-08 19:23 | 18:49 | 40.2935 | -122.4089 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | TOM STROING, RED BLUFF | 101526269 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42924.8076 | 0.78403 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1234 | 2017 | 7 | 8 | 18 | 49 | 17-0061469 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 157484 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-08 18:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-09 07:22 | 7:07 | 36.5092 | -121.4465 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103011964 | Unknown | 12000 | Conductor | Overhead | Yes | 42925.307 | 0.29653 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1235 | 2017 | 7 | 9 | 7 | 7 | 17-0061517 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 45241 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-09 07:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-09 11:06 | 11:00 | 39.4201 | -121.5439 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100394209 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42925.4628 | 0.45833 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1236 | 2017 | 7 | 9 | 11 | 0 | 17-0061541 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 9983 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-09 11:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-10 09:08 | 09:07 | 38.2074 | -121.2335 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 102083900 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42926.3804 | 09:07 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1237 | 2017 | 7 | 10 | 9 | 7 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-10 09:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-10 12:34 | 12:32 | 40.2603 | -123.8253 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103139646 | Unknown | 12000 | Conductor | Overhead | Yes | 42926.5237 | 0.52222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1238 | 2017 | 7 | 10 | 12 | 32 | 17-0061771 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 5910 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-10 12:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-10 16:41 | 16:39 | 36.962 | -120.8584 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | EFRAIN CHAVARRIA | 101203174 | Unknown | 12000 | Conductor | Overhead | Yes | 42926.6952 | 0.69375 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1239 | 2017 | 7 | 10 | 16 | 39 | 17-0061840 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-10 16:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-10 18:00 | 17:00 | 37.3768 | -122.3597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | David Hibdon 831-254-1763 | 100270370 | Unknown | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1240 | 2017 | 7 | 10 | 17 | 0 | 17-0061857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3322 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-10 17:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-11 08:13 | 8:11 | 38.1337 | -121.1054 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102072316 | None | 21000 | Other | Overhead | Yes | 42927.3427 | 0.34097 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1241 | 2017 | 7 | 11 | 8 | 11 | 17-0061968 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 562 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-11 08:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-11 11:53 | 11:53 | 38.0338 | -121.3224 | Vegetation | Urban | < 0.25 Acres | Utility: PG&E | N.A. | 102118581 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42927.4954 | 11:53 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1242 | 2017 | 7 | 11 | 11 | 53 | 17-0062075 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | 3567 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-11 11:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-11 13:56 | 13:56 | 39.4506 | -121.7153 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chip fowler | 100423597 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42927.5807 | 13:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1243 | 2017 | 7 | 11 | 13 | 56 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-11 13:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-11 22:13 | 22:12 | 37.0122 | -121.9497 | Vegetation | Rural | < 3 Meters | Fire Agency | CAPT PHIL CRAMBLET 831-479-6842 | 101676689 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42927.9254 | 22:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1244 | 2017 | 7 | 11 | 22 | 12 | 17-0062198 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 714 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-11 22:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-12 | 16:04 | 40.6531 | -122.3343 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 000/001 | Unknown | 60000 | Conductor | Overhead | Yes | 42928 | 0.66944 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1245 | 2017 | 7 | 12 | 16 | 4 | INT-09837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-12 16:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-12 05:52 | 05:51 | 38.3932 | -121.8044 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101584920 | Unknown | 12000 | Conductor | Overhead | Yes | 42928.2443 | 05:51 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1246 | 2017 | 7 | 12 | 5 | 51 | 17-0062214 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4336 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-12 05:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-12 10:49 | 10:48 | 36.9625 | -120.0463 | Other | Urban | < 0.25 Acres | Fire Agency | Barbera Riley 661-5499 ext. 2 | 103222654 | None | 0 – 750 | Conductor | Overhead | Yes | 42928.4506 | 10:48 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | no-match | 1247 | 2017 | 7 | 12 | 10 | 48 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-12 10:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-12 15:09 | 15:09 | 37.1491 | -122.0037 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 103565794 | Unknown | 21000 | Conductor | Overhead | Yes | 42928.6313 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1248 | 2017 | 7 | 12 | 15 | 9 | 17-0062439 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24690 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-12 15:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-12 20:22 | 20:21 | 40.0808 | -123.8339 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103841917 | Unknown | 12000 | Conductor | Overhead | Yes | 42928.8485 | 20:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1249 | 2017 | 7 | 12 | 20 | 21 | 17-0062445 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 4616 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-12 20:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-13 | 5:13 | 38.1201 | -122.1858 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Tower 025/173 | Unknown | 115000 | Conductor | Overhead | Yes | 42929 | 0.21736 | Contact From Object | N.A. | Other | Electric Facility | Other | bird material | no-match | 1250 | 2017 | 7 | 13 | 5 | 13 | INT-09838 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-13 05:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-13 07:44 | 07:43 | 39.4064 | -122.1263 | Vegetation | Rural | < 3 Meters | Fire Agency | AXS-N/A FIRE NEAR POLE PER FD. NO STDBY. WANT CHECK OF POLE 530-458-0200 | 100406386 | None | 0 – 750 | Conductor | Overhead | Yes | 42929.3222 | 07:43 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1251 | 2017 | 7 | 13 | 7 | 43 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-13 07:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-13 19:30 | 19:29 | 36.8504 | -119.55 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | chis waters bat.chief 559-281-4308 | 100728986 | Unknown | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1252 | 2017 | 7 | 13 | 19 | 29 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-13 19:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-14 17:55 | 17:54 | 37.7095 | -121.2921 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TRACY | 102070196 | Unknown | 12000 | Conductor | Overhead | Yes | 42930.7465 | 17:54 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1253 | 2017 | 7 | 14 | 17 | 54 | 17-0063032 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 11012 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-14 17:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-15 14:35 | 14:34 | 39.6231 | -121.5328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | russ fowler | 100404385 | Unknown | 12000 | Conductor | Overhead | Yes | 42931.6076 | 14:34 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1254 | 2017 | 7 | 15 | 14 | 34 | 17-0063126 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 54372 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-15 14:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-15 14:57 | 14:56 | 37.3074 | -122.0355 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100538519 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42931.6227 | 14:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1255 | 2017 | 7 | 15 | 14 | 56 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-15 14:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-15 20:17 | 20:16 | 39.459 | -121.5313 | Vegetation | Rural | < 3 Meters | Fire Agency | oroville station | 100429093 | Unknown | 12000 | Conductor | Overhead | Yes | 42931.8448 | 20:16 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1256 | 2017 | 7 | 15 | 20 | 16 | 17-0063151 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 300753 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-15 20:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-15 21:01 | 21:01 | 38.2128 | -121.834 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101658237 | Unknown | 21000 | Conductor | Overhead | Yes | 42931.8758 | 21:01 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1257 | 2017 | 7 | 15 | 21 | 1 | 17-0063175 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1638 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-15 21:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-16 10:40 | 10:39 | 40.3414 | -123.8786 | Vegetation | Rural | < 3 Meters | Fire Agency | 707-726-1280 | 100990019 | Unknown | 12000 | Conductor | Overhead | Yes | 42932.4443 | 10:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1258 | 2017 | 7 | 16 | 10 | 39 | 17-0063223 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 198 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-16 10:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-16 11:59 | 11:59 | 36.6669 | -121.7515 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101761892 | None | 21000 | Fuse | Overhead | Yes | 42932.4994 | 11:59 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1259 | 2017 | 7 | 16 | 11 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-16 11:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-16 12:10 | 12:10 | 35.6613 | -120.922 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101942626 | Unknown | 21000 | Conductor | Overhead | Yes | 42932.5072 | 12:10 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1260 | 2017 | 7 | 16 | 12 | 10 | 17-0063242 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1304 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-16 12:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-16 17:07 | 17:07 | 37.3441 | -122.0363 | Vegetation | Urban | < 3 Meters | Fire Agency | sunnyvale fire | 100532224 | PACIFIC BELL | 0 – 750 | Transformer | Overhead | Yes | 42932.7134 | 17:07 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1261 | 2017 | 7 | 16 | 17 | 7 | 17-0063269 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4940 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-16 17:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-17 07:40 | 07:39 | 40.1653 | -122.2228 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 101543808 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42933.3191 | 07:39 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1262 | 2017 | 7 | 17 | 7 | 39 | 17-0063338 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 56757 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-17 07:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-17 10:01 | 10:00 | 35.956 | -120.8515 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101765495 | Unknown | 12000 | Conductor | Overhead | Yes | 42933.417 | 10:00 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1263 | 2017 | 7 | 17 | 10 | 0 | 17-0063297 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1560769 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-17 10:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-17 18:59 | 18:58 | 38.8885 | -121.9898 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Dunnigan Fire Dept | 101602915 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42933.7909 | 18:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1264 | 2017 | 7 | 17 | 18 | 58 | 17-0063505 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 27007 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-17 18:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-18 | 11:30 | 38.0484 | -120.5565 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 012/071 | Unknown | 115000 | Conductor | Overhead | Yes | 42934 | 0.47917 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1265 | 2017 | 7 | 18 | 11 | 30 | INT-09873 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 55499 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-18 11:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-18 | 21:40 | 38.0031 | -122.2093 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | Pole 000/002 to 000/003 | Unknown | 60000 | Conductor | Overhead | Yes | 42934 | 0.90278 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1266 | 2017 | 7 | 18 | 21 | 40 | INT-09875 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-18 21:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-18 07:39 | 07:39 | 38.0704 | -120.5452 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101269434 | Unknown | 0 – 750 | Other | Overhead | Yes | 42934.3188 | 07:39 | Other | N.A. | N.A. | N.A. | Unknown |  | no-match | 1267 | 2017 | 7 | 18 | 7 | 39 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-18 07:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-18 11:46 | 11:45 | 36.8308 | -119.8623 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100624764 | PACIFIC BELL | 21000 | Capacitor Bank | Overhead | Yes | 42934.4903 | 11:45 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1268 | 2017 | 7 | 18 | 11 | 45 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-18 11:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-19 | 5:52 | 37.0905 | -119.6047 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Tower 003/001 | Unknown | 115000 | Conductor | Overhead | Yes | 42935 | 0.24444 | Contact From Object | N.A. | Other | Electric Facility | Unknown |  | no-match | 1269 | 2017 | 7 | 19 | 5 | 52 | INT-09877 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-19 05:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-19 09:33 | 09:33 | 35.3446 | -118.8609 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 100159158 | Unknown | 12000 | Capacitor Bank | Overhead | Yes | 42935.3979 | 09:33 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1270 | 2017 | 7 | 19 | 9 | 33 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-19 09:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-19 17:20 | 17:19 | 39.4124 | -123.8123 | Vegetation | Rural | < 0.25 Acres | Fire Agency | DRUE RHOADS 707 964 5673 | 102201550 | YES | 12000 | Conductor | Overhead | Yes | 42935.722 | 17:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1271 | 2017 | 7 | 19 | 17 | 19 | 17-0064059 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5553 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-19 17:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-20 | 20:57 | 37.7361 | -122.4921 | Building | Urban | Structure Only | Unknown | N.A. | 101813719 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42936 | 0.87292 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1272 | 2017 | 7 | 20 | 20 | 57 | 17-0064391 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | 9056 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-20 20:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-20 01:47 | 01:46 | 36.5254 | -119.682 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100830639 | Unknown | 0 – 750 | Lightning Arrestor | Overhead | Yes | 42936.074 | 01:46 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | no-match | 1273 | 2017 | 7 | 20 | 1 | 46 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-20 01:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-20 04:27 | 04:27 | 38.0642 | -120.8711 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | chris costales 209 754 2735 | 102142834 | Unknown | 12000 | Conductor | Overhead | Yes | 42936.1856 | 04:27 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1274 | 2017 | 7 | 20 | 4 | 27 | 17-0064078 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 19996 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-20 04:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-20 13:46 | 13:45 | 35.0804 | -120.5538 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | PAUL LEE 805 903-3416 INC # 8291 | 101941116 | Unknown | 12000 | Conductor | Overhead | Yes | 42936.5736 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1275 | 2017 | 7 | 20 | 13 | 45 | 17-0064321 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 45999 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-20 13:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-20 17:01 | 17:00 | 37.9265 | -121.232 | Vegetation | Urban | < 3 Meters | Customer | N.A. | 103384380 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | Yes | 42936.7089 | 17:00 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1276 | 2017 | 7 | 20 | 17 | 0 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-20 17:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-21 | 13:27 | 38.2685 | -120.9372 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101245524 | Unknown | 12000 | Conductor | Overhead | Yes | 42937 | 0.56042 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1277 | 2017 | 7 | 21 | 13 | 27 | 17-0064623 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 122488 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-21 13:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-21 | 20:26 | 41.0655 | -121.3932 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101549629 | Unknown | 12000 | Conductor | Overhead | Yes | 42937 | 0.85139 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1278 | 2017 | 7 | 21 | 20 | 26 | 17-0064666 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 46616 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-21 20:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-22 12:26 | 12:25 | 40.8795 | -123.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Josh , comander chief of forest service. | 100980577 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.518 | 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1279 | 2017 | 7 | 22 | 12 | 25 | 17-0064721 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 23227 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-22 12:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-22 14:38 | 14:38 | 37.2994 | -122.1631 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100265488 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.6101 | 14:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1280 | 2017 | 7 | 22 | 14 | 38 | 17-0064738 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49181 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-22 14:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-22 16:02 | 16:01 | 40.8314 | -124.0539 | Vegetation | Rural | < 0.25 Acres | Fire Agency | BATTALION CHIEF CURT WATKINS, 707-825.2000 | 100983827 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42938.6679 | 16:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1281 | 2017 | 7 | 22 | 16 | 1 | 17-0064750 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 11207 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-22 16:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-23 09:22 | 09:22 | 40.642 | -122.2302 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT? | 101459708 | FRONTIER COMMUNICATI | 12000 | Conductor | Overhead | Yes | 42939.3906 | 09:22 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1282 | 2017 | 7 | 23 | 9 | 22 | 17-0064801 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 184712 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-23 09:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-23 16:33 | 16:32 | 36.2405 | -119.8128 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Brandon Jones (559) 852-2884 | 100783832 | Unknown | 12000 | Conductor | Overhead | Yes | 42939.6896 | 16:32 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1283 | 2017 | 7 | 23 | 16 | 32 | 17-0064841 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4672 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-23 16:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-23 18:25 | 18:25 | 39.6723 | -123.5336 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103823226 | Unknown | 12000 | Conductor | Overhead | Yes | 42939.7676 | 18:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1284 | 2017 | 7 | 23 | 18 | 25 | 17-0064854 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 12864 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-23 18:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-23 19:41 | 19:41 | 36.2171 | -119.9097 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Brandon Jones (559) 852-2884 | 103846605 | Unknown | 12000 | Conductor | Overhead | Yes | 42939.8205 | 19:41 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1285 | 2017 | 7 | 23 | 19 | 41 | 17-0064852 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 16251 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-23 19:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-24 14:02 | 14:01 | 37.2635 | -122.3364 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike klink 650-879-0121 | 100322130 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42940.5845 | 14:01 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1286 | 2017 | 7 | 24 | 14 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-24 14:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-24 16:07 | 16:07 | 37.2537 | -121.9676 | Vegetation | Urban | < 0.25 Acres | Fire Agency | C1702050039 | 103447162 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42940.6716 | 16:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1287 | 2017 | 7 | 24 | 16 | 7 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-24 16:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-24 19:31 | 19:31 | 38.3519 | -120.7103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.8134 | 19:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1288 | 2017 | 7 | 24 | 19 | 31 | 17-0065145 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14281 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-24 19:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-24 21:45 | 21:45 | 35.6024 | -120.9211 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101860186 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.9063 | 21:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1289 | 2017 | 7 | 24 | 21 | 45 | 17-0065191 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 21231 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-24 21:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-25 15:52 | 15:51 | 38.3779 | -122.5388 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102031447 | Unknown | 12000 | Conductor | Overhead | Yes | 42941.6609 | 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1290 | 2017 | 7 | 25 | 15 | 51 | 17-0065437 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 18584 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-25 15:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-25 19:13 | 19:12 | 39.5997 | -121.4449 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100403612 | Unknown | 12000 | Conductor | Overhead | Yes | 42941.8004 | 19:12 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1291 | 2017 | 7 | 25 | 19 | 12 | 17-0065453 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 68452 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-25 19:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-26 06:55 | 06:55 | 36.7812 | -119.7553 | Vegetation | Urban | < 3 Meters | Fire Agency | FRESNO FIRE, BATALION 1, FULMER 559 993 2661 | 100866522 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42942.2883 | 06:55 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1292 | 2017 | 7 | 26 | 6 | 55 | 17-0065504 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 246896 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-26 06:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-28 | 14:02 | 40.9997 | -121.9579 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101512624 | Unknown | 12000 | Conductor | Overhead | Yes | 42944 | 0.58472 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1293 | 2017 | 7 | 28 | 14 | 2 | 17-0066367 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 46581 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-28 14:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-28 16:57 | 16:57 | 35.4727 | -120.9908 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | TOM MCEWEN 805-903-3409 | 101933868 | Unknown | 12000 | Conductor | Overhead | Yes | 42944.7064 | 16:57 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1294 | 2017 | 7 | 28 | 16 | 57 | 17-0066372 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 10337 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-28 16:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-28 19:21 | 19:20 | 35.7276 | -120.9903 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Luis Obispo CDF | 101945496 | None | 21000 | Conductor | Overhead | Yes | 42944.8062 | 19:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1295 | 2017 | 7 | 28 | 19 | 20 | 17-0066392 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 8300 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-28 19:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-29 13:19 | 13:18 | 39.4631 | -121.4595 | Vegetation | Rural | < 0.25 Acres | Fire Agency | russ fowler 530 521 8056 | 103846763 | Unknown | 12000 | Conductor | Overhead | Yes | 42945.5548 | 13:18 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1296 | 2017 | 7 | 29 | 13 | 18 | 17-0066455 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 148419 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-29 13:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-29 13:28 | 13:28 | 35.4523 | -120.3834 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101889516 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42945.5612 | 13:28 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1297 | 2017 | 7 | 29 | 13 | 28 | 17-0066472 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1962 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-29 13:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-29 14:52 | 14:52 | 37.06 | -122.0011 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Scotts Valley Fire Dept. | 101679068 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42945.6197 | 14:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1298 | 2017 | 7 | 29 | 14 | 52 | 17-0066465 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 172672 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-29 14:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-29 17:57 | 17:56 | 37.0251 | -121.5358 | Vegetation | Rural | < 3 Meters | Fire Agency | GEORGE MARSHALL | 100610842 | Unknown | 21000 | Conductor | Overhead | Yes | 42945.7478 | 17:56 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1299 | 2017 | 7 | 29 | 17 | 56 | 17-0066482 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 942 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-29 17:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-29 18:09 | 18:08 | 37.9487 | -121.3457 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 911 | 102126507 | Unknown | 12000 | Conductor | Overhead | Yes | 42945.7561 | 18:08 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1300 | 2017 | 7 | 29 | 18 | 8 | 17-0066487 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 29252 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-29 18:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-29 20:46 | 20:45 | 35.4517 | -120.6171 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101941008 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42945.8649 | 20:45 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | Third-party caused | no-match | 1301 | 2017 | 7 | 29 | 20 | 45 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-29 20:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-30 09:47 | 09:46 | 38.9132 | -122.6179 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike wink | 102151066 | None | 0 – 750 | Conductor | Overhead | Yes | 42946.4075 | 09:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1302 | 2017 | 7 | 30 | 9 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-30 09:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-31 12:58 | 12:58 | 37.0971 | -122.2797 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101679025 | Unknown | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1303 | 2017 | 7 | 31 | 12 | 58 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-31 12:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-31 14:11 | 14:10 | 35.9787 | -120.111 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 100695130 | Unknown | 21000 | Conductor | Overhead | Yes | 42947.5908 | 14:10 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1304 | 2017 | 7 | 31 | 14 | 10 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-07-31 14:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-07-31 14:42 | 14:41 | 38.7967 | -121.1329 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103782414 | Unknown | 12000 | Conductor | Overhead | Yes | 42947.6123 | 14:41 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1305 | 2017 | 7 | 31 | 14 | 41 | 17-0066797 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 210 | 0 | NA | <25mph | <15mph | #REF! | 2017-07-31 14:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-01 12:23 | 12:23 | 36.0412 | -119.5053 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100661556 | Unknown | 0 – 750 | Other | Overhead | Yes | 42948.5162 | 12:23 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | no-match | 1306 | 2017 | 8 | 1 | 12 | 23 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-01 12:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-02 | 9:42 | 39.2274 | -123.1081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 5/0 | None | 60000 | Conductor | Overhead | Yes | 42949 | 0.40417 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1307 | 2017 | 8 | 2 | 9 | 42 | INT-09925 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-02 09:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-02 06:01 | 5:54 | 40.7986 | -123.3961 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 100974913 | Unknown | 12000 | Conductor | Overhead | Yes | 42949.251 | 0.24583 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1308 | 2017 | 8 | 2 | 5 | 54 | 17-0067270 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 5832 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-02 05:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-02 09:06 | 8:58 | 37.5618 | -121.9486 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FREMONT FIRE DEPT. 911 | 100940374 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 42949.3788 | 0.37361 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1309 | 2017 | 8 | 2 | 8 | 58 | 17-0067345 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 100546 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-02 08:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-02 17:09 | 17:04 | 37.3163 | -122.0723 | Vegetation | Urban | < 0.25 Acres | Fire Agency | TONY RAINIERI 408-378-4010 | 100534186 | Unknown | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1310 | 2017 | 8 | 2 | 17 | 4 | 17-0067504 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 38228 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-02 17:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-02 18:20 | 18:16 | 37.393 | -120.6213 | Vegetation | Urban | < 3 Meters | Fire Agency | 2099663621 | 101190510 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42949.7636 | 0.76111 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1311 | 2017 | 8 | 2 | 18 | 16 | 17-0067519 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 3416 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-02 18:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-03 11:01 | 10:53 | 39.0732 | -121.0868 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100072742 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42950.4588 | 0.45347 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1312 | 2017 | 8 | 3 | 10 | 53 | 17-0067679 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 127440 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-03 10:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-03 11:28 | 11:16 | 38.1192 | -122.5015 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SSR172150008 | 102227219 | Unknown | 12000 | Conductor | Overhead | Yes | 42950.4775 | 0.46944 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1313 | 2017 | 8 | 3 | 11 | 16 | 17-0067691 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 67329 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-03 11:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-03 22:45 | 22:44 | 39.0711 | -121.487 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | ART PAQUETTE 530-633-0861 | 101335644 | PACIFIC BELL | 12000 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1314 | 2017 | 8 | 3 | 22 | 44 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-03 22:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-04 09:54 | 09:54 | 38.6039 | -121.0592 | Vegetation | Rural | < 3 Meters | Fire Agency | D. Franks 530-622-3858, Incident #022602 | 101411052 | PACIFIC BELL | 21000 | Capacitor Bank | Overhead | Yes | 42951.4126 | 09:54 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1315 | 2017 | 8 | 4 | 9 | 54 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-04 09:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-04 18:21 | 18:14 | 35.6193 | -120.6589 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101912293 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 42951.7647 | 0.75972 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1316 | 2017 | 8 | 4 | 18 | 14 | 17-0068101 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 33644 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-04 18:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-05 08:33 | 08:33 | 38.4583 | -120.8695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JEFF MICHEL- 530 409 2223 | 101236223 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42952.3565 | 08:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1317 | 2017 | 8 | 5 | 8 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-05 08:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-05 18:13 | 18:08 | 39.0968 | -123.2147 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102196629 | Unknown | 12000 | Conductor | Overhead | Yes | 42952.7592 | 0.75556 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1318 | 2017 | 8 | 5 | 18 | 8 | 17-0068200 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 134239 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-05 18:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-05 18:21 | 18:09 | 36.9675 | -120.0899 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | 911 | 101136476 | Unknown | 12000 | Conductor | Overhead | Yes | 42952.7644 | 0.75625 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1319 | 2017 | 8 | 5 | 18 | 9 | 17-0068199 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 57700 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-05 18:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-05 19:43 | 19:21 | 36.7691 | -119.6101 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100725102 | Unknown | 12000 | Other | Overhead | Yes | 42952.8213 | 0.80625 | Equipment/ Facility Failure | Recloser | N.A. | N.A. | Unknown |  | Other/Unknown | 1320 | 2017 | 8 | 5 | 19 | 21 | 17-0068204 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 14256 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-05 19:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-06 11:38 | 11:38 | 36.5857 | -121.7121 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101747125 | Unknown | 12000 | Conductor | Overhead | Yes | 42953.4849 | 11:38 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1321 | 2017 | 8 | 6 | 11 | 38 | 17-0068279 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 87172 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-06 11:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-06 19:23 | 18:21 | 40.6012 | -122.2346 | Vegetation | Rural | < 3 Meters | Fire Agency | 17CASH4007992 | 101470083 | Unknown | 12000 | Other | Overhead | Yes | 42953.8076 | 0.76458 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 1322 | 2017 | 8 | 6 | 18 | 21 | 17-0068302 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 447 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-06 18:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-08 | 13:46 | 38.4366 | -122.726 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | Tower 005/090 | None | 115000 | Conductor | Overhead | Yes | 42955 | 0.57361 | Contact From Object | N.A. | Other | Electric Facility | Human Error |  | no-match | 1323 | 2017 | 8 | 8 | 13 | 46 | INT-09957 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-08 13:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-08 00:42 | 0:36 | 35.4269 | -119.0572 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 100167715 | PACIFIC BELL | 12000 | Unknown | Subsurface | Yes | 42955.0293 | 0.025 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1324 | 2017 | 8 | 8 | 0 | 36 | 17-0068636 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 167326 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-08 00:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-08 04:23 | 4:10 | 38.4949 | -122.6685 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 102025742 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42955.1829 | 0.17361 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1325 | 2017 | 8 | 8 | 4 | 10 | 17-0068642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2750 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-08 04:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-08 11:28 | 11:27 | 37.0445 | -121.6343 | Vegetation | Urban | < 3 Meters | Utility: PG&E | N.A. | 100613200 | VERIZON CALIFORNIA | 21000 | Capacitor Bank | Overhead | Yes | 42955.4775 | 11:27 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | Other/Unknown | 1326 | 2017 | 8 | 8 | 11 | 27 | 17-0068774 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 34192 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-08 11:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-08 20:35 | 20:35 | 37.2637 | -119.7103 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TROY CHEEK1-209-966-3621 | 103793352 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42955.8578 | 20:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1327 | 2017 | 8 | 8 | 20 | 35 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-08 20:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-09 11:29 | 11:29 | 38.6532 | -120.6273 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101402496 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42956.4786 | 11:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1328 | 2017 | 8 | 9 | 11 | 29 | 17-0069107 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 54216 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-09 11:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-11 07:56 | 07:55 | 38.2649 | -120.9748 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101253880 | None | 12000 | Conductor | Overhead | Yes | 42958.3305 | 07:55 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1329 | 2017 | 8 | 11 | 7 | 55 | 17-0070265 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-11 07:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-12 09:09 | 09:08 | 34.6689 | -120.0286 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103391912 | Unknown | 12000 | Conductor | Overhead | Yes | 42959.3812 | 09:08 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | wire cut | Other/Unknown | 1330 | 2017 | 8 | 12 | 9 | 8 | 17-0069829 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 26070 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-12 09:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-13 13:11 | 13:11 | 38.5094 | -122.77 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 101961046 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42960.5496 | 13:11 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1331 | 2017 | 8 | 13 | 13 | 11 | 17-0069940 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 69483 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-13 13:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-14 | 6:14 | 40.1164 | -123.8064 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100986364 | Unknown | 12000 | Conductor | Overhead | Yes | 42961 | 0.25972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1332 | 2017 | 8 | 14 | 6 | 14 | 17-0070003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 959989 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-14 06:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-14 | 23:52 | 37.1272 | -122.1689 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 015/127 | None | 60000 | Conductor | Overhead | Yes | 42961 | 0.99444 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1333 | 2017 | 8 | 14 | 23 | 52 | INT-09976 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1790869 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-14 23:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-14 07:56 | 07:56 | 39.1794 | -120.9761 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100083743 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42961.3308 | 07:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1334 | 2017 | 8 | 14 | 7 | 56 | 17-0070063 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 3012 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-14 07:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-15 19:29 | 19:28 | 39.5037 | -121.2783 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 100396172 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42962.8116 | 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1335 | 2017 | 8 | 15 | 19 | 28 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-15 19:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-16 | 20:24 | 35.7813 | -119.9153 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Span 0/6 to 0/7 | None | 70000 | Conductor | Overhead | Yes | 42963 | 0.85 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1336 | 2017 | 8 | 16 | 20 | 24 | INT-09987 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-16 20:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-17 | 2:33 | 39.1934 | -121.4227 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 911 | 101304315 | Unknown | 12000 | Conductor | Overhead | Yes | 42964 | 0.10625 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | pole cut down | Other/Unknown | 1337 | 2017 | 8 | 17 | 2 | 33 | 17-0070915 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 66 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-17 02:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-17 | 15:15 | 39.3703 | -121.0484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | PHIL MICHAEL 265-2894 INCIENT # CA NEV 21642 | 100083029 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42964 | 0.63542 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1338 | 2017 | 8 | 17 | 15 | 15 | 17-0071121 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 32850 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-17 15:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-18 | 17:09 | 37.0921 | -121.6691 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100608897 | VERIZON CALIFORNIA | 21000 | Conductor | Overhead | Yes | 42965 | 0.71458 | Other | N.A. | N.A. | N.A. | Human Error | CIP contractor | Other/Unknown | 1339 | 2017 | 8 | 18 | 17 | 9 | 17-0071393 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 28967 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-18 17:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-19 | 11:31 | 37.6891 | -121.2506 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102053834 | Unknown | 17000 | Conductor | Overhead | Yes | 42966 | 0.47986 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1340 | 2017 | 8 | 19 | 11 | 31 | 17-0071465 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 21661 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-19 11:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-19 | 21:16 | 40.5752 | -122.2985 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464623 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42966 | 0.88611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1341 | 2017 | 8 | 19 | 21 | 16 | 17-0071522 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 19044 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-19 21:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-20 | 11:38 | 39.2764 | -122.1407 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101634861 | Unknown | 12000 | Conductor | Overhead | Yes | 42967 | 0.48472 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1342 | 2017 | 8 | 20 | 11 | 38 | 17-0071568 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 9190 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-20 11:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-21 | 15:07 | 38.608 | -122.3531 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Aaron Latta 707 339 2918 | 102254922 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42968 | 0.62986 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1343 | 2017 | 8 | 21 | 15 | 7 | 17-0071815 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2079 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-21 15:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-21 | 19:31 | 39.7258 | -121.8205 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100341323 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42968 | 0.81319 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1344 | 2017 | 8 | 21 | 19 | 31 | 17-0071807 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 224572 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-21 19:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-22 | 14:17 | 38.4902 | -122.8918 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 102001687 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42969 | 0.59514 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1345 | 2017 | 8 | 22 | 14 | 17 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-22 14:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-24 | 6:32 | 36.5905 | -119.5929 | Vegetation | Rural | < 3 Meters | Fire Agency | ca fku 012333 | 100897456 | Unknown | 12000 | Conductor | Overhead | Yes | 42971 | 0.27222 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1346 | 2017 | 8 | 24 | 6 | 32 | 17-0072487 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 52298 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-24 06:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-25 | 9:47 | 39.0251 | -121.5775 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101314075 | Unknown | 21000 | Conductor | Overhead | Yes | 42972 | 0.40764 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1347 | 2017 | 8 | 25 | 9 | 47 | 17-0072817 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 26160 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-25 09:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-26 | 7:10 | 38.8252 | -121.3953 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100101888 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42973 | 0.29861 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | Third-party caused | no-match | 1348 | 2017 | 8 | 26 | 7 | 10 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-26 07:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-26 | 20:39 | 38.4707 | -122.6472 | Vegetation | Urban | < 3 Meters | Fire Agency | Santa Rosa Fire Dept | 101966474 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42973 | 0.86042 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1349 | 2017 | 8 | 26 | 20 | 39 | 17-0073092 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 361520 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-26 20:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-26 | 20:53 | 38.7066 | -121.0193 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101382231 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42973 | 0.87014 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1350 | 2017 | 8 | 26 | 20 | 53 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-26 20:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-27 | 18:11 | 37.9916 | -121.3479 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Unknown | 103193823 | Unknown | 21000 | Conductor | Overhead | Yes | 42974 | 0.75764 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1351 | 2017 | 8 | 27 | 18 | 11 | 17-0073193 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 227252 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-27 18:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-27 | 20:04 | 38.9165 | -121.151 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-477-0641 x7, log 22629 | 100077184 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42974 | 0.83611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1352 | 2017 | 8 | 27 | 20 | 4 | 17-0073228 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 905 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-27 20:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-27 | 22:16 | 37.3585 | -120.8503 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CHRIS ALLEN 209-634-7086 | 103346364 | Unknown | 12000 | Conductor | Overhead | Yes | 42974 | 0.92778 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1353 | 2017 | 8 | 27 | 22 | 16 | 17-0073245 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 81574 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-27 22:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-28 | 6:32 | 35.4218 | -119.0304 | Vegetation | Urban | < 0.25 Acres | Fire Agency | BCFD/KCFD 661-324-6551 | 103139674 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42975 | 0.27222 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1354 | 2017 | 8 | 28 | 6 | 32 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-28 06:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-28 | 8:36 | 35.7245 | -119.5341 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100171751 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 0.35833 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1355 | 2017 | 8 | 28 | 8 | 36 | 17-0073312 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 12343 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-28 08:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-28 | 9:14 | 38.7443 | -122.6491 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 103781085 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42975 | 0.38472 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1356 | 2017 | 8 | 28 | 9 | 14 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-28 09:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-28 | 10:07 | 39.0472 | -120.7859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | FORESTHILL | 100019525 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 0.42153 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1357 | 2017 | 8 | 28 | 10 | 7 | 17-0073379 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 10077 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-28 10:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-28 | 13:55 | 37.6857 | -120.8067 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 102327313 | None | 0 – 750 | Conductor | Overhead | Yes | 42975 | 0.57986 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1358 | 2017 | 8 | 28 | 13 | 55 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-28 13:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-28 | 14:06 | 38.634 | -122.4194 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102253236 | Unknown | 21000 | Conductor | Overhead | Yes | 42975 | 0.5875 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1359 | 2017 | 8 | 28 | 14 | 6 | 17-0073526 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1896 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-28 14:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-28 | 14:23 | 38.5054 | -120.7592 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101260228 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 42975 | 0.59931 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1360 | 2017 | 8 | 28 | 14 | 23 | 17-0073516 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 588 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-28 14:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-28 | 14:59 | 40.2853 | -123.8728 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 100990599 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 0.62431 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1361 | 2017 | 8 | 28 | 14 | 59 | 17-0073546 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2688 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-28 14:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-28 | 23:56 | 40.1197 | -123.644 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103844288 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 0.99722 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1362 | 2017 | 8 | 28 | 23 | 56 | 17-0073645 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 3892 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-28 23:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-29 | 6:08 | 38.2365 | -122.4608 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101998998 | Unknown | 12000 | Conductor | Overhead | Yes | 42976 | 0.25556 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1363 | 2017 | 8 | 29 | 6 | 8 | 17-0073687 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 13813 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-29 06:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-29 | 10:27 | 38.3687 | -122.0012 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 101661402 | PACIFIC BELL | 12000 | Lightning Arrestor | Overhead | Yes | 42976 | 0.43542 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1364 | 2017 | 8 | 29 | 10 | 27 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-29 10:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-29 | 10:40 | 38.2066 | -121.1576 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102082031 | Unknown | 12000 | Conductor | Overhead | Yes | 42976 | 0.44444 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1365 | 2017 | 8 | 29 | 10 | 40 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-29 10:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-29 | 12:49 | 37.4507 | -119.6454 | Vegetation | Rural | > 5000 Acres | Fire Agency | USFS | 101017368 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-29 | 0.53403 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1366 | 2017 | 8 | 29 | 12 | 49 | 17-0073823 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | 3rd Party | 3rd Party - Unknown | 5894785 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-29 12:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-29 | 15:54 | 38.302 | -122.5431 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 911 | 102026119 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 42976 | 0.6625 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1367 | 2017 | 8 | 29 | 15 | 54 | 17-0073928 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 485 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-29 15:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-30 | 16:17 | 35.3528 | -119.0538 | Vegetation | Urban | < 0.25 Acres | Fire Agency | BCFD/KCFD 661-324-6551 | 100145928 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42977 | 0.67847 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1368 | 2017 | 8 | 30 | 16 | 17 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-30 16:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-30 | 18:21 | 40.6243 | -122.3039 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CASHU008896 | 103151338 | YES | 12000 | Conductor | Overhead | Yes | 42977 | 0.76458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1369 | 2017 | 8 | 30 | 18 | 21 | 17-0074287 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 76344 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-30 18:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-30 | 22:37 | 38.9993 | -120.9887 | Vegetation | Rural | < 3 Meters | Fire Agency | Andy 530-889-0111 | 100026238 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42977 | 0.94236 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1370 | 2017 | 8 | 30 | 22 | 37 | 17-0074333 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 3750 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-30 22:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-30 | 22:39 | 38.1662 | -121.9381 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | suisun | 103850994 | Unknown | 12000 | Conductor | Overhead | Yes | 42977 | 0.94375 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1371 | 2017 | 8 | 30 | 22 | 39 | 17-0074326 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 12250 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-30 22:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-31 | 6:42 | 35.616 | -120.8577 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Derrick | 101860075 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 0.27917 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1372 | 2017 | 8 | 31 | 6 | 42 | 17-0074386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1620 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-31 06:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-31 | 11:33 | 37.1379 | -121.9966 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100519201 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 0.48125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1373 | 2017 | 8 | 31 | 11 | 33 | 17-0074457 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 99153 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-31 11:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-31 | 11:51 | 38.3917 | -122.3195 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102291943 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42978 | 0.49375 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1374 | 2017 | 8 | 31 | 11 | 51 | 17-0074477 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 63514 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-31 11:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-31 | 21:07 | 41.0605 | -124.1038 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100977438 | Unknown | 12000 | Conductor | Overhead | Yes | 42978 | 0.87986 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1375 | 2017 | 8 | 31 | 21 | 7 | 17-0074619 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 8532 | 0 | NA | <25mph | <15mph | #REF! | 2017-08-31 21:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-08-31 | 22:50 | 36.815 | -119.7763 | Vegetation | Urban | < 3 Meters | Customer | N.A. | 100851402 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42978 | 0.95139 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1376 | 2017 | 8 | 31 | 22 | 50 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-08-31 22:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-01 | 6:09 | 36.1949 | -120.7079 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101705717 | Unknown | 12000 | Fuse | Overhead | Yes | 42979 | 0.25625 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1377 | 2017 | 9 | 1 | 6 | 9 | 17-0074671 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2755 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-01 06:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-01 | 8:00 | 37.3757 | -119.8886 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101067028 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42979 | 0.33333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1378 | 2017 | 9 | 1 | 8 | 0 | 17-0074724 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 680 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-01 08:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-01 | 12:07 | 40.5938 | -124.136 | Vegetation | Rural | < 3 Meters | Fire Agency | DISPATCH FIRE 707-725-7550 | 100993250 | PACIFIC BELL | 12000 | Lightning Arrestor | Overhead | No |  |  | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | no-match | 1379 | 2017 | 9 | 1 | 12 | 7 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-09-01 12:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-01 | 12:52 | 37.1667 | -121.7069 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100601982 | VERIZON CALIFORNIA | 21000 | Conductor | Overhead | Yes | 42979 | 0.53611 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1380 | 2017 | 9 | 1 | 12 | 52 | 17-0074791 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 175821 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-01 12:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-01 | 12:59 | 38.4527 | -122.7845 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102015626 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 42979 | 0.54097 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | no-match | 1381 | 2017 | 9 | 1 | 12 | 59 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-09-01 12:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-01 | 17:48 | 36.6518 | -121.7249 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MCFD | 103155761 | Unknown | 12000 | Conductor | Overhead | Yes | 42979 | 0.74167 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1382 | 2017 | 9 | 1 | 17 | 48 | 17-0074898 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 8152 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-01 17:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-01 | 18:42 | 38.2939 | -122.5039 | Other | Rural | < 0.25 Acres | Fire Agency | BOB NORRBOM 707 996 2102 | 101982894 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 42979 | 0.77917 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1383 | 2017 | 9 | 1 | 18 | 42 | 17-0074933 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2094 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-01 18:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-02 | 12:01 | 37.6645 | -121.9223 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 100956020 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42980 | 0.50069 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1384 | 2017 | 9 | 2 | 12 | 1 | 17-0075132 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 7152 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-02 12:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-02 | 16:18 | 37.269 | -121.8056 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100584311 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42980 | 0.67917 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1385 | 2017 | 9 | 2 | 16 | 18 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-09-02 16:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-02 | 18:00 | 37.9338 | -122.4069 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102347407 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42980 | 0.75 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1386 | 2017 | 9 | 2 | 18 | 0 | 17-0075226 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 2236 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-02 18:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-03 | 7:12 | 37.3743 | -122.2184 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Local | 100270106 | Unknown | 12000 | Conductor | Overhead | Yes | 42981 | 0.3 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1387 | 2017 | 9 | 3 | 7 | 12 | 17-0075491 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 16728 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-03 07:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-03 | 12:52 | 37.2162 | -119.4807 | Vegetation | Rural | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103345573 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-09-03 | 0.53611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1388 | 2017 | 9 | 3 | 12 | 52 | 17-0075546 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 2362 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-03 12:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-03 | 17:52 | 37.4956 | -119.8367 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101086621 | Unknown | 21000 | Transformer | Overhead | Yes | 42981 | 0.74444 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 1389 | 2017 | 9 | 3 | 17 | 52 | 17-0075617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 4512 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-03 17:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-03 | 22:57 | 36.0953 | -120.517 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | CHRIS CHRISTOPHERSON 559-281-4320 | 100739435 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42981 | 0.95625 | Contact Between Third Party Facility on Pole and Supply Lines | N.A. | N.A. | N.A. | Weather |  | Other/Unknown | 1390 | 2017 | 9 | 3 | 22 | 57 | 17-0075710 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 6121 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-03 22:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-04 | 0:57 | 36.8024 | -119.8254 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100856132 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42982 | 0.039583 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1391 | 2017 | 9 | 4 | 0 | 57 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-09-04 00:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-04 | 3:29 | 39.8317 | -121.8444 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102300100 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1392 | 2017 | 9 | 4 | 3 | 29 | 17-0075723 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 214974 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-04 03:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-04 | 6:43 | 37.4546 | -121.9331 | Other | Rural | Structure Only | Customer | N.A. | 100557780 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42982 | 0.27986 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1393 | 2017 | 9 | 4 | 6 | 43 | 17-0075743 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 3948 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-04 06:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-05 | 1:24 | 39.4317 | -121.5529 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100420238 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42983 | 0.058333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1394 | 2017 | 9 | 5 | 1 | 24 | 17-0075956 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 8888 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-05 01:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-05 | 6:58 | 39.6727 | -123.5128 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 102194697 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 42983 | 0.29028 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1395 | 2017 | 9 | 5 | 6 | 58 | 17-0075976 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10528 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-05 06:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-05 | 7:20 | 39.7109 | -121.7972 | Vegetation | Rural | < 3 Meters | Fire Agency | (530) 538-6841 | 100355255 | Unknown | 12000 | Conductor | Overhead | Yes | 42983 | 0.30556 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1396 | 2017 | 9 | 5 | 7 | 20 | 17-0075968 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | 9500 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-05 07:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-05 | 13:51 | 38.1897 | -121.3175 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103218208 | Unknown | 12000 | Conductor | Overhead | Yes | 42983 | 0.57708 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1397 | 2017 | 9 | 5 | 13 | 51 | 17-0076099 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 8843 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-05 13:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-05 | 17:51 | 38.3407 | -122.2578 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 102284869 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42983 | 0.74375 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1398 | 2017 | 9 | 5 | 17 | 51 | 17-0076150 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 17019 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-05 17:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-06 | 19:26 | 40.8392 | -122.3635 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103643183 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 0.80972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1399 | 2017 | 9 | 6 | 19 | 26 | 17-0076501 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 23830 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-06 19:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-06 | 20:08 | 37.2925 | -122.294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100256917 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 0.83889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1400 | 2017 | 9 | 6 | 20 | 8 | 17-0076502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4914 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-06 20:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-08 | 4:47 | 38.7478 | -120.859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101391575 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42986 | 0.19931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1401 | 2017 | 9 | 8 | 4 | 47 | 17-0076889 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 39736 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-08 04:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-08 | 17:21 | 38.6039 | -120.9275 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101379094 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42986 | 0.72292 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1402 | 2017 | 9 | 8 | 17 | 21 | 17-0077122 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 8504 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-08 17:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-08 | 21:14 | 37.9604 | -120.3764 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | John Lite 209-984-5623 | 101042521 | Unknown | 17000 | Conductor | Overhead | Yes | 42986 | 0.88472 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1403 | 2017 | 9 | 8 | 21 | 14 | 17-0077137 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49858 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-08 21:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-09 | 18:36 | 36.6618 | -121.5477 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101769870 | Unknown | 12000 | Conductor | Overhead | Yes | 42987 | 0.775 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1404 | 2017 | 9 | 9 | 18 | 36 | 17-0077248 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 3776 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-09 18:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-10 | 1:22 | 39.2599 | -121.4902 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | TYLER LOPEZ | 101289867 | None | 12000 | Conductor | Overhead | Yes | 42988 | 0.056944 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1405 | 2017 | 9 | 10 | 1 | 22 | 17-0077285 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 803 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-10 01:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-10 | 16:30 | 37.3039 | -120.5275 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Merced County FD | 101161316 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42988 | 0.6875 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1406 | 2017 | 9 | 10 | 16 | 30 | 17-0077362 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 228 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-10 16:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-11 | 7:18 | 37.0008 | -121.6667 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100621936 | VERIZON CALIFORNIA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1407 | 2017 | 9 | 11 | 7 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-09-11 07:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-11 | 8:50 | 36.9515 | -121.842 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101790954 | PACIFIC BELL | 21000 | Fuse | Overhead | Yes | 42989 | 0.36806 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | no-match | 1408 | 2017 | 9 | 11 | 8 | 50 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-09-11 08:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-11 | 23:50 | 40.8672 | -124.0883 | Vegetation | Urban | < 3 Meters | Fire Agency | BOB | 100964579 | Unknown | 12000 | Conductor | Overhead | Yes | 42989 | 0.99306 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1409 | 2017 | 9 | 11 | 23 | 50 | 17-0078018 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 20370 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-11 23:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-12 | 9:24 | 39.741 | -121.6079 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 911 | 100330302 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42990 | 0.39167 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1410 | 2017 | 9 | 12 | 9 | 24 | 17-0078149 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 402890 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-12 09:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-12 | 17:18 | 39.4511 | -121.6052 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | tom klage 530 538-7888 | 100419482 | Unknown | 12000 | Conductor | Overhead | Yes | 42990 | 0.72083 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1411 | 2017 | 9 | 12 | 17 | 18 | 17-0078354 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 66807 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-12 17:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-14 | 11:02 | 39.1111 | -121.5565 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 101320308 | None | 12000 | Switch | Overhead | Yes | 42992 | 0.45972 | Equipment/ Facility Failure | Switch | N.A. | N.A. | Unknown |  | Other/Unknown | 1412 | 2017 | 9 | 14 | 11 | 2 | 17-0079046 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 22127 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-14 11:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-14 | 12:09 | 39.5039 | -121.5453 | Vegetation | Urban | < 0.25 Acres | Fire Agency | 530-538-2448 | 100372805 | Unknown | 12000 | Conductor | Overhead | Yes | 42992 | 0.50625 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1413 | 2017 | 9 | 14 | 12 | 9 | 17-0078947 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 68082 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-14 12:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-14 | 14:06 | 40.2942 | -123.8174 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100989497 | Unknown | 12000 | Conductor | Overhead | Yes | 42992 | 0.5875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1414 | 2017 | 9 | 14 | 14 | 6 | 17-0079010 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 19722 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-14 14:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-15 | 14:55 | 39.7461 | -121.4885 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100335239 | Unknown | 12000 | Conductor | Overhead | Yes | 42993 | 0.62153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1415 | 2017 | 9 | 15 | 14 | 55 | 17-0079388 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 8834 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-15 14:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-17 | 15:05 | 36.6473 | -119.3861 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 100738741 | VERIZON CALIFORNIA | 0 – 750 | Conductor | Overhead | Yes | 42995 | 0.62847 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1416 | 2017 | 9 | 17 | 15 | 5 | 17-0079580 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 2216 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-17 15:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-17 | 17:38 | 38.9946 | -121.0261 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100029537 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42995 | 0.73472 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Branch (OverHanging) | 1417 | 2017 | 9 | 17 | 17 | 38 | 17-0079585 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 28509 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-17 17:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-18 | 13:01 | 39.3889 | -121.4054 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 103795057 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42996 | 0.54236 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1418 | 2017 | 9 | 18 | 13 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-09-18 13:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-18 | 15:10 | 39.6013 | -122.0555 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103849874 | Unknown | 12000 | Conductor | Overhead | Yes | 42996 | 0.63194 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1419 | 2017 | 9 | 18 | 15 | 10 | 17-0079776 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 34081 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-18 15:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-18 | 18:01 | 38.2197 | -122.543 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101997149 | Unknown | 12000 | Conductor | Overhead | Yes | 42996 | 0.75069 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1420 | 2017 | 9 | 18 | 18 | 1 | 17-0079821 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 24834 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-18 18:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-18 | 19:01 | 38.0742 | -122.8286 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102229215 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42996 | 0.79236 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1421 | 2017 | 9 | 18 | 19 | 1 | 17-0079828 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 2784 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-18 19:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-18 | 23:50 | 37.9088 | -120.4865 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | incident comander geoff marshall 209-419-4407 | 101040882 | Unknown | 17000 | Conductor | Overhead | Yes | 42996 | 0.99306 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1422 | 2017 | 9 | 18 | 23 | 50 | 17-0079858 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 382303 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-18 23:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-19 | 19:13 | 35.4784 | -119.2959 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100207112 | Unknown | 12000 | Conductor | Overhead | Yes | 42997 | 0.80069 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1423 | 2017 | 9 | 19 | 19 | 13 | 17-0080147 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 102195 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-19 19:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-20 | 2:06 | 37.2597 | -122.3222 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100322388 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42998 | 0.0875 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1424 | 2017 | 9 | 20 | 2 | 6 | 17-0080179 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 36593 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-20 02:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-20 | 8:41 | 36.9404 | -120.9014 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 2/6 - Arburua Tap | None | 70000 | Conductor | Overhead | Yes | 42998 | 0.36181 | Contact From Object | N.A. | Other | Electric Facility | Other | bird's nest | no-match | 1425 | 2017 | 9 | 20 | 8 | 41 | INT-10165 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-20 08:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-21 | 8:39 | 39.6147 | -121.7258 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 100347380 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42999 | 0.36042 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1426 | 2017 | 9 | 21 | 8 | 39 | 17-0080558 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2231 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-21 08:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-22 | 14:28 | 36.0961 | -120.0577 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SAME AS TAG. FD NOT STANDING BY UPON ARRIVAL | 100663084 | Unknown | 12000 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1427 | 2017 | 9 | 22 | 14 | 28 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-09-22 14:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-23 | 9:16 | 37.0127 | -120.6256 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101181497 | Unknown | 12000 | Conductor | Overhead | Yes | 43001 | 0.38611 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1428 | 2017 | 9 | 23 | 9 | 16 | 17-0081190 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 10366 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-23 09:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-23 | 14:17 | 40.6509 | -122.2974 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DARREN STEWART 448-2421 | 101467221 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43001 | 0.59514 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1429 | 2017 | 9 | 23 | 14 | 17 | 17-0081216 | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 98820 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-23 14:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-24 | 2:13 | 38.1046 | -120.989 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 016/297 | Unknown | 60000 | Conductor | Overhead | Yes | 43002 | 0.092361 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1430 | 2017 | 9 | 24 | 2 | 13 | INT-10181 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-24 02:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-24 | 7:54 | 37.4014 | -122.0274 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100515206 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43002 | 0.32917 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1431 | 2017 | 9 | 24 | 7 | 54 | 17-0081260 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 28758 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-24 07:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-24 | 16:42 | 38.3869 | -122.9667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DOUG JONES | 101973946 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43002 | 0.69583 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1432 | 2017 | 9 | 24 | 16 | 42 | 17-0081329 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 22574 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-24 16:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-25 | 19:49 | 36.8137 | -121.721 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | Tower 058/249 | Unknown | 230000 | Conductor | Overhead | Yes | 43003 | 0.82569 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | no-match | 1433 | 2017 | 9 | 25 | 19 | 49 | INT-10186 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-25 19:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-26 | 17:44 | 38.0643 | -122.8056 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102228291 | Unknown | 12000 | Other | Overhead | Yes | 43004 | 0.73889 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1434 | 2017 | 9 | 26 | 17 | 44 | 17-0081913 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 305236 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-26 17:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-27 | 9:11 | 39.0163 | -122.8685 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 102143577 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 43005 | 0.38264 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1435 | 2017 | 9 | 27 | 9 | 11 | 17-0082050 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-09-27 09:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-27 | 12:12 | 39.4845 | -121.3545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | bill lopez cell 530 521-8052 | 100429924 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 43005 | 0.50833 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1436 | 2017 | 9 | 27 | 12 | 12 | 17-0082180 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 6370 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-27 12:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-27 | 19:06 | 40.7592 | -123.995 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103660812 | Unknown | 12000 | Conductor | Overhead | Yes | 43005 | 0.79583 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1437 | 2017 | 9 | 27 | 19 | 6 | 17-0082303 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 35394 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-27 19:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-28 | 18:28 | 37.9884 | -122.097 | Vegetation | Urban | < 3 Meters | Fire Agency | (510)374-7070 | 103627505 | Unknown | 21000 | Conductor | Overhead | Yes | 43006 | 0.76944 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | Third-party caused | no-match | 1438 | 2017 | 9 | 28 | 18 | 28 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-09-28 18:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-29 | 2:01 | 39.5317 | -122.1857 | Vegetation | Urban | < 3 Meters | Unknown | N.A. | 100419384 | Unknown | 21000 | Transformer | Padmounted | Yes | 43007 | 0.084028 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1439 | 2017 | 9 | 29 | 2 | 1 | 17-0082713 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-09-29 02:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-09-30 | 15:08 | 37.4109 | -121.1747 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Tower 030/132 | None | 230000 | Conductor | Overhead | Yes | 43008 | 0.63056 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | Third-party caused | no-match | 1440 | 2017 | 9 | 30 | 15 | 8 | INT-10207 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-09-30 15:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-01 | 7:24 | 37.914 | -122.3771 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101437028 | Unknown | 12000 | Transformer | Overhead | Yes | 43009 | 0.30833 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1441 | 2017 | 10 | 1 | 7 | 24 | 17-0083120 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 46128 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-01 07:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-01 | 16:11 | 39.797 | -122.1185 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103850270 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43009 | 0.67431 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1442 | 2017 | 10 | 1 | 16 | 11 | 17-0083168 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 14337 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-01 16:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-01 | 23:51 | 40.0192 | -122.1452 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MARK FRITZ | 101534592 | Unknown | 12000 | Conductor | Overhead | Yes | 43009 | 0.99375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1443 | 2017 | 10 | 1 | 23 | 51 | 17-0083226 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 33448 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-01 23:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-02 | 2:55 | 37.3314 | -120.5243 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101160137 | Unknown | 12000 | Conductor | Overhead | Yes | 43010 | 0.12153 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1444 | 2017 | 10 | 2 | 2 | 55 | 17-0083233 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 184228 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-02 02:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-02 | 7:07 | 38.2949 | -122.1066 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101658181 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 43010 | 0.29653 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1445 | 2017 | 10 | 2 | 7 | 7 | 17-0083252 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 523 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-02 07:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-02 | 12:22 | 39.6313 | -122.0069 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 103224422 | Unknown | 12000 | Conductor | Overhead | Yes | 43010 | 0.51528 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1446 | 2017 | 10 | 2 | 12 | 22 | 17-0083366 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 13548 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-02 12:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-02 | 14:56 | 38.9102 | -120.9185 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100110800 | None | 21000 | Other | Overhead | Yes | 43010 | 0.62222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1447 | 2017 | 10 | 2 | 14 | 56 | 17-0083516 | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 160 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-02 14:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-02 | 16:05 | 38.7182 | -120.9756 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101375963 | Unknown | 21000 | Conductor | Overhead | Yes | 43010 | 0.67014 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1448 | 2017 | 10 | 2 | 16 | 5 | 17-0083539 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4797 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-02 16:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-02 | 17:30 | 38.3634 | -122.2846 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102282538 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1449 | 2017 | 10 | 2 | 17 | 30 | 17-0083551 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 5621 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-02 17:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-03 | 17:48 | 35.1084 | -119.3786 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | span 001/019 - 001/020 | Unknown | 70000 | Conductor | Overhead | Yes | 43011 | 0.74167 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | no-match | 1450 | 2017 | 10 | 3 | 17 | 48 | INT-10211 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-03 17:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-04 | 12:20 | 37.8169 | -121.2715 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LATHROP | 102091094 | Unknown | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1451 | 2017 | 10 | 4 | 12 | 20 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-04 12:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-04 | 23:42 | 38.6554 | -120.9934 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101375442 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 43012 | 0.9875 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1452 | 2017 | 10 | 4 | 23 | 42 | 17-0084323 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 7553 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-04 23:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-05 | 0:20 | 38.0052 | -121.7545 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 100456226 | Unknown | 21000 | Switch | Subsurface | Yes | 43013 | 0.013889 | Equipment/ Facility Failure | Switch | N.A. | N.A. | Unknown |  | Other/Unknown | 1453 | 2017 | 10 | 5 | 0 | 20 | 17-0084324 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 125529 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-05 00:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-05 | 10:57 | 39.4664 | -122.167 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100343435 | PACIFIC BELL | 21000 | Other | Overhead | Yes | 43013 | 0.45625 | Contact From Object | N.A. | Other | Electric Facility | Other | bird's Nest | no-match | 1454 | 2017 | 10 | 5 | 10 | 57 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-05 10:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-06 | 7:24 | 38.5607 | -121.7642 | Vegetation | Urban | < 3 Meters | Fire Agency | 5307583600 | 101639481 | PACIFIC BELL | 12000 | Lightning Arrestor | Overhead | Yes | 43014 | 0.30833 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | Other/Unknown | 1455 | 2017 | 10 | 6 | 7 | 24 | 17-0084680 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-06 07:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-06 | 12:03 | 39.4645 | -122.1124 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100344016 | Unknown | 21000 | Conductor | Overhead | Yes | 43014 | 0.50208 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1456 | 2017 | 10 | 6 | 12 | 3 | 17-0084731 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 15345 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-06 12:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-06 | 16:04 | 40.9712 | -124.0372 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JO BOB | 100978977 | Unknown | 12000 | Conductor | Overhead | Yes | 43014 | 0.66944 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1457 | 2017 | 10 | 6 | 16 | 4 | 17-0084817 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 19136 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-06 16:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-07 | 10:11 | 37.1988 | -121.8325 | Vegetation | Urban | < 0.25 Acres | Fire Agency | JOHN PAVLOFF | 100600703 | PACIFIC BELL | 21000 | Other | Overhead | Yes | 43015 | 0.42431 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1458 | 2017 | 10 | 7 | 10 | 11 | 17-0084938 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-07 10:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-08 | 5:11 | 40.3252 | -124.2881 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100987374 | FRONTIER COMMUNICATI | 12000 | Conductor | Overhead | Yes | 43016 | 0.21597 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1459 | 2017 | 10 | 8 | 5 | 11 | 17-0085031 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 5896 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 05:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-08 | 16:41 | 39.589 | -122.2015 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100341037 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43016 | 0.69514 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1460 | 2017 | 10 | 8 | 16 | 41 | No ILIS or TOTL available | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 16:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-08 | 16:43 | 40.8876 | -123.9918 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 100972408 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 0.69653 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1461 | 2017 | 10 | 8 | 16 | 43 | 17-0085141 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 132299 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 16:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-08 | 17:39 | 38.5331 | -121.5424 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 101585529 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 0.73542 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1462 | 2017 | 10 | 8 | 17 | 39 | 17-0085163 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 20460 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 17:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-08 | 19:11 | 37.2071 | -121.862 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100622560 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43016 | 0.79931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1463 | 2017 | 10 | 8 | 19 | 11 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 19:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-08 | 19:44 | 39.7446 | -121.597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100330456 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 0.82222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1464 | 2017 | 10 | 8 | 19 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 19:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-08 | 20:35 | 39.6315 | -121.4225 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100347747 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 0.85764 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1465 | 2017 | 10 | 8 | 20 | 35 | 17-0085196 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 181992 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 20:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-08 | 21:10 | 39.4554 | -121.0498 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100099226 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 0.88194 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (Not overhanging, > 12ft) | 1466 | 2017 | 10 | 8 | 21 | 10 | 17-0085261 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 255784 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 21:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-08 | 21:46 | 39.2595 | -120.9965 | Vegetation | Urban | < 0.25 Acres | Fire Agency | PHILLIP NUNNICK 530 273-3158 INCENDENT # 26264 | 100072730 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 43016 | 0.90694 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1467 | 2017 | 10 | 8 | 21 | 46 | 17-0085308 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 12650 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 21:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-08 | 22:19 | 39.7371 | -121.6464 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 103319605 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43016 | 0.92986 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1468 | 2017 | 10 | 8 | 22 | 19 | 17-0085504 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 42839 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 22:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-08 | 22:30 | 38.3226 | -121.9431 | Vegetation | Rural | < 0.25 Acres | Fire Agency | vaca | 101561309 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 43016 | 0.9375 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1469 | 2017 | 10 | 8 | 22 | 30 | 17-0085250 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 162623 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 22:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-08 | 22:54 | 35.5528 | -118.9681 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | span 7/87-7/88, Vedder Tap | Unknown | 115000 | Conductor | Overhead | Yes | 43016 | 0.95417 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1470 | 2017 | 10 | 8 | 22 | 54 | INT-10231 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 66311 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 22:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-08 | 22:58 | 39.3642 | -121.1131 | Vegetation | Rural | < 3 Meters | Fire Agency | INCIDENT NUMBER 26268 | 100068104 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43016 | 0.95694 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Fell into (No defect) | 1471 | 2017 | 10 | 8 | 22 | 58 | 17-0085355 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 198802 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 22:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-08 | 23:51 | 38.2758 | -121.9617 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 707-428-7305 | 101660727 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43016 | 0.99375 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 1472 | 2017 | 10 | 8 | 23 | 51 | No ILIS or TOTL available | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 23:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-09 | 1:02 | 38.7037 | -120.6725 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101408485 | Unknown | 21000 | Other | Overhead | Yes | 43017 | 0.043056 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1473 | 2017 | 10 | 9 | 1 | 2 | 17-0085324 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 419843 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-09 01:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-09 | 1:13 | 38.101 | -122.2196 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 102218775 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Grow Into | 1474 | 2017 | 10 | 9 | 1 | 13 | 17-0085350 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Grow Into | 15824 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-09 01:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-09 | 1:25 | 38.1906 | -121.9497 | Vegetation | Rural | 10 - 99 Acres | Unknown | N.A. | 101559973 | Unknown | 21000 | Conductor | Overhead | Yes | 43017 | 0.059028 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1475 | 2017 | 10 | 9 | 1 | 25 | 17-0085346 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 59416 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-09 01:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-09 | 1:29 | 37.8416 | -121.9583 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100501933 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43017 | 0.061806 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1476 | 2017 | 10 | 9 | 1 | 29 | No ILIS or TOTL available | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-09 01:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-09 | 1:45 | 38.8576 | -122.7221 | Vegetation | Rural | < 0.25 Acres | Fire Agency | wink | 103570679 | Unknown | 12000 | Conductor | Overhead | Yes | 43017 | 0.072917 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Other/Unknown | 1477 | 2017 | 10 | 9 | 1 | 45 | 17-0085344 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 219653 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-09 01:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-09 | 2:27 | 37.7293 | -122.1378 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100903727 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43017 | 0.10208 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Fell into (No defect) | 1478 | 2017 | 10 | 9 | 2 | 27 | 17-0085325 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 376540 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-09 02:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-09 | 4:36 | 38.2643 | -122.0488 | Vegetation | Urban | < 3 Meters | Fire Agency | Fairfield | 101660707 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43017 | 0.19167 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1479 | 2017 | 10 | 9 | 4 | 36 | 17-0085424 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 16160 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-09 04:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-09 | 12:05 | 35.4067 | -118.9623 | Vegetation | Urban | < 3 Meters | Customer | N.A. | 100252698 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43017 | 0.50347 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1480 | 2017 | 10 | 9 | 12 | 5 | 17-0085709 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2079 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-09 12:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-10 | 13:36 | 38.931 | -123.3023 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 102214553 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43018 | 0.56667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1481 | 2017 | 10 | 10 | 13 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-10 13:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-10 | 16:17 | 38.3148 | -122.7067 | Vegetation | Urban | .26 - 9.99 Acres | Unknown | N.A. | 101996286 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43018 | 0.67847 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1482 | 2017 | 10 | 10 | 16 | 17 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-10 16:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-10 | 16:29 | 37.2559 | -121.9586 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100542800 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 43018 | 0.68681 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1483 | 2017 | 10 | 10 | 16 | 29 | 17-0086126 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 235299 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-10 16:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-11 | 11:57 | 38.5015 | -123.0237 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101974930 | Unknown | 12000 | Conductor | Overhead | Yes | 43019 | 0.49792 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1484 | 2017 | 10 | 11 | 11 | 57 | 17-0086350 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 226925 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-11 11:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-11 | 16:41 | 38.679 | -121.9487 | Vegetation | Rural | < 3 Meters | Fire Agency | ESPARTO FIRE PROTECTION DISTRICT- (530) 787-3300 | 101591668 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43019 | 0.69514 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1485 | 2017 | 10 | 11 | 16 | 41 | No ILIS or TOTL available | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-11 16:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-13 | 8:30 | 38.0234 | -122.5376 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 102246021 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 43021 | 0.35417 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1486 | 2017 | 10 | 13 | 8 | 30 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-13 08:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-13 | 10:27 | 37.0561 | -122.0206 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Scotts Valley Fire Dept. | 101677721 | Unknown | 21000 | Conductor | Overhead | Yes | 43021 | 0.43542 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Grow Into | 1487 | 2017 | 10 | 13 | 10 | 27 | 17-0087093 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Grow Into | 201996 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-13 10:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-13 | 19:15 | 36.9415 | -120.0397 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 101224900 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43021 | 0.80208 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1488 | 2017 | 10 | 13 | 19 | 15 | 17-0087240 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 40212 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-13 19:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-13 | 22:19 | 39.7648 | -121.6307 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100325368 | PACIFIC BELL | 0 – 750 | Transformer | Overhead | Yes | 43021 | 0.92986 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1489 | 2017 | 10 | 13 | 22 | 19 | 17-0087321 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 7056 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-13 22:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-14 | 8:37 | 37.3944 | -122.0915 | Building | Urban | Structure Only | Fire Agency | Unknown | 100513237 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 43022 | 0.35903 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1490 | 2017 | 10 | 14 | 8 | 37 | 17-0087303 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 653412 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-14 08:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-14 | 14:43 | 40.1122 | -122.1737 | Vegetation | Rural | < 0.25 Acres | Self Extinguished | N.A. | 101539953 | None | 12000 | Fuse | Overhead | Yes | 43022 | 0.61319 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1491 | 2017 | 10 | 14 | 14 | 43 | 17-0087411 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2175 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-14 14:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-15 | 13:15 | 37.3855 | -121.8133 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | SA JOSE FD | 100563705 | Unknown | 12000 | Conductor | Overhead | Yes | 43023 | 0.55208 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1492 | 2017 | 10 | 15 | 13 | 15 | 17-0087543 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 65732 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-15 13:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-16 | 12:10 | 36.5831 | -121.9368 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101781248 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43024 | 0.50694 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | Other/Unknown | 1493 | 2017 | 10 | 16 | 12 | 10 | 17-0087767 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 6313 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-16 12:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-16 | 12:20 | 37.72 | -122.0687 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100900970 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43024 | 0.51389 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | no-match | 1494 | 2017 | 10 | 16 | 12 | 20 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-16 12:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-16 | 12:26 | 36.6641 | -121.0995 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Nick Shawkey E4462 209-402-1645 Cover Engine from Tuolumne Calaveras Unit | 101689865 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43024 | 0.51806 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1495 | 2017 | 10 | 16 | 12 | 26 | 17-0087754 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 519 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-16 12:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-17 | 18:22 | 35.4257 | -119.0297 | Vegetation | Urban | < 3 Meters | Self Extinguished | N.A. | 100144662 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | Yes | 43025 | 0.76528 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1496 | 2017 | 10 | 17 | 18 | 22 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-17 18:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-18 | 13:58 | 37.636 | -122.0793 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100952408 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43026 | 0.58194 | Contact From Object | N.A. | Vehicle | N.A. | Human Error |  | no-match | 1497 | 2017 | 10 | 18 | 13 | 58 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-18 13:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-20 | 5:59 | 36.7475 | -119.763 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100859697 | Unknown | 12000 | Conductor | Overhead | Yes | 43028 | 0.24931 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1498 | 2017 | 10 | 20 | 5 | 59 | 17-0089003 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 181677 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-20 05:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-20 | 6:18 | 39.2922 | -121.0157 | Vegetation | Rural | < 3 Meters | Fire Agency | PHILLIP NUNNINK INCIDENT # 27272 | 100087647 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43028 | 0.2625 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1499 | 2017 | 10 | 20 | 6 | 18 | 17-0088957 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 102410 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-20 06:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-20 | 9:06 | 36.036 | -120.058 | Vegetation | Rural | 300 - 999 Acres | Fire Agency | Unknown | Pole 009/009 | Unknown | 70000 | Conductor | Overhead | Yes | 2017-10-20 | 0.37917 | Contact From Object | N.A. | Other | Electric Facility | Other | bird's nest | no-match | 1500 | 2017 | 10 | 20 | 9 | 6 | INT-10298 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | Unk or Other | Unk or Other - Other | 603172 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-20 09:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-20 | 13:43 | 35.353 | -119.9873 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Kevin McLean Office(805)593-3421, Cell(805)903-3421 | 100136483 | Unknown | 12000 | Conductor | Overhead | Yes | 43028 | 0.57153 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1501 | 2017 | 10 | 20 | 13 | 43 | 17-0089282 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 5250 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-20 13:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-20 | 13:45 | 34.5532 | -120.5303 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 101921492 | Unknown | 12000 | Conductor | Overhead | Yes | 43028 | 0.57292 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1502 | 2017 | 10 | 20 | 13 | 45 | 17-0089249 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 173 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-20 13:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-20 | 14:00 | 36.9216 | -119.7283 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100727124 | Unknown | 21000 | Fuse | Overhead | Yes | 43028 | 0.58333 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1503 | 2017 | 10 | 20 | 14 | 0 | 17-0089227 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 7170 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-20 14:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-21 | 15:08 | 39.064 | -122.7765 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102155186 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43029 | 0.63056 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1504 | 2017 | 10 | 21 | 15 | 8 | 17-0089392 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 13374 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-21 15:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-21 | 16:05 | 37.5911 | -122.0099 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Unknown | 103516949 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43029 | 0.67014 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | Third-party caused | no-match | 1505 | 2017 | 10 | 21 | 16 | 5 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-21 16:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-23 | 19:34 | 36.0772 | -121.019 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101763398 | Unknown | 12000 | Conductor | Overhead | Yes | 43031 | 0.81528 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1506 | 2017 | 10 | 23 | 19 | 34 | 17-0089813 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1050 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-23 19:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-23 | 21:24 | 37.3713 | -122.348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100270421 | Unknown | 12000 | Conductor | Overhead | Yes | 43031 | 0.89167 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1507 | 2017 | 10 | 23 | 21 | 24 | 17-0089820 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1768 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-23 21:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-24 | 15:23 | 36.8599 | -121.7947 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101789001 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 43032 | 0.64097 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1508 | 2017 | 10 | 24 | 15 | 23 | 17-0090025 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 119910 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-24 15:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-26 | 10:53 | 36.4036 | -121.9122 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101777002 | Unknown | 12000 | Conductor | Overhead | Yes | 43034 | 0.45347 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | no-match | 1509 | 2017 | 10 | 26 | 10 | 53 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-26 10:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-28 | 15:26 | 39.4516 | -123.3838 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102209084 | Unknown | 12000 | Conductor | Overhead | Yes | 43036 | 0.64306 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | no-match | 1510 | 2017 | 10 | 28 | 15 | 26 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-10-28 15:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-28 | 20:08 | 35.0222 | -118.7691 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100223850 | Unknown | 12000 | Fuse | Overhead | Yes | 43036 | 0.83889 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1511 | 2017 | 10 | 28 | 20 | 8 | 17-0091074 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 6993 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-28 20:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-31 | 18:56 | 39.0034 | -121.6907 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | Pole 010/208 | Unknown | 60000 | Conductor | Overhead | Yes | 43039 | 0.78889 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | Third-party caused | no-match | 1512 | 2017 | 10 | 31 | 18 | 56 | INT-10324 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 289611 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-31 18:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-10-31 | 21:02 | 39.1119 | -122.9163 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Structure 020/003 | Unknown | 60000 | Conductor | Overhead | Yes | 43039 | 0.87639 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | no-match | 1513 | 2017 | 10 | 31 | 21 | 2 | INT-10325 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 50730 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-31 21:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-06 | 9:59 | 37.146 | -121.6675 | Vegetation | Rural | < 0.25 Acres | Fire Agency | INCIDENT # 1717CASCU008183 | 103570543 | YES | 21000 | Conductor | Overhead | Yes | 43045 | 0.41597 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1514 | 2017 | 11 | 6 | 9 | 59 | 17-0092884 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-11-06 09:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-06 | 15:06 | 38.2998 | -122.503 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 101982913 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43045 | 0.62917 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1515 | 2017 | 11 | 6 | 15 | 6 | 17-0093035 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 511197 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-06 15:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-08 07:12 | 07:11 | 37.7367 | -120.3459 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101191714 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43047.2998 | 07:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1516 | 2017 | 11 | 8 | 7 | 11 | 17-0093414 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 1573 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-08 07:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-08 14:53 | 14:53 | 37.792 | -122.2221 | Building | Urban | Structure Only | Fire Agency | Unknown | 101352529 | Unknown | 4000 | Conductor | Overhead | Yes | 43047.6202 | 14:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1517 | 2017 | 11 | 8 | 14 | 53 | 17-0093620 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 119122 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-08 14:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-11 12:17 | 11:57 | 35.1191 | -120.3936 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Jordan Dayley ph#929-3911,engine#3467 | 101931190 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43050.5115 | 0.49792 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1518 | 2017 | 11 | 11 | 11 | 57 | 17-0094408 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29093 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-11 11:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-12 19:45 | 19:44 | 36.7378 | -119.7769 | Building | Urban | < 0.25 Acres | Fire Agency | capt will johnson | 100871063 | Unknown | 12000 | Capacitor Bank | Overhead | Yes | 43051.8227 | 19:44 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | Other/Unknown | 1519 | 2017 | 11 | 12 | 19 | 44 | 17-0094544 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 315 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-12 19:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-14 07:43 | 07:43 | 37.324 | -120.8146 | Vegetation | Rural | < 3 Meters | Fire Agency | cammu #023223 | 103853299 | Unknown | 12000 | Transformer | Overhead | Yes | 43053.3219 | 07:43 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1520 | 2017 | 11 | 14 | 7 | 43 | 17-0094855 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4416 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-14 07:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-17 09:53 | 09:53 | 37.0802 | -120.0194 | Other | Rural | < 3 Meters | Utility: PG&E | N.A. | 101029626 | Unknown | 12000 | Fuse | Overhead | Yes | 43056.4118 | 09:53 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1521 | 2017 | 11 | 17 | 9 | 53 | 17-0095883 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4741 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-17 09:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-20 08:33 | 08:32 | 38.7584 | -120.8439 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101389405 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43059.3562 | 08:32 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1522 | 2017 | 11 | 20 | 8 | 32 | 17-0096436 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 12376 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-20 08:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-20 20:06 | 20:05 | 35.4995 | -118.9099 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 661-324-6551 | 103782809 | None | 0 – 750 | Conductor | Overhead | Yes | 43059.8372 | 20:05 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1523 | 2017 | 11 | 20 | 20 | 5 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-11-20 20:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-21 11:55 | 11:55 | 37.6101 | -121.3332 | Vegetation | Rural | < 0.25 Acres | Fire Agency | tracy fire dept | 102053617 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43060.4966 | 11:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1524 | 2017 | 11 | 21 | 11 | 55 | 17-0096814 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 7290 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-21 11:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-22 14:03 | 13:44 | 36.752 | -121.6636 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103154362 | Unknown | 12000 | Conductor | Overhead | Yes | 43061.5857 | 0.57222 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1525 | 2017 | 11 | 22 | 13 | 44 | 17-0097162 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-11-22 13:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-23 16:34 | 16:29 | 35.7755 | -120.6941 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101860971 | Unknown | 12000 | Conductor | Overhead | Yes | 43062.6902 | 0.68681 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1526 | 2017 | 11 | 23 | 16 | 29 | 17-0097311 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 17501 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-23 16:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-24 10:33 | 10:33 | 36.6213 | -120.0617 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | KERMAN FIRE DEP. | 100700090 | Unknown | 12000 | Conductor | Overhead | Yes | 43063.4398 | 10:33 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1527 | 2017 | 11 | 24 | 10 | 33 | 17-0097379 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 15795 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-24 10:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-25 06:51 | 6:29 | 36.0144 | -119.9556 | Vegetation | Rural | < 3 Meters | Utility: PG&E | N.A. | 100693913 | Unknown | 12000 | Conductor | Overhead | Yes | 43064.2855 | 0.27014 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1528 | 2017 | 11 | 25 | 6 | 29 | 17-0097454 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 36494 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-25 06:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-26 10:16 | 10:10 | 36.7098 | -119.5632 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100815464 | VERIZON CALIFORNIA | 0 – 750 | Conductor | Overhead | Yes | 43065.4276 | 0.42361 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1529 | 2017 | 11 | 26 | 10 | 10 | 17-0097585 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 5876 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-26 10:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-27 06:24 | 06:23 | 36.6942 | -121.6583 | Vegetation | Urban | < 3 Meters | Fire Agency | 831-758-7261 | 101723997 | Unknown | 12000 | Conductor | Overhead | Yes | 43066.2666 | 06:23 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1530 | 2017 | 11 | 27 | 6 | 23 | 17-0097701 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 10196 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-27 06:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-27 11:11 | 11:11 | 37.1296 | -122.3124 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100268264 | Unknown | 12000 | Conductor | Overhead | Yes | 43066.4661 | 11:11 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1531 | 2017 | 11 | 27 | 11 | 11 | 17-0097825 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 3620 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-27 11:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-28 15:50 | 15:49 | 36.4974 | -119.7909 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 100806272 | Unknown | 12000 | Other | Overhead | Yes | 43067.6597 | 15:49 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1532 | 2017 | 11 | 28 | 15 | 49 | 17-0098188 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 26000 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-28 15:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-11-29 17:35 | 17:34 | 38.6841 | -120.6546 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 101419450 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 43068.7326 | 17:34 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1533 | 2017 | 11 | 29 | 17 | 34 | 17-0098456 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 582825 | 0 | NA | <25mph | <15mph | #REF! | 2017-11-29 17:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-07 12:26 | 12:25 | 34.7115 | -120.1772 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 015/220 | Unknown | 115000 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1534 | 2017 | 12 | 7 | 12 | 25 | 17-0097211 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-12-07 12:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-12 04:57 | 4:40 | 39.7711 | -121.5973 | Building | Urban | Structure Only | Fire Agency | paradise fire city department | 100324902 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 43081.2064 | 0.19444 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1535 | 2017 | 12 | 12 | 4 | 40 | 17-0101233 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 50315 | 0 | NA | <25mph | <15mph | #REF! | 2017-12-12 04:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-13 | 12:13 | 35.5922 | -120.6474 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103390807 | Unknown | 21000 | Other | Overhead | Yes | 43082 | 0.50903 | Equipment/ Facility Failure | Recloser | N.A. | N.A. | Unknown |  | Other/Unknown | 1536 | 2017 | 12 | 13 | 12 | 13 | 17-0101477 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 53490 | 0 | NA | <25mph | <15mph | #REF! | 2017-12-13 12:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-14 | 1:33 | 37.1979 | -121.8375 | Building | Rural | Structure Only | Fire Agency | Unknown | 100622323 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43083 | 0.064583 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1537 | 2017 | 12 | 14 | 1 | 33 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-12-14 01:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-14 | 17:16 | 34.5878 | -120.3566 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101911004 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 43083 | 0.71944 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1538 | 2017 | 12 | 14 | 17 | 16 | 17-0101672 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2896 | 0 | NA | <25mph | <15mph | #REF! | 2017-12-14 17:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-16 | 7:01 | 39.7447 | -122.1961 | Building | Urban | Structure Only | Fire Agency | ORLAND CITY FIRE DEPT | 100428554 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43085 | 0.29236 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1539 | 2017 | 12 | 16 | 7 | 1 | 17-0101912 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2793 | 0 | NA | <25mph | <15mph | #REF! | 2017-12-16 07:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-16 | 11:51 | 38.8171 | -122.7041 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Shawn Ohare | 102167231 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43085 | 0.49375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1540 | 2017 | 12 | 16 | 11 | 51 | 17-0102101 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26120 | 0 | NA | <25mph | <15mph | #REF! | 2017-12-16 11:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-16 | 13:39 | 37.9702 | -121.6409 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE CAPTAIN ON DUTY | 100473121 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43085 | 0.56875 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1541 | 2017 | 12 | 16 | 13 | 39 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-12-16 13:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-16 | 16:03 | 35.6593 | -120.4946 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103131190 | Unknown | 21000 | Conductor | Overhead | Yes | 43085 | 0.66875 | Other | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1542 | 2017 | 12 | 16 | 16 | 3 | 17-0102180 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 32 | 0 | NA | <25mph | <15mph | #REF! | 2017-12-16 16:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-19 | 7:05 | 36.2715 | -120.3927 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100745841 | Unknown | 12000 | Fuse | Overhead | Yes | 43088 | 0.29514 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1543 | 2017 | 12 | 19 | 7 | 5 | 17-0102522 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 1301 | 0 | NA | <25mph | <15mph | #REF! | 2017-12-19 07:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-19 | 16:55 | 35.2309 | -119.5984 | Vegetation | Rural | < 0.25 Acres | Fire Agency | KC FIRE DEPT | 100165540 | Unknown | 21000 | Conductor | Overhead | Yes | 43088 | 0.70486 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1544 | 2017 | 12 | 19 | 16 | 55 | 17-0102576 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 3351 | 0 | NA | <25mph | <15mph | #REF! | 2017-12-19 16:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-19 | 19:45 | 40.7271 | -122.3263 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101457738 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43088 | 0.82292 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1545 | 2017 | 12 | 19 | 19 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-12-19 19:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-20 07:55 | 07:54 | 37.4012 | -122.3606 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100318864 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43089.3298 | 07:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1546 | 2017 | 12 | 20 | 7 | 54 | 17-0102756 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6602 | 0 | NA | <25mph | <15mph | #REF! | 2017-12-20 07:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-20 14:04 | 14:03 | 35.6646 | -121.244 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103857828 | Unknown | 12000 | Fuse | Overhead | No |  |  | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1547 | 2017 | 12 | 20 | 14 | 3 | 17-0102828 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 31041 | 0 | NA | <25mph | <15mph | #REF! | 2017-12-20 14:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-20 16:05 | 16:04 | 34.6105 | -120.3218 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101906902 | VERIZON CALIFORNIA | 12000 | Fuse | Overhead | Yes | 43089.6701 | 16:04 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1548 | 2017 | 12 | 20 | 16 | 4 | 17-0102840 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 581 | 0 | NA | <25mph | <15mph | #REF! | 2017-12-20 16:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-22 14:38 | 14:38 | 35.3375 | -119.0637 | Building | Urban | Structure Only | Fire Agency | Unknown | 5895SW | Unknown | 21000 | Switch | Subsurface | Yes | 43091.61 | 14:38 | Equipment/ Facility Failure | Switch | N.A. | N.A. | Unknown |  | Other/Unknown | 1549 | 2017 | 12 | 22 | 14 | 38 | 17-0103055 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 544 | 0 | NA | <25mph | <15mph | #REF! | 2017-12-22 14:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-24 | 6:41 | 37.4444 | -122.1898 | Building | Urban | Structure Only | Fire Agency | Menlo Park FD | 103511827 | Unknown | 4000 | Conductor | Overhead | Yes | 43093 | 0.27847 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1550 | 2017 | 12 | 24 | 6 | 41 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-12-24 06:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-24 03:54 | 03:53 | 40.4618 | -122.3277 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101496394 | Unknown | 12000 | Conductor | Overhead | Yes | 43093.1623 | 03:53 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1551 | 2017 | 12 | 24 | 3 | 53 | 17-0103187 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 387230 | 0 | NA | <25mph | <15mph | #REF! | 2017-12-24 03:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2017-12-29 | 16:31 | 37.8517 | -122.1586 | Vegetation | Rural | < 3 Meters | Fire Agency | 925-933-1313 | 100488954 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1552 | 2017 | 12 | 29 | 16 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2017-12-29 16:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-01-01 | 1:35 | 37.1246 | -120.3042 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Prison system fire Dept. | 101128983 | Unknown | 12000 | Conductor | Overhead | No | N.A. | N.A. | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1553 | 2018 | 1 | 1 | 1 | 35 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-01-01 01:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-01-01 | 16:00 | 35.4578 | -120.9578 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101882074 | Unknown | 12000 | Conductor | Overhead | No | N.A. | N.A. | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1554 | 2018 | 1 | 1 | 16 | 0 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-01-01 16:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-01-13 | 18:34 | 35.3643 | -120.8218 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | Str. 002/010 | None | 230000 | Conductor | Overhead | No | N.A. | N.A. | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Marker ball | no-match | 1555 | 2018 | 1 | 13 | 18 | 34 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-01-13 18:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-01-16 | 14:25 | 34.5703 | -119.9645 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101921689 | Verizon | 12000 | Conductor | Overhead | Yes | 43116 | 0.60069 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1556 | 2018 | 1 | 16 | 14 | 25 | 18-0006506 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 23519 | 0 | NA | <25mph | <15mph | #REF! | 2018-01-16 14:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-02-01 | 17:41 | 37.972 | -121.3229 | Building | Urban | Structure Only | Self Extinguished | N.A. | 102057437 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43132 | 0.73681 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | no-match | 1557 | 2018 | 2 | 1 | 17 | 41 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-02-01 17:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-02-07 | 5:44 | 40.6543 | -122.5198 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 103922730 | Unknown | 12000 | Conductor | Overhead | Yes | 43138 | 0.23889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1558 | 2018 | 2 | 7 | 5 | 44 | 18-0012073 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 9610 | 0 | NA | <25mph | <15mph | #REF! | 2018-02-07 05:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-02-07 | 9:16 | 38.0369 | -120.2096 | Vegetation | Rural | < 3 meters | Fire Agency | Jason Podesta 209-586-3362 | 101038120 | AT&T | 17000 | Conductor | Overhead | Yes | 43138 | 0.38611 | Contact From Object | N.A. | Other | Electric Facility | Human Error | third-party caused | Other/Unknown | 1559 | 2018 | 2 | 7 | 9 | 16 | 18-0012146 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 78738 | 0 | NA | <25mph | <15mph | #REF! | 2018-02-07 09:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-02-09 | 18:56 | 39.1529 | -122.2296 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101626240 | Unknown | 12000 | Conductor | Overhead | Yes | 43140 | 0.78889 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1560 | 2018 | 2 | 9 | 18 | 56 | 18-0013023 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 41556 | 0 | NA | <25mph | <15mph | #REF! | 2018-02-09 18:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-02-12 | 20:20 | 39.9395 | -121.6494 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430947 | Unknown | 12000 | Conductor | Overhead | Yes | 43143 | 0.84722 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1561 | 2018 | 2 | 12 | 20 | 20 | 18-0013604 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 149212 | 0 | NA | <25mph | <15mph | #REF! | 2018-02-12 20:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-02-25 | 13:19 | 36.253 | -120.3153 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 559-294-6818 | 100744054 | Unknown | 12000 | Conductor | Overhead | Yes | 43156 | 0.55486 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1562 | 2018 | 2 | 25 | 13 | 19 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-02-25 13:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-02-26 | 16:33 | 35.5302 | -118.9695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100208194 | Unknown | 21000 | Conductor | Overhead | Yes | 43157 | 0.68958 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1563 | 2018 | 2 | 26 | 16 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-02-26 16:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-03-03 | 12:15 | 39.1213 | -121.055 | Building | Urban | Structure Only | Unknown | N.A. | 100095928 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43162 | 0.51042 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1564 | 2018 | 3 | 3 | 12 | 15 | 18-0019280 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 15750 | 0 | NA | <25mph | <15mph | #REF! | 2018-03-03 12:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-03-05 | 16:24 | 34.993 | -118.9011 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Kern County FD | 103235837 | Unknown | 12000 | Unknown | Overhead | Yes | 43164 | 0.68333 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1565 | 2018 | 3 | 5 | 16 | 24 | 18-0020085 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 356 | 0 | NA | <25mph | <15mph | #REF! | 2018-03-05 16:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-03-06 | 17:57 | 38.2811 | -120.8965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-647-5220 | 101238429 | AT&T | 12000 | Conductor | Overhead | Yes | 43165 | 0.74792 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1566 | 2018 | 3 | 6 | 17 | 57 | 18-0020396 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 142000 | 0 | NA | <25mph | <15mph | #REF! | 2018-03-06 17:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-03-10 | 15:22 | 39.2731 | -122.1818 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101635717 | Unknown | 12000 | Lightning Arrestor | Overhead | Yes | 43169 | 0.64028 | Contact From Object | N.A. | Other | Electric Facility | Other | bird's nest | Other/Unknown | 1567 | 2018 | 3 | 10 | 15 | 22 | 18-0021576 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 103540 | 0 | NA | <25mph | <15mph | #REF! | 2018-03-10 15:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-03-12 | 3:26 | 38.9513 | -122.0647 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 103781246 | Unknown | 12000 | Other | Overhead | Yes | 43171 | 0.14306 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1568 | 2018 | 3 | 12 | 3 | 26 | 18-0021726 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 17820 | 0 | NA | <25mph | <15mph | #REF! | 2018-03-12 03:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-03-26 | 17:06 | 38.7304 | -122.6215 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102166450 | AT&T | 12000 | Conductor | Overhead | Yes | 43185 | 0.7125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1569 | 2018 | 3 | 26 | 17 | 6 | 18-0026824 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3255 | 0 | NA | <25mph | <15mph | #REF! | 2018-03-26 17:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-04-02 | 11:36 | 38.48 | -121.9946 | Vegetation | Rural | < 0.25 Acres | Fire Agency | WINTERS FIRE DEPT | 101577668 | Unknown | 12000 | Conductor | Overhead | Yes | 43192 | 0.48333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1570 | 2018 | 4 | 2 | 11 | 36 | 18-0028522 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10252 | 0 | NA | <25mph | <15mph | #REF! | 2018-04-02 11:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-04-03 | 14:46 | 37.0118 | -121.6152 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100611410 | Verizon | 21000 | Conductor | Overhead | Yes | 43193 | 0.61528 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1571 | 2018 | 4 | 3 | 14 | 46 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-04-03 14:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-04-12 | 14:17 | 34.966 | -120.4283 | Other | Urban | < 3 meters | Fire Agency | santa maria FD | 101871639 | Verizon | 0 – 750 | Conductor | Overhead | Yes | 43202 | 0.59514 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1572 | 2018 | 4 | 12 | 14 | 17 | 18-0031819 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 9002 | 0 | NA | <25mph | <15mph | #REF! | 2018-04-12 14:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-04-16 | 20:02 | 35.4365 | -118.8949 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 103228190 | Unknown | 12000 | Conductor | Overhead | Yes | 43206 | 0.83472 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1573 | 2018 | 4 | 16 | 20 | 2 | 18-0032836 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 17993 | 0 | NA | <25mph | <15mph | #REF! | 2018-04-16 20:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-04-23 | 20:20 | 37.6138 | -121.3612 | Vegetation | Rural | < 3 meters | Fire Agency | 209-464-4650 | Pole 1/9 | None | 115000 | Conductor | Overhead | Yes | 43213 | 0.84722 | Contact From Object | N.A. | Other | Electric Facility | Other | bird's nest | no-match | 1574 | 2018 | 4 | 23 | 20 | 20 | INT-10949 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 0 | 0 | NA | <25mph | <15mph | #REF! | 2018-04-23 20:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-04-24 | 12:00 | 36.386 | -119.7764 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 559-924-2150 Jason Allen | 102305550 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43214 | 0.5 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1575 | 2018 | 4 | 24 | 12 | 0 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-04-24 12:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-04-24 | 19:15 | 36.8112 | -119.826 | Building | Urban | Structure Only | Fire Agency | FRESNO FIRE DEPT, 559 621 4199 | 100830359 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43214 | 0.80208 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1576 | 2018 | 4 | 24 | 19 | 15 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-04-24 19:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-04-27 | 12:48 | 39.1717 | -120.8652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | incident # 9960 ph # 530-8850111 | 100075314 | Unknown | 12000 | Conductor | Overhead | Yes | 43217 | 0.53333 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Dead | 1577 | 2018 | 4 | 27 | 12 | 48 | 18-0036310 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 28650 | 0 | NA | <25mph | <15mph | #REF! | 2018-04-27 12:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-04-29 | 11:54 | 36.1346 | -119.5489 | Vegetation | Rural | < 3 meters | Self Extinguished | N.A. | 103247569 | Unknown | 12000 | Fuse | Overhead | Yes | 43219 | 0.49583 | Contact from Object | N.A. | Other | Electric Facility | Other | bird's nest | Other/Unknown | 1578 | 2018 | 4 | 29 | 11 | 54 | 18-0036609 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 480 | 0 | NA | <25mph | <15mph | #REF! | 2018-04-29 11:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-04-30 | 14:33 | 35.0437 | -120.4942 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Chris Compmas 805-929-3911 | 101893032 | Unknown | 12000 | Conductor | Overhead | Yes | 43220 | 0.60625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1579 | 2018 | 4 | 30 | 14 | 33 | 18-0036977 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 70104 | 0 | NA | <25mph | <15mph | #REF! | 2018-04-30 14:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-04 | 16:34 | 38.0148 | -121.9988 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Contra Costa FD | 103148775 | None | 0 – 750 | Conductor | Overhead | No | N.A. | N.A. | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1580 | 2018 | 5 | 4 | 16 | 34 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-05-04 16:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-06 | 15:02 | 39.1384 | -122.0787 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101623905 | Unknown | 12000 | Conductor | Overhead | Yes | 43226 | 0.62639 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1581 | 2018 | 5 | 6 | 15 | 2 | 18-0038644 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 5802 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-06 15:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-08 | 17:49 | 38.2546 | -122.4528 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101992211 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43228 | 0.74236 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Grow Into | 1582 | 2018 | 5 | 8 | 17 | 49 | 18-0039383 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Grow Into | 1355 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-08 17:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-09 | 13:47 | 35.4001 | -118.897 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kern County FD | 103924151 | Unknown | 12000 | Capacitor Bank | Overhead | No | N.A. | N.A. | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1583 | 2018 | 5 | 9 | 13 | 47 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-05-09 13:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-09 | 14:00 | 38.5908 | -123.3423 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CASE# 18CALNU 005865 | 101998286 | Unknown | 12000 | Conductor | Overhead | Yes | 43229 | 0.58333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1584 | 2018 | 5 | 9 | 14 | 0 | 18-0039683 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 29522 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-09 14:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-11 | 10:13 | 38.387 | -122.9856 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101973909 | Unknown | 12000 | Conductor | Overhead | Yes | 43231 | 0.42569 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1585 | 2018 | 5 | 11 | 10 | 13 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-05-11 10:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-11 | 12:45 | 38.9256 | -121.2468 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100035269 | AT&T | 12000 | Conductor | Overhead | Yes | 43231 | 0.53125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1586 | 2018 | 5 | 11 | 12 | 45 | 18-0040310 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 48331 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-11 12:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-11 | 15:51 | 40.3385 | -123.9137 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100989912 | Unknown | 12000 | Conductor | Overhead | Yes | 43231 | 0.66042 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1587 | 2018 | 5 | 11 | 15 | 51 | 18-0040389 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 5926 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-11 15:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-11 | 17:43 | 38.8218 | -120.9295 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Douglas Ferro. cell-530-708-2715. office-530-677-6192 | 101388939 | AT&T | 21000 | Conductor | Overhead | Yes | 43231 | 0.73819 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1588 | 2018 | 5 | 11 | 17 | 43 | 18-0040415 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 53784 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-11 17:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-12 | 15:50 | 38.6541 | -121.7642 | Vegetation | Rural | < 3 meters | Fire Agency | Woodland FD | 101606060 | None | 12000 | Conductor | Overhead | Yes | 43232 | 0.65972 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1589 | 2018 | 5 | 12 | 15 | 50 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-05-12 15:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-13 | 0:26 | 38.9119 | -122.0606 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101604030 | Unknown | 12000 | Conductor | Overhead | Yes | 43233 | 0.018056 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1590 | 2018 | 5 | 13 | 0 | 26 | 18-0040582 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1953 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-13 00:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-13 | 11:04 | 37.5235 | -120.3299 | Building | Rural | Structure Only | Fire Agency | Unknown | Twr 13/10 | None | 70000 | Switch | Overhead | Yes | 43233 | 0.46111 | Contact From Object | N.A. | Other | Electric Facility | Other | bird's nest | no-match | 1591 | 2018 | 5 | 13 | 11 | 4 | INT-10995 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 0 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-13 11:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-14 | 14:02 | 35.4036 | -119.0413 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100240571 | AT&T | 12000 | Conductor | Overhead | Yes | 43234 | 0.58472 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1592 | 2018 | 5 | 14 | 14 | 2 | 18-0040905 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 73062 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-14 14:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-14 | 21:10 | 35.2385 | -119.0833 | Vegetation | Rural | < 3 meters | Fire Agency | kern county FD | 100164480 | AT&T | 21000 | Conductor | Overhead | Yes | 43234 | 0.88194 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1593 | 2018 | 5 | 14 | 21 | 10 | 18-0040990 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 18061 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-14 21:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-15 | 4:22 | 37.4401 | -121.9247 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 103776080 | Unknown | 21000 | Conductor | Overhead | Yes | 43235 | 0.18194 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1594 | 2018 | 5 | 15 | 4 | 22 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-05-15 04:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-16 | 9:12 | 35.3106 | -118.9164 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100143713 | None | 12000 | Conductor | Overhead | Yes | 43236 | 0.38333 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1595 | 2018 | 5 | 16 | 9 | 12 | 18-0041497 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4420 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-16 09:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-17 | 17:41 | 35.2235 | -119.1549 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 103854888 | Unknown | 12000 | Conductor | Overhead | Yes | 43237 | 0.73681 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1596 | 2018 | 5 | 17 | 17 | 41 | 18-0042150 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 12815 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-17 17:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-19 | 9:39 | 38.9326 | -121.4937 | Vegetation | Rural | < 3 meters | Fire Agency | EAST NICHOLOUS ? SUTTER CO. | Str. 41/319 | None | 115000 | Conductor | Overhead | Yes | 43239 | 0.40208 | Contact From Object | N.A. | Other | Electric Facility | Human Error | aircraft | no-match | 1597 | 2018 | 5 | 19 | 9 | 39 | INT-11018 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 0 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-19 09:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-19 | 13:58 | 36.4706 | -121.4669 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Gonz FD-911 | 101744837 | Unknown | 12000 | Conductor | Overhead | Yes | 43239 | 0.58194 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1598 | 2018 | 5 | 19 | 13 | 58 | 18-0042540 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 13380 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-19 13:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-19 | 19:44 | 40.2665 | -122.2727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103899310 | Unknown | 12000 | Conductor | Overhead | Yes | 43239 | 0.82222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1599 | 2018 | 5 | 19 | 19 | 44 | 18-0042559 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 31980 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-19 19:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-19 | 21:02 | 36.8764 | -120.2191 | Vegetation | Rural | 300 - 999 Acres | Fire Agency | Madera County | 101089905 | None | 12000 | Conductor | Overhead | Yes | 2018-05-19 | 0.87639 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1600 | 2018 | 5 | 19 | 21 | 2 | 18-0042560 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | 3rd Party | Balloons | 59621 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-19 21:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-20 | 17:14 | 36.5904 | -119.2752 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | FIRE CAPT TOM CRASS, 554-732 | 100685366 | Unknown | 12000 | Conductor | Overhead | Yes | 43240 | 0.71806 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | Other/Unknown | 1601 | 2018 | 5 | 20 | 17 | 14 | 18-0042645 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1312 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-20 17:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-22 | 8:14 | 39.4591 | -121.5322 | Vegetation | Rural | < 3 meters | Fire Agency | Oroville FD | 100371407 | Unknown | 12000 | Conductor | Overhead | Yes | 43242 | 0.34306 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1602 | 2018 | 5 | 22 | 8 | 14 | 18-0043080 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 43763 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-22 08:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-22 | 15:51 | 38.3543 | -121.7495 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101570356 | None | 0 – 750 | Conductor | Overhead | Yes | 43242 | 0.66042 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1603 | 2018 | 5 | 22 | 15 | 51 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-05-22 15:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-23 | 14:03 | 37.3636 | -120.5032 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101013307 | AT&T | 12000 | Conductor | Overhead | Yes | 43243 | 0.58542 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1604 | 2018 | 5 | 23 | 14 | 3 | 18-0043671 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 14545 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-23 14:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-23 | 15:37 | 37.0197 | -119.7297 | Vegetation | Rural | 10 - 99 Acres | Unknown | N.A. | 103312862 | Unknown | 21000 | Conductor | Overhead | Yes | 43243 | 0.65069 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1605 | 2018 | 5 | 23 | 15 | 37 | 18-0043760 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 19440 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-23 15:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-24 | 12:12 | 35.5079 | -120.0935 | Vegetation | Rural | 100 - 299 Acres | Unknown | N.A. | 103010228 | None | 12000 | Conductor | Overhead | Yes | 43244 | 0.50833 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1606 | 2018 | 5 | 24 | 12 | 12 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-05-24 12:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-25 | 11:38 | 36.7132 | -119.4389 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 100762959 | Verizon | 12000 | Conductor | Overhead | Yes | 43245 | 0.48472 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1607 | 2018 | 5 | 25 | 11 | 38 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-05-25 11:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-26 | 11:28 | 37.5219 | -120.6278 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101191128 | Unknown | 21000 | conductor | Overhead | Yes | 43246 | 0.47778 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1608 | 2018 | 5 | 26 | 11 | 28 | 18-0044638 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 1349 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-26 11:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-28 | 1:56 | 35.3921 | -120.6081 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101849984 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43248 | 0.080556 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1609 | 2018 | 5 | 28 | 1 | 56 | 18-0044791 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2304 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-28 01:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-28 | 6:30 | 40.4382 | -122.3001 | Building | Rural | Structure Only | Unknown | N.A. | 101495757 | Unknown | 0 – 750 | conductor | Overhead | Yes | 43248 | 0.27083 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1610 | 2018 | 5 | 28 | 6 | 30 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-05-28 06:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-29 | 15:52 | 37.5092 | -121.9545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 925-422-7595 | 107589613 | N.A. | 21000 | Conductor | Subsurface | Yes | 43249 | 0.66111 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1611 | 2018 | 5 | 29 | 15 | 52 | 18-0045397 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 212547 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-29 15:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-30 | 13:00 | 38.5275 | -121.8214 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101641285 | None | 12000 | Conductor | Overhead | Yes | 43250 | 0.54167 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1612 | 2018 | 5 | 30 | 13 | 0 | 18-0045687 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 38459 | 0 | NA | <25mph | <15mph | #REF! | 2018-05-30 13:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-30 | 16:58 | 38.3247 | -121.8235 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103900943 | Unknown | 21000 | Conductor | Overhead | Yes | 43250 | 0.70694 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | no-match | 1613 | 2018 | 5 | 30 | 16 | 58 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-05-30 16:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-31 | 6:30 | 38.9745 | -121.6102 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Sutter County FD | 103127037 | None | 12000 | Conductor | Overhead | Yes | 43251 | 0.27083 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1614 | 2018 | 5 | 31 | 6 | 30 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-05-31 06:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-31 | 8:50 | 36.1673 | -119.8612 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kings County, Fire took off as soon as T-Man was onsite | 100688476 | Unknown | 12000 | Conductor | Overhead | Yes | 43251 | 0.36806 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1615 | 2018 | 5 | 31 | 8 | 50 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-05-31 08:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-31 | 12:28 | 36.7711 | -119.7417 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Garcia | 100841706 | AT&T | 12000 | Conductor | Overhead | Yes | 43251 | 0.51944 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | no-match | 1616 | 2018 | 5 | 31 | 12 | 28 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-05-31 12:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-05-31 | 14:34 | 35.4848 | -119.0468 | Vegetation | Rural | < 0.25 Acres | Fire Agency | REPORT NUMBER 1821047----(661) 324-6551 STATAION 63 RESPONDED | 100114852 | Unknown | 12000 | Conductor | Overhead | Yes | 43251 | 0.60694 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1617 | 2018 | 5 | 31 | 14 | 34 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-05-31 14:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-02 | 12:02 | 40.4553 | -122.3201 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101496970 | AT&T | 12000 | Conductor | Overhead | Yes | 43253 | 0.50139 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1618 | 2018 | 6 | 2 | 12 | 2 | 18-0046635 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 9576 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-02 12:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-02 | 16:11 | 37.3156 | -122.0222 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Santa Clara County Fire | 100555119 | AT&T | 12000 | Conductor | Overhead | Yes | 43253 | 0.67431 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Grow Into | 1619 | 2018 | 6 | 2 | 16 | 11 | 18-0046654 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Grow Into | 2114 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-02 16:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-02 | 21:37 | 37.311 | -121.9071 | Vegetation | Urban | < 3 meters | Fire Agency | San Jose FD | 103781309 | Unknown | 12000 | Conductor | Overhead | Yes | 43253 | 0.90069 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1620 | 2018 | 6 | 2 | 21 | 37 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-02 21:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-03 | 8:39 | 39.8042 | -122.3462 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 103387870 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43254 | 0.36042 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1621 | 2018 | 6 | 3 | 8 | 39 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-03 08:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-03 | 15:01 | 36.8324 | -121.3627 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103901497 | AT&T | 21000 | Conductor | Overhead | Yes | 43254 | 0.62569 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1622 | 2018 | 6 | 3 | 15 | 1 | 18-0046761 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 4420 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-03 15:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-03 | 15:08 | 39.5157 | -121.5421 | Vegetation | Urban | < 3 meters | Customer | N.A. | 100374172 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43254 | 0.63056 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1623 | 2018 | 6 | 3 | 15 | 8 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-03 15:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-04 | 9:25 | 35.4593 | -120.4921 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101895513 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43255 | 0.39236 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1624 | 2018 | 6 | 4 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-04 09:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-04 | 13:18 | 37.0159 | -120.0012 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101108691 | Unknown | 12000 | Conductor | Overhead | Yes | 43255 | 0.55417 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1625 | 2018 | 6 | 4 | 13 | 18 | 18-0047239 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 630 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-04 13:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-04 | 14:31 | 35.1333 | -119.4813 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Unknown | 100193277 | None | 12000 | Conductor | Overhead | Yes | 43255 | 0.60486 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1626 | 2018 | 6 | 4 | 14 | 31 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-04 14:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-04 | 14:45 | 36.5182 | -119.6314 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 100831403 | Unknown | 12000 | Conductor | Overhead | Yes | 43255 | 0.61458 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1627 | 2018 | 6 | 4 | 14 | 45 | 18-0047221 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 9782 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-04 14:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-04 | 17:38 | 36.4002 | -120.985 | Vegetation | Rural | 1000 - 4999 Acres | Fire Agency | CAL FIRE | 103850438 | Unknown | 12000 | Conductor | Overhead | Yes | 2018-06-04 | 0.73472 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1628 | 2018 | 6 | 4 | 17 | 38 | 18-0047273 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | Equip Failure | #REF! | 319671 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-04 17:38:00 | #REF! | 0 | TRUE | <25mph
PG&E | 2018-06-04 | 17:38 | 36.3792 | -120.9084 | Vegetation | Rural | 300 - 999 Acres | Fire Agency | CAL FIRE | 101733595 | Unknown | 12000 | Conductor | Overhead | Yes | 2018-06-04 | 0.73472 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1629 | 2018 | 6 | 4 | 17 | 38 | 18-0047273 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 319671 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-04 17:38:00 | #REF! | 0 | TRUE | <25mph
PG&E | 2018-06-04 | 21:42 | 35.363 | -118.9846 | Vegetation | Urban | < 3 meters | Fire Agency | Unknown | 100146786 | Yes | 0 – 750 | Conductor | Overhead | Yes | 43255 | 0.90417 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1630 | 2018 | 6 | 4 | 21 | 42 | 18-0047306 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4110 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-04 21:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-05 | 10:13 | 40.6183 | -122.3173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JASON COLLINS 530-225-4628 | 101467801 | None | 12000 | Conductor | Overhead | Yes | 43256 | 0.42569 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1631 | 2018 | 6 | 5 | 10 | 13 | 18-0047539 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 277 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-05 10:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-05 | 11:46 | 38.2464 | -122.4494 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101998865 | Unknown | 12000 | Conductor | Overhead | Yes | 43256 | 0.49028 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1632 | 2018 | 6 | 5 | 11 | 46 | 18-0047564 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 161809 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-05 11:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-05 | 13:45 | 38.5432 | -122.7202 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 102031673 | Unknown | 12000 | Conductor | Overhead | Yes | 43256 | 0.57292 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1633 | 2018 | 6 | 5 | 13 | 45 | 18-0047625 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 40599 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-05 13:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-05 | 16:46 | 38.7245 | -120.802 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 103667302 | AT&T | 12000 | Conductor | Overhead | Yes | 43256 | 0.69861 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1634 | 2018 | 6 | 5 | 16 | 46 | 18-0047702 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 40590 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-05 16:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-05 | 19:10 | 35.8767 | -119.5434 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LT. Stewart. (559) 949-8343 djstewart@co.tulare.ca.us | 100649683 | Unknown | 12000 | Conductor | Overhead | Yes | 43256 | 0.79861 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | Other/Unknown | 1635 | 2018 | 6 | 5 | 19 | 10 | 18-0047737 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 3605 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-05 19:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-06 | 10:32 | 36.2837 | -119.7734 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Kings County FD | 100711710 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43257 | 0.43889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1636 | 2018 | 6 | 6 | 10 | 32 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-06 10:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-06 | 11:07 | 38.2734 | -122.4385 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102005548 | AT&T | 12000 | Conductor | Overhead | Yes | 43257 | 0.46319 | Wire-Wire Contact | N.A. | N.A. | N.A. | Human Error | Work error | Other/Unknown | 1637 | 2018 | 6 | 6 | 11 | 7 | 18-0047901 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 30878 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-06 11:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-06 | 15:00 | 38.795 | -121.4848 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Adrian Rogers (530) 682-7908 | 103815399 | AT&T | 12000 | Conductor | Overhead | Yes | 43257 | 0.625 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1638 | 2018 | 6 | 6 | 15 | 0 | 18-0048080 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 53140 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-06 15:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-06 | 16:28 | 38.0801 | -121.2289 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Fire Chief Steve Henry 6925 E Foppiano Ln Stockton Ca 95212 209/931-3107 | 102105447 | AT&T | 12000 | Conductor | Overhead | Yes | 43257 | 0.68611 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1639 | 2018 | 6 | 6 | 16 | 28 | 18-0047776 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 54160 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-06 16:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-06 | 19:13 | 37.146 | -121.6676 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103790604 | None | 0 – 750 | Conductor | Overhead | Yes | 43257 | 0.80069 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1640 | 2018 | 6 | 6 | 19 | 13 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-06 19:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-06 | 19:21 | 38.0012 | -121.0952 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 103351400 | Unknown | 12000 | Conductor | Overhead | Yes | 43257 | 0.80625 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1641 | 2018 | 6 | 6 | 19 | 21 | 18-0048155 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 5112 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-06 19:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-06 | 21:06 | 38.151 | -121.6804 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101665829 | Frontier | 21000 | Conductor | Overhead | Yes | 43257 | 0.87917 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1642 | 2018 | 6 | 6 | 21 | 6 | 18-0048158 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 47015 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-06 21:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-08 | 17:10 | 35.477 | -120.6541 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 101936165 | Unknown | 12000 | Conductor | Overhead | Yes | 43259 | 0.71528 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1643 | 2018 | 6 | 8 | 17 | 10 | 18-0049050 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 101222 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-08 17:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-08 | 19:03 | 35.154 | -120.594 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101852092 | AT&T | 12000 | Conductor | Overhead | Yes | 43259 | 0.79375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1644 | 2018 | 6 | 8 | 19 | 3 | 18-0049130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2473 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-08 19:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-09 | 0:46 | 35.0745 | -120.5167 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101927520 | Unknown | 12000 | Conductor | Overhead | Yes | 43260 | 0.031944 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1645 | 2018 | 6 | 9 | 0 | 46 | 18-0049171 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 16825 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-09 00:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-09 | 16:02 | 37.8785 | -121.6474 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | east county fire | 100497205 | Unknown | 21000 | Conductor | Overhead | Yes | 43260 | 0.66806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1646 | 2018 | 6 | 9 | 16 | 2 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-09 16:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-10 | 17:19 | 38.4157 | -122.9184 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101978419 | AT&T | 12000 | Conductor | Overhead | Yes | 43261 | 0.72153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1647 | 2018 | 6 | 10 | 17 | 19 | 18-0049445 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2386 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-10 17:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-11 | 14:20 | 38.8975 | -121.3119 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100042575 | N.A. | 12000 | Conductor | Subsurface | Yes | 43262 | 0.59722 | Contact From Object | N.A. | Other | Electric Facility | Human Error | third-party dig in | Other/Unknown | 1648 | 2018 | 6 | 11 | 14 | 20 | 18-0049689 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 312909 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-11 14:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-11 | 17:49 | 34.7329 | -120.0861 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103015183 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43262 | 0.74236 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1649 | 2018 | 6 | 11 | 17 | 49 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-11 17:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-11 | 19:59 | 38.2311 | -120.7944 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Twr 2/25 | None | 60000 | Conductor | Overhead | Yes | 43262 | 0.83264 | Contamination | N.A. | N.A. | N.A. | Unknown |  | no-match | 1650 | 2018 | 6 | 11 | 19 | 59 | INT-11106 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 0 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-11 19:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-12 | 8:55 | 35.8507 | -119.8915 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Jason Brown 559-935-0756 | 100649777 | None | 21000 | Conductor | Overhead | Yes | 43263 | 0.37153 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1651 | 2018 | 6 | 12 | 8 | 55 | 18-0050070 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 1324 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-12 08:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-12 | 12:12 | 38.589 | -121.52 | Vegetation | Urban | < 3 meters | Fire Agency | West Sac FD | 101657851 | Unknown | 12000 | Conductor | Overhead | Yes | 43263 | 0.50833 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1652 | 2018 | 6 | 12 | 12 | 12 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-12 12:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-13 | 2:53 | 36.8964 | -121.8374 | Vegetation | Rural | < 3 meters | Fire Agency | Sean Murray -Phone # 831-728-8290 and cell # 831254-1716 | 101699116 | AT&T | 21000 | Conductor | Overhead | Yes | 43264 | 0.12014 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | no-match | 1653 | 2018 | 6 | 13 | 2 | 53 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-13 02:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-13 | 11:18 | 35.2927 | -120.429 | Vegetation | Rural | < 3 meters | Customer | N.A. | 101884565 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 0.47083 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1654 | 2018 | 6 | 13 | 11 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-13 11:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-13 | 16:27 | 36.633 | -119.9897 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100667215 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 0.68542 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1655 | 2018 | 6 | 13 | 16 | 27 | 18-0050714 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 33689 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-13 16:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-13 | 22:40 | 38.4901 | -122.6661 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SRS181640125 | 101966547 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 0.94444 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1656 | 2018 | 6 | 13 | 22 | 40 | 18-0050782 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 295146 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-13 22:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-14 | 14:25 | 39.5246 | -121.4626 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Mike Waters (investigator 530 538-7888) | 100426966 | None | 12000 | Conductor | Overhead | Yes | 43265 | 0.60069 | Contact From Object | N.A. | Other | Electric Facility | Human Error | bucket truck | Other/Unknown | 1657 | 2018 | 6 | 14 | 14 | 25 | 18-0051129 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 249298 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-14 14:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-14 | 16:12 | 40.4419 | -124.0197 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 101005522 | AT&T | 12000 | Conductor | Overhead | Yes | 43265 | 0.675 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1658 | 2018 | 6 | 14 | 16 | 12 | 18-0051223 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 19601 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-14 16:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-15 | 2:56 | 37.4869 | -122.4223 | Vegetation | Rural | < 0.25 Acres | Utility: PG&E | N.A. | Pole 10/5 | None | 60000 | Conductor | Overhead | Yes | 43266 | 0.12222 | Contamination | N.A. | N.A. | N.A. | Unknown |  | no-match | 1659 | 2018 | 6 | 15 | 2 | 56 | INT-11115 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 0 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-15 02:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-15 | 9:51 | 37.1986 | -119.4709 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RANCHARIA ENGINE 4255 USFS ENG 52 | 101058060 | Unknown | 12000 | Conductor | Overhead | Yes | 43266 | 0.41042 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1660 | 2018 | 6 | 15 | 9 | 51 | 18-0051354 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 35146 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-15 09:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-15 | 10:05 | 38.6238 | -121.0221 | Vegetation | Rural | < 3 meters | Customer | N.A. | 101376538 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43266 | 0.42014 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1661 | 2018 | 6 | 15 | 10 | 5 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-15 10:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-16 | 9:56 | 38.6559 | -121.7937 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101606330 | Unknown | 12000 | Conductor | Overhead | Yes | 43267 | 0.41389 | Contact From Object | N.A. | Other | Electric Facility | Unknown | bird's nest | Other/Unknown | 1662 | 2018 | 6 | 16 | 9 | 56 | 18-0051610 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 35150 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-16 09:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-16 | 13:17 | 38.6197 | -121.8455 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Woodland FD | 103905392 | Unknown | 12000 | Conductor | Overhead | Yes | 43267 | 0.55347 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1663 | 2018 | 6 | 16 | 13 | 17 | 18-0051627 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 299489 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-16 13:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-16 | 16:28 | 37.0737 | -120.1924 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101133603 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43267 | 0.68611 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | Other/Unknown | 1664 | 2018 | 6 | 16 | 16 | 28 | 18-0051660 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 5604 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-16 16:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-16 | 18:06 | 38.095 | -122.2101 | Vegetation | Urban | < 0.25 Acres | Fire Agency | 707 648-4488 | 102218342 | AT&T | 12000 | Conductor | Overhead | Yes | 43267 | 0.75417 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1665 | 2018 | 6 | 16 | 18 | 6 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-16 18:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-16 | 18:15 | 39.1335 | -121.5436 | Building | Urban | Structure Only | Fire Agency | 530-743-1553 | 101319352 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43267 | 0.76042 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1666 | 2018 | 6 | 16 | 18 | 15 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-16 18:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-16 | 18:46 | 39.3321 | -121.537 | Vegetation | Rural | < 3 meters | Fire Agency | palermo | 100381711 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43267 | 0.78194 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1667 | 2018 | 6 | 16 | 18 | 46 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-16 18:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-16 | 19:37 | 38.7526 | -121.4439 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100102668 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43267 | 0.81736 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1668 | 2018 | 6 | 16 | 19 | 37 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-16 19:37:00 | #REF! | 0 | TRUE | <25mph
PG&E | 2018-06-16 | 19:37 | 38.699 | -122.0209 | Vegetation | Rural | < 3 meters | Fire Agency | ESPARTO FIRE DEPT | 101644179 | AT&T | 12000 | Conductor | Overhead | Yes | 43267 | 0.81736 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1669 | 2018 | 6 | 16 | 19 | 37 | 18-0051673 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 8016 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-16 19:37:00 | #REF! | 0 | TRUE | <25mph
PG&E | 2018-06-16 | 19:58 | 37.907 | -121.8063 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100483910 | Unknown | 21000 | Conductor | Overhead | Yes | 43267 | 0.83194 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1670 | 2018 | 6 | 16 | 19 | 58 | 18-0051687 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 3322 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-16 19:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-16 | 20:33 | 38.0494 | -122.206 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Contra Costa FD | 101423963 | Unknown | 21000 | Conductor | Overhead | Yes | 43267 | 0.85625 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 1671 | 2018 | 6 | 16 | 20 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-16 20:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-17 | 16:01 | 38.0932 | -120.945 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CATCU006927 incident # | 102042425 | Unknown | 12000 | Conductor | Overhead | Yes | 43268 | 0.66736 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1672 | 2018 | 6 | 17 | 16 | 1 | 18-0051778 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 1601 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-17 16:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-18 | 8:31 | 35.527 | -120.6475 | Vegetation | Rural | < 3 meters | Customer | N.A. | 101887037 | Unknown | 21000 | Conductor | Overhead | Yes | 43269 | 0.35486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1673 | 2018 | 6 | 18 | 8 | 31 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-18 08:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-18 | 16:06 | 37.8053 | -121.3795 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Stockton FD | 103569107 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43269 | 0.67083 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1674 | 2018 | 6 | 18 | 16 | 6 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-18 16:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-19 | 0:27 | 38.7604 | -120.8224 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101388356 | Unknown | 12000 | Conductor | Overhead | Yes | 43270 | 0.01875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1675 | 2018 | 6 | 19 | 0 | 27 | 18-0052111 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 141652 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-19 00:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-19 | 9:43 | 38.531 | -121.5505 | Vegetation | Rural | < 3 meters | Fire Agency | Yolo County FD | 101585318 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43270 | 0.40486 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1676 | 2018 | 6 | 19 | 9 | 43 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-19 09:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-19 | 10:17 | 38.5918 | -120.7097 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101395943 | AT&T | 21000 | Conductor | Overhead | Yes | 43270 | 0.42847 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1677 | 2018 | 6 | 19 | 10 | 17 | 18-0052222 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 4094 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-19 10:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-19 | 11:45 | 35.9851 | -120.1417 | Vegetation | Rural | < 3 meters | Self Extinguished | N.A. | 100698130 | Unknown | 21000 | Conductor | Overhead | Yes | 43270 | 0.48958 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1678 | 2018 | 6 | 19 | 11 | 45 | 18-0052302 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1386 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-19 11:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-19 | 14:41 | 37.2158 | -119.6811 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JOE QUINSTORFF 559-683-8008 | 103372829 | Unknown | 21000 | Conductor | Overhead | Yes | 43270 | 0.61181 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1679 | 2018 | 6 | 19 | 14 | 41 | 18-0052327 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 123838 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-19 14:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-20 | 8:30 | 34.7561 | -120.2281 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101858890 | None | 0 – 750 | Conductor | Overhead | Yes | 43271 | 0.35417 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1680 | 2018 | 6 | 20 | 8 | 30 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-20 08:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-21 | 17:36 | 38.1046 | -121.8145 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Twr 21/142 | None | 230000 | Unknown | Overhead | Yes | 43272 | 0.73333 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1681 | 2018 | 6 | 21 | 17 | 36 | INT-11136 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 0 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-21 17:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-21 | 17:51 | 38.8059 | -121.1965 | Vegetation | Rural | < 3 meters | Customer | N.A. | 100060316 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43272 | 0.74375 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1682 | 2018 | 6 | 21 | 17 | 51 | No ILIS or TOTL available | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-21 17:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-21 | 18:58 | 35.1224 | -120.3938 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101878933 | AT&T | 12000 | Conductor | Overhead | Yes | 43272 | 0.79028 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1683 | 2018 | 6 | 21 | 18 | 58 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-21 18:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-22 | 6:44 | 38.627 | -121.962 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Str. 16/230 | None | 60000 | Conductor | Overhead | Yes | 43273 | 0.28056 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1684 | 2018 | 6 | 22 | 6 | 44 | INT-11140 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 54901 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-22 06:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-22 | 16:28 | 36.458 | -119.3435 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | MARK FLEMING @ 559 731-8674 | 100729160 | AT&T | 12000 | Conductor | Overhead | Yes | 43273 | 0.68611 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1685 | 2018 | 6 | 22 | 16 | 28 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-22 16:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-22 | 17:44 | 37.2485 | -119.5625 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Madera County | 101117749 | None | 0 – 750 | Conductor | Overhead | Yes | 43273 | 0.73889 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1686 | 2018 | 6 | 22 | 17 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-22 17:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-22 | 18:48 | 40.3237 | -124.293 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100987410 | None | 0 – 750 | Conductor | Overhead | Yes | 43273 | 0.78333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1687 | 2018 | 6 | 22 | 18 | 48 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-22 18:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-23 | 9:31 | 40.8632 | -122.3962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | RYAN MEANS 530-238-2416 | 101472252 | AT&T | 12000 | Conductor | Overhead | Yes | 43274 | 0.39653 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1688 | 2018 | 6 | 23 | 9 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-23 09:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-23 | 17:33 | 38.2034 | -122.1569 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101663196 | None | 0 – 750 | Transformer | Overhead | Yes | 43274 | 0.73125 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1689 | 2018 | 6 | 23 | 17 | 33 | 18-0053911 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1202 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-23 17:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-23 | 17:47 | 37.9427 | -121.7735 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Unknown | 100483944 | AT&T | 21000 | Conductor | Overhead | Yes | 43274 | 0.74097 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1690 | 2018 | 6 | 23 | 17 | 47 | 18-0053914 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 30484 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-23 17:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-23 | 18:12 | 41.0466 | -124.1186 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100976559 | Unknown | 12000 | Conductor | Overhead | Yes | 43274 | 0.75833 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1691 | 2018 | 6 | 23 | 18 | 12 | 18-0053951 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4428 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-23 18:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-23 | 21:05 | 37.2099 | -121.0123 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101231316 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43274 | 0.87847 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1692 | 2018 | 6 | 23 | 21 | 5 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-23 21:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-24 | 13:07 | 38.947 | -121.0911 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100040793 | Unknown | 12000 | Conductor | Overhead | Yes | 43275 | 0.54653 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1693 | 2018 | 6 | 24 | 13 | 7 | 18-0054038 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 26593 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-24 13:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-24 | 19:41 | 39.4983 | -121.5778 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Oroville FD | 100374765 | Unknown | 12000 | Conductor | Overhead | Yes | 43275 | 0.82014 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | no-match | 1694 | 2018 | 6 | 24 | 19 | 41 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-24 19:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-26 | 9:28 | 37.9811 | -120.3908 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101048302 | AT&T | 17000 | Conductor | Overhead | Yes | 43277 | 0.39444 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1695 | 2018 | 6 | 26 | 9 | 28 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-26 09:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-26 | 11:24 | 38.4636 | -122.8161 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 102016986 | AT&T | 12000 | Conductor | Overhead | Yes | 43277 | 0.475 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1696 | 2018 | 6 | 26 | 11 | 24 | 18-0054647 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 25102 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-26 11:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-26 | 13:58 | 37.9198 | -121.2405 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | fd office 209 937 8801 | 102130589 | N.A. | 12000 | Conductor | Subsurface | Yes | 43277 | 0.58194 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | elbow | Other/Unknown | 1697 | 2018 | 6 | 26 | 13 | 58 | 18-0054723 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 62835 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-26 13:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-26 | 15:53 | 39.5991 | -121.7155 | Vegetation | Rural | 300 - 999 Acres | Fire Agency | Butte County FD | 103310830 | None | 0 – 750 | Conductor | Overhead | Yes | 2018-06-26 | 0.66181 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1698 | 2018 | 6 | 26 | 15 | 53 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-26 15:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-27 | 17:06 | 39.2813 | -123.2335 | Vegetation | Rural | < 0.25 Acres | Utility: PG&E | N.A. | 103907070 | AT&T | 12000 | Conductor | Overhead | Yes | 43278 | 0.7125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1699 | 2018 | 6 | 27 | 17 | 6 | 18-0055190 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 57703 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-27 17:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-27 | 18:46 | 40.218 | -123.7989 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TJ alderpoint fire | 100990381 | Unknown | 12000 | Conductor | Overhead | Yes | 43278 | 0.78194 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1700 | 2018 | 6 | 27 | 18 | 46 | 18-0055205 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 21357 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-27 18:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-27 | 21:19 | 39.8714 | -123.7119 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 103775148 | Verizon | 12000 | Conductor | Overhead | Yes | 43278 | 0.88819 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1701 | 2018 | 6 | 27 | 21 | 19 | 18-0055211 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 75544 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-27 21:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-28 | 12:27 | 38.5982 | -121.0081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | John Reis, 530-622-3858 | 101376954 | Unknown | 21000 | Conductor | Overhead | Yes | 43279 | 0.51875 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1702 | 2018 | 6 | 28 | 12 | 27 | 18-0055479 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 24671 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-28 12:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-28 | 18:38 | 38.0823 | -122.1981 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | Twr 27/190 | None | 115000 | Unknown | Overhead | Yes | 43279 | 0.77639 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1703 | 2018 | 6 | 28 | 18 | 38 | INT-11158 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 0 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-28 18:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-28 | 19:41 | 38.5575 | -122.5043 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Brian Coffee | 102267918 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43279 | 0.82014 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1704 | 2018 | 6 | 28 | 19 | 41 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-28 19:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-29 | 3:50 | 37.3624 | -120.6412 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 209 356 2900 | 101168362 | Unknown | 12000 | Conductor | Overhead | Yes | 43280 | 0.15972 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1705 | 2018 | 6 | 29 | 3 | 50 | 18-0055612 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 163 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-29 03:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-29 | 11:30 | 38.6587 | -122.8715 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 102032815 | AT&T | 12000 | Capacitor Bank | Overhead | Yes | 43280 | 0.47917 | Equipment/ Facility Failure | capacitor bank | N.A. | N.A. | Unknown |  | no-match | 1706 | 2018 | 6 | 29 | 11 | 30 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-29 11:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-29 | 13:18 | 39.4359 | -121.5377 | Vegetation | Rural | < 3 meters | Fire Agency | Oroville FD | 100431936 | Unknown | 12000 | Conductor | Overhead | Yes | 43280 | 0.55417 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1707 | 2018 | 6 | 29 | 13 | 18 | 18-0055725 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 59898 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-29 13:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-29 | 15:10 | 38.0529 | -120.9391 | Vegetation | Rural | > 5000 Acres | Fire Agency | MATT GILBERT 209-419-4420 | 103840725 | None | 12000 | Conductor | Overhead | Yes | 2018-06-29 | 0.63194 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1708 | 2018 | 6 | 29 | 15 | 10 | 18-0055786 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | 3rd Party | Vehicle | 500 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-29 15:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-29 | 15:19 | 37.5343 | -121.988 | Vegetation | Urban | < 0.25 Acres | Fire Agency | truck 215008 B-5 | 100947879 | AT&T | 12000 | Conductor | Overhead | Yes | 43280 | 0.63819 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1709 | 2018 | 6 | 29 | 15 | 19 | 18-0055783 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 239227 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-29 15:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-29 | 19:34 | 38.514 | -122.7748 | Vegetation | Urban | < 3 meters | Customer | N.A. | 102025571 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43280 | 0.81528 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1710 | 2018 | 6 | 29 | 19 | 34 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-29 19:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-30 | 3:32 | 36.0439 | -120.0917 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Avenal Kings County Fire Dept | 100700210 | Unknown | 12000 | Conductor | Overhead | Yes | 43281 | 0.14722 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1711 | 2018 | 6 | 30 | 3 | 32 | 18-0055849 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 9598 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-30 03:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-30 | 8:04 | 35.4401 | -119.0132 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Str. 0/5 | None | 115000 | Conductor | Overhead | Yes | 43281 | 0.33611 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1712 | 2018 | 6 | 30 | 8 | 4 | INT-11159 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 0 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-30 08:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-30 | 11:14 | 39.3621 | -121.0809 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ENGINEER YUREK | 100091354 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 0.46806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1713 | 2018 | 6 | 30 | 11 | 14 | 18-0055945 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5724 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-30 11:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-30 | 13:32 | 38.6957 | -120.8248 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Ken Earle | 101403788 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 0.56389 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1714 | 2018 | 6 | 30 | 13 | 32 | 18-0055968 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 210734 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-30 13:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-30 | 17:54 | 37.2161 | -121.7394 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100600855 | AT&T | 21000 | Conductor | Overhead | Yes | 43281 | 0.74583 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1715 | 2018 | 6 | 30 | 17 | 54 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-30 17:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-30 | 22:18 | 40.6043 | -122.24 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101469808 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43281 | 0.92917 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1716 | 2018 | 6 | 30 | 22 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-06-30 22:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-06-30 | 22:36 | 39.1141 | -121.077 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Matt Wallen (530) 277-3312 Incident # NEU015486 | 100105380 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 0.94167 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1717 | 2018 | 6 | 30 | 22 | 36 | 18-0056039 | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 8004 | 0 | NA | <25mph | <15mph | #REF! | 2018-06-30 22:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-01 | 0:23 | 40.2697 | -124.2386 | Vegetation | Rural | < 3 meters | Fire Agency | fire chief | 100986962 | Unknown | 12000 | Conductor | Overhead | Yes | 43282 | 0.015972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1718 | 2018 | 7 | 1 | 0 | 23 | 18-0056043 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 22872 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-01 00:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-01 | 0:45 | 38.8842 | -120.847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Brian Mackwood (530)708-2711 | 100109003 | None | 21000 | Conductor | Overhead | Yes | 43282 | 0.03125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1719 | 2018 | 7 | 1 | 0 | 45 | 18-0056045 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5760 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-01 00:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-01 | 8:13 | 39.4154 | -121.5122 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430344 | AT&T | 12000 | Conductor | Overhead | Yes | 43282 | 0.34236 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1720 | 2018 | 7 | 1 | 8 | 13 | 18-0056061 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 7848 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-01 08:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-02 | 2:26 | 37.7087 | -121.2773 | Vegetation | Rural | < 3 meters | Fire Agency | 209236-8105 | 103921895 | Unknown | 17000 | Conductor | Overhead | Yes | 43283 | 0.10139 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1721 | 2018 | 7 | 2 | 2 | 26 | 18-0056177 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1542 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-02 02:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-02 | 5:12 | 38.6092 | -122.4595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 707-967-1467 | 102252558 | AT&T | 21000 | Conductor | Overhead | Yes | 43283 | 0.21667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1722 | 2018 | 7 | 2 | 5 | 12 | 18-0056178 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 403 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-02 05:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-02 | 11:35 | 39.0995 | -122.9001 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 102146848 | AT&T | 12000 | Conductor | Overhead | Yes | 43283 | 0.48264 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1723 | 2018 | 7 | 2 | 11 | 35 | 18-0056340 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 3828 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-02 11:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-02 | 17:15 | 36.6052 | -119.8239 | Vegetation | Rural | < 3 meters | Customer | N.A. | 100753607 | Unknown | 12000 | Conductor | Overhead | Yes | 43283 | 0.71875 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1724 | 2018 | 7 | 2 | 17 | 15 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-02 17:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-03 | 18:02 | 39.7112 | -121.8282 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103387781 | Unknown | 12000 | Conductor | Overhead | Yes | 43284 | 0.75139 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1725 | 2018 | 7 | 3 | 18 | 2 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-03 18:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-04 | 15:26 | 39.5538 | -123.4255 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102196183 | Verizon | 12000 | Conductor | Overhead | Yes | 43285 | 0.64306 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1726 | 2018 | 7 | 4 | 15 | 26 | 18-0056986 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 32269 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-04 15:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-05 | 12:45 | 39.7786 | -121.8699 | Vegetation | Urban | < 3 meters | Customer | N.A. | 103350704 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43286 | 0.53125 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1727 | 2018 | 7 | 5 | 12 | 45 | 18-0057193 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 360 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-05 12:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-06 | 17:13 | 35.029 | -120.5279 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103401924 | Unknown | 12000 | Conductor | Overhead | Yes | 43287 | 0.71736 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1728 | 2018 | 7 | 6 | 17 | 13 | 18-0057559 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 31695 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-06 17:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-06 | 20:39 | 37.3832 | -120.6151 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 103217389 | Unknown | 12000 | Conductor | Overhead | No | N.A. | N.A. | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1729 | 2018 | 7 | 6 | 20 | 39 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-06 20:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-07 | 6:11 | 38.0836 | -121.855 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101582721 | Frontier | 21000 | Conductor | Overhead | Yes | 43288 | 0.25764 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1730 | 2018 | 7 | 7 | 6 | 11 | 18-0057648 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 302 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-07 06:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-07 | 9:05 | 39.2745 | -121.6647 | Vegetation | Urban | < 3 meters | Unknown | N.A. | 101327124 | Unknown | 12000 | Conductor | Overhead | Yes | 43288 | 0.37847 | Contact From Object | N.A. | Other | Electric Facility | Human Error | third-party caused | no-match | 1731 | 2018 | 7 | 7 | 9 | 5 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-07 09:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-07 | 20:24 | 35.0211 | -120.5004 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 101893417 | AT&T | 12000 | Conductor | Overhead | Yes | 43288 | 0.85 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1732 | 2018 | 7 | 7 | 20 | 24 | 18-0057707 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 141241 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-07 20:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-08 | 19:32 | 38.7736 | -122.0621 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101661938 | None | 21000 | Conductor | Overhead | Yes | 43289 | 0.81389 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1733 | 2018 | 7 | 8 | 19 | 32 | 18-0057783 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1504 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-08 19:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-08 | 20:04 | 39.7915 | -123.1981 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 102182026 | Verizon | 12000 | Conductor | Overhead | Yes | 43289 | 0.83611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1734 | 2018 | 7 | 8 | 20 | 4 | 18-0057794 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 3448 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-08 20:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-09 | 7:27 | 35.0785 | -120.3948 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101861366 | Unknown | 12000 | Conductor | Overhead | Yes | 43290 | 0.31042 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1735 | 2018 | 7 | 9 | 7 | 27 | 18-0057904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 21045 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-09 07:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-10 | 5:05 | 38.8541 | -121.1806 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100052871 | AT&T | 12000 | Conductor | Overhead | Yes | 43291 | 0.21181 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1736 | 2018 | 7 | 10 | 5 | 5 | 18-0058148 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 27849 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-10 05:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-10 | 6:45 | 37.085 | -122.0744 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 101675262 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43291 | 0.28125 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1737 | 2018 | 7 | 10 | 6 | 45 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-10 06:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-10 | 18:58 | 40.1384 | -122.2085 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 101538131 | Unknown | 12000 | Conductor | Overhead | Yes | 43291 | 0.79028 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1738 | 2018 | 7 | 10 | 18 | 58 | 18-0058583 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 21195 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-10 18:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-11 | 2:11 | 37.7104 | -121.4733 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Pole 7/8 | None | 115000 | Conductor | Overhead | Yes | 43292 | 0.090972 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1739 | 2018 | 7 | 11 | 2 | 11 | INT-11195 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 0 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-11 02:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-11 | 10:10 | 37.0725 | -120.9495 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103920696 | None | 12000 | Conductor | Overhead | Yes | 43292 | 0.42361 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1740 | 2018 | 7 | 11 | 10 | 10 | 18-0058772 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 601 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-11 10:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-13 | 8:10 | 37.0997 | -120.8361 | Vegetation | Rural | < 3 meters | Fire Agency | Merced FD | 101178812 | Unknown | 12000 | Capacitor Bank | Overhead | No | N.A. | N.A. | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1741 | 2018 | 7 | 13 | 8 | 10 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-13 08:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-13 | 10:59 | 39.4836 | -123.7924 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102184869 | AT&T | 12000 | Conductor | Overhead | Yes | 43294 | 0.45764 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1742 | 2018 | 7 | 13 | 10 | 59 | 18-0059522 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 328 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-13 10:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-13 | 15:45 | 40.4831 | -122.3225 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103160260 | Unknown | 12000 | Conductor | Overhead | Yes | 43294 | 0.65625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1743 | 2018 | 7 | 13 | 15 | 45 | 18-0059601 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 39212 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-13 15:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-13 | 18:51 | 39.779 | -122.1409 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100421715 | Unknown | 12000 | Conductor | Overhead | Yes | 43294 | 0.78542 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1744 | 2018 | 7 | 13 | 18 | 51 | 18-0059672 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 36254 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-13 18:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-14 | 11:34 | 38.4026 | -122.5489 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103141862 | Verizon | 12000 | Conductor | Overhead | Yes | 43295 | 0.48194 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1745 | 2018 | 7 | 14 | 11 | 34 | 18-0059821 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 6426 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-14 11:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-14 | 12:40 | 38.5793 | -122.878 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103122744 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 0.52778 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1746 | 2018 | 7 | 14 | 12 | 40 | 18-0059799 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 20804 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-14 12:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-14 | 12:56 | 39.2093 | -121.197 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE DEPT LEFT BEFORE UPTAINING THAT INFO | 100086833 | None | 21000 | Conductor | Overhead | Yes | 43295 | 0.53889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1747 | 2018 | 7 | 14 | 12 | 56 | 18-0059841 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 3720 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-14 12:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-14 | 14:44 | 38.9524 | -121.2467 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100035452 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 0.61389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1748 | 2018 | 7 | 14 | 14 | 44 | 18-0059847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2430 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-14 14:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-14 | 15:01 | 37.8387 | -121.0165 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 102330872 | Unknown | 17000 | Conductor | Overhead | Yes | 43295 | 0.62569 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1749 | 2018 | 7 | 14 | 15 | 1 | 18-0059849 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 18780 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-14 15:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-14 | 15:58 | 35.4281 | -119.059 | Vegetation | Urban | < 3 meters | Unknown | N.A. | 100238826 | None | 12000 | Conductor | Overhead | Yes | 43295 | 0.66528 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1750 | 2018 | 7 | 14 | 15 | 58 | 18-0059855 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 936 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-14 15:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-14 | 21:38 | 36.3314 | -121.8829 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | ASSISTED JAIMIE | 101672234 | Unknown | 12000 | Conductor | Overhead | Yes | 43295 | 0.90139 | Contact From Object | N.A. | Animal | Pole | Other | bull rubbing pole | Other/Unknown | 1751 | 2018 | 7 | 14 | 21 | 38 | 18-0059900 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 493416 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-14 21:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-15 | 10:06 | 35.5301 | -119.0718 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100206898 | Unknown | 12000 | Conductor | Overhead | Yes | 43296 | 0.42083 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1752 | 2018 | 7 | 15 | 10 | 6 | 18-0059940 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 12550 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-15 10:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-16 | 12:57 | 35.5901 | -120.6433 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101904896 | Unknown | 21000 | Capacitor Bank | Overhead | Yes | 43297 | 0.53958 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | Other/Unknown | 1753 | 2018 | 7 | 16 | 12 | 57 | 18-0060227 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 42564 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-16 12:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-17 | 5:59 | 37.938 | -122.5142 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 102231901 | Unknown | 12000 | Conductor | Overhead | Yes | 43298 | 0.24931 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1754 | 2018 | 7 | 17 | 5 | 59 | 18-0060406 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 8521 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-17 05:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-17 | 11:11 | 35.6986 | -120.9777 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | dennis byrnes 8055434244 inc # = 18ca-slu-007640 | 103886652 | Unknown | 21000 | Conductor | Overhead | Yes | 43298 | 0.46597 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1755 | 2018 | 7 | 17 | 11 | 11 | 18-0060637 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 9121 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-17 11:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-17 | 11:58 | 37.2217 | -121.6778 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Luis Morado state arson fire fighter | 100601345 | Unknown | 12000 | Conductor | Overhead | Yes | 43298 | 0.49861 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1756 | 2018 | 7 | 17 | 11 | 58 | 18-0060617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 5865 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-17 11:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-17 | 15:16 | 39.0063 | -122.8763 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102158497 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43298 | 0.63611 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1757 | 2018 | 7 | 17 | 15 | 16 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-17 15:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-17 | 15:53 | 35.3498 | -119.0362 | Vegetation | Urban | < 3 meters | Unknown | N.A. | 100244890 | Yes | 0 – 750 | Conductor | Overhead | Yes | 43298 | 0.66181 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1758 | 2018 | 7 | 17 | 15 | 53 | 18-0060815 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1530 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-17 15:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-17 | 16:53 | 38.3955 | -122.9212 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101978449 | AT&T | 12000 | Conductor | Overhead | Yes | 43298 | 0.70347 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1759 | 2018 | 7 | 17 | 16 | 53 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-17 16:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-17 | 19:40 | 40.5927 | -122.4886 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101477082 | AT&T | 12000 | Conductor | Overhead | Yes | 43298 | 0.81944 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1760 | 2018 | 7 | 17 | 19 | 40 | 18-0060840 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 30162 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-17 19:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-18 | 1:14 | 38.3671 | -120.5578 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101247987 | Unknown | 12000 | Conductor | Overhead | Yes | 43299 | 0.051389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1761 | 2018 | 7 | 18 | 1 | 14 | 18-0060882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6420 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-18 01:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-18 | 3:46 | 37.1267 | -121.6597 | Vegetation | Urban | < 3 meters | Unknown | N.A. | 103426203 | Yes | 21000 | Conductor | Overhead | Yes | 43299 | 0.15694 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1762 | 2018 | 7 | 18 | 3 | 46 | 18-0060884 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 117738 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-18 03:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-18 | 7:16 | 35.617 | -119.1953 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103909160 | None | 12000 | Conductor | Overhead | Yes | 43299 | 0.30278 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1763 | 2018 | 7 | 18 | 7 | 16 | 18-0060905 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 21669 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-18 07:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-18 | 11:19 | 39.0714 | -121.463 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101324059 | Unknown | 12000 | Conductor | Overhead | Yes | 43299 | 0.47153 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1764 | 2018 | 7 | 18 | 11 | 19 | 18-0061060 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 336 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-18 11:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-18 | 14:50 | 38.9982 | -121.3166 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Fire insp. Cris Mertens 530-277-2322 | 100028525 | Unknown | 12000 | Conductor | Overhead | Yes | 43299 | 0.61806 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1765 | 2018 | 7 | 18 | 14 | 50 | 18-0061197 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 687 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-18 14:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-19 | 0:08 | 36.9372 | -119.4557 | Vegetation | Rural | < 0.25 Acres | Fire Agency | incident # 10559 | 100677019 | AT&T | 12000 | Conductor | Overhead | Yes | 43300 | 0.0055556 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1766 | 2018 | 7 | 19 | 0 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-19 00:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-19 | 5:29 | 40.1918 | -123.5373 | Vegetation | Rural | < 0.25 Acres | Fire Agency | fire captain | 103909820 | Unknown | 12000 | Conductor | Overhead | Yes | 43300 | 0.22847 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1767 | 2018 | 7 | 19 | 5 | 29 | 18-0061308 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 73380 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-19 05:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-19 | 10:44 | 36.2222 | -119.7796 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 103369868 | Unknown | 12000 | Conductor | Overhead | Yes | 43300 | 0.44722 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1768 | 2018 | 7 | 19 | 10 | 44 | 18-0061429 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 5254 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-19 10:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-19 | 15:03 | 38.231 | -122.1495 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103919648 | Unknown | 12000 | Capacitor Bank | Overhead | Yes | 43300 | 0.62708 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1769 | 2018 | 7 | 19 | 15 | 3 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-19 15:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-19 | 15:52 | 36.6102 | -119.6382 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 100842711 | Unknown | 12000 | Conductor | Overhead | Yes | 43300 | 0.66111 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1770 | 2018 | 7 | 19 | 15 | 52 | 18-0061598 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 49853 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-19 15:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-20 | 6:31 | 37.4318 | -119.9441 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ZACH RUTHERFORD 209-966-3621 | 103909942 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43301 | 0.27153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1771 | 2018 | 7 | 20 | 6 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-20 06:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-20 | 15:36 | 37.2433 | -121.8374 | Vegetation | Urban | < 3 meters | Fire Agency | Unknown | 100624129 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43301 | 0.65 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1772 | 2018 | 7 | 20 | 15 | 36 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-20 15:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-20 | 22:44 | 38.8804 | -121.2378 | Vegetation | Rural | < 0.25 Acres | Fire Agency | (916)645-4040 | 100043038 | AT&T | 12000 | Conductor | Overhead | Yes | 43301 | 0.94722 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1773 | 2018 | 7 | 20 | 22 | 44 | 18-0062201 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 2150 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-20 22:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-21 | 0:23 | 38.6927 | -120.7921 | Vegetation | Rural | < 3 meters | Fire Agency | CAMINO | 101415904 | AT&T | 12000 | Conductor | Overhead | Yes | 43302 | 0.015972 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1774 | 2018 | 7 | 21 | 0 | 23 | 18-0062206 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 107552 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-21 00:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-21 | 14:51 | 35.6846 | -120.9427 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101943190 | Unknown | 21000 | Conductor | Overhead | Yes | 43302 | 0.61875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1775 | 2018 | 7 | 21 | 14 | 51 | 18-0062364 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 110814 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-21 14:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-21 | 16:16 | 40.3439 | -123.7092 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 101009789 | Unknown | 12000 | Conductor | Overhead | Yes | 43302 | 0.67778 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1776 | 2018 | 7 | 21 | 16 | 16 | 18-0062375 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 5184 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-21 16:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-21 | 17:03 | 36.3353 | -119.7447 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kings County FD | 100800906 | Unknown | 12000 | Conductor | Overhead | Yes | 43302 | 0.71042 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1777 | 2018 | 7 | 21 | 17 | 3 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-21 17:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-21 | 21:03 | 38.8371 | -121.573 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101296310 | Unknown | 12000 | Conductor | Overhead | Yes | 43302 | 0.87708 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1778 | 2018 | 7 | 21 | 21 | 3 | 18-0062454 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 2926 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-21 21:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-23 | 3:36 | 38.9869 | -121.3167 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Jim Hudson (530)277-2317 or Staion 70 at (916)645-2360 | 100028520 | AT&T | 12000 | Conductor | Overhead | Yes | 43304 | 0.15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1779 | 2018 | 7 | 23 | 3 | 36 | 18-0062563 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 34919 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-23 03:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-23 | 8:46 | 39.6909 | -122.2236 | Vegetation | Rural | < 0.25 Acres | Self Extinguished | N.A. | 100366942 | AT&T | 21000 | Conductor | Overhead | Yes | 43304 | 0.36528 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1780 | 2018 | 7 | 23 | 8 | 46 | 18-0062626 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 5567 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-23 08:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-23 | 15:11 | 39.4911 | -123.7844 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102184598 | Yes | 12000 | Conductor | Overhead | Yes | 43304 | 0.63264 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1781 | 2018 | 7 | 23 | 15 | 11 | 18-0062842 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 44840 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-23 15:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-23 | 17:27 | 39.734 | -121.4965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103843963 | AT&T | 12000 | Conductor | Overhead | Yes | 43304 | 0.72708 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1782 | 2018 | 7 | 23 | 17 | 27 | 18-0062874 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 183629 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-23 17:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-23 | 20:35 | 35.0098 | -119.0693 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | 661-324-6551 | 100221432 | Unknown | 12000 | Conductor | Overhead | Yes | 43304 | 0.85764 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1783 | 2018 | 7 | 23 | 20 | 35 | 18-0062907 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 8506 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-23 20:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-24 | 9:00 | 37.9838 | -122.0637 | Vegetation | Rural | < 3 meters | Fire Agency | Contra Costa FD | 100460575 | Unknown | 21000 | Transformer | Overhead | Yes | 43305 | 0.375 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1784 | 2018 | 7 | 24 | 9 | 0 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-24 09:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-24 | 13:01 | 37.1342 | -120.144 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | chief Vance Killion | 101061631 | Unknown | 12000 | Conductor | Overhead | Yes | 43305 | 0.54236 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1785 | 2018 | 7 | 24 | 13 | 1 | 18-0063175 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 702 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-24 13:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-24 | 13:47 | 39.0606 | -123.4456 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102212216 | Unknown | 12000 | Conductor | Overhead | Yes | 43305 | 0.57431 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1786 | 2018 | 7 | 24 | 13 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-24 13:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-24 | 21:08 | 37.3527 | -122.399 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100318130 | AT&T | 12000 | Conductor | Overhead | Yes | 43305 | 0.88056 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1787 | 2018 | 7 | 24 | 21 | 8 | 18-0063293 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 237000 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-24 21:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-25 | 0:42 | 39.7791 | -121.6173 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100327443 | Unknown | 12000 | Conductor | Overhead | Yes | 43306 | 0.029167 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1788 | 2018 | 7 | 25 | 0 | 42 | 18-0063320 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6742 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-25 00:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-25 | 12:19 | 37.2554 | -121.0093 | Vegetation | Urban | < 3 meters | Customer | N.A. | 101219602 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43306 | 0.51319 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | no-match | 1789 | 2018 | 7 | 25 | 12 | 19 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-25 12:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-25 | 23:16 | 38.4032 | -121.9391 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | VACAVILLE FIRE OFF EUBANKS | 101599788 | AT&T | 12000 | Conductor | Overhead | Yes | 43306 | 0.96944 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1790 | 2018 | 7 | 25 | 23 | 16 | 18-0063319 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 224 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-25 23:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-26 | 19:23 | 39.2559 | -122.4749 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | JEREMIAH KARLONAS 530-473-2615 | 100330499 | Unknown | 12000 | Conductor | Overhead | Yes | 43307 | 0.80764 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1791 | 2018 | 7 | 26 | 19 | 23 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-26 19:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-26 | 20:42 | 40.3551 | -122.3444 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101509573 | Unknown | 12000 | Conductor | Overhead | Yes | 43307 | 0.8625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1792 | 2018 | 7 | 26 | 20 | 42 | 18-0064231 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 42287 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-26 20:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-27 | 23:12 | 37.18 | -122.029 | Vegetation | Rural | < 3 meters | Fire Agency | Jeremy Wise 408-378-4010 Incident # C182080066 | 100518365 | Unknown | 12000 | Conductor | Overhead | Yes | 43308 | 0.96667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1793 | 2018 | 7 | 27 | 23 | 12 | 18-0064525 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 30475 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-27 23:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-28 | 6:51 | 38.7473 | -120.7866 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101418155 | AT&T | 21000 | Conductor | Overhead | Yes | 43309 | 0.28542 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1794 | 2018 | 7 | 28 | 6 | 51 | 18-0064545 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 15429 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-28 06:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-28 | 8:47 | 37.8802 | -122.0804 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 100493058 | Yes | 12000 | Conductor | Overhead | Yes | 43309 | 0.36597 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1795 | 2018 | 7 | 28 | 8 | 47 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-28 08:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-29 | 11:39 | 39.0968 | -123.5018 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102177329 | Unknown | 12000 | Conductor | Overhead | Yes | 43310 | 0.48542 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1796 | 2018 | 7 | 29 | 11 | 39 | 18-0064779 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4329 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-29 11:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-29 | 17:29 | 38.5777 | -120.8556 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101383255 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43310 | 0.72847 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1797 | 2018 | 7 | 29 | 17 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-29 17:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-30 | 7:49 | 37.737 | -122.1878 | Building | Urban | Structure Only | Unknown | N.A. | 103753582 | Unknown | 21000 | Conductor | Overhead | Yes | 43311 | 0.32569 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | no-match | 1798 | 2018 | 7 | 30 | 7 | 49 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-30 07:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-30 | 8:50 | 40.1064 | -123.7138 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100986799 | Unknown | 12000 | Conductor | Overhead | Yes | 43311 | 0.36806 | Equipment/ Facility Failure | crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1799 | 2018 | 7 | 30 | 8 | 50 | 18-0064882 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 18362 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-30 08:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-30 | 14:36 | 38.1987 | -120.3638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NICK WEBB ( 209) 532-7424 | 103336176 | Unknown | 17000 | Conductor | Overhead | Yes | 43311 | 0.60833 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1800 | 2018 | 7 | 30 | 14 | 36 | 18-0065131 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18530 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-30 14:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-30 | 22:01 | 36.3942 | -120.934 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101733550 | Unknown | 21000 | Conductor | Overhead | Yes | 43311 | 0.91736 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1801 | 2018 | 7 | 30 | 22 | 1 | 18-0065201 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 4735 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-30 22:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-31 | 7:07 | 37.8212 | -121.45 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102065265 | Unknown | 12000 | Conductor | Overhead | Yes | 43312 | 0.29653 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1802 | 2018 | 7 | 31 | 7 | 7 | 18-0065255 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 22890 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-31 07:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-31 | 7:57 | 38.9559 | -122.7274 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102162351 | AT&T | 12000 | Conductor | Overhead | Yes | 43312 | 0.33125 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1803 | 2018 | 7 | 31 | 7 | 57 | 18-0065276 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 89832 | 0 | NA | <25mph | <15mph | #REF! | 2018-07-31 07:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-07-31 | 11:01 | 40.1332 | -122.2244 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103133510 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43312 | 0.45903 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1804 | 2018 | 7 | 31 | 11 | 1 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-07-31 11:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-01 | 17:58 | 38.9155 | -122.799 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102156435 | Unknown | 12000 | Conductor | Overhead | Yes | 43313 | 0.74861 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1805 | 2018 | 8 | 1 | 17 | 58 | 18-0065921 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2744 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-01 17:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-01 | 19:06 | 40.8202 | -124.1835 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100968544 | AT&T | 12000 | Conductor | Overhead | Yes | 43313 | 0.79583 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1806 | 2018 | 8 | 1 | 19 | 6 | 18-0065955 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 52951 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-01 19:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-02 | 9:48 | 39.4768 | -121.5395 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 100370637 | Unknown | 12000 | Conductor | Overhead | Yes | 43314 | 0.40833 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1807 | 2018 | 8 | 2 | 9 | 48 | 18-0066104 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 37366 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-02 09:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-02 | 15:54 | 38.9324 | -122.7492 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | kelsey cobb station 707-2794924 kits incident | 102162100 | Unknown | 12000 | Conductor | Overhead | Yes | 43314 | 0.6625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1808 | 2018 | 8 | 2 | 15 | 54 | 18-0066244 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 384442 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-02 15:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-02 | 17:34 | 37.0502 | -120.5412 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101114879 | None | 12000 | Conductor | Overhead | Yes | 43314 | 0.73194 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | Other/Unknown | 1809 | 2018 | 8 | 2 | 17 | 34 | 18-0066260 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 9258 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-02 17:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-02 | 20:27 | 38.1513 | -121.0778 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102072797 | AT&T | 21000 | Conductor | Overhead | Yes | 43314 | 0.85208 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1810 | 2018 | 8 | 2 | 20 | 27 | 18-0066333 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 7065 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-02 20:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-03 | 0:09 | 36.9869 | -120.0597 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Madera County | 101225773 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43315 | 0.00625 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | no-match | 1811 | 2018 | 8 | 3 | 0 | 9 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-08-03 00:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-03 | 9:45 | 40.4988 | -121.8381 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | ZEIGGLER | 101492431 | Frontier | 12000 | Conductor | Overhead | Yes | 43315 | 0.40625 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1812 | 2018 | 8 | 3 | 9 | 45 | 18-0066484 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 4625 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-03 09:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-03 | 16:13 | 37.8765 | -122.0888 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | VIC MASSENKOFF 925-941-3541 CASE # 18-79509 | 100491885 | None | 12000 | Conductor | Overhead | Yes | 43315 | 0.67569 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1813 | 2018 | 8 | 3 | 16 | 13 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-08-03 16:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-03 | 19:19 | 35.4386 | -118.7969 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100203794 | AT&T | 12000 | Conductor | Overhead | Yes | 43315 | 0.80486 | Contact From Object | N.A. | Other | Electric Facility | Human Error | helicopter | Other/Unknown | 1814 | 2018 | 8 | 3 | 19 | 19 | 18-0066608 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 11466 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-03 19:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-03 | 19:51 | 38.6655 | -121.7843 | Vegetation | Urban | < 3 meters | Fire Agency | Woodland FD | 101607437 | Unknown | 12000 | Conductor | Overhead | Yes | 43315 | 0.82708 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1815 | 2018 | 8 | 3 | 19 | 51 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-08-03 19:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-04 | 6:21 | 37.2741 | -120.6336 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 101145547 | Unknown | 12000 | Conductor | Overhead | Yes | 43316 | 0.26458 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1816 | 2018 | 8 | 4 | 6 | 21 | 18-0066660 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 14486 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-04 06:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-04 | 7:22 | 37.9756 | -122.5537 | Building | Urban | Structure Only | Fire Agency | ROSS VALLEY | 102241252 | AT&T | 12000 | Conductor | Overhead | Yes | 43316 | 0.30694 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1817 | 2018 | 8 | 4 | 7 | 22 | 18-0066666 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 6260 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-04 07:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-04 | 14:33 | 38.9262 | -121.4209 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100034761 | AT&T | 12000 | Conductor | Overhead | Yes | 43316 | 0.60625 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1818 | 2018 | 8 | 4 | 14 | 33 | 18-0066768 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 20103 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-04 14:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-04 | 17:18 | 37.0472 | -122.0329 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 101798912 | AT&T | 21000 | Conductor | Overhead | Yes | 43316 | 0.72083 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1819 | 2018 | 8 | 4 | 17 | 18 | 18-0066787 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 29355 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-04 17:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-05 | 13:40 | 37.3178 | -121.8575 | Vegetation | Urban | < 0.25 Acres | Fire Agency | San Jose FD | 103542217 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43317 | 0.56944 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | no-match | 1820 | 2018 | 8 | 5 | 13 | 40 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-08-05 13:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-05 | 13:56 | 37.4005 | -119.7532 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | JIM FORGA 209-966-3621 | 101017235 | Unknown | 12000 | Conductor | Overhead | Yes | 43317 | 0.58056 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1821 | 2018 | 8 | 5 | 13 | 56 | 18-0066905 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 7325 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-05 13:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-06 | 17:27 | 39.3361 | -121.5982 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 100393693 | Yes | 12000 | Conductor | Overhead | Yes | 43318 | 0.72708 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1822 | 2018 | 8 | 6 | 17 | 27 | 18-0067234 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 35675 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-06 17:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-07 | 9:47 | 38.6556 | -121.0226 | Vegetation | Urban | < 3 meters | Fire Agency | CAL FIRE | 103902317 | AT&T | 21000 | Conductor | Overhead | Yes | 43319 | 0.40764 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1823 | 2018 | 8 | 7 | 9 | 47 | 18-0067412 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 243 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-07 09:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-07 | 10:19 | 38.1052 | -120.4978 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101282323 | Unknown | 17000 | Lightning Arrestor | Overhead | Yes | 43319 | 0.42986 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1824 | 2018 | 8 | 7 | 10 | 19 | 18-0067659 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 388 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-07 10:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-07 | 15:22 | 36.7989 | -119.7646 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 103278630 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43319 | 0.64028 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | no-match | 1825 | 2018 | 8 | 7 | 15 | 22 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-08-07 15:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-07 | 15:46 | 40.4465 | -122.446 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464611 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43319 | 0.65694 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1826 | 2018 | 8 | 7 | 15 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-08-07 15:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-07 | 17:15 | 37.1181 | -122.1093 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101670606 | AT&T | 12000 | Conductor | Overhead | Yes | 43319 | 0.71875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1827 | 2018 | 8 | 7 | 17 | 15 | 18-0067641 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1988 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-07 17:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-07 | 21:03 | 38.2129 | -120.9184 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102042811 | Unknown | 12000 | Conductor | Overhead | Yes | 43319 | 0.87708 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1828 | 2018 | 8 | 7 | 21 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-08-07 21:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-08 | 10:03 | 40.7933 | -124.0242 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CHIEF | 100983089 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 0.41875 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1829 | 2018 | 8 | 8 | 10 | 3 | 18-0067921 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 27379 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-08 10:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-08 | 16:02 | 36.4703 | -121.7143 | Vegetation | Rural | < 3 meters | Customer | N.A. | 103910535 | None | 12000 | Conductor | Overhead | Yes | 43320 | 0.66806 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1830 | 2018 | 8 | 8 | 16 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-08-08 16:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-08 | 16:03 | 37.2974 | -122.2651 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 100307515 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 0.66875 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1831 | 2018 | 8 | 8 | 16 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-08-08 16:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-10 | 12:54 | 38.799 | -120.73 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101386272 | AT&T | 12000 | Conductor | Overhead | Yes | 43322 | 0.5375 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1832 | 2018 | 8 | 10 | 12 | 54 | 18-0068798 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 26532 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-10 12:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-10 | 15:39 | 38.2025 | -122.1579 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103697205 | Unknown | 12000 | Conductor | Overhead | Yes | 43322 | 0.65208 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1833 | 2018 | 8 | 10 | 15 | 39 | 18-0068856 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4953 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-10 15:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-10 | 19:18 | 35.7652 | -120.3136 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 18ca-slu-008722 dennis 805 543 4244 | 101876421 | Unknown | 21000 | Conductor | Overhead | Yes | 43322 | 0.80417 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1834 | 2018 | 8 | 10 | 19 | 18 | 18-0068881 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 70040 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-10 19:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-10 | 20:18 | 39.2093 | -121.0615 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100075517 | AT&T | 12000 | Conductor | Overhead | Yes | 43322 | 0.84583 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1835 | 2018 | 8 | 10 | 20 | 18 | 18-0068886 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 581901 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-10 20:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-11 | 16:58 | 38.1952 | -120.6758 | Vegetation | Rural | < 0.25 Acres | Fire Agency | DON YOUNG | 101250814 | Unknown | 12000 | Conductor | Overhead | Yes | 43323 | 0.70694 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1836 | 2018 | 8 | 11 | 16 | 58 | 18-0069021 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 2332 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-11 16:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-12 | 11:42 | 35.6327 | -119.2545 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100140952 | None | 12000 | Conductor | Overhead | Yes | 43324 | 0.4875 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1837 | 2018 | 8 | 12 | 11 | 42 | 18-0069071 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 5854 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-12 11:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-12 | 14:46 | 38.6443 | -120.9211 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101410516 | Unknown | 21000 | Conductor | Overhead | Yes | 43324 | 0.61528 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1838 | 2018 | 8 | 12 | 14 | 46 | 18-0069084 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4032 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-12 14:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-13 | 15:11 | 37.8832 | -121.2483 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 102137301 | Unknown | 12000 | Conductor | Overhead | Yes | 43325 | 0.63264 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1839 | 2018 | 8 | 13 | 15 | 11 | 18-0069409 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 21555 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-13 15:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-13 | 15:33 | 38.708 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101377799 | Unknown | 21000 | Conductor | Overhead | Yes | 43325 | 0.64792 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1840 | 2018 | 8 | 13 | 15 | 33 | 18-0069470 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1004 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-13 15:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-13 | 18:43 | 36.2265 | -121.1111 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101729151 | Unknown | 12000 | Conductor | Overhead | Yes | 43325 | 0.77986 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1841 | 2018 | 8 | 13 | 18 | 43 | 18-0069468 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 22851 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-13 18:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-14 | 6:43 | 40.686 | -122.141 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | j.t. zulliger 530-225-2420 | 103379843 | Unknown | 12000 | Conductor | Overhead | Yes | 43326 | 0.27986 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1842 | 2018 | 8 | 14 | 6 | 43 | 18-0069529 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 37986 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-14 06:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-14 | 15:18 | 36.9656 | -121.8681 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 103128221 | AT&T | 21000 | Conductor | Overhead | Yes | 43326 | 0.6375 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1843 | 2018 | 8 | 14 | 15 | 18 | 18-0069846 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 15580 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-14 15:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-14 | 15:46 | 38.0878 | -122.6002 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103916882 | Verizon | 0 – 750 | Conductor | Overhead | Yes | 43326 | 0.65694 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1844 | 2018 | 8 | 14 | 15 | 46 | 18-0069929 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 546 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-14 15:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-17 | 9:38 | 40.2997 | -122.3322 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chief | 101509747 | AT&T | 12000 | Conductor | Overhead | Yes | 43329 | 0.40139 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1845 | 2018 | 8 | 17 | 9 | 38 | 18-0071042 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 15510 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-17 09:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-17 | 17:18 | 37.5258 | -121.9698 | Vegetation | Urban | < 3 meters | Self Extinguished | N.A. | 100946234 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43329 | 0.72083 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Grow Into | 1846 | 2018 | 8 | 17 | 17 | 18 | 18-0071252 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Grow Into | 4763 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-17 17:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-18 | 6:15 | 38.4026 | -121.9635 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | Twr 2/18 | None | 115000 | Conductor | Overhead | Yes | 43330 | 0.26042 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | no-match | 1847 | 2018 | 8 | 18 | 6 | 15 | INT-11294 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 0 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-18 06:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-20 | 5:26 | 37.1334 | -121.6282 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 103560218 | Unknown | 21000 | Capacitor Bank | Overhead | Yes | 43332 | 0.22639 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1848 | 2018 | 8 | 20 | 5 | 26 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-08-20 05:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-20 | 9:34 | 39.8014 | -121.5813 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100400441 | Unknown | 12000 | Conductor | Overhead | Yes | 43332 | 0.39861 | Contact From Object | N.A. | Other | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1849 | 2018 | 8 | 20 | 9 | 34 | 18-0071596 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 394259 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-20 09:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-20 | 10:06 | 37.0326 | -120.4059 | Vegetation | Rural | .26 - 9.99 Acres | Self Extinguished | N.A. | 101090947 | Unknown | 12000 | Lightning Arrestor | Overhead | Yes | 43332 | 0.42083 | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | no-match | 1850 | 2018 | 8 | 20 | 10 | 6 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-08-20 10:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-21 | 0:23 | 37.0625 | -120.0521 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103117111 | Unknown | 17000 | Conductor | Overhead | Yes | 43333 | 0.015972 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1851 | 2018 | 8 | 21 | 0 | 23 | 18-0071915 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 1641 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-21 00:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-21 | 10:13 | 38.6972 | -120.889 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101385436 | Unknown | 12000 | Conductor | Overhead | Yes | 43333 | 0.42569 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1852 | 2018 | 8 | 21 | 10 | 13 | 18-0072055 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4572 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-21 10:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-22 | 17:24 | 37.9519 | -120.3103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101030620 | Unknown | 17000 | Conductor | Overhead | Yes | 43334 | 0.725 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | dampeners | no-match | 1853 | 2018 | 8 | 22 | 17 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-08-22 17:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-22 | 21:56 | 39.0425 | -120.9695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100024728 | Verizon | 12000 | Conductor | Overhead | Yes | 43334 | 0.91389 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1854 | 2018 | 8 | 22 | 21 | 56 | 18-0072654 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 29727 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-22 21:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-23 | 14:23 | 34.608 | -120.1937 | Vegetation | Urban | < 3 meters | Fire Agency | Unknown | 101917609 | Unknown | 12000 | Conductor | Overhead | Yes | 43335 | 0.59931 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1855 | 2018 | 8 | 23 | 14 | 23 | 18-0072921 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 51634 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-23 14:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-23 | 16:06 | 36.7349 | -120.1107 | Vegetation | Rural | < 3 meters | Fire Agency | TRUCK 21 MENDOZA (559)621-4181 | 103258579 | Unknown | 12000 | Conductor | Overhead | Yes | 43335 | 0.67083 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1856 | 2018 | 8 | 23 | 16 | 6 | 18-0072974 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 38864 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-23 16:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-24 | 1:38 | 39.2029 | -121.2766 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100087099 | AT&T | 21000 | Conductor | Overhead | Yes | 43336 | 0.068056 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1857 | 2018 | 8 | 24 | 1 | 38 | 18-0073021 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 24360 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-24 01:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-24 | 5:03 | 39.1184 | -121.0154 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JIM SMITH BATT CHIEF 3 | 100097647 | Unknown | 12000 | Conductor | Overhead | Yes | 43336 | 0.21042 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1858 | 2018 | 8 | 24 | 5 | 3 | 18-0073024 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 4048 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-24 05:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-25 | 17:15 | 40.573 | -122.2386 | Vegetation | Rural | < 0.25 Acres | Fire Agency | BRIAN NOEL (530)448-2411 | 101472424 | Frontier | 12000 | Conductor | Overhead | Yes | 43337 | 0.71875 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1859 | 2018 | 8 | 25 | 17 | 15 | 18-0073439 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 22273 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-25 17:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-26 | 15:29 | 39.3599 | -121.1209 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100107472 | Unknown | 12000 | Conductor | Overhead | Yes | 43338 | 0.64514 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1860 | 2018 | 8 | 26 | 15 | 29 | 18-0073601 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 36162 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-26 15:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-26 | 16:50 | 39.7585 | -123.2359 | Vegetation | Rural | < 0.25 Acres | Fire Agency | HOWARD FOREST | 102183272 | Verizon | 12000 | Conductor | Overhead | Yes | 43338 | 0.70139 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1861 | 2018 | 8 | 26 | 16 | 50 | 18-0073619 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1457 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-26 16:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-27 | 5:54 | 36.7865 | -119.5221 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100798371 | Unknown | 12000 | Conductor | Overhead | Yes | 43339 | 0.24583 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1862 | 2018 | 8 | 27 | 5 | 54 | 18-0073650 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 7074 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-27 05:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-27 | 13:56 | 37.0127 | -121.6026 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 103918532 | Verizon | 21000 | Conductor | Overhead | Yes | 43339 | 0.58056 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1863 | 2018 | 8 | 27 | 13 | 56 | 18-0073960 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 392154 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-27 13:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-27 | 16:45 | 36.7489 | -119.7471 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 100845137 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43339 | 0.69792 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1864 | 2018 | 8 | 27 | 16 | 45 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-08-27 16:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-28 | 2:00 | 36.5645 | -119.606 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100864815 | AT&T | 12000 | Conductor | Overhead | Yes | 43340 | 0.083333 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1865 | 2018 | 8 | 28 | 2 | 0 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-08-28 02:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-28 | 12:50 | 40.2139 | -123.5966 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100994840 | Unknown | 12000 | Conductor | Overhead | Yes | 43340 | 0.53472 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1866 | 2018 | 8 | 28 | 12 | 50 | 18-0074371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 82754 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-28 12:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-28 | 16:14 | 39.2284 | -123.1995 | Vegetation | Rural | < 0.25 Acres | Fire Agency | howard forest | 102174042 | AT&T | 12000 | Conductor | Overhead | Yes | 43340 | 0.67639 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1867 | 2018 | 8 | 28 | 16 | 14 | 18-0074611 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 58921 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-28 16:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-29 | 16:19 | 38.7732 | -121.431 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103918537 | Unknown | 12000 | Conductor | Overhead | Yes | 43341 | 0.67986 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1868 | 2018 | 8 | 29 | 16 | 19 | 18-0074979 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 12467 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-29 16:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-30 | 15:38 | 38.2544 | -122.5754 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101990006 | Unknown | 12000 | Conductor | Overhead | Yes | 43342 | 0.65139 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | no-match | 1869 | 2018 | 8 | 30 | 15 | 38 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-08-30 15:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-31 | 5:07 | 36.7875 | -119.6552 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CLOVIS F.D. | 103281648 | None | 12000 | Conductor | Overhead | Yes | 43343 | 0.21319 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1870 | 2018 | 8 | 31 | 5 | 7 | 18-0075344 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 170596 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-31 05:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-31 | 12:30 | 37.9917 | -121.3478 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 103193823 | Unknown | 21000 | Conductor | Overhead | Yes | 43343 | 0.52083 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1871 | 2018 | 8 | 31 | 12 | 30 | 18-0075648 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 17819 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-31 12:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-31 | 13:02 | 40.4775 | -122.4847 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103918932 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 0.54306 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1872 | 2018 | 8 | 31 | 13 | 2 | 18-0075616 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18300 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-31 13:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-31 | 18:04 | 39.5785 | -123.3842 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102196393 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 0.75278 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1873 | 2018 | 8 | 31 | 18 | 4 | 18-0075741 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18540 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-31 18:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-08-31 | 18:09 | 37.0548 | -122.0472 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 101803212 | Unknown | 21000 | Conductor | Overhead | Yes | 43343 | 0.75625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1874 | 2018 | 8 | 31 | 18 | 9 | 18-0075730 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 197397 | 0 | NA | <25mph | <15mph | #REF! | 2018-08-31 18:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-01 | 14:25 | 36.8088 | -121.5916 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Twr 35/222 | None | 115000 | Conductor | Overhead | Yes | 43344 | 0.60069 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1875 | 2018 | 9 | 1 | 14 | 25 | INT-11331 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 702145 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-01 14:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-02 | 15:36 | 37.4714 | -122.4248 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Arie Delay 659-740-4636 | 103808872 | Unknown | 12000 | Capacitor Bank | Overhead | Yes | 43345 | 0.65 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1876 | 2018 | 9 | 2 | 15 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-09-02 15:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-02 | 16:11 | 37.2653 | -121.8051 | Vegetation | Urban | < 3 meters | Unknown | N.A. | 103436542 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43345 | 0.67431 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1877 | 2018 | 9 | 2 | 16 | 11 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-09-02 16:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-02 | 23:18 | 37.7942 | -121.5773 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102051470 | Unknown | 12000 | Conductor | Overhead | Yes | 43345 | 0.97083 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1878 | 2018 | 9 | 2 | 23 | 18 | 18-0075936 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 9408 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-02 23:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-03 | 12:00 | 38.9181 | -121.5435 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Str. 017/369 | None | 60000 | Conductor | Overhead | Yes | 43346 | 0.5 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1879 | 2018 | 9 | 3 | 12 | 0 | INT-11338 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-03 12:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-03 | 18:29 | 39.4547 | -121.4955 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100395672 | Unknown | 12000 | Conductor | Overhead | Yes | 43346 | 0.77014 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1880 | 2018 | 9 | 3 | 18 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-09-03 18:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-05 | 11:39 | 38.997 | -121.5427 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101331539 | Unknown | 21000 | Conductor | Overhead | Yes | 43348 | 0.48542 | Contact From Object | N.A. | Other | Electric Facility | Human Error | third-party caused | Other/Unknown | 1881 | 2018 | 9 | 5 | 11 | 39 | 18-0076669 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 100103 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-05 11:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-05 | 16:55 | 37.4655 | -119.9005 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JON BERRY 209-966-4700 | 101087053 | Unknown | 21000 | Conductor | Overhead | Yes | 43348 | 0.70486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1882 | 2018 | 9 | 5 | 16 | 55 | 18-0076909 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 4017 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-05 16:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-05 | 17:34 | 39.2586 | -123.2017 | Vegetation | Rural | < 3 meters | Fire Agency | redwood valley fire | 102202457 | AT&T | 12000 | Conductor | Overhead | Yes | 43348 | 0.73194 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1883 | 2018 | 9 | 5 | 17 | 34 | 18-0076917 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 20230 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-05 17:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-05 | 20:02 | 39.7545 | -123.2202 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 102183324 | Verizon | 12000 | Conductor | Overhead | Yes | 43348 | 0.83472 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1884 | 2018 | 9 | 5 | 20 | 2 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-09-05 20:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-06 | 1:19 | 37.0598 | -121.0169 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Pole 088/386 | None | 70000 | Conductor | Overhead | Yes | 43349 | 0.054861 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | no-match | 1885 | 2018 | 9 | 6 | 1 | 19 | INT-11343 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 105728 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-06 01:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-06 | 16:19 | 39.0904 | -120.9464 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 100020676 | Unknown | 12000 | Conductor | Overhead | Yes | 43349 | 0.67986 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1886 | 2018 | 9 | 6 | 16 | 19 | 18-0077280 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 30780 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-06 16:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-09 | 4:25 | 38.6534 | -122.8538 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 13/1 | None | 60000 | Conductor | Overhead | Yes | 43352 | 0.18403 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1887 | 2018 | 9 | 9 | 4 | 25 | INT-11353 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 0 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-09 04:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-10 | 7:05 | 35.0423 | -120.5673 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101924034 | Unknown | 12000 | Conductor | Overhead | Yes | 43353 | 0.29514 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1888 | 2018 | 9 | 10 | 7 | 5 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-09-10 07:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-10 | 20:37 | 38.0188 | -122.7225 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 102252760 | Unknown | 12000 | Conductor | Overhead | Yes | 43353 | 0.85903 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1889 | 2018 | 9 | 10 | 20 | 37 | 18-0078359 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 219903 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-10 20:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-10 | 21:25 | 37.0984 | -120.2583 | Building | Rural | Structure Only | Unknown | N.A. | 101129394 | Unknown | 12000 | Conductor | Overhead | Yes | 43353 | 0.89236 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1890 | 2018 | 9 | 10 | 21 | 25 | 18-0078361 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 825 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-10 21:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-11 | 5:23 | 37.376 | -119.6304 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | TROY CHEEK 209-966-3621 | 101023184 | Unknown | 12000 | Conductor | Overhead | Yes | 43354 | 0.22431 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1891 | 2018 | 9 | 11 | 5 | 23 | 18-0078387 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 288 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-11 05:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-11 | 11:19 | 35.4213 | -120.8627 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101928875 | Unknown | 12000 | Conductor | Overhead | Yes | 43354 | 0.47153 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1892 | 2018 | 9 | 11 | 11 | 19 | 18-0078555 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1158 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-11 11:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-11 | 18:51 | 38.3958 | -121.6382 | Vegetation | Rural | 10 - 99 Acres | Unknown | N.A. | 101586871 | AT&T | 12000 | Conductor | Overhead | Yes | 43354 | 0.78542 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1893 | 2018 | 9 | 11 | 18 | 51 | 18-0078774 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 85675 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-11 18:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-11 | 21:44 | 34.8553 | -119.4864 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Santa Barbara Co. FD | 100165137 | Unknown | 21000 | Conductor | Overhead | Yes | 43354 | 0.90556 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1894 | 2018 | 9 | 11 | 21 | 44 | 18-0078787 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 108 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-11 21:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-12 | 19:38 | 38.1228 | -121.8125 | Building | Rural | Structure Only | Fire Agency | Solano FD | 101566543 | Unknown | 21000 | Conductor | Overhead | Yes | 43355 | 0.81806 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1895 | 2018 | 9 | 12 | 19 | 38 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-09-12 19:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-13 | 9:02 | 40.1746 | -122.2412 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Red Bluff FD | 101541885 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43356 | 0.37639 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1896 | 2018 | 9 | 13 | 9 | 2 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-09-13 09:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-14 | 9:06 | 40.1336 | -122.2049 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 101537662 | Unknown | 12000 | Capacitor Bank | Overhead | Yes | 43357 | 0.37917 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1897 | 2018 | 9 | 14 | 9 | 6 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-09-14 09:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-14 | 15:08 | 35.328 | -120.6982 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Sean Hernandez Cell # 805 903 3423 | 103400199 | Unknown | 12000 | Conductor | Overhead | Yes | 43357 | 0.63056 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1898 | 2018 | 9 | 14 | 15 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-09-14 15:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-15 | 3:47 | 35.4417 | -119.1614 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 103920769 | Unknown | 21000 | Conductor | Overhead | Yes | 43358 | 0.15764 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1899 | 2018 | 9 | 15 | 3 | 47 | 18-0079945 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 188488 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-15 03:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-15 | 9:57 | 38.6938 | -122.832 | Vegetation | Rural | < 3 meters | Customer | N.A. | 102034048 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43358 | 0.41458 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1900 | 2018 | 9 | 15 | 9 | 57 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-09-15 09:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-15 | 13:34 | 37.2464 | -120.4376 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101154147 | None | 0 – 750 | Conductor | Overhead | Yes | 43358 | 0.56528 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1901 | 2018 | 9 | 15 | 13 | 34 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-09-15 13:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-16 | 8:10 | 37.9953 | -122.2834 | Vegetation | Urban | < 3 meters | Unknown | N.A. | 101425698 | Unknown | 12000 | Conductor | Overhead | Yes | 43359 | 0.34028 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1902 | 2018 | 9 | 16 | 8 | 10 | 18-0080091 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 160675 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-16 08:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-16 | 8:26 | 35.3046 | -120.6389 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | Pole 4/23A | None | 70000 | Conductor | Overhead | Yes | 43359 | 0.35139 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1903 | 2018 | 9 | 16 | 8 | 26 | INT-11371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 29925 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-16 08:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-16 | 10:22 | 39.4627 | -123.7837 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 102184303 | AT&T | 12000 | Conductor | Overhead | Yes | 43359 | 0.43194 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1904 | 2018 | 9 | 16 | 10 | 22 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-09-16 10:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-17 | 16:05 | 36.8145 | -119.9795 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Fresno FD | 100664916 | None | 12000 | Conductor | Overhead | Yes | 43360 | 0.67014 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1905 | 2018 | 9 | 17 | 16 | 5 | 18-0080639 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 36360 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-17 16:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-19 | 6:04 | 37.5315 | -120.3284 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Pole 13/4 | None | 70000 | Conductor | Overhead | Yes | 43362 | 0.25278 | Contact From Object | N.A. | Other | Electric Facility | Unknown | guano | no-match | 1906 | 2018 | 9 | 19 | 6 | 4 | INT-11378 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 0 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-19 06:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-21 | 11:26 | 37.7448 | -121.5136 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102064462 | AT&T | 12000 | Conductor | Overhead | Yes | 43364 | 0.47639 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1907 | 2018 | 9 | 21 | 11 | 26 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-09-21 11:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-21 | 21:10 | 39.0273 | -122.6627 | Vegetation | Rural | < 3 meters | Customer | N.A. | 102147414 | Unknown | 12000 | Conductor | Overhead | Yes | 43364 | 0.88194 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1908 | 2018 | 9 | 21 | 21 | 10 | 18-0082278 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 281055 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-21 21:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-21 | 23:02 | 38.6428 | -122.7453 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102218862 | Unknown | 12000 | Conductor | Overhead | Yes | 43364 | 0.95972 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1909 | 2018 | 9 | 21 | 23 | 2 | 18-0082304 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 9470 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-21 23:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-22 | 17:56 | 37.0127 | -120.8459 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101198814 | None | 12000 | Fuse | Overhead | Yes | 43365 | 0.74722 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1910 | 2018 | 9 | 22 | 17 | 56 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-09-22 17:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-23 | 3:18 | 38.416 | -121.7303 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101587125 | AT&T | 12000 | Conductor | Overhead | Yes | 43366 | 0.1375 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1911 | 2018 | 9 | 23 | 3 | 18 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-09-23 03:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-23 | 15:57 | 37.335 | -121.7679 | Vegetation | Urban | 10 - 99 Acres | Fire Agency | San Jose FD | 100576722 | AT&T | 21000 | Conductor | Overhead | Yes | 43366 | 0.66458 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1912 | 2018 | 9 | 23 | 15 | 57 | 18-0082586 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 231441 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-23 15:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-24 | 0:35 | 39.8152 | -121.6438 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Pole 3/42B | None | 60000 | Conductor | Overhead | Yes | 43367 | 0.024306 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1913 | 2018 | 9 | 24 | 0 | 35 | INT-11388 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 2407691 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-24 00:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-24 | 12:07 | 37.5953 | -122.0175 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 103505364 | Unknown | 12000 | Conductor | Overhead | Yes | 43367 | 0.50486 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1914 | 2018 | 9 | 24 | 12 | 7 | 18-0082813 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 97478 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-24 12:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-24 | 17:06 | 37.2915 | -121.9357 | Vegetation | Urban | < 3 meters | Unknown | N.A. | 100521762 | Unknown | 12000 | Conductor | Overhead | Yes | 43367 | 0.7125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1915 | 2018 | 9 | 24 | 17 | 6 | 18-0082985 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 83850 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-24 17:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-27 | 3:40 | 37.5473 | -120.3255 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Twr 12/2 | None | 70000 | Conductor | Overhead | Yes | 43370 | 0.15278 | Contact From Object | N.A. | Other | Electric Facility | Unknown | guano | no-match | 1916 | 2018 | 9 | 27 | 3 | 40 | INT-11393 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 0 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-27 03:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-27 | 12:43 | 38.5148 | -122.4463 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Twr 000/010 | None | 60000 | Conductor | Overhead | Yes | 43370 | 0.52986 | Contact From Object | N.A. | Other | Electric Facility | Human Error | helicopter | no-match | 1917 | 2018 | 9 | 27 | 12 | 43 | INT-11394 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1488992 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-27 12:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-27 | 15:25 | 36.5008 | -119.2913 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100779012 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43370 | 0.64236 | Contact From Object | N.A. | Other | Pole | Human Error | third-party caused | no-match | 1918 | 2018 | 9 | 27 | 15 | 25 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-09-27 15:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-27 | 17:19 | 36.5498 | -120.3893 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 103921482 | Verizon | 12000 | Conductor | Overhead | Yes | 43370 | 0.72153 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1919 | 2018 | 9 | 27 | 17 | 19 | 18-0084318 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 19682 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-27 17:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-28 | 4:31 | 35.2307 | -119.0922 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 100162524 | Unknown | 12000 | Conductor | Overhead | Yes | 43371 | 0.18819 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1920 | 2018 | 9 | 28 | 4 | 31 | 18-0084364 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 8748 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-28 04:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-28 | 9:55 | 37.0564 | -120.8008 | Vegetation | Rural | < 3 meters | Unknown | N.A. | Pole 23/8 | None | 70000 | Conductor | Overhead | Yes | 43371 | 0.41319 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1921 | 2018 | 9 | 28 | 9 | 55 | INT-11395 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 0 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-28 09:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-29 | 13:11 | 40.9061 | -124.0625 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100973832 | Unknown | 12000 | Conductor | Overhead | Yes | 43372 | 0.54931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1922 | 2018 | 9 | 29 | 13 | 11 | 18-0084851 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 1776 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-29 13:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-29 | 16:16 | 41.0219 | -123.655 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Hoopa Fire Dept | 100962165 | Unknown | 12000 | Conductor | Overhead | Yes | 43372 | 0.67778 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1923 | 2018 | 9 | 29 | 16 | 16 | 18-0084877 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 16028 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-29 16:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-09-30 | 14:40 | 39.9301 | -122.2491 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101499723 | AT&T | 12000 | Conductor | Overhead | Yes | 43373 | 0.61111 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1924 | 2018 | 9 | 30 | 14 | 40 | 18-0084966 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 12905 | 0 | NA | <25mph | <15mph | #REF! | 2018-09-30 14:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-01 | 15:10 | 36.82 | -121.6869 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103839895 | AT&T | 12000 | Conductor | Overhead | Yes | 43374 | 0.63194 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1925 | 2018 | 10 | 1 | 15 | 10 | 18-0085308 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 502 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-01 15:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-03 | 16:16 | 38.9306 | -121.1825 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100069555 | None | 12000 | Conductor | Overhead | Yes | 43376 | 0.67778 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1926 | 2018 | 10 | 3 | 16 | 16 | 18-0086333 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 3368 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-03 16:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-06 | 14:56 | 39.9285 | -122.2255 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Red Bluff FD | 101499494 | Unknown | 12000 | Conductor | Overhead | Yes | 43379 | 0.62222 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1927 | 2018 | 10 | 6 | 14 | 56 | No ILIS or TOTL available | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-10-06 14:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-06 | 17:29 | 37.3281 | -120.5288 | Vegetation | Urban | < 3 meters | Unknown | N.A. | 101160081 | Unknown | 12000 | Conductor | Overhead | Yes | 43379 | 0.72847 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1928 | 2018 | 10 | 6 | 17 | 29 | 18-0087674 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 6810 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-06 17:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-07 | 1:44 | 37.178 | -122.0267 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Mike Mathiesen 408-472-1613 Incident # SCU7096 | 100518363 | Unknown | 12000 | Conductor | Overhead | Yes | 43380 | 0.072222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1929 | 2018 | 10 | 7 | 1 | 44 | 18-0087807 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 224444 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-07 01:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-07 | 8:45 | 41.0569 | -124.1024 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 100977448 | None | 12000 | Conductor | Overhead | Yes | 43380 | 0.36458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1930 | 2018 | 10 | 7 | 8 | 45 | 18-0087893 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 11792 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-07 08:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-07 | 8:46 | 38.3581 | -121.7393 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101570462 | Unknown | 12000 | Conductor | Overhead | Yes | 43380 | 0.36528 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1931 | 2018 | 10 | 7 | 8 | 46 | 18-0087853 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 13518 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-07 08:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-07 | 17:48 | 37.6829 | -122.1114 | Vegetation | Urban | < 3 meters | Unknown | N.A. | 100910270 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43380 | 0.74167 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1932 | 2018 | 10 | 7 | 17 | 48 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-10-07 17:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-08 | 11:03 | 38.2621 | -122.7881 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101987186 | AT&T | 12000 | Conductor | Overhead | No | N.A. | N.A. | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1933 | 2018 | 10 | 8 | 11 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-10-08 11:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-10 | 13:24 | 38.5357 | -121.5541 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 101585188 | Unknown | 12000 | Conductor | Overhead | Yes | 43383 | 0.55833 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1934 | 2018 | 10 | 10 | 13 | 24 | 18-0089140 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 13636 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-10 13:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-11 | 10:40 | 39.3621 | -121.8548 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 103381647 | Unknown | 12000 | Conductor | Overhead | Yes | 43384 | 0.44444 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1935 | 2018 | 10 | 11 | 10 | 40 | 18-0089422 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 16966 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-11 10:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-11 | 12:00 | 38.6924 | -121.774 | Vegetation | Rural | < 3 meters | Fire Agency | Woodland FD | 101625618 | Yes | 0 – 750 | Conductor | Overhead | Yes | 43384 | 0.5 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1936 | 2018 | 10 | 11 | 12 | 0 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-10-11 12:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-11 | 22:39 | 36.9897 | -121.9767 | Vegetation | Urban | < 3 meters | Fire Agency | Unknown | 101684569 | AT&T | 21000 | Conductor | Overhead | Yes | 43384 | 0.94375 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1937 | 2018 | 10 | 11 | 22 | 39 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-10-11 22:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-14 | 11:40 | 40.3598 | -122.4388 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TOM STROING 530-200-5113 | 101506416 | AT&T | 12000 | Conductor | Overhead | Yes | 43387 | 0.48611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1938 | 2018 | 10 | 14 | 11 | 40 | 18-0090193 | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 945 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-14 11:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-14 | 19:39 | 38.446 | -120.5147 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | IC- Dillon Gissell- 209-295-7735 | 103384485 | Unknown | 12000 | Conductor | Overhead | Yes | 43387 | 0.81875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1939 | 2018 | 10 | 14 | 19 | 39 | 18-0090288 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3497327 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-14 19:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-14 | 20:08 | 38.8935 | -120.8497 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103674516 | Unknown | 21000 | Conductor | Overhead | Yes | 43387 | 0.83889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1940 | 2018 | 10 | 14 | 20 | 8 | 18-0090299 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 48095 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-14 20:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-15 | 3:23 | 38.2897 | -120.5803 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103378003 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43388 | 0.14097 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1941 | 2018 | 10 | 15 | 3 | 23 | 18-0090342 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1464 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-15 03:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-16 | 10:44 | 40.5097 | -124.1624 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101004106 | Unknown | 12000 | Conductor | Overhead | Yes | 43389 | 0.44722 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1942 | 2018 | 10 | 16 | 10 | 44 | 18-0090952 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 2081 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-16 10:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-16 | 16:30 | 38.7754 | -122.8976 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MARK GRADEK (707) 889-4303 | 101962692 | AT&T | 12000 | Conductor | Overhead | Yes | 43389 | 0.6875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1943 | 2018 | 10 | 16 | 16 | 30 | 18-0091127 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 744 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-16 16:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-17 | 17:41 | 38.0311 | -121.9334 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100450321 | Unknown | 21000 | Conductor | Overhead | Yes | 43390 | 0.73681 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1944 | 2018 | 10 | 17 | 17 | 41 | 18-0091501 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 128894 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-17 17:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-19 | 15:45 | 35.0395 | -120.4763 | Vegetation | Urban | < 3 meters | Unknown | N.A. | 101893816 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43392 | 0.65625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1945 | 2018 | 10 | 19 | 15 | 45 | 18-0092287 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 31777 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-19 15:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-20 | 8:01 | 35.0077 | -120.4938 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101893623 | Unknown | 12000 | Conductor | Overhead | Yes | 43393 | 0.33403 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1946 | 2018 | 10 | 20 | 8 | 1 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-10-20 08:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-20 | 14:31 | 40.5218 | -124.1137 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Str. 003/000 | None | 60000 | Conductor | Overhead | Yes | 43393 | 0.60486 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1947 | 2018 | 10 | 20 | 14 | 31 | INT-11477 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 410982 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-20 14:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-21 | 0:32 | 35.5035 | -120.6025 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101886776 | Unknown | 21000 | Conductor | Overhead | Yes | 43394 | 0.022222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1948 | 2018 | 10 | 21 | 0 | 32 | 18-0092526 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 302559 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-21 00:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-24 | 7:08 | 37.9475 | -120.2671 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SCOTT PITTMAN 209-768-8182 TCU INCIDENT# 012528 | 101047865 | Unknown | 17000 | Conductor | Overhead | Yes | 43397 | 0.29722 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1949 | 2018 | 10 | 24 | 7 | 8 | 18-0093599 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 13433 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-24 07:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-24 | 14:18 | 36.7265 | -119.1086 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CHRIS CHRISTOPHERSON (559)493-4320 I.C #18CAFKUO15649 | 100691946 | None | 12000 | Conductor | Overhead | Yes | 43397 | 0.59583 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1950 | 2018 | 10 | 24 | 14 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-10-24 14:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-25 | 18:47 | 35.5566 | -118.8168 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | GREG BLACK (661)391-7000 | 100203660 | None | 0 – 750 | Conductor | Overhead | Yes | 43398 | 0.78264 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1951 | 2018 | 10 | 25 | 18 | 47 | 18-0094369 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1309 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-25 18:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-26 | 2:11 | 37.7553 | -122.4345 | Vegetation | Urban | < 3 meters | Unknown | N.A. | 101838487 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43399 | 0.090972 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1952 | 2018 | 10 | 26 | 2 | 11 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-10-26 02:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-26 | 20:55 | 40.1528 | -122.3634 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT. ROB WAELTY 530-527-6113 | 101553579 | Unknown | 12000 | Conductor | Overhead | Yes | 43399 | 0.87153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1953 | 2018 | 10 | 26 | 20 | 55 | 18-0094702 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4812 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-26 20:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-28 | 8:50 | 36.3792 | -121.8454 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TONY (831) 625-6415 | 101672342 | Unknown | 12000 | Conductor | Overhead | Yes | 43401 | 0.36806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1954 | 2018 | 10 | 28 | 8 | 50 | 18-0094889 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 3046 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-28 08:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-29 | 19:09 | 39.4645 | -122.2487 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100343112 | None | 21000 | Conductor | Overhead | Yes | 43402 | 0.79792 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1955 | 2018 | 10 | 29 | 19 | 9 | 18-0095375 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 22833 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-29 19:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-30 | 15:40 | 37.1779 | -120.6309 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101185288 | Unknown | 12000 | Conductor | Overhead | Yes | 43403 | 0.65278 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1956 | 2018 | 10 | 30 | 15 | 40 | 18-0095710 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 528 | 0 | NA | <25mph | <15mph | #REF! | 2018-10-30 15:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-10-31 | 12:50 | 37.3348 | -121.937 | Vegetation | Urban | < 3 meters | Fire Agency | San Jose FD | 103780642 | AT&T | 12000 | Capacitor Bank | Overhead | Yes | 43404 | 0.53472 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1957 | 2018 | 10 | 31 | 12 | 50 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-10-31 12:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-01 | 20:45 | 38.372 | -123.0507 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103852431 | AT&T | 12000 | Conductor | Overhead | Yes | 43405 | 0.86458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1958 | 2018 | 11 | 1 | 20 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-11-01 20:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-07 | 15:49 | 37.0003 | -121.9802 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 101684527 | Unknown | 21000 | Capacitor Bank | Overhead | Yes | 43411 | 0.65903 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1959 | 2018 | 11 | 7 | 15 | 49 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-11-07 15:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-08 | 11:41 | 34.8649 | -120.3402 | Vegetation | Rural | 10 - 99 Acres | Unknown | N.A. | 101862240 | Verizon | 12000 | Conductor | Overhead | Yes | 43412 | 0.48681 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1960 | 2018 | 11 | 8 | 11 | 41 | 18-0098258 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 99262 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-08 11:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-08 | 13:19 | 38.7884 | -120.1529 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101407590 | AT&T | 21000 | Conductor | Overhead | Yes | 43412 | 0.55486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1961 | 2018 | 11 | 8 | 13 | 19 | 18-0098381 | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 671513 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-08 13:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-08 | 21:30 | 36.7364 | -119.4988 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103818023 | Unknown | 12000 | Conductor | Overhead | Yes | 43412 | 0.89583 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1962 | 2018 | 11 | 8 | 21 | 30 | 18-0098466 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 16642 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-08 21:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-09 | 4:49 | 39.8234 | -121.8382 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100402367 | AT&T | 12000 | Conductor | Overhead | Yes | 43413 | 0.20069 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1963 | 2018 | 11 | 9 | 4 | 49 | 18-0098482 | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 11900 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-09 04:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-09 | 8:59 | 37.2809 | -122.1214 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100546562 | AT&T | 12000 | Conductor | Overhead | Yes | 43413 | 0.37431 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1964 | 2018 | 11 | 9 | 8 | 59 | 18-0098521 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 77077 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-09 08:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-09 | 15:34 | 35.0512 | -118.8112 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 103930710 | None | 12000 | Conductor | Overhead | Yes | 43413 | 0.64861 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1965 | 2018 | 11 | 9 | 15 | 34 | 18-0098725 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 1976 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-09 15:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-10 | 13:31 | 37.0467 | -121.9853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101671641 | Unknown | 21000 | Conductor | Overhead | Yes | 43414 | 0.56319 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1966 | 2018 | 11 | 10 | 13 | 31 | 18-0098856 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 1482 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-10 13:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-11 | 4:18 | 38.4341 | -122.5522 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102032588 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43415 | 0.17917 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1967 | 2018 | 11 | 11 | 4 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-11-11 04:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-11 | 10:40 | 37.0984 | -120.7416 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103934503 | Unknown | 12000 | Conductor | Overhead | Yes | 43415 | 0.44444 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1968 | 2018 | 11 | 11 | 10 | 40 | 18-0098979 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 49010 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-11 10:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-11 | 13:06 | 37.3202 | -122.0023 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 103927631 | AT&T | 12000 | Capacitor Bank | Overhead | Yes | 43415 | 0.54583 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | Other/Unknown | 1969 | 2018 | 11 | 11 | 13 | 6 | 18-0098972 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 56462 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-11 13:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-12 | 5:17 | 38.4852 | -122.8046 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 102027067 | Unknown | 12000 | Conductor | Overhead | Yes | 43416 | 0.22014 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1970 | 2018 | 11 | 12 | 5 | 17 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-11-12 05:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-12 | 14:39 | 36.993 | -120.0372 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 101015260 | AT&T | 12000 | Conductor | Overhead | Yes | 43416 | 0.61042 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1971 | 2018 | 11 | 12 | 14 | 39 | 18-0099193 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 36 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-12 14:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-13 | 11:34 | 34.9942 | -118.9924 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100195031 | None | 0 – 750 | Conductor | Overhead | Yes | 43417 | 0.48194 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1972 | 2018 | 11 | 13 | 11 | 34 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-11-13 11:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-13 | 15:41 | 37.0644 | -121.9578 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101680441 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43417 | 0.65347 | Other | N.A. | N.A. | N.A. | Human Error | Grow house | Other/Unknown | 1973 | 2018 | 11 | 13 | 15 | 41 | 18-0099492 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 21484 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-13 15:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-15 | 6:09 | 38.3599 | -122.3682 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102241814 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43419 | 0.25625 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1974 | 2018 | 11 | 15 | 6 | 9 | 18-0099862 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 441 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-15 06:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-15 | 6:34 | 38.6082 | -120.9532 | Vegetation | Rural | < 0.25 Acres | Self Extinguished | N.A. | 101414740 | Unknown | 12000 | Conductor | Overhead | Yes | 43419 | 0.27361 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1975 | 2018 | 11 | 15 | 6 | 34 | 18-0099901 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 5325 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-15 06:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-16 | 17:02 | 38.7574 | -120.9012 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101409894 | AT&T | 21000 | Conductor | Overhead | Yes | 43420 | 0.70972 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1976 | 2018 | 11 | 16 | 17 | 2 | 18-0100490 | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 119860 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-16 17:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-17 | 17:20 | 38.7082 | -120.6927 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101421319 | Unknown | 12000 | Conductor | Overhead | Yes | 43421 | 0.72222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1977 | 2018 | 11 | 17 | 17 | 20 | 18-0100697 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 35749 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-17 17:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-18 | 1:37 | 34.9526 | -120.4364 | Other | Urban | < 3 meters | Unknown | N.A. | 103420365 | N.A. | 12000 | Transformer | Padmounted | Yes | 43422 | 0.067361 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1978 | 2018 | 11 | 18 | 1 | 37 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-11-18 01:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-18 | 14:31 | 40.7968 | -124.1338 | Building | Rural | Structure Only | Fire Agency | Unknown | 100974896 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43422 | 0.60486 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | no-match | 1979 | 2018 | 11 | 18 | 14 | 31 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-11-18 14:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-19 | 9:46 | 38.5053 | -121.6956 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 101577202 | Unknown | 12000 | Conductor | Overhead | Yes | 43423 | 0.40694 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1980 | 2018 | 11 | 19 | 9 | 46 | No ILIS or TOTL available | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-11-19 09:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-20 | 13:07 | 35.3043 | -120.8048 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101928023 | Unknown | 12000 | Conductor | Overhead | Yes | 43424 | 0.54653 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1981 | 2018 | 11 | 20 | 13 | 7 | 18-0101510 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 21149 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-20 13:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-21 | 2:16 | 40.4383 | -124.3847 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101005309 | Frontier | 12000 | Conductor | Overhead | Yes | 43425 | 0.094444 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | Other/Unknown | 1982 | 2018 | 11 | 21 | 2 | 16 | 18-0101683 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 4834 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-21 02:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-11-23 | 22:14 | 38.2666 | -122.0212 | Building | Urban | Structure Only | Unknown | N.A. | 101668121 | AT&T | 12000 | Conductor | Overhead | Yes | 43427 | 0.92639 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1983 | 2018 | 11 | 23 | 22 | 14 | 18-0102707 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 414656 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-23 22:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-12-12 | 12:09 | 38.727 | -120.7947 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 101404403 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43446 | 0.50625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1984 | 2018 | 12 | 12 | 12 | 9 | No ILIS or TOTL available | Zone 1 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-12-12 12:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-12-14 | 10:32 | 40.4379 | -123.7834 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101009136 | Unknown | 12000 | Conductor | Overhead | Yes | 43448 | 0.43889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1985 | 2018 | 12 | 14 | 10 | 32 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2018-12-14 10:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2018-12-31 | 21:43 | 39.738 | -122.0163 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 103801376 | None | 12000 | Conductor | Overhead | Yes | 43465 | 0.90486 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1986 | 2018 | 12 | 31 | 21 | 43 | 18-0111307 | non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 47338 | 0 | NA | <25mph | <15mph | #REF! | 2018-12-31 21:43:00 | #REF! | 0 | FALSE | <25mph
1. Butte | 2015-09-09 | 14:26 | 38.3297 | -120.7042 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1987 | 2015 | 9 | 9 | 14 | 26 |  | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 1353755 | 0 | NA | <25mph | <15mph | #REF! | 2015-09-09 14:26:00 | #REF! | 0 | FALSE | <25mph
2. Cascade (Neu Wind Complex) | 2017-10-08 | 23:45 | 39.322 | -121.4021 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1988 | 2017 | 10 | 8 | 23 | 45 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | Equip Failure | #REF! | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 23:45:00 | #REF! | 0 | FALSE | <25mph
3. Redwood Valley (Mendocino Lake Complex) | 2017-10-08 | 23:36 | 39.2487 | -123.1663 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1989 | 2017 | 10 | 8 | 23 | 36 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 23:36:00 | #REF! | 0 | FALSE | <25mph
4. Nuns (Central LNU Complex) | 2017-10-08 | 22:00 | 38.4041 | -122.5209 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1990 | 2017 | 10 | 8 | 22 | 0 |  | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 22:00:00 | #REF! | 0 | FALSE | <25mph
5. Atlas (Southern LNU Complex) | 2017-10-08 | 21:52 | 38.3921 | -122.2437 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1991 | 2017 | 10 | 8 | 21 | 52 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 21:52:00 | #REF! | 0 | FALSE | <25mph
6. Sulphur (Mendocino Lake Complex) | 2017-10-08 | 23:59 | 39.0139 | -122.6454 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Equipment/ Facility Failure | Pole | N.A. |  |  |  | no-match | 1992 | 2017 | 10 | 8 | 23 | 59 |  | non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | Equip Failure | #REF! | 0 | 0 | NA | <25mph | <15mph | #REF! | 2017-10-08 23:59:00 | #REF! | 0 | FALSE | <25mph
7. Camp Fire | 2018-11-08 | 6:33 | 39.8134 | -121.4347 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 60000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1993 | 2018 | 11 | 8 | 6 | 33 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Greater than 300 Acres | Equip Failure | #REF! | 826291590 | 0 | NA | <25mph | <15mph | #REF! | 2018-11-08 06:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-01-14 | 8:32 | 35.3266 | -118.8432 |  | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Bakersfield FD | 253911104-2100007706{4113} |  | 12000 | Line Recloser | Overhead | Yes | 43479 | 0.35556 | Equipment - PG&E | Line Recloser |  |  |  |  | Other/Unknown | 2019-303 | 2019 | 1 | 14 | 8 | 32 | 19-0008511 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 9256 | 0 | NA | <25mph | <15mph | #REF! | 2019-01-14 08:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-01-16 | 0:17 | 38.0621 | -120.1964 | Vegetation | Conifer Forest | Structure Only | Cal Fire |  | 163661701 |  | 17000 | Conductor | Overhead | Yes | 43481 | 0.011806 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-01 | 2019 | 1 | 16 | 0 | 17 | 19-0010443 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1041827 | 0 | NA | <25mph | <15mph | #REF! | 2019-01-16 00:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-01-23 | 0:26 | 38.6802 | -121.7773 |  | Urban | 1 meter - < 3 meters | Fire Dept | Woodland FD | 220639836908 |  | 12000 | Conductor | Overhead | Yes | 43488 | 0.018056 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-245 | 2019 | 1 | 23 | 0 | 26 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-01-23 00:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-02-01 | 21:40 | 34.8688 | -120.4114 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Unknown | 512768950741{T0541} |  | 12000 | Conductor | Overhead | Yes | 43497 | 0.90278 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match |  | 2019 | 2 | 1 | 21 | 40 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-02-01 21:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-02-11 | 10:55 | 37.2414 | -121.982 | Animal Found | Urban | Structure Only | Fire Dept | Los Gatos FD | 315688127328 |  | 12000 | Conductor | Overhead | Yes | 43507 | 0.45486 | Contact - Animal - Other |  |  |  | Animal Contact |  | no-match | 2019-305 | 2019 | 2 | 11 | 10 | 55 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-02-11 10:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-02-23 | 11:11 | 35.3388 | -119.0283 | Vegetation | Urban | 1 meter - < 3 meters | Fire Dept | Bakersfield FD | 100256235 |  | 12000 | Conductor | Overhead | Yes | 43519 | 0.46597 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match |  | 2019 | 2 | 23 | 11 | 11 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-02-23 11:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-02-26 | 12:49 | 36.1379 | -119.8877 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Kings County FD | 10069349 |  | 12000 | Transformer | Overhead | Yes | 43522 | 0.53403 | Equipment - PG&E | Transformer |  |  |  |  | Other/Unknown | 2019-196 | 2019 | 2 | 26 | 12 | 49 | 19-0028313 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 270 | 0 | NA | <25mph | <15mph | #REF! | 2019-02-26 12:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-03-13 | 16:08 | 39.8831 | -122.5498 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 6Fn0313191607 |  | 12000 | Conductor | Overhead | Yes | 43537 | 0.67222 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-194 | 2019 | 3 | 13 | 16 | 8 | 19-0033617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 21012 | 0 | NA | <25mph | <15mph | #REF! | 2019-03-13 16:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-03-14 | 14:42 | 36.0367 | -120.1116 |  | Herbaceous | 0.25 - 10 Acres | Fire Dept | Kings County FD | 100701237 |  | 21000 | Pole | Overhead | Yes | 43538 | 0.6125 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown |  | 2019 | 3 | 14 | 14 | 42 | 19-0033940 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 107909 | 0 | NA | <25mph | <15mph | #REF! | 2019-03-14 14:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-03-19 | 12:52 | 37.9956 | -120.3244 | Tree - cutting, 3rd party | Hardwood Forest | 1 meter - < 3 meters | Self Extinguished |  | 101045032 |  | 17000 | Conductor | Overhead | Yes | 43543 | 0.53611 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-187 | 2019 | 3 | 19 | 12 | 52 | 19-0035101 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 70602 | 0 | NA | <25mph | <15mph | #REF! | 2019-03-19 12:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-09 | 14:07 | 34.6311 | -119.9813 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Fire Dept | Santa Barbra County FD | 101863014 |  | 12000 | Conductor | Overhead | Yes | 43564 | 0.58819 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-263 | 2019 | 4 | 9 | 14 | 7 | 19-0040969 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 70756 | 0 | NA | <25mph | <15mph | #REF! | 2019-04-09 14:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-09 | 17:00 | 36.8225 | -119.6294 |  | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Fresno FD | 100770778 |  | 12000 | Pole | Overhead | Yes | 43564 | 0.70833 | Weather - High Wind |  |  |  | High Winds |  | Other/Unknown | 2019-264 | 2019 | 4 | 9 | 17 | 0 | 19-0041058 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip failure | Pole | 2880 | 0 | NA | <25mph | <15mph | #REF! | 2019-04-09 17:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-09 | 15:27 | 37.7341 | -120.0776 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 101076921 |  | 21000 | Pole | Overhead | Yes | 43564 | 0.64375 | Vegetation |  | Veg. contact | Pole |  |  | Branch (Not overhanging, > 12ft) | 2019-313 | 2019 | 4 | 9 | 15 | 27 | 19-0041008 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 179862 | 0 | NA | <25mph | <15mph | #REF! | 2019-04-09 15:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-09 | 17:59 | 36.9711 | -120.067 | Vegetation | Urban | 1 meter - < 3 meters | Fire Dept | Madera FD | 254611106 |  | 12000 | Conductor | Overhead | Yes | 43564 | 0.74931 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-201 | 2019 | 4 | 9 | 17 | 59 | 19-0041092 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 65267 | 0 | NA | <25mph | <15mph | #REF! | 2019-04-09 17:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-10 | 22:19 | 36.6131 | -119.6688 |  | Urban | 3 meters - 0.25 Acres | Self Extinguished |  | 254121108 |  | 12000 | Conductor | Overhead | Yes | 43565 | 0.92986 | Weather - High Wind |  |  |  | High Winds |  | no-match | 2019-307 | 2019 | 4 | 10 | 22 | 19 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip failure | Conductor | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-04-10 22:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-10 | 12:43 | 35.5804 | -120.3344 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | Shandon FD | 513053576740 |  | 21000 | Transformer | Overhead | Yes | 43565 | 0.52986 | Contact - Animal - Other |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-317 | 2019 | 4 | 10 | 12 | 43 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-04-10 12:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-12 | 10:45 | 36.6144 | -120.4245 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 253671101 |  | 12000 | Conductor | Overhead | Yes | 43567 | 0.44792 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | no-match | 2019-246 | 2019 | 4 | 12 | 10 | 45 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-04-12 10:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-20 | 6:57 | 37.8686 | -121.6843 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | East County FD | Unknown |  | 17000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-321 | 2019 | 4 | 20 | 6 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-04-20 06:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-23 | 11:08 | 38.0594 | -122.1627 | Bird Found | Urban | 1 meter - < 3 meters | Fire Dept | Benicia FD | 7Ny0423191108 |  | 12000 | Conductor | Overhead | Yes | 43578 | 0.46389 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-304 | 2019 | 4 | 23 | 11 | 8 | 19-0045231 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 35997 | 0 | NA | <25mph | <15mph | #REF! | 2019-04-23 11:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-24 | 18:01 | 35.7759 | -119.9153 | Bird Found | Herbaceous | 10 - 100 Acres | Unknown |  | Unknown |  | 70000 | Conductor | Overhead | Yes | 43579 | 0.75069 | Contact - Animal - Other |  | Animal contact |  | Animal Contact |  | no-match | 2019-26 | 2019 | 4 | 24 | 18 | 1 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-04-24 18:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-24 | 11:59 | 38.0776 | -122.548 |  | Herbaceous | 1 meter - < 3 meters | Fire Dept | Novato FD | Jumper @ 5003 |  | 12000 | Conductor | Overhead | Yes | 43579 | 0.49931 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown |  | 2019 | 4 | 24 | 11 | 59 | 19-0045653 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 331737 | 0 | NA | <25mph | <15mph | #REF! | 2019-04-24 11:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-25 | 12:18 | 37.2746 | -121.9449 |  | Urban | 1 meter - < 3 meters | Fire Dept | Santa Clara County FD | K1048 |  | 12000 | Capacitor Bank | Overhead | No |  |  | Equipment - PG&E | Capacitor Bank |  |  |  |  | no-match | 2019-108 | 2019 | 4 | 25 | 12 | 18 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-04-25 12:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-25 | 12:40 | 35.4398 | -119.0759 | Vehicle | Urban | 3 meters - 0.25 Acres | Fire Dept | Kern County FD | 103230987 |  | 12000 | Conductor | Overhead | Yes | 43580 | 0.52778 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-193 | 2019 | 4 | 25 | 12 | 40 | 19-0046102 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 20356 | 0 | NA | <25mph | <15mph | #REF! | 2019-04-25 12:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-26 | 3:26 | 36.4354 | -119.6747 | Bird Found | Agriculture | 1 meter - < 3 meters | Fire Dept | Laton FD | 4Tt0426190326 |  | 12000 | Conductor | Overhead | Yes | 43581 | 0.14306 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-195 | 2019 | 4 | 26 | 3 | 26 | 19-0046324 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 44092 | 0 | NA | <25mph | <15mph | #REF! | 2019-04-26 03:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-26 | 16:53 | 36.8145 | -119.8119 | Vegetation | Urban | Structure Only | Fire Dept | Fresno FD | 100829139 |  | 21000 | Other | Overhead | Yes | 43581 | 0.70347 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, > 12ft) | 2019-199 | 2019 | 4 | 26 | 16 | 53 | 19-0046618 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 8028 | 0 | NA | <25mph | <15mph | #REF! | 2019-04-26 16:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-28 | 12:36 | 39.6756 | -121.5677 |  | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 100404366 |  | 12000 | Conductor | Overhead | Yes | 43583 | 0.525 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-166 | 2019 | 4 | 28 | 12 | 36 | 19-0046853 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 79810 | 0 | NA | <25mph | <15mph | #REF! | 2019-04-28 12:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-29 | 8:53 | 36.7841 | -119.5856 | Animal Found | Agriculture | Structure Only | Cal Fire |  | 418295052848 |  | 12000 | Conductor | Overhead | Yes | 43584 | 0.37014 | Contact - Animal - Other |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-320 | 2019 | 4 | 29 | 8 | 53 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-04-29 08:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-04-29 | 18:07 | 38.6587 | -121.7265 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire | Woodland FD | 103691007 |  | 12000 | Conductor | Overhead | Yes | 43584 | 0.75486 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-174 | 2019 | 4 | 29 | 18 | 7 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-04-29 18:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-01 | 17:51 | 37.3928 | -121.8242 |  | Urban | 1 meter - < 3 meters | Fire Dept | San Jose FD | 103900972 |  | 12000 | Conductor | Overhead | Yes | 43586 | 0.74375 | Contact - 3rd Party |  | Other | Electric Facility | Human Error |  | no-match | 2019-23 | 2019 | 5 | 1 | 17 | 51 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-01 17:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-03 | 13:47 | 37.0553 | -120.3362 | Vehicle | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 103794549 |  | 12000 | Guy/Span Wire | Overhead | Yes | 43588 | 0.57431 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-191 | 2019 | 5 | 3 | 13 | 47 | 19-0048693 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 21896 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-03 13:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-03 | 15:45 | 39.4943 | -121.6887 | Vehicle | Urban | 3 meters - 0.25 Acres | Fire Dept | Richvale FD | 100360352 |  | 12000 | Pole | Overhead | Yes | 43588 | 0.65625 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-185 | 2019 | 5 | 3 | 15 | 45 | 19-0048754 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 23826 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-03 15:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-03 | 19:11 | 36.5001 | -119.5393 |  | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Tulare County FD | 100894245 |  | 12000 | Other | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-308 | 2019 | 5 | 3 | 19 | 11 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-03 19:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-03 | 21:28 | 36.7505 | -119.6998 | Vehicle | Urban | 3 meters - 0.25 Acres | Fire Dept | Fresno FD | 103270078 |  | 12000 | Pole | Overhead | Yes | 43588 | 0.89444 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown |  | 2019 | 5 | 3 | 21 | 28 | 19-0048792 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 67287 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-03 21:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-04 | 17:48 | 36.0472 | -120.9188 | Bird Found | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | Tower 4/35 |  | 115000 | Pole | Overhead | Yes | 43589 | 0.74167 | Contact - Animal - Other |  | Animal contact | Pole | Animal Contact |  | no-match | 2019-315 | 2019 | 5 | 4 | 17 | 48 | N/A | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-04 17:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-04 | 23:19 | 39.9592 | -121.9397 | Gun Shot | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 3302 |  | 12000 | Recloser | Overhead | Yes | 43589 | 0.97153 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown |  | 2019 | 5 | 4 | 23 | 19 | 19-0048958 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 82572 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-04 23:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-05 | 6:40 | 35.6737 | -120.0873 | Vehicle | Urban | 10 - 100 Acres | Fire Dept | Kern County FD | 252021101 |  | 12000 | Conductor | Overhead | Yes | 43590 | 0.27778 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown |  | 2019 | 5 | 5 | 6 | 40 | 19-0048987 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 2740 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-05 06:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-07 | 21:33 | 36.458 | -119.3493 |  | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Tulare County FD | 7927F |  | 12000 | Fuse | Overhead | Yes | 43592 | 0.89792 | Equipment - PG&E | Fuse |  |  |  |  | Other/Unknown |  | 2019 | 5 | 7 | 21 | 33 | 19-0049826 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 6882 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-07 21:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-08 | 10:23 | 39.3851 | -122.557 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | Colusa FD | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-312 | 2019 | 5 | 8 | 10 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-08 10:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-10 | 13:00 | 39.2755 | -121.6876 | Gun Shot | Urban | 0.25 - 10 Acres | Fire Dept | Sutter County FD | 153771104 |  | 12000 | Conductor | Overhead | Yes | 43595 | 0.54167 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-427 | 2019 | 5 | 10 | 13 | 0 | 19-0050820 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 3784 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-10 13:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-10 | 14:52 | 40.704 | -122.8314 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Fire Dept | Lewiston FD | Keswick-Trinity 60Kv Line |  | 60000 | Conductor | Overhead | Yes | 43595 | 0.61944 | Vegetation |  | Contact from Object - Other | Electric Facility |  |  | no-match | 2019-301 | 2019 | 5 | 10 | 14 | 52 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-10 14:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-14 | 8:56 | 38.7989 | -121.3782 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | California Department of Forestry | 152442110 |  | 21000 | Conductor | Overhead | Yes | 43599 | 0.37222 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown |  | 2019 | 5 | 14 | 8 | 56 | 19-0051674 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1049 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-14 08:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-14 | 11:55 | 38.2371 | -122.0433 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Suisun FD | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match |  | 2019 | 5 | 14 | 11 | 55 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-14 11:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-14 | 16:17 | 36.6477 | -119.8006 | Vehicle | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Fresno County FD | 417651147966 |  | 12000 | Pole | Overhead | Yes | 43599 | 0.67847 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-188 | 2019 | 5 | 14 | 16 | 17 | 19-0051881 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 2828 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-14 16:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-14 | 7:17 | 39.5037 | -121.5593 |  | Urban | 3 meters - 0.25 Acres | Unknown |  | 22/450 |  | 60000 | Pole | Overhead | Yes | 43599 | 0.30347 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-192 | 2019 | 5 | 14 | 7 | 17 | 19-0051586 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 136640 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-14 07:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-14 | 18:11 | 38.435 | -121.9517 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Vacaville FD | 103951176 |  | 12000 | Pole | Overhead | Yes | 43599 | 0.75764 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | no-match | 2019-188 | 2019 | 5 | 14 | 18 | 11 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-14 18:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-14 | 21:03 | 39.0553 | -121.3224 | Vehicle | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Wheatland FD | 103944282 |  | 12000 | Pole | Overhead | Yes | 43599 | 0.87708 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown |  | 2019 | 5 | 14 | 21 | 3 | 19-0051893 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 41776 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-14 21:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-15 | 16:22 | 37.1531 | -120.2777 | Vehicle | Agriculture | 1 meter - < 3 meters | Cal Fire |  | 254101103 |  | 12000 | Conductor | Overhead | Yes | 43600 | 0.68194 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-319 | 2019 | 5 | 15 | 16 | 22 | 19-0052273 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 1040 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-15 16:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-15 | 21:31 | 38.5731 | -122.9603 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Unknown |  | 103931177 |  | 12000 | Conductor | Overhead | Yes | 43600 | 0.89653 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-316 | 2019 | 5 | 15 | 21 | 31 | 19-0052480 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 27780 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-15 21:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-17 | 15:12 | 38.4797 | -123.1486 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 42811111 |  | 12000 | Conductor | Overhead | Yes | 43602 | 0.63333 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-200 | 2019 | 5 | 17 | 15 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-17 15:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-17 | 18:54 | 38.0476 | -122.2064 | Bird Found | Urban | 3 meters - 0.25 Acres | Fire Dept | Crockett FD | 2Jt0517191854 |  | 21000 | Pole | Overhead | Yes | 43602 | 0.7875 | Contact - Animal - Bird |  | Animal contact | Pole | Animal Contact |  | Other/Unknown | 2019-02 | 2019 | 5 | 17 | 18 | 54 | 19-0053464 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-17 18:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-21 | 15:50 | 34.8658 | -120.4214 | Vegetation | Urban | 1 meter - < 3 meters | Fire Dept | Santa Barbara FD | 182571102 |  | 12000 | Conductor | Overhead | Yes | 43606 | 0.65972 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-311 | 2019 | 5 | 21 | 15 | 50 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-21 15:50:00 | #REF! | 0 | TRUE | <25mph
PG&E | 2019-05-21 | 15:50 | 38.0132 | -121.8541 |  | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 15553 |  | 21000 | Fuse | Overhead | Yes | 43606 | 0.65972 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-311 | 2019 | 5 | 21 | 15 | 50 | 19-0055013 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 1350 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-21 15:50:00 | #REF! | 0 | TRUE | <25mph
PG&E | 2019-05-24 | 11:52 | 38.1121 | -122.6214 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Novato FD | 043201101 |  | 12000 | Conductor | Overhead | Yes | 43609 | 0.49444 | Contact - Customer (Equip/Structure/Veg) |  | Veg. contact | Electric Facility |  |  | no-match | 2019-306 | 2019 | 5 | 24 | 11 | 52 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-24 11:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-24 | 19:14 | 37.0779 | -120.881 | Bird Found | Water | 1 meter - < 3 meters | Cal Fire | Los Banos FD | 3015781291 |  | 12000 | Transformer | Overhead | Yes | 43609 | 0.80139 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-310 | 2019 | 5 | 24 | 19 | 14 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-24 19:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-24 | 15:03 | 35.1696 | -120.5103 |  | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 40589503 |  | 500000 | Pole | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-100 | 2019 | 5 | 24 | 15 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-24 15:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-25 | 18:29 | 37.0116 | -120.1288 | Vehicle | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 254611104 |  | 12000 | Conductor | Overhead | Yes | 43610 | 0.77014 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-198 | 2019 | 5 | 25 | 18 | 29 | 19-0057638 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 15054 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-25 18:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-25 | 20:51 | 38.7799 | -121.5175 |  | Agriculture | 0.25 - 10 Acres | Fire Dept | Pleasant Grove FD | 153761102 |  | 12000 | Conductor | Overhead | Yes | 43610 | 0.86875 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-197 | 2019 | 5 | 25 | 20 | 51 | 19-0057650 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 35108 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-25 20:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-27 | 18:04 | 36.2495 | -120.3016 |  | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 702250 |  | 12000 | Recloser | Overhead | No |  |  | Equipment - PG&E | Recloser |  |  |  |  | no-match | 2019-165 | 2019 | 5 | 27 | 18 | 4 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-27 18:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-28 | 12:57 | 37.39 | -122.01 |  | Urban | 0.25 - 10 Acres | Fire Dept | Mountain View FD | 1110/2 |  | 12000 | Circuit Breaker | Overhead | Yes | 43613 | 0.53958 | Weather - High Wind |  |  |  | High Winds |  | Other/Unknown | 2019-419 | 2019 | 5 | 28 | 12 | 57 | 19-0058574 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip failure | Equip Failure - Other | 14888 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-28 12:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-29 | 13:03 | 40.1387 | -122.2088 |  | Herbaceous | 1 meter - < 3 meters | Self Extinguished |  | 10357{Tyler} |  | 60000 | Transformer | Pad mount | Yes | 43614 | 0.54375 | Equipment - PG&E | Transformer |  |  |  |  | no-match |  | 2019 | 5 | 29 | 13 | 3 | 19-0059088 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-29 13:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-29 | 16:54 | 37.0371 | -119.5209 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 100680674 |  | 12000 | Pole | Overhead | Yes | 43614 | 0.70417 | Vegetation |  | Veg. contact | Pole |  |  | Dead | 2019-202 | 2019 | 5 | 29 | 16 | 54 | 19-0059237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 6780 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-29 16:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-29 | 19:13 | 36.5602 | -119.286 | Bird Found | Agriculture | 0.25 - 10 Acres | Fire Dept | Tulare County FD | 4Tj0529191913 |  | 12000 | Transformer | Overhead | No |  |  | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-454 | 2019 | 5 | 29 | 19 | 13 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-29 19:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-29 | 20:25 | 39.0194 | -121.0608 |  | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match |  | 2019 | 5 | 29 | 20 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-29 20:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-30 | 7:27 | 37.3545 | -121.8703 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | San Jose FD | K215 |  | 12000 | Other | Overhead | Yes | 43615 | 0.31042 | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-420 | 2019 | 5 | 30 | 7 | 27 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-05-30 07:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-30 | 8:18 | 35.7005 | -120.8104 | Vehicle | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 101871463 |  | 12000 | Pole | Overhead | Yes | 43615 | 0.34583 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-274 | 2019 | 5 | 30 | 8 | 18 | 19-0059906 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 171603 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-30 08:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-30 | 15:21 | 36.8953 | -119.9627 | Vehicle | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 101222476 |  | 12000 | Pole | Overhead | Yes | 43615 | 0.63958 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-203 | 2019 | 5 | 30 | 15 | 21 | 19-0060214 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 2213 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-30 15:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-30 | 22:25 | 35.538 | -119.8056 |  | Herbaceous | 10 - 100 Acres | Fire Dept | Kern County FD | 100127383 |  | 12000 | Other | Overhead | Yes | 43615 | 0.93403 | Equipment - PG&E | Other |  |  |  |  | Other/Unknown | 2019-204 | 2019 | 5 | 30 | 22 | 25 | 19-0060556 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 574 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-30 22:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-31 | 13:34 | 34.9856 | -118.9088 |  | Agriculture | 3 meters - 0.25 Acres | Unknown |  | 100337543 |  | 12000 | Fuse | Overhead | Yes | 43616 | 0.56528 | Equipment - PG&E | Fuse |  |  |  |  | Other/Unknown | 2019-220 | 2019 | 5 | 31 | 13 | 34 | 19-0060863 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 157 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-31 13:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-05-31 | 15:25 | 40.4431 | -121.8211 |  | Hardwood Woodland | 1 meter - < 3 meters | Self Extinguished |  | 101556319 |  | 12000 | Conductor | Overhead | Yes | 43616 | 0.64236 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-88 | 2019 | 5 | 31 | 15 | 25 | 19-0060901 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 55546 | 0 | NA | <25mph | <15mph | #REF! | 2019-05-31 15:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-01 | 6:38 | 38.07 | -122.1284 | Vehicle | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Benicia FD | 103848169 |  | 12000 | Pole | Overhead | Yes | 43617 | 0.27639 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-109 | 2019 | 6 | 1 | 6 | 38 | 19-0061080 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 93996 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-01 06:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-01 | 14:32 | 36.9871 | -120.6229 | Vegetation | Water | 1 meter - < 3 meters | Cal Fire |  | 254041101 |  | 12000 | Other | Overhead | Yes | 43617 | 0.60556 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-121 | 2019 | 6 | 1 | 14 | 32 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-01 14:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-03 | 6:57 | 35.5878 | -119.0104 | Bird Found | Herbaceous | 1 meter - < 3 meters | Fire Dept | Kern County FD | Sw1694 |  | 21000 | Switch | Overhead | No |  |  | Contact - Animal - Other |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-65 | 2019 | 6 | 3 | 6 | 57 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-03 06:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-03 | 14:31 | 40.6822 | -122.2806 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 101466598 |  | 12000 | Transformer | Overhead | Yes | 43619 | 0.60486 | Equipment - Overloaded | Transformer |  |  |  |  | no-match | 2019-161 | 2019 | 6 | 3 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-03 14:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-03 | 14:47 | 40.4419 | -122.3036 |  | Herbaceous | 1 meter - < 3 meters | Fire Dept | Anderson FD | 101495889 |  | 12000 | Insulator | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-456 | 2019 | 6 | 3 | 14 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-03 14:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-03 | 18:11 | 36.5579 | -119.633 |  | Agriculture | 10 - 100 Acres | Cal Fire |  | 252241116 |  | 12000 | Conductor | Overhead | Yes | 43619 | 0.75764 | Equipment - PG&E | [5 empty] | no-match | 2019-08 | 2019 | 6 | 3 | 18 | 11 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-03 18:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-04 | 13:00 | 36.5543 | -119.8822 | Bird Found | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 4Tt0604191259 |  | 12000 | Fuse | Overhead | Yes | 43620 | 0.54167 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-131 | 2019 | 6 | 4 | 13 | 0 | 19-0062634 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 912 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-04 13:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-05 | 21:01 | 38.558 | -121.7545 |  | Urban | Structure Only | Fire Dept | Unknown | 06204-2100957897{1105/2} |  | 12000 | Circuit Breaker | Overhead | Yes | 43621 | 0.87569 | Equipment - PG&E | Circuit Breaker |  |  |  |  | Other/Unknown |  | 2019 | 6 | 5 | 21 | 1 | 19-0063395 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 122307 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-05 21:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-06 | 9:01 | 35.6384 | -118.9687 | Bird Found | Herbaceous | 0.25 - 10 Acres | Fire Dept | Kern County FD | 100216096 |  | 21000 | Conductor | Overhead | No |  |  | Contact - Animal - Other |  | Animal contact |  | Animal Contact |  | no-match | 2019-228 | 2019 | 6 | 6 | 9 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-06 09:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-06 | 20:30 | 38.4969 | -122.6435 |  | Barren/Other | < 1 meter | Self Extinguished |  | Unknown |  | 230000 | Circuit Breaker | Overhead | Yes | 43622 | 0.85417 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | no-match | 2019-102 | 2019 | 6 | 6 | 20 | 30 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-06 20:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-07 | 9:58 | 38.7285 | -123.3528 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 042861101 |  | 21000 | Conductor | Overhead | Yes | 43623 | 0.41528 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-358 | 2019 | 6 | 7 | 9 | 58 | 19-0064216 | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 5301 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-07 09:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-07 | 11:59 | 36.8295 | -119.9134 |  | Agriculture | 0.25 - 10 Acres | Fire Dept | Fresno FD | 417384054240 |  | 21000 | Transformer | Overhead | Yes | 43623 | 0.49931 | Equipment - PG&E | Transformer |  |  |  |  | Other/Unknown | 2019-76 | 2019 | 6 | 7 | 11 | 59 | 19-0064229 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 368 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-07 11:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-07 | 12:44 | 39.0672 | -121.8693 |  | Hardwood Woodland | 1 meter - < 3 meters | Self Extinguished |  | 4391 |  | 12000 | Switch | Overhead | Yes | 43623 | 0.53056 | Equipment - PG&E | Switch |  |  |  |  | Other/Unknown | 2019-212 | 2019 | 6 | 7 | 12 | 44 | 19-0064311 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1400 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-07 12:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-07 | 16:44 | 37.3335 | -120.5424 | Vegetation | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 253881104 |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-354 | 2019 | 6 | 7 | 16 | 44 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-07 16:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-08 | 9:21 | 39.0926 | -121.5482 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Olivehurst FD | 152901104 |  | 12000 | Conductor | Overhead | Yes | 43624 | 0.38958 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-333 | 2019 | 6 | 8 | 9 | 21 | No ILIS or TOTL available | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-08 09:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-08 | 10:13 | 37.3731 | -121.9192 | Metallic Balloon | Urban | 3 meters - 0.25 Acres | Fire Dept | Unknown | 100566596 |  | 12000 | Pole | Overhead | Yes | 43624 | 0.42569 | Contact - 3rd Party |  | Balloon contact | Pole | Human Error |  | Other/Unknown | 2019-32 | 2019 | 6 | 8 | 10 | 13 | 19-0064568 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 2340 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-08 10:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-08 | 14:31 | 34.8934 | -120.3152 | Metallic Balloon | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 182811103 |  | 12000 | Conductor | Overhead | Yes | 43624 | 0.60486 | Contact - 3rd Party |  | Balloon contact | Electric Facility | Human Error |  | no-match | 2019-33 | 2019 | 6 | 8 | 14 | 31 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-08 14:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-08 | 18:51 | 38.6105 | -122.9732 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 42751113 |  | 12000 | Conductor | Overhead | Yes | 43624 | 0.78542 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-355 | 2019 | 6 | 8 | 18 | 51 | 19-0064689 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 44664 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-08 18:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-08 | 23:26 | 37.3607 | -122.1708 | Vegetation | Urban | 1 meter - < 3 meters | Fire Dept | Santa Clara County FD | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match |  | 2019 | 6 | 8 | 23 | 26 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-08 23:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-09 | 3:07 | 36.1428 | -120.754 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 3Bj0609190229 |  | 12000 | Conductor | Overhead | Yes | 43625 | 0.12986 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-258 | 2019 | 6 | 9 | 3 | 7 | 19-0064780 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 34875 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-09 03:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-09 | 12:46 | 38.2966 | -122.4747 | Vegetation | Urban | 1 meter - < 3 meters | Fire Dept | Sonoma FD | Unknown |  | 12000 | Other | Subsurface | Yes | 43625 | 0.53194 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-457 | 2019 | 6 | 9 | 12 | 46 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-09 12:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-09 | 13:53 | 36.9235 | -121.7461 | Metallic Balloon | Urban | 3 meters - 0.25 Acres | Fire Dept | Watsonville FD | 83192104 |  | 21000 | Conductor | Overhead | Yes | 43625 | 0.57847 | Contact - 3rd Party |  | Balloon contact | Electric Facility | Human Error |  | Other/Unknown | 2019-34 | 2019 | 6 | 9 | 13 | 53 | 19-0064855 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 252750 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-09 13:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-09 | 15:23 | 37.8943 | -122.5581 |  | Barren/Other | 3 meters - 0.25 Acres | Fire Dept | Mill Valley FD | 902 |  | 12000 | Recloser | Overhead | Yes | 43625 | 0.64097 | Equipment - PG&E | Recloser |  |  |  |  | Other/Unknown | 2019-256 | 2019 | 6 | 9 | 15 | 23 | 19-0064860 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 377029 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-09 15:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-09 | 15:34 | 34.8995 | -120.4382 |  | Urban | 1 meter - < 3 meters | Fire Dept | Unknown | 45711 |  | 12000 | Lightning Arrestor | Overhead | Yes | 43625 | 0.64861 | Equipment - PG&E | Lightning Arrestor |  |  |  |  | Other/Unknown | 2019-72 | 2019 | 6 | 9 | 15 | 34 | 19-0064866 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 6107 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-09 15:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-09 | 18:07 | 39.5067 | -121.5985 | Bird Found | Urban | 1 meter - < 3 meters | Fire Dept | Oroville FD | 6Fq0609191756 |  | 12000 | Transformer | Overhead | Yes | 43625 | 0.75486 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-53 | 2019 | 6 | 9 | 18 | 7 | 19-0064901 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 44200 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-09 18:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-09 | 20:22 | 37.9631 | -121.9913 |  | Urban | 1 meter - < 3 meters | Fire Dept | Contra Costa FD | Circuit 012022217 |  | 21000 | Transformer | Subsurface | Yes | 43625 | 0.84861 | Equipment - PG&E | Transformer |  |  |  |  | Other/Unknown | 2019-81 | 2019 | 6 | 9 | 20 | 22 | 19-0064918 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 165109 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-09 20:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-10 | 11:44 | 37.2735 | -120.6334 | Vehicle | Herbaceous | 3 meters - 0.25 Acres | Unknown |  | 253611102 |  | 12000 | Conductor | Overhead | Yes | 43626 | 0.48889 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-326 | 2019 | 6 | 10 | 11 | 44 | 19-0065293 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 11812 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-10 11:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-10 | 13:28 | 37.2698 | -121.881 |  | Urban | 1 meter - < 3 meters | Fire Dept | San Jose FD | 315977228341 |  | 12000 | Transformer | Overhead | Yes | 43626 | 0.56111 | Equipment - PG&E | Transformer |  |  |  |  | no-match | 2019-24 | 2019 | 6 | 10 | 13 | 28 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-10 13:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-10 | 13:29 | 38.8137 | -120.9433 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Other | Customer | 153652109 |  | 21000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-243 | 2019 | 6 | 10 | 13 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-10 13:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-10 | 15:53 | 37.4929 | -121.9086 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Fresno FD | Circuit Id 014722109 |  | 21000 | Splice/Clamp/Connector | Subsurface | Yes | 43626 | 0.66181 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | no-match | 2019-157 | 2019 | 6 | 10 | 15 | 53 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-10 15:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-10 | 16:05 | 37.2595 | -121.9123 |  | Urban | 1 meter - < 3 meters | Fire Dept | San Jose FD | 315893027963 |  | 12000 | Transformer | Overhead | Yes | 43626 | 0.67014 | Equipment - PG&E | Transformer |  |  |  |  | no-match | 2019-98 | 2019 | 6 | 10 | 16 | 5 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-10 16:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-10 | 16:18 | 38.1107 | -122.9025 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 42291101 |  | 12000 | Conductor | Overhead | Yes | 43626 | 0.67917 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-401 | 2019 | 6 | 10 | 16 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-10 16:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-10 | 16:34 | 38.821 | -120.846 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Garden Valley FD | 153082106 |  | 21000 | Conductor | Overhead | Yes | 43626 | 0.69028 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-372 | 2019 | 6 | 10 | 16 | 34 | 19-0065481 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14169 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-10 16:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-10 | 18:52 | 36.7428 | -120.0958 | Bird Found | Agriculture | 1 meter - < 3 meters | Self Extinguished |  | 4Tk0610191850 |  | 12000 | Lightning Arrestor | Overhead | Yes | 43626 | 0.78611 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-38 | 2019 | 6 | 10 | 18 | 52 | 19-0065545 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 2773 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-10 18:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-11 | 3:40 | 37.937 | -122.3386 |  | Urban | 1 meter - < 3 meters | Fire Dept | Richmond FD | 13020402 | Yes | 4000 | Conductor | Overhead | Yes | 43627 | 0.15278 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-458 | 2019 | 6 | 11 | 3 | 40 | 19-0065825 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 8360 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-11 03:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-11 | 8:49 | 36.9708 | -121.9919 | Vegetation | Urban | 1 meter - < 3 meters | Fire Dept | Santa Cruz FD | 83252107 |  | 21000 | Conductor | Overhead | Yes | 43627 | 0.36736 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-330 | 2019 | 6 | 11 | 8 | 49 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-11 08:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-11 | 12:41 | 37.3735 | -121.8159 | Vegetation | Urban | 0.25 - 10 Acres | Fire Dept | San Jose FD | 83531107 |  | 12000 | Conductor | Overhead | Yes | 43627 | 0.52847 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-251 | 2019 | 6 | 11 | 12 | 41 | 19-0065998 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 9336 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-11 12:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-11 | 15:41 | 37.6689 | -122.4493 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Colma FD | 314364543100 |  | 12000 | Transformer | Overhead | Yes | 43627 | 0.65347 | Equipment - PG&E | Transformer |  |  |  |  | no-match | 2019-276 | 2019 | 6 | 11 | 15 | 41 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-11 15:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-11 | 16:31 | 36.776 | -119.7502 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Fresno FD | D9876 |  | 12000 | Fuse | Overhead | Yes | 43627 | 0.68819 | Equipment - PG&E | Fuse |  |  |  |  | Other/Unknown | 2019-267 | 2019 | 6 | 11 | 16 | 31 | 19-0066149 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 13964 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-11 16:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-11 | 17:16 | 36.7917 | -119.5176 |  | Agriculture | 1 meter - < 3 meters | Cal Fire | California Department of Forestry | 418483253125 |  | 12000 | Transformer | Overhead | Yes | 43627 | 0.71944 | Equipment - PG&E | Transformer |  |  |  |  | Other/Unknown | 2019-73 | 2019 | 6 | 11 | 17 | 16 | 19-0066424 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 551 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-11 17:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-12 | 7:55 | 38.5052 | -121.9997 |  | Agriculture | 1 meter - < 3 meters | Self Extinguished |  | 220003830547 |  | 12000 | Transformer | Overhead | Yes | 43628 | 0.32986 | Contact - Customer (Equip/Structure/Veg) |  | Contact from Object - Other | Electric Facility |  |  | no-match | 2019-137 | 2019 | 6 | 12 | 7 | 55 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-12 07:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-12 | 6:12 | 38.1463 | -122.1684 | Metallic Balloon | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 115000 | Other | Overhead | Yes | 43628 | 0.25833 | Contact - 3rd Party |  | Balloon contact | Electric Facility | Human Error |  | no-match | 2019-322 | 2019 | 6 | 12 | 6 | 12 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-12 06:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-12 | 13:16 | 37.9914 | -121.3119 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | San Francisco FD | 317662554392 |  | 12000 | Transformer | Overhead | Yes | 43628 | 0.55278 | Equipment - PG&E | Transformer |  |  |  |  | Other/Unknown | 2019-74 | 2019 | 6 | 12 | 13 | 16 | 19-0066727 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 18873 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-12 13:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-13 | 0:30 | 36.5759 | -121.7284 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire |  | 182222104 |  | 21000 | Conductor | Overhead | Yes | 43629 | 0.020833 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-341 | 2019 | 6 | 13 | 0 | 30 | 19-0067072 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 148986 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-13 00:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-14 | 4:38 | 37.5525 | -120.3254 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 011/008 |  | 70000 | Insulator | Overhead | No |  |  | Equipment - PG&E | Insulator |  |  |  |  | no-match | 2019-79 | 2019 | 6 | 14 | 4 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-14 04:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-14 | 14:34 | 37.9844 | -122.5143 | Vegetation | Urban | 1 meter - < 3 meters | Fire Dept | San Rafael FD | 42011109 |  | 12000 | Conductor | Overhead | Yes | 43630 | 0.60694 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-83 | 2019 | 6 | 14 | 14 | 34 | 19-0067841 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 33000 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-14 14:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-15 | 14:08 | 38.8802 | -122.6125 | Tree - cutting, 3rd party | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 43361103 |  | 12000 | Pole | Overhead | Yes | 43631 | 0.58889 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | Other/Unknown | 2019-19 | 2019 | 6 | 15 | 14 | 8 | 19-0068074 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 259562 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-15 14:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-16 | 11:28 | 35.4171 | -118.9139 | Metallic Balloon | Herbaceous | 0.25 - 10 Acres | Fire Dept | Bakersfield FD | 13859 |  | 12000 | Other | Overhead | Yes | 43632 | 0.47778 | Contact - 3rd Party |  | Balloon contact | Electric Facility | Human Error |  | Other/Unknown | 2019-29 | 2019 | 6 | 16 | 11 | 28 | 19-0068224 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 808 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-16 11:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-17 | 10:25 | 38.511 | -122.2134 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 43051101 |  | 12000 | Conductor | Overhead | Yes | 43633 | 0.43403 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-84 | 2019 | 6 | 17 | 10 | 25 | 19-0068579 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 306900 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-17 10:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-17 | 16:37 | 38.6676 | -121.8032 |  | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Woodland FD | 12789 |  | 12000 | Insulator | Overhead | Yes | 43633 | 0.69236 | Equipment - PG&E | Insulator |  |  |  |  | Other/Unknown | 2019-178 | 2019 | 6 | 17 | 16 | 37 | 19-0068770 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1764 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-17 16:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-17 | 18:07 | 38.2778 | -122.4384 | Vegetation | Herbaceous | 1 meter - < 3 meters | Fire Dept | Unknown | 42721105 |  | 12000 | Conductor | Overhead | Yes | 43633 | 0.75486 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-406 | 2019 | 6 | 17 | 18 | 7 | 19-0068776 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 118211 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-17 18:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-17 | 18:19 | 38.0984 | -122.8786 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Fire Dept | Marin County FD | 42291101 |  | 12000 | Conductor | Overhead | Yes | 43633 | 0.76319 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-85 | 2019 | 6 | 17 | 18 | 19 | 19-0068786 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3472 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-17 18:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-17 | 23:31 | 36.7084 | -119.7636 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Fresno County FD | 1004291789 |  | 12000 | Secondary | Overhead | Yes | 43633 | 0.97986 | Equipment - PG&E | [5 empty] | no-match | 2019-163 | 2019 | 6 | 17 | 23 | 31 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-17 23:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-17 | 20:58 | 35.404 | -118.895 |  | Urban | 1 meter - < 3 meters | Other | Customer | Unknown |  | 12000 | Other | Subsurface | No |  |  | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-265 | 2019 | 6 | 17 | 20 | 58 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-17 20:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-18 | 8:26 | 36.9812 | -119.8799 |  | Urban | 3 meters - 0.25 Acres | Cal Fire | Madera County FD | 321813417576 |  | 12000 | Transformer | Overhead | Yes | 43634 | 0.35139 | Equipment - PG&E | Transformer |  |  |  |  | Other/Unknown | 2019-75 | 2019 | 6 | 18 | 8 | 26 | 19-0069041 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 200 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-18 08:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-18 | 19:38 | 39.6816 | -122.2716 |  | Agriculture | 1 meter - < 3 meters | Fire Dept | Artois FD | 100367422 |  | 21000 | Crossarm | Overhead | Yes | 43634 | 0.81806 | Equipment - PG&E | Crossarm |  |  |  |  | Other/Unknown | 2019-89 | 2019 | 6 | 18 | 19 | 38 | 19-0069403 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 10987 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-18 19:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-18 | 19:49 | 35.8876 | -120.9217 | Bird Found | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Pole | Overhead | Yes | 43634 | 0.82569 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | no-match | 2019-55 | 2019 | 6 | 18 | 19 | 49 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-18 19:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-18 | 13:05 | 35.0232 | -119.0957 |  | Herbaceous | 1 meter - < 3 meters | Self Extinguished |  | 253411106 |  | 12000 | Other | Overhead | No |  |  | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-230 | 2019 | 6 | 18 | 13 | 5 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-18 13:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-19 | 9:02 | 37.7927 | -121.287 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Lathrop FD | 102100188 |  | 17000 | Conductor | Overhead | Yes | 43635 | 0.37639 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-90 | 2019 | 6 | 19 | 9 | 2 | 19-0069581 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 107730 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-19 09:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-19 | 11:44 | 39.8612 | -121.6907 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100400933 |  | 12000 | Conductor | Overhead | Yes | 43635 | 0.48889 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-224 | 2019 | 6 | 19 | 11 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-19 11:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-19 | 12:15 | 39.407 | -122.2294 | Bird Found | Urban | 1 meter - < 3 meters | Fire Dept | Willows FD | 69G0619191201 |  | 21000 | Conductor | Overhead | Yes | 43635 | 0.51042 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-52 | 2019 | 6 | 19 | 12 | 15 | 19-0069679 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 35698 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-19 12:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-19 | 8:31 | 35.3834 | -119.6965 |  | Herbaceous | 3 meters - 0.25 Acres | Other | Third Party Field Worker | Unknown |  | 115000 | Jumper | Overhead | Yes | 43635 | 0.35486 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | no-match | 2019-103 | 2019 | 6 | 19 | 8 | 31 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-19 08:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-20 | 5:58 | 38.3158 | -121.8931 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | Unknown |  | 21000 | Other | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-418 | 2019 | 6 | 20 | 5 | 58 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-20 05:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-20 | 16:32 | 36.8514 | -120.0549 | Bird Found | Agriculture | 1 meter - < 3 meters | Self Extinguished |  | 5Tn0620191624 |  | 12000 | Transformer | Overhead | Yes | 43636 | 0.68889 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-58 | 2019 | 6 | 20 | 16 | 32 | 19-0070343 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 364 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-20 16:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-21 | 2:37 | 38.9026 | -121.0682 | Vegetation | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 103957753 |  | 21000 | Pole | Overhead | Yes | 43637 | 0.10903 | Vegetation |  | Veg. contact | Pole |  |  | Branch (OverHanging) | 2019-374 | 2019 | 6 | 21 | 2 | 37 | 19-0070502 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 23024 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-21 02:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-21 | 10:56 | 39.5251 | -121.6886 | Bird Found | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Butte County FD | 6Fq0621191046 |  | 12000 | Conductor | Underbuild | Yes | 43637 | 0.45556 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-459 | 2019 | 6 | 21 | 10 | 56 | 19-0070659 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 12496 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-21 10:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-21 | 11:33 | 39.1288 | -121.4773 |  | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Linda FD | 103954219 |  | 12000 | Pole | Overhead | Yes | 43637 | 0.48125 | Weather - High Wind | Fuse |  |  | High Winds |  | Other/Unknown | 2019-437 | 2019 | 6 | 21 | 11 | 33 | 19-0070703 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip failure | Pole | 63102 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-21 11:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-22 | 23:30 | 38.0133 | -121.356 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Stockton FD | 6446 |  | 21000 | Line Recloser | Overhead | Yes | 43638 | 0.97917 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-223 | 2019 | 6 | 22 | 23 | 30 | 19-0071180 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 60291 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-22 23:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-23 | 12:41 | 37.1891 | -121.7851 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 83242111 |  | 21000 | Conductor | Overhead | No |  |  | Equipment - Overloaded | Conductor |  |  |  |  | no-match | 2019-180 | 2019 | 6 | 23 | 12 | 41 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-23 12:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-23 | 14:43 | 37.821 | -121.9888 |  | Urban | 1 meter - < 3 meters | Fire Dept | Contra Costa FD | 14662107 |  | 21000 | Splice/Clamp/Connector | Overhead | Yes | 43639 | 0.61319 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | no-match | 2019-97 | 2019 | 6 | 23 | 14 | 43 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-23 14:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-24 | 9:53 | 37.327 | -122.0731 |  | Herbaceous | 3 meters - 0.25 Acres | Self Extinguished |  | Unknown |  | 60000 | Other | Overhead | Yes | 43640 | 0.41181 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-209 | 2019 | 6 | 24 | 9 | 53 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-24 09:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-25 | 6:49 | 39.0042 | -122.8674 | Vehicle | Agriculture | 1 meter - < 3 meters | Cal Fire |  | 102144284 |  | 12000 | Pole | Overhead | Yes | 43641 | 0.28403 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-112 | 2019 | 6 | 25 | 6 | 49 | 19-0071714 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 51676 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-25 06:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-25 | 16:32 | 36.2221 | -121.0738 | Bird Found | Herbaceous | 100+ Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | Yes | 43641 | 0.68889 | Contact - Animal - Other |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-11 | 2019 | 6 | 25 | 16 | 32 | 19-0071999 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 52017 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-25 16:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-26 | 7:48 | 36.3585 | -119.8285 | Vegetation | Agriculture | 1 meter - < 3 meters | Fire Dept | Unknown | 252301103 |  | 12000 | Conductor | Overhead | Yes | 43642 | 0.325 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-407 | 2019 | 6 | 26 | 7 | 48 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-26 07:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-26 | 9:29 | 38.1889 | -121.6622 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Rio Vista FD | 103951387 |  | 21000 | Pole | Overhead | Yes | 43642 | 0.39514 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-269 | 2019 | 6 | 26 | 9 | 29 | 19-0072104 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 82835 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-26 09:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-26 | 13:14 | 40.0185 | -122.4107 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | Circuit Id 103331101 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43642 | 0.55139 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-331 | 2019 | 6 | 26 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-26 13:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-26 | 15:22 | 38.511 | -122.0057 | Vehicle | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Winters FD | 103953484 |  | 12000 | Pole | Overhead | Yes | 43642 | 0.64028 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-323 | 2019 | 6 | 26 | 15 | 22 | 19-0072377 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 1406 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-26 15:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-27 | 2:23 | 36.8198 | -119.3334 | Bird Found | Hardwood Woodland | 0.25 - 10 Acres | Self Extinguished |  | Kings River-Sanger-Reedley 115Kv At 16/089 |  | 115000 | Insulator | Overhead | Yes | 43643 | 0.099306 | Equipment - PG&E | Insulator |  |  |  |  | no-match | 2019-104 | 2019 | 6 | 27 | 2 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-06-27 02:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-28 | 13:45 | 36.7207 | -119.8625 |  | Agriculture | 0.25 - 10 Acres | Fire Dept | Fresno FD | Circuit Id 253731112 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43644 | 0.57292 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-126 | 2019 | 6 | 28 | 13 | 45 | 19-0073176 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 83232 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-28 13:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-29 | 11:41 | 37.7397 | -121.4225 | Metallic Balloon | Urban | 3 meters - 0.25 Acres | Fire Dept | Tracy FD | 162881104 |  | 12000 | Conductor | Overhead | Yes | 43645 | 0.48681 | Contact - 3rd Party |  | Balloon contact | Electric Facility | Human Error |  | Other/Unknown | 2019-30 | 2019 | 6 | 29 | 11 | 41 | 19-0073343 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 67398 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-29 11:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-30 | 5:22 | 38.985 | -121.3071 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 6Hb0630190426 |  | 12000 | Conductor | Overhead | Yes | 43646 | 0.22361 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-40 | 2019 | 6 | 30 | 5 | 22 | 19-0073413 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 82904 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-30 05:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-30 | 17:30 | 40.5261 | -122.3338 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 374 |  | 12000 | Capacitor Bank | Overhead | Yes | 43646 | 0.72917 | Equipment - PG&E | Capacitor Bank |  |  |  |  | Other/Unknown | 2019-210 | 2019 | 6 | 30 | 17 | 30 | 19-0073476 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 21640 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-30 17:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-06-30 | 18:02 | 37.7217 | -121.5223 |  | Urban | 3 meters - 0.25 Acres | Employee |  | 162771101 |  | 12000 | Splice/Clamp/Connector | Subsurface | Yes | 43646 | 0.75139 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-213 | 2019 | 6 | 30 | 18 | 2 | 19-0073477 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 18146 | 0 | NA | <25mph | <15mph | #REF! | 2019-06-30 18:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-01 | 2:15 | 38.2955 | -120.8335 |  | Shrub | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-252 | 2019 | 7 | 1 | 2 | 15 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-01 02:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-01 | 13:51 | 40.9789 | -124.0366 | Vehicle | Conifer Forest | 0.25 - 10 Acres | Cal Fire |  | 005/004 |  | 60000 | Pole | Overhead | Yes | 43647 | 0.57708 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-177 | 2019 | 7 | 1 | 13 | 51 | 19-0073704 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 81002 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-01 13:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-02 | 10:59 | 38.9266 | -121.2603 |  | Herbaceous | 3 meters - 0.25 Acres | Self Extinguished |  | 153701104 |  | 12000 | Conductor | Overhead | Yes | 43648 | 0.45764 | Equipment - PG&E | [5 empty] | no-match | 2019-250 | 2019 | 7 | 2 | 10 | 59 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-02 10:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-02 | 11:48 | 36.2146 | -121.1226 | Bird Found | Barren/Other | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | No |  |  | Contact - Animal - Other |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-67 | 2019 | 7 | 2 | 11 | 48 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-02 11:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-02 | 22:51 | 36.3357 | -121.2563 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Green Field FD | 3-170516 |  | 12000 | Transformer | Overhead | No |  |  | Equipment - PG&E | Transformer |  |  |  |  | no-match | 2019-218 | 2019 | 7 | 2 | 22 | 51 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-02 22:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-04 | 16:44 | 39.9813 | -122.224 | Bird Found | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 103331102 |  | 12000 | Conductor | Overhead | Yes | 43650 | 0.69722 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-56 | 2019 | 7 | 4 | 16 | 44 | 19-0074649 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 23413 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-04 16:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-05 | 1:36 | 37.6969 | -121.1055 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Tracy FD | 162471101 |  | 12000 | Conductor | Overhead | Yes | 43651 | 0.066667 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-86 | 2019 | 7 | 5 | 1 | 36 | 19-0074673 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 25526 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-05 01:36:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-05 | 16:49 | 38.4029 | -121.9373 | Bird Found | Urban | 0.25 - 10 Acres | Fire Dept | Unknown | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-50 | 2019 | 7 | 5 | 16 | 49 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-05 16:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-05 | 16:02 | 39.0804 | -122.9061 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Lakeport FD | 43211102 |  | 12000 | Conductor | Overhead | Yes | 43651 | 0.66806 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-87 | 2019 | 7 | 5 | 16 | 2 | 19-0074867 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 139684 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-05 16:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-05 | 8:15 | 37.9778 | -121.2458 | Metallic Balloon | Urban | 3 meters - 0.25 Acres | Fire Dept | Stockton FD | 1101/2 |  | 12000 | Pole | Overhead | Yes | 43651 | 0.34375 | Contact - 3rd Party |  | Balloon contact | Pole | Human Error |  | Other/Unknown | 2019-27 | 2019 | 7 | 5 | 8 | 15 | 19-0074699 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 51548 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-05 08:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-05 | 15:10 | 36.2745 | -119.7809 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Kings County FD | Circuit Id 253601102 |  | 12000 | Splice/Clamp/Connector | Overhead | No |  |  | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | no-match | 2019-147 | 2019 | 7 | 5 | 15 | 10 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-05 15:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-06 | 15:34 | 37.73 | -121.4269 |  | Urban | 1 meter - < 3 meters | Fire Dept | Tracy FD | 317321944923 |  | 12000 | Transformer | Overhead | Yes | 43652 | 0.64861 | Equipment - PG&E | Transformer |  |  |  |  | Other/Unknown | 2019-248 | 2019 | 7 | 6 | 15 | 34 | 19-0074962 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1212 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-06 15:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-06 | 14:22 | 34.6388 | -119.9695 |  | Herbaceous | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | 182721104 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43652 | 0.59861 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-153 | 2019 | 7 | 6 | 14 | 22 | 19-0074960 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 14213 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-06 14:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-07 | 19:14 | 38.2679 | -122.0175 | Metallic Balloon | Urban | 1 meter - < 3 meters | Fire Dept | Fairfield FD | 1105/2 |  | 12000 | Conductor | Overhead | Yes | 43653 | 0.80139 | Contact - 3rd Party |  | Balloon contact |  | Human Error |  | Other/Unknown | 2019-28 | 2019 | 7 | 7 | 19 | 14 | 19-0075043 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 467277 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-07 19:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-07 | 18:23 | 40.3867 | -122.2747 | Vegetation | Urban | 1 meter - < 3 meters | Fire Dept | Cottonwood FD | Unknown |  | 12000 | Other | Overhead | Yes | 43653 | 0.76597 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-139 | 2019 | 7 | 7 | 18 | 23 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-07 18:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-07 | 16:24 | 38.2498 | -122.0342 |  | Urban | 1 meter - < 3 meters | Fire Dept | Fairfield FD | Unknown |  | 12000 | Other | Overhead | No |  |  | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-28 | 2019 | 7 | 7 | 16 | 24 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-07 16:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-10 | 14:25 | 36.9581 | -120.1094 | Bird Found | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 255391102 |  | 12000 | Conductor | Overhead | Yes | 43656 | 0.60069 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-441 | 2019 | 7 | 10 | 14 | 25 | 19-0076068 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 18807 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-10 14:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-11 | 15:27 | 39.5657 | -120.6614 | Vegetation | Conifer Forest | 0.25 - 10 Acres | Unknown |  | 100102596 |  | 12000 | Pole | Overhead | Yes | 43657 | 0.64375 | Vegetation |  | Veg. contact | Pole |  |  | no-match | 2019-03 | 2019 | 7 | 11 | 15 | 27 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-11 15:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-12 | 14:18 | 35.3338 | -118.9911 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Bakersfield FD | 253372104 |  | 21000 | Conductor | Overhead | Yes | 43658 | 0.59583 | Contact - 3rd Party |  | Conductor failure-all | Electric Facility | Human Error |  | no-match | 2019-432 | 2019 | 7 | 12 | 14 | 18 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-12 14:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-12 | 16:40 | 37.8599 | -120.9061 |  | Herbaceous | < 1 meter | Self Extinguished |  | 318851549660 |  | 17000 | Conductor | Overhead | Yes | 43658 | 0.69444 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown |  | 2019 | 7 | 12 | 16 | 40 | 19-0076952 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 236 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-12 16:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-12 | 19:38 | 36.8079 | -119.5264 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 254441106 |  | 12000 | Conductor | Overhead | Yes | 43658 | 0.81806 | Vegetation |  | Veg. contact |  |  |  | Branch (OverHanging) | 2019-342 | 2019 | 7 | 12 | 19 | 38 | 19-0076962 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 7614 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-12 19:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-13 | 13:13 | 34.7273 | -120.4357 |  | Shrub | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | Y44 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43659 | 0.55069 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-154 | 2019 | 7 | 13 | 13 | 13 | 19-0077070 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 18256 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-13 13:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-13 | 15:56 | 36.9907 | -119.8686 |  | Urban | 1 meter - < 3 meters | Other | Customer | 5Tn0713191555 |  | 12000 | Other | Overhead | Yes | 43659 | 0.66389 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-266 | 2019 | 7 | 13 | 15 | 56 | 19-0077099 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 10021 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-13 15:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-13 | 12:43 | 37.2015 | -120.3296 |  | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Merced FD | 320508025527 |  | 12000 | Pole | Overhead | Yes | 43659 | 0.52986 | Other Fire: Non-PG&E related | [5 empty] | no-match |  | 2019 | 7 | 13 | 12 | 43 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip failure | Pole | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-13 12:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-13 | 12:04 | 37.3904 | -120.6194 |  | Urban | 1 meter - < 3 meters | Cal Fire |  | 253611103 |  | 12000 | Conductor | Overhead | Yes | 43659 | 0.50278 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-159 | 2019 | 7 | 13 | 12 | 4 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-13 12:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-13 | 22:16 | 38.6069 | -121.0688 | Metallic Balloon | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 21000 | Conductor | Overhead | No |  |  | Contact - 3rd Party | Conductor | Balloon contact | Electric Facility | Human Error |  | no-match |  | 2019 | 7 | 13 | 22 | 16 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-13 22:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-15 | 7:51 | 38.3266 | -122.568 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 42721104 |  | 12000 | Conductor | Overhead | Yes | 43661 | 0.32708 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-343 | 2019 | 7 | 15 | 7 | 51 | 19-0077351 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2348 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-15 07:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-15 | 13:50 | 35.6028 | -119.0898 | Bird Found | Agriculture | 0.25 - 10 Acres | Fire Dept | Kern County FD | 516762776845 |  | 12000 | Transformer | Overhead | Yes | 43661 | 0.57639 | Contact - Animal - Other |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-35 | 2019 | 7 | 15 | 13 | 50 | 19-0077564 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 639 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-15 13:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-15 | 14:12 | 37.9904 | -121.2857 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Stockton FD | 317740654408 |  | 12000 | Crossarm | Overhead | Yes | 43661 | 0.59167 | Equipment - PG&E | Crossarm |  |  |  |  | no-match | 2019-272 | 2019 | 7 | 15 | 14 | 12 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-15 14:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-15 | 16:31 | 37.9573 | -121.2233 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Stockton FD | 163211103 |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-292 | 2019 | 7 | 15 | 16 | 31 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-15 16:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-16 | 17:31 | 40.1691 | -122.3053 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103541103 |  | 12000 | Conductor | Overhead | Yes | 43662 | 0.72986 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-375 | 2019 | 7 | 16 | 17 | 31 | 19-0078094 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 45533 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-16 17:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-17 | 7:49 | 34.5066 | -120.2247 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Santa Barbara County FD | 4Bx0717190747 |  | 12000 | Other | Overhead | Yes | 43663 | 0.32569 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-425 | 2019 | 7 | 17 | 7 | 49 | 19-0078239 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 19608 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-17 07:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-17 | 18:00 | 37.2882 | -122.0171 |  | Urban | 1 meter - < 3 meters | Fire Dept | Santa Clara County FD | 83371114 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43663 | 0.75 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | no-match | 2019-335 | 2019 | 7 | 17 | 18 | 0 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-17 18:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-18 | 12:10 | 36.923 | -119.9396 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 255121101 |  | 12000 | Conductor | Underbuild | Yes | 43664 | 0.50694 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-128 | 2019 | 7 | 18 | 12 | 10 | 19-0078794 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 21434 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-18 12:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-18 | 15:23 | 37.3552 | -120.5999 |  | Urban | 1 meter - < 3 meters | Cal Fire | Atwater FD | 253611104 |  | 12000 | Conductor | Overhead | Yes | 43664 | 0.64097 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-280 | 2019 | 7 | 18 | 15 | 23 | 19-0078937 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 69013 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-18 15:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-18 | 19:57 | 37.081 | -119.4865 |  | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | No |  |  | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-09 | 2019 | 7 | 18 | 19 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-18 19:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-18 | 10:27 | 38.3033 | -120.6718 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | B561 |  | 12000 | Other | Overhead | Yes | 43664 | 0.43542 | Equipment - PG&E | Other |  |  |  |  | Other/Unknown | 2019-68 | 2019 | 7 | 18 | 10 | 27 | 19-0078904 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 45558 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-18 10:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-18 | 19:12 | 36.6339 | -119.7913 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | Circuit Id 253531104 |  | 12000 | Other | Overhead | Yes | 43664 | 0.8 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-289 | 2019 | 7 | 18 | 19 | 12 | 19-0078996 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 2255 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-18 19:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-19 | 11:59 | 37.9162 | -120.349 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 163351703 |  | 17000 | Conductor | Overhead | Yes | 43665 | 0.49931 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-376 | 2019 | 7 | 19 | 11 | 59 | 19-0079030 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24042 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-19 11:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-21 | 15:22 | 37.6322 | -122.1198 | Vehicle | Urban | 1 meter - < 3 meters | Fire Dept | Hayward FD | 102345568 |  | 12000 | Pole | Overhead | Yes | 43667 | 0.64028 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-422 | 2019 | 7 | 21 | 15 | 22 | 19-0079612 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 3768 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-21 15:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-21 | 12:46 | 37.0517 | -122.1522 | Vegetation | Urban | 1 meter - < 3 meters | Cal Fire |  | 82931101 |  | 12000 | Conductor | Overhead | Yes | 43667 | 0.53194 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-377 | 2019 | 7 | 21 | 12 | 46 | 19-0079583 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 89102 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-21 12:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-21 | 10:19 | 36.7581 | -119.7778 | Contact with High Voltage, 3rd party | Urban | 1 meter - < 3 meters | Fire Dept | Fresno FD | Mtr#1004290776 |  | 12000 | Secondary | Overhead | Yes | 43667 | 0.42986 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | Other/Unknown | 2019-14 | 2019 | 7 | 21 | 10 | 19 | 19-0079564 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 9345 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-21 10:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-21 | 10:14 | 38.9716 | -120.9991 |  | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire | Placer Hill FD | 152241102 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43667 | 0.42639 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-127 | 2019 | 7 | 21 | 10 | 14 | 19-0079578 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 32850 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-21 10:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-22 | 8:11 | 38.7687 | -120.9633 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | El Dorado County FD | 6Ht0722190809 |  | 21000 | Other | Overhead | Yes | 43668 | 0.34097 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-49 | 2019 | 7 | 22 | 8 | 11 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-22 08:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-22 | 21:39 | 38.8618 | -121.1044 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 152561103 |  | 12000 | Conductor | Overhead | Yes | 43668 | 0.90208 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-336 | 2019 | 7 | 22 | 21 | 39 | 19-0080025 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 9842 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-22 21:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-23 | 16:31 | 37.2447 | -121.9999 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Santa Clara County FD | 83371104 |  | 12000 | Conductor | Overhead | Yes | 43669 | 0.68819 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-378 | 2019 | 7 | 23 | 16 | 31 | 19-0080428 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 19250 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-23 16:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-23 | 16:55 | 37.2128 | -119.505 | Gun Shot | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | 252521103 |  | 12000 | Conductor | Overhead | Yes | 43669 | 0.70486 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-434 | 2019 | 7 | 23 | 16 | 55 | 19-0080383 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 513358 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-23 16:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-24 | 2:31 | 37.7804 | -121.5105 |  | Urban | 0.25 - 10 Acres | Fire Dept | Tracy FD | 317082046775 |  | 12000 | Transformer | Overhead | Yes | 43670 | 0.10486 | Equipment - PG&E | [5 empty] | no-match |  | 2019 | 7 | 24 | 2 | 31 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-24 02:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-24 | 5:09 | 36.991 | -121.5733 |  | Urban | 1 meter - < 3 meters | Unknown |  | 72159 |  | 21000 | Other | Overhead | Yes | 43670 | 0.21458 | Equipment - PG&E | Other |  |  |  |  | Other/Unknown | 2019-293 | 2019 | 7 | 24 | 5 | 9 | 19-0080501 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 114674 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-24 05:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-24 | 15:38 | 38.3599 | -121.9934 | Animal Found | Urban | 3 meters - 0.25 Acres | Fire Dept | Vacaville FD | 220022225257 |  | 12000 | Transformer | Overhead | Yes | 43670 | 0.65139 | Contact - Animal - Other |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-277 | 2019 | 7 | 24 | 15 | 38 | 19-0080841 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 114112 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-24 15:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-25 | 0:15 | 39.0662 | -120.9754 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Placer Hills FD | 152491101 |  | 12000 | Conductor | Overhead | Yes | 43671 | 0.010417 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-379 | 2019 | 7 | 25 | 0 | 15 | 19-0080924 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7845 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-25 00:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-25 | 7:39 | 39.1735 | -123.5763 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Oj 2 P/Ss Of Cgc# 215532055340 |  | 12000 | Other | Overhead | Yes | 43671 | 0.31875 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-380 | 2019 | 7 | 25 | 7 | 39 | 19-0080947 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 790 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-25 07:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-25 | 15:47 | 37.2493 | -121.8869 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | San Jose FD | 74 |  | 12000 | Other | Overhead | Yes | 43671 | 0.65764 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-332 | 2019 | 7 | 25 | 15 | 47 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-25 15:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-25 | 19:34 | 37.2046 | -120.4366 | Bird Found | Urban | 1 meter - < 3 meters | Unknown |  | 5Tr0725191902 |  | 12000 | Other | Overhead | Yes | 43671 | 0.81528 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-51 | 2019 | 7 | 25 | 19 | 34 | 19-0081350 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 213 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-25 19:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-26 | 12:03 | 38.8003 | -120.8258 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire |  | 153082106 |  | 21000 | Conductor | Overhead | Yes | 43672 | 0.50208 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-381 | 2019 | 7 | 26 | 12 | 3 | 19-0081559 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 16465 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-26 12:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-26 | 18:37 | 38.7072 | -122.0481 |  | Agriculture | 1 meter - < 3 meters | Cal Fire |  | 101604865 |  | 21000 | Pole | Overhead | No |  |  | Equipment - PG&E | Pole |  |  |  |  | no-match | 2019-70 | 2019 | 7 | 26 | 18 | 37 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-26 18:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-27 | 15:30 | 35.4879 | -120.6507 | Vegetation | Urban | 1 meter - < 3 meters | Fire Dept | Atascadero FD | 103952454 |  | 12000 | Pole | Overhead | Yes | 43673 | 0.64583 | Vegetation |  | Veg. contact | Pole |  |  | no-match | 2019-356 | 2019 | 7 | 27 | 15 | 30 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-27 15:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-27 | 8:22 | 40.3789 | -122.1873 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Self Extinguished |  | 103461102 |  | 12000 | Conductor | Overhead | Yes | 43673 | 0.34861 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-382 | 2019 | 7 | 27 | 8 | 22 | 19-0081756 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 456 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-27 08:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-27 | 16:17 | 37.7266 | -120.3246 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire |  | 252811102 |  | 12000 | Conductor | Overhead | Yes | 43673 | 0.67847 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-383 | 2019 | 7 | 27 | 16 | 17 | 19-0081851 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 2694 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-27 16:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-27 | 3:43 | 38.6557 | -122.8952 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Employee |  | 42751113 |  | 12000 | Conductor | Overhead | Yes | 43673 | 0.15486 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-384 | 2019 | 7 | 27 | 3 | 43 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-27 03:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-27 | 4:51 | 37.9486 | -120.4656 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 163781705 |  | 17000 | Conductor | Overhead | Yes | 43673 | 0.20208 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-385 | 2019 | 7 | 27 | 4 | 51 | 19-0081744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 1364 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-27 04:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-28 | 23:13 | 36.9608 | -119.728 |  | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 255292108 |  | 21000 | Conductor | Overhead | Yes | 43674 | 0.96736 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-268 | 2019 | 7 | 28 | 23 | 13 | 19-0082036 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 762 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-28 23:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-29 | 15:11 | 38.5144 | -121.7751 |  | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Unknown | Near Meter 1009500196 |  | 12000 | Other | Overhead | Yes | 43675 | 0.63264 | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-138 | 2019 | 7 | 29 | 15 | 11 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-29 15:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-30 | 0:17 | 38.5156 | -122.8269 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Windsor FD | 217640530998 |  | 12000 | Transformer | Overhead | Yes | 43676 | 0.011806 | Equipment - PG&E | Transformer |  |  |  |  | Other/Unknown | 2019-219 | 2019 | 7 | 30 | 0 | 17 | 19-0082406 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 628 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-30 00:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-30 | 15:15 | 39.1207 | -121.072 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 152691104 |  | 12000 | Conductor | Overhead | Yes | 43676 | 0.63542 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-386 | 2019 | 7 | 30 | 15 | 15 | 19-0082713 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 31302 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-30 15:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-30 | 14:16 | 40.9703 | -124.0435 | Vehicle | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 103967110 | Yes | 12000 | Pole | Overhead | Yes | 43676 | 0.59444 | Contact - 3rd Party |  | Vehicle contact |  | Human Error |  | Other/Unknown | 2019-225 | 2019 | 7 | 30 | 14 | 16 | 19-0082659 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 52246 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-30 14:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-30 | 15:24 | 37.4504 | -121.8496 |  | Urban | 0.25 - 10 Acres | Cal Fire |  | 82831109 |  | 12000 | Conductor | Overhead | Yes | 43676 | 0.64167 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-443 | 2019 | 7 | 30 | 15 | 24 | 19-0082688 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 68088 | 0 | NA | <25mph | <15mph | #REF! | 2019-07-30 15:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-07-31 | 18:34 | 36.3106 | -121.0437 | Bird Found | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 3Bj0731191818 |  | 21000 | Other | Overhead | Yes | 43677 | 0.77361 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-57 | 2019 | 7 | 31 | 18 | 34 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-07-31 18:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-01 | 13:28 | 38.5721 | -120.6803 | Equipment Failure/Involved, Overhead | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 153662102 |  | 21000 | Conductor | Overhead | Yes | 43678 | 0.56111 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-170 | 2019 | 8 | 1 | 13 | 28 | 19-0083500 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1374 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-01 13:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-02 | 3:28 | 38.0934 | -122.1984 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Vallejo FD | 7Ny0802190243 |  | 12000 | Switch | Overhead | Yes | 43679 | 0.14444 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-275 | 2019 | 8 | 2 | 3 | 28 | 19-0083636 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 233244 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-02 03:28:00 | #REF! | 0 | TRUE | <25mph
PG&E | 2019-08-02 | 3:28 | 36.7863 | -119.5198 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 254441106 |  | 12000 | Conductor | Overhead | Yes | 43679 | 0.14444 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-275 | 2019 | 8 | 2 | 3 | 28 | 19-0083637 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 47131 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-02 03:28:00 | #REF! | 0 | TRUE | <25mph
PG&E | 2019-08-02 | 4:51 | 38.3736 | -121.1395 | Bird Found | Herbaceous | 10 - 100 Acres | Self Extinguished |  | 2222 Gold Hill-Bellota-Lockeford 115Kv Line |  | 115000 | Conductor | Overhead | Yes | 43679 | 0.20208 | Contact - Animal - Other |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-433 | 2019 | 8 | 2 | 4 | 51 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-08-02 04:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-03 | 13:30 | 39.0883 | -122.3092 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 7049 |  | 21000 | Conductor | Overhead | Yes | 43680 | 0.5625 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown |  | 2019 | 8 | 3 | 13 | 30 | 19-0084059 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 3417 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-03 13:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-03 | 11:37 | 35.6909 | -119.8232 | Bird Found | Agriculture | 10 - 100 Acres | Cal Fire |  | 4Tx0803191135 |  | 12000 | Other | Overhead | Yes | 43680 | 0.48403 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-39 | 2019 | 8 | 3 | 11 | 37 | 19-0084060 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 1587 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-03 11:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-05 | 11:55 | 38.251 | -122.5824 | Bird Found | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 7Nr0805191142 |  | 12000 | Conductor | Underbuild | Yes | 43682 | 0.49653 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-62 | 2019 | 8 | 5 | 11 | 55 | 19-0084361 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 127118 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-05 11:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-05 | 22:38 | 37.1869 | -119.7902 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Unknown |  | 322066125092 |  | 21000 | Transformer | Overhead | Yes | 43682 | 0.94306 | Equipment - Overloaded | Transformer |  |  |  |  | Other/Unknown | 2019-134 | 2019 | 8 | 5 | 22 | 38 | 19-0084586 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 996 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-05 22:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-05 | 23:32 | 38.2843 | -122.1183 | Vegetation | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 43051101 |  | 12000 | Conductor | Overhead | Yes | 43682 | 0.98056 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-394 | 2019 | 8 | 5 | 23 | 32 | 19-0084585 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 53600 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-05 23:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-06 | 15:47 | 36.5718 | -121.7364 | Vehicle | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 182222104 |  | 21000 | Conductor | Overhead | Yes | 43683 | 0.65764 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-141 | 2019 | 8 | 6 | 15 | 47 | 19-0084968 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 6209 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-06 15:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-06 | 12:12 | 39.0506 | -121.0614 | Vegetation | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 100107532 |  | 12000 | Insulator | Overhead | Yes | 43683 | 0.50833 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-391 | 2019 | 8 | 6 | 12 | 12 | 19-0084799 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 60943 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-06 12:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-06 | 18:33 | 37.403 | -121.9056 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Unknown | 83892108 |  | 21000 | Conductor | Overhead | Yes | 43683 | 0.77292 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-442 | 2019 | 8 | 6 | 18 | 33 | 19-0085010 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 59778 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-06 18:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-07 | 7:29 | 37.1412 | -122.3282 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 24101103 |  | 12000 | Conductor | Overhead | Yes | 43684 | 0.31181 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-345 | 2019 | 8 | 7 | 7 | 29 | 19-0085095 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 808 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-07 07:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-07 | 12:55 | 37.1422 | -120.4953 | Bird Found | Agriculture | 1 meter - < 3 meters | Cal Fire |  | 5Tr0807191434 |  | 12000 | Pole | Overhead | Yes | 43684 | 0.53819 | Contact - Animal - Bird |  | Animal contact | Pole | Animal Contact |  | Other/Unknown | 2019-69 | 2019 | 8 | 7 | 12 | 55 | 19-0085300 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 1496 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-07 12:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-07 | 10:42 | 37.2834 | -120.4524 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Splice/Clamp/Connector | Overhead | No |  |  | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | no-match |  | 2019 | 8 | 7 | 10 | 42 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-08-07 10:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-08 | 16:40 | 37.0837 | -120.4943 | Bird Found | Agriculture | 1 meter - < 3 meters | Cal Fire |  | 5Tr0808191639 |  | 12000 | Transformer | Overhead | Yes | 43685 | 0.69444 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-64 | 2019 | 8 | 8 | 16 | 40 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-08-08 16:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-10 | 7:26 | 39.0125 | -121.4884 | Bird Found | Agriculture | 1 meter - < 3 meters | Cal Fire |  | 6Hp0810190609 |  | 12000 | Conductor | Overhead | Yes | 43687 | 0.30972 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-44 | 2019 | 8 | 10 | 7 | 26 | 19-0086456 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 23627 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-10 07:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-10 | 8:19 | 39.4899 | -121.5339 | Animal Found | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 1008809971 |  | 12000 | Transformer | Overhead | Yes | 43687 | 0.34653 | Contact - Animal - Other |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-120 | 2019 | 8 | 10 | 8 | 19 | 19-0086464 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 730 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-10 08:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-10 | 17:30 | 35.368 | -118.9638 |  | Urban | 3 meters - 0.25 Acres | Unknown |  | 253372106 |  | 21000 | Conductor | Overhead | Yes | 43687 | 0.72917 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-227 | 2019 | 8 | 10 | 17 | 30 | 19-0086585 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1206 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-10 17:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-10 | 22:27 | 35.6961 | -120.6977 |  | Barren/Other | 0.25 - 10 Acres | Cal Fire |  | 152481106 |  | 12000 | Conductor | Overhead | Yes | 43687 | 0.93542 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-124 | 2019 | 8 | 10 | 22 | 27 | 19-0086588 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 9844 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-10 22:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-11 | 1:19 | 39.1152 | -121.001 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100097796 |  | 12000 | Other | Overhead | Yes | 43688 | 0.054861 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-387 | 2019 | 8 | 11 | 1 | 19 | 19-0086613 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6200 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-11 01:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-11 | 16:56 | 39.6243 | -122.1951 |  | Urban | 0.25 - 10 Acres | Cal Fire |  | 1010028782 |  | 12000 | Other | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-16 | 2019 | 8 | 11 | 16 | 56 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-08-11 16:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-12 | 10:40 | 37.9834 | -122.4531 | Bird Found | Urban | 1 meter - < 3 meters | Unknown |  | 42011105 |  | 12000 | Switch | Overhead | Yes | 43689 | 0.44444 | Contact - Animal - Other |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-66 | 2019 | 8 | 12 | 10 | 40 | 19-0086839 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 504659 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-12 10:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-12 | 17:43 | 37.0508 | -121.5894 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 100612948 |  | 21000 | Conductor | Overhead | Yes | 43689 | 0.73819 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-439 | 2019 | 8 | 12 | 17 | 43 | 19-0087072 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 67266 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-12 17:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-12 | 20:06 | 39.0952 | -123.4937 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 102177212 |  | 12000 | Conductor | Overhead | Yes | 43689 | 0.8375 | Vegetation |  | Veg. contact |  |  |  | Fell into (No defect) | 2019-400 | 2019 | 8 | 12 | 20 | 6 | 19-0087090 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2508 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-12 20:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-12 | 17:42 | 38.6618 | -120.7451 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 101415488, 101404439 |  | 12000 | Pole | Overhead | Yes | 43689 | 0.7375 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (slight defect) | 2019-241 | 2019 | 8 | 12 | 17 | 42 | 19-0087080 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 54604 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-12 17:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-13 | 0:55 | 36.9509 | -119.8307 |  | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 40239045 |  | 21000 | Capacitor Bank | Overhead | Yes | 43690 | 0.038194 | Equipment - PG&E | Capacitor Bank |  |  |  |  | Other/Unknown | 2019-107 | 2019 | 8 | 13 | 0 | 55 | 19-0087114 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 53760 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-13 00:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-13 | 2:50 | 38.0004 | -121.7119 | Contact with High Voltage, 3rd party | Urban | 0.25 - 10 Acres | Fire Dept | Unknown | 13652107 |  | 21000 | Conductor | Subsurface | Yes | 43690 | 0.11806 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-96 | 2019 | 8 | 13 | 2 | 50 | 19-0087117 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 162205 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-13 02:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-13 | 10:30 | 36.6102 | -121.4452 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 40761041 |  | 115000 | Other | Overhead | Yes | 43690 | 0.4375 | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-164 | 2019 | 8 | 13 | 10 | 30 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-08-13 10:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-14 | 19:42 | 37.3367 | -121.8966 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Unknown | 82191104 |  | 12000 | Other | Overhead | Yes | 43691 | 0.82083 | Equipment - PG&E | [5 empty] | no-match | 2019-273 | 2019 | 8 | 14 | 19 | 42 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-08-14 19:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-14 | 16:35 | 35.2726 | -120.642 | Metallic Balloon | Urban | 1 meter - < 3 meters | Fire Dept | San Luis Obispo FD | 101935033 |  | 12000 | Conductor | Overhead | Yes | 43691 | 0.69097 | Contact - 3rd Party |  | Balloon contact | Electric Facility | Human Error |  | Other/Unknown | 2019-238 | 2019 | 8 | 14 | 16 | 35 | 19-0088022 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 355765 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-14 16:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-14 | 14:04 | 36.9789 | -120.0332 |  | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 101216303 |  | 12000 | Conductor | Overhead | Yes | 43691 | 0.58611 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-183 | 2019 | 8 | 14 | 14 | 4 | 19-0087876 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 414 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-14 14:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-14 | 10:16 | 35.379 | -120.4232 | Vegetation | Hardwood Woodland | < 1 meter | Cal Fire |  | 512769069280 |  | 21000 | Conductor | Overhead | Yes | 43691 | 0.42778 | Vegetation | [5 empty] | no-match |  | 2019 | 8 | 14 | 10 | 16 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-08-14 10:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-14 | 9:19 | 38.0909 | -121.2605 | Vegetation | Urban | 1 meter - < 3 meters | Fire Dept | Waterloo Morada FD | 102107171 | Yes | 21000 | Other | Overhead | Yes | 43691 | 0.38819 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-334 | 2019 | 8 | 14 | 9 | 19 | 19-0087715 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1075 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-14 09:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-14 | 7:56 | 39.8176 | -121.9085 | Animal Found | Urban | 1 meter - < 3 meters | Cal Fire |  | 102841106 |  | 12000 | Other | Overhead | No |  |  | Contact - Animal - Other |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-299 | 2019 | 8 | 14 | 7 | 56 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-08-14 07:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-15 | 12:24 | 37.2165 | -121.7563 | Vehicle | Urban | 10 - 100 Acres | Fire Dept | San Jose FD | 82952107 |  | 21000 | Conductor | Overhead | Yes | 43692 | 0.51667 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-113 | 2019 | 8 | 15 | 12 | 24 | 19-0088301 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 118854 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-15 12:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-15 | 12:10 | 36.6024 | -119.4583 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Reedley FD | 254531110 |  | 12000 | Conductor | Overhead | No |  |  | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | no-match | 2019-15 | 2019 | 8 | 15 | 12 | 10 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-08-15 12:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-16 | 13:20 | 36.5844 | -119.7754 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Pole | Overhead | Yes | 43693 | 0.55556 | Vegetation | [5 empty] | no-match |  | 2019 | 8 | 16 | 13 | 20 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-08-16 13:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-16 | 8:19 | 40.1235 | -123.8758 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Self Extinguished |  | 192221102-2101118022{5563} |  | 12000 | Conductor | Overhead | Yes | 43693 | 0.34653 | Vegetation | [5 empty] | Other/Unknown |  | 2019 | 8 | 16 | 8 | 19 | 19-0088744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 2979 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-16 08:19:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-16 | 1:37 | 40.2949 | -121.2407 | Animal Found | Urban | 1 meter - < 3 meters | Cal Fire | Chester FD | 103181102 |  | 12000 | Fuse | Overhead | Yes | 43693 | 0.067361 | Contact - Animal - Other |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-281 | 2019 | 8 | 16 | 1 | 37 | 19-0088645 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 6845 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-16 01:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-16 | 10:31 | 39.3714 | -121.3221 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103191101 |  | 12000 | Conductor | Overhead | Yes | 43693 | 0.43819 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-397 | 2019 | 8 | 16 | 10 | 31 | 19-0088805 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4580 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-16 10:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-16 | 18:11 | 36.5841 | -119.7731 |  | Agriculture | 0.25 - 10 Acres | Cal Fire |  | MTR#1009552365 |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-99 | 2019 | 8 | 16 | 18 | 11 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-08-16 18:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-18 | 8:20 | 36.733 | -119.6922 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Unknown | R9547 |  | 12000 | Other | Overhead | Yes | 43695 | 0.34722 | Equipment - PG&E | Other |  |  |  |  | Other/Unknown | 2019-95 | 2019 | 8 | 18 | 8 | 20 | 19-0089197 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 27813 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-18 08:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-18 | 15:46 | 34.8713 | -120.2624 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Santa Barbara County FD | 182811103 |  | 12000 | Conductor | Overhead | Yes | 43695 | 0.65694 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-435 | 2019 | 8 | 18 | 15 | 46 | 19-0089229 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 5932 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-18 15:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-19 | 17:27 | 40.9399 | -123.6322 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | California Department of Forestry | 192171101 |  | 12000 | Conductor | Overhead | Yes | 43696 | 0.72708 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-340 | 2019 | 8 | 19 | 17 | 27 | 19-0089645 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 410686 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-19 17:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-20 | 9:03 | 41.1088 | -121.5034 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-297 | 2019 | 8 | 20 | 9 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-08-20 09:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-20 | 22:04 | 38.2285 | -121.0293 |  | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 17493 |  | 21000 | Fuse | Overhead | Yes | 43697 | 0.91944 | Equipment - PG&E | Fuse |  |  |  |  | Other/Unknown | 2019-93 | 2019 | 8 | 20 | 22 | 4 | 19-0090197 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 21420 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-20 22:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-21 | 7:50 | 38.5217 | -121.5495 |  | Agriculture | 0.25 - 10 Acres | Fire Dept | West Sacramento FD | 63621107 |  | 12000 | Conductor | Overhead | Yes | 43698 | 0.32639 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-233 | 2019 | 8 | 21 | 7 | 50 | 19-0090235 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 746212 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-21 07:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-22 | 22:23 | 39.139 | -121.0194 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 152481106 |  | 12000 | Conductor | Overhead | Yes | 43699 | 0.93264 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-346 | 2019 | 8 | 22 | 22 | 23 | 19-0091224 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38628 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-22 22:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-23 | 21:39 | 34.948 | -118.9327 | Vehicle | Urban | 3 meters - 0.25 Acres | Fire Dept | Kern County FD | 5/104,5/105, |  | 12000 | Pole | Overhead | Yes | 43700 | 0.90208 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-111 | 2019 | 8 | 23 | 21 | 39 | 19-0091690 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 284004 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-23 21:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-23 | 23:40 | 35.9905 | -119.9616 | Bird Found | Urban | 3 meters - 0.25 Acres | Cal Fire | Kettleman FD | Unknown |  | 12000 | Other | Overhead | Yes | 43700 | 0.98611 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-61 | 2019 | 8 | 23 | 23 | 40 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-08-23 23:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-23 | 17:54 | 36.756 | -119.8644 | Thrown Object | Urban | 0.25 - 10 Acres | Fire Dept | Unknown | D7143 |  | 12000 | Conductor | Overhead | Yes | 43700 | 0.74583 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | Other/Unknown | 2019-173 | 2019 | 8 | 23 | 17 | 54 | 19-0091655 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 14056 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-23 17:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-23 | 13:17 | 36.7262 | -119.4742 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 254531108 |  | 12000 | Conductor | Overhead | Yes | 43700 | 0.55347 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-399 | 2019 | 8 | 23 | 13 | 17 | 19-0091504 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 19377 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-23 13:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-24 | 20:26 | 37.5908 | -122.4127 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Millbrae FD | 314464040259 |  | 12000 | Pole | Overhead | Yes | 43701 | 0.85139 | Equipment - PG&E | Pole |  |  |  |  | no-match | 2019-25 | 2019 | 8 | 24 | 20 | 26 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-08-24 20:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-24 | 19:02 | 39.0497 | -121.0614 | Vehicle | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 103956556 |  | 12000 | Pole | Overhead | Yes | 43701 | 0.79306 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-114 | 2019 | 8 | 24 | 19 | 2 | 19-0091826 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 144608 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-24 19:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-25 | 13:13 | 41.0935 | -123.6942 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Unknown | 115334464574 |  | 12000 | Transformer | Overhead | Yes | 43702 | 0.55069 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-351 | 2019 | 8 | 25 | 13 | 13 | 19-0091921 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 20311 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-25 13:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-25 | 0:50 | 38.5922 | -122.5791 |  | Herbaceous | 1 meter - < 3 meters | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | No |  |  | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-294 | 2019 | 8 | 25 | 0 | 50 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-08-25 00:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-27 | 14:47 | 37.5361 | -120.462 | Vehicle | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 101197621 |  | 12000 | Pole | Overhead | Yes | 43704 | 0.61597 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-324 | 2019 | 8 | 27 | 14 | 47 | 19-0092697 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 29092 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-27 14:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-28 | 2:15 | 36.8649 | -119.6206 | Animal Found | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Fresno FD | Lr3010 |  | 12000 | Recloser | Overhead | Yes | 43705 | 0.09375 | Contact - Animal - Other |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-282 | 2019 | 8 | 28 | 2 | 15 | 19-0092813 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 44737 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-28 02:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-28 | 16:43 | 39.7457 | -123.2009 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 43061101 |  | 12000 | Conductor | Overhead | Yes | 43705 | 0.69653 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-242 | 2019 | 8 | 28 | 16 | 43 | 19-0093286 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 3546 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-28 16:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-28 | 14:12 | 36.7818 | -119.8714 | Tree - cutting, 3rd party | Urban | 0.25 - 10 Acres | Fire Dept | Unknown | 252051113 |  | 12000 | Conductor | Overhead | Yes | 43705 | 0.59167 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-404 | 2019 | 8 | 28 | 14 | 12 | 19-0093176 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 23384 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-28 14:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-30 | 16:37 | 37.7967 | -121.4489 | Vehicle | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Unknown | 162881106 |  | 12000 | Conductor | Overhead | Yes | 43707 | 0.69236 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-288 | 2019 | 8 | 30 | 16 | 37 | 19-0094223 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 41486 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-30 16:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-08-31 | 10:20 | 40.661 | -122.356 | Vehicle | Barren/Other | 3 meters - 0.25 Acres | Fire Dept | Shasta Lake FD | 103571671 | Yes | 12000 | Fuse | Overbuild | Yes | 43708 | 0.43056 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-421 | 2019 | 8 | 31 | 10 | 20 | 19-0094332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 3050 | 0 | NA | <25mph | <15mph | #REF! | 2019-08-31 10:20:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-01 | 16:50 | 35.908 | -121.011 |  | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 103477437 |  | 12000 | Pole | Overhead | Yes | 43709 | 0.70139 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-17 | 2019 | 9 | 1 | 16 | 50 | 19-0094475 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45432 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-01 16:50:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-01 | 22:01 | 36.7702 | -119.7629 | Vegetation | Urban | 1 meter - < 3 meters | Fire Dept | Unknown | Unknown |  | 12000 | Conductor | Overhead | Yes | 43709 | 0.91736 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-392 | 2019 | 9 | 1 | 22 | 1 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-01 22:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-01 | 6:59 | 38.0617 | -122.5327 | Vehicle | Urban | 1 meter - < 3 meters | Fire Dept | Novato FD | 04248-2100893893{1103/2} |  | 12000 | Pole | Overhead | Yes | 43709 | 0.29097 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-110 | 2019 | 9 | 1 | 6 | 59 | 19-0094413 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 566508 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-01 06:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-01 | 21:34 | 34.6265 | -120.0892 |  | Herbaceous | 1 meter - < 3 meters | Fire Dept | Santa Barbara County FD | 182721104 |  | 12000 | Other | Overhead | No |  |  | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-239 | 2019 | 9 | 1 | 21 | 34 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-01 21:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-03 | 6:42 | 39.2219 | -121.4482 |  | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 152331108 |  | 12000 | Conductor | Overhead | Yes | 43711 | 0.27917 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-249 | 2019 | 9 | 3 | 6 | 42 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-03 06:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-03 | 21:27 | 35.2362 | -119.5971 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Kern County FD | 100222922 |  | 21000 | Conductor | Overhead | Yes | 43711 | 0.89375 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-122 | 2019 | 9 | 3 | 21 | 27 | 19-0095018 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 3780 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-03 21:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-04 | 11:45 | 35.7759 | -119.7144 | Gun Shot | Herbaceous | 0.25 - 10 Acres | Self Extinguished |  | 100172031 |  | 21000 | Conductor | Overhead | Yes | 43712 | 0.48958 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-123 | 2019 | 9 | 4 | 11 | 45 | 19-0095229 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 11531 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-04 11:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-05 | 13:53 | 36.166 | -120.2552 |  | Agriculture | 10 - 100 Acres | Cal Fire |  | 100717742 |  | 12000 | Pole | Overhead | Yes | 43713 | 0.57847 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-295 | 2019 | 9 | 5 | 13 | 53 | 19-0095727 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 18767 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-05 13:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-05 | 23:02 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire | California Department of Forestry | 101670112 |  | 12000 | Fuse | Overhead | Yes | 43713 | 0.95972 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-388 | 2019 | 9 | 5 | 23 | 2 | 19-0095858 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 17920 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-05 23:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-06 | 19:16 | 38.904 | -121.2123 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 153701101 |  | 12000 | Conductor | Overhead | Yes | 43714 | 0.80278 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-347 | 2019 | 9 | 6 | 19 | 16 | 19-0096284 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1764 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-06 19:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-06 | 8:55 | 34.8937 | -120.301 |  | Barren/Other | 1 meter - < 3 meters | Fire Dept | Santa Barbara County FD | C921 |  | 12000 | Capacitor Bank | Overhead | Yes | 43714 | 0.37153 | Equipment - PG&E | Capacitor Bank |  |  |  |  | Other/Unknown | 2019-106 | 2019 | 9 | 6 | 8 | 55 | 19-0095977 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2970 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-06 08:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-06 | 12:34 | 40.0698 | -122.2315 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 162 |  | 12000 | Capacitor Bank | Underbuild | No |  |  | Equipment - PG&E | Capacitor Bank |  |  |  |  | no-match | 2019-105 | 2019 | 9 | 6 | 12 | 34 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-06 12:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-07 | 15:07 | 36.7604 | -119.7962 | Vegetation | Urban | 1 meter - < 3 meters | Fire Dept | Fresno FD | 100861440 |  | 12000 | Conductor | Overhead | Yes | 43715 | 0.62986 | Vegetation |  | Veg. contact | Electric Facility |  |  | Grow Into | 2019-413 | 2019 | 9 | 7 | 15 | 7 | 19-0096452 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Grow Into | 7395 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-07 15:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-07 | 11:42 | 38.8938 | -121.3586 | Contact with High Voltage, 3rd party | Agriculture | 0.25 - 10 Acres | Fire Dept | Lincoln FD | 153701105-2101075312{1276} | Yes | 12000 | Conductor | Overhead | Yes | 43715 | 0.4875 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-20 | 2019 | 9 | 7 | 11 | 42 | 19-0096402 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 6900 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-07 11:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-07 | 16:03 | 37.7904 | -121.2306 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Manteca City FD | 162611706 |  | 17000 | Conductor | Overhead | Yes | 43715 | 0.66875 | Vegetation |  | Veg. contact |  |  |  | no-match | 2019-410 | 2019 | 9 | 7 | 16 | 3 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-07 16:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-07 | 17:25 | 39.0167 | -122.9113 |  | Urban | 1 meter - < 3 meters | Fire Dept | Lakeport FD | Unknown |  | 12000 | Conductor | Overhead | Yes | 43715 | 0.72569 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-129 | 2019 | 9 | 7 | 17 | 25 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-07 17:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-07 | 19:09 | 36.8446 | -119.5391 | Vegetation | Agriculture | 0.25 - 10 Acres | Cal Fire |  | R1426 |  | 12000 | Conductor | Overhead | Yes | 43715 | 0.79792 | Vegetation |  | Veg. contact |  |  |  | Branch (Not overhanging, Distance Unknown) | 2019-402 | 2019 | 9 | 7 | 19 | 9 | 19-0096479 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 48705 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-07 19:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-08 | 16:08 | 39.7537 | -121.919 | Bird Found | Agriculture | 0.25 - 10 Acres | Fire Dept | Butte County FD | 1104/2 |  | 12000 | Conductor | Overhead | Yes | 43716 | 0.67222 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-63 | 2019 | 9 | 8 | 16 | 8 | 19-0096585 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 70204 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-08 16:08:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-08 | 12:14 | 35.4159 | -119.0403 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Kern County FD | 252721109 |  | 12000 | Conductor | Overhead | Yes | 43716 | 0.50972 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-286 | 2019 | 9 | 8 | 12 | 14 | 19-0096565 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2358 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-08 12:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-09 | 12:38 | 37.7183 | -122.4119 | Metallic Balloon | Urban | 0.25 - 10 Acres | Fire Dept | San Francisco FD | 2210 |  | 12000 | Conductor | Overhead | Yes | 43717 | 0.52639 | Contact - 3rd Party |  | Balloon contact | Electric Facility | Human Error |  | Other/Unknown | 2019-236 | 2019 | 9 | 9 | 12 | 38 | 19-0096832 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 26703 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-09 12:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-09 | 12:35 | 35.6959 | -120.6808 | Bird Found | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 4Bk0909191234 |  | 12000 | Fuse | Overhead | Yes | 43717 | 0.52431 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-45 | 2019 | 9 | 9 | 12 | 35 | 19-0096890 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 5148 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-09 12:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-10 | 7:13 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 82841102 |  | 12000 | Conductor | Overhead | Yes | 43718 | 0.30069 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-369 | 2019 | 9 | 10 | 7 | 13 | 19-0097264 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 23500 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-10 07:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-10 | 15:03 | 36.4311 | -119.6993 |  | Agriculture | 1 meter - < 3 meters | Fire Dept | Fresno FD | Unknown |  | 12000 | Conductor | Overhead | Yes | 43718 | 0.62708 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-296 | 2019 | 9 | 10 | 15 | 3 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-10 15:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-11 | 12:57 | 37.6093 | -122.397 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | North County FD | Lr76108 |  | 12000 | Recloser | Overhead | No |  |  | Equipment - PG&E | Recloser |  |  |  |  | no-match | 2019-152 | 2019 | 9 | 11 | 12 | 57 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-11 12:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-11 | 17:13 | 35.7177 | -119.3838 |  | Agriculture | 1 meter - < 3 meters | Fire Dept | Kern County FD | 7072 |  | 12000 | Fuse | Overhead | Yes | 43719 | 0.71736 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-175 | 2019 | 9 | 11 | 17 | 13 | 19-0097980 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 930 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-11 17:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-11 | 18:28 | 35.8493 | -120.065 | Bird Found | Herbaceous | 100+ Acres | Cal Fire |  | 416842619006 |  | 12000 | Transformer | Overhead | Yes | 43719 | 0.76944 | Contact - Animal - Other |  | Contact from Object - Other | Electric Facility | Animal Contact |  | no-match | 2019-59 | 2019 | 9 | 11 | 18 | 28 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-11 18:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-11 | 21:03 | 38.3132 | -120.9809 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 163341103 |  | 12000 | Conductor | Overhead | Yes | 43719 | 0.87708 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-370 | 2019 | 9 | 11 | 21 | 3 | 19-0098003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25994 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-11 21:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-11 | 18:56 | 37.9937 | -122.137 | Bird Found | Hardwood Woodland | Other | Unknown |  | Unknown |  | 115000 | Other | Overhead | Yes | 43719 | 0.78889 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-42 | 2019 | 9 | 11 | 18 | 56 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-11 18:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-12 | 14:25 | 37.3144 | -122.1865 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 024131103 |  | 12000 | Conductor | Overhead | Yes | 43720 | 0.60069 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-217 | 2019 | 9 | 12 | 14 | 25 | 19-0098386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 89097 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-12 14:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-13 | 6:30 | 37.3348 | -121.7716 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 83392110 |  | 21000 | Splice/Clamp/Connector | Overhead | Yes | 43721 | 0.27083 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-444 | 2019 | 9 | 13 | 6 | 30 | 19-0098560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 35534 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-13 06:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-13 | 16:38 | 37.4256 | -121.9245 | Aircraft | Urban | 0.25 - 10 Acres | Fire Dept | Milpitas FD | 2103/2 |  | 21000 | Conductor | Overhead | Yes | 43721 | 0.69306 | Contact - 3rd Party |  | Vehicle contact |  | Human Error |  | Other/Unknown | 2019-140 | 2019 | 9 | 13 | 16 | 38 | 19-0098969 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 7341 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-13 16:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-13 | 15:47 | 37.6446 | -122.1187 |  | Urban | 1 meter - < 3 meters | Fire Dept | Alameda County FD | 50325 |  | 12000 | Transformer | Overhead | Yes | 43721 | 0.65764 | Equipment - PG&E | Transformer |  |  |  |  | Other/Unknown | 2019-244 | 2019 | 9 | 13 | 15 | 47 | 19-0098974 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 13198 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-13 15:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-13 | 20:26 | 40.7973 | -124.1968 | Vegetation | Urban | 0.25 - 10 Acres | Fire Dept | Samoa FD | 192451104 |  | 12000 | Conductor | Overhead | Yes | 43721 | 0.85139 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-365 | 2019 | 9 | 13 | 20 | 26 | 19-0099034 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 12570 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-13 20:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-13 | 8:53 | 39.0754 | -121.1717 | Bird Found | Herbaceous | 0.25 - 10 Acres | Fire Dept | Consolidated FD | Etr0913190810 |  | 12000 | Other | Overhead | Yes | 43721 | 0.37014 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-46 | 2019 | 9 | 13 | 8 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-13 08:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-13 | 10:30 | 36.9041 | -121.4034 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Hollister FD | 9019 |  | 21000 | Conductor | Overhead | Yes | 43721 | 0.4375 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-43 | 2019 | 9 | 13 | 10 | 30 | 19-0098731 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 3417 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-13 10:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-15 | 12:38 | 38.1194 | -120.8013 | Vehicle | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103959405 |  | 12000 | Pole | Overhead | Yes | 43723 | 0.52639 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-118 | 2019 | 9 | 15 | 12 | 38 | 19-0099234 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 5378 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-15 12:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-15 | 12:58 | 38.1057 | -122.6456 | Vegetation | Urban | 0.25 - 10 Acres | Fire Dept | Novato FD | 103958177 |  | 12000 | Pole | Overhead | Yes | 43723 | 0.54028 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (slight defect) | 2019-403 | 2019 | 9 | 15 | 12 | 58 | 19-0099253 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 21038 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-15 12:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-16 | 14:39 | 37.3762 | -119.8729 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 254452102 |  | 21000 | Conductor | Overhead | Yes | 43724 | 0.61042 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-417 | 2019 | 9 | 16 | 14 | 39 | 19-0099772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 121254 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-16 14:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-17 | 13:21 | 38.6018 | -121.6928 | Vehicle | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Davis FD | 62041106 |  | 12000 | Conductor | Overhead | Yes | 43725 | 0.55625 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-145 | 2019 | 9 | 17 | 13 | 21 | 19-0100275 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 6393 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-17 13:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-17 | 14:11 | 38.8066 | -121.308 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Unknown |  | Unknown |  | 115000 | Other | Overhead | Yes | 43725 | 0.59097 | Contact - Animal - Other |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-60 | 2019 | 9 | 17 | 14 | 11 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-17 14:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-20 | 10:58 | 39.9804 | -122.1407 | Vegetation | Urban | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Service Conductor | Overhead | Yes | 43728 | 0.45694 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-353 | 2019 | 9 | 20 | 10 | 58 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-20 10:58:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-22 | 11:45 | 38.6039 | -121.0591 |  | Urban | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 21000 | Other | Pad mount | Yes | 43730 | 0.48958 | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-327 | 2019 | 9 | 22 | 11 | 45 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-22 11:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-22 | 11:34 | 36.0264 | -121.2508 | Vegetation | Herbaceous | 0.25 - 10 Acres | Fire Dept | Unknown | 103958188 |  | 12000 | Pole | Overhead | Yes | 43730 | 0.48194 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (Moderate-Severe defect) | 2019-215 | 2019 | 9 | 22 | 11 | 34 | 19-0102235 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2721 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-22 11:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-22 | 11:56 | 37.5168 | -119.9159 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103967994 |  | 21000 | Pole | Overhead | Yes | 43730 | 0.49722 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-452 | 2019 | 9 | 22 | 11 | 56 | 19-0102232 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 133232 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-22 11:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-23 | 16:04 | 37.8799 | -122.0789 | Animal Found | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 1105/2 |  | 12000 | Pothead | Overhead | Yes | 43731 | 0.66944 | Contact - Animal - Other |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-22 | 2019 | 9 | 23 | 16 | 4 | 19-0102630 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 52593 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-23 16:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-23 | 16:39 | 38.6299 | -121.7109 |  | Agriculture | 0.25 - 10 Acres | Fire Dept | Woodland FD | 62041106 |  | 12000 | Conductor | Overhead | No |  |  | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | no-match | 2019-12 | 2019 | 9 | 23 | 16 | 39 | No ILIS or TOTL available | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-23 16:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-23 | 19:13 | 38.4316 | -121.9155 | Bird Found | Urban | 3 meters - 0.25 Acres | Fire Dept | Dixon FD | 6Pk0923191913 |  | 12000 | Conductor | Overhead | Yes | 43731 | 0.80069 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-167 | 2019 | 9 | 23 | 19 | 13 | 19-0102726 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 2795 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-23 19:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-24 | 13:13 | 38.4912 | -122.4797 | Bird Found | Urban | 3 meters - 0.25 Acres | Fire Dept | Saint Helena FD | Silverado 2103 |  | 21000 | Crossarm | Overhead | Yes | 43732 | 0.55069 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-41 | 2019 | 9 | 24 | 13 | 13 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-24 13:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-24 | 13:59 | 35.1314 | -119.4617 |  | Urban | 1 meter - < 3 meters | Fire Dept | Kern County FD | 252081108 |  | 12000 | Conductor | Overhead | Yes | 43732 | 0.58264 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-92 | 2019 | 9 | 24 | 13 | 59 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-24 13:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-25 | 9:45 | 38.7951 | -121.4756 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | Fuses At C943 |  | 12000 | Fuse | Overhead | No |  |  | Equipment - PG&E | Fuse |  |  |  |  | no-match | 2019-278 | 2019 | 9 | 25 | 9 | 45 | No ILIS or TOTL available | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-25 09:45:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-26 | 11:12 | 38.5895 | -121.698 |  | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Woodland FD | Cutouts And Jumpers At 9127 |  | 12000 | Conductor | Overhead | Yes | 43734 | 0.46667 | Equipment - PG&E | [5 empty] | no-match | 2019-171 | 2019 | 9 | 26 | 11 | 12 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-26 11:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-26 | 13:47 | 38.1123 | -122.2215 | Vegetation | Urban | 0.25 - 10 Acres | Fire Dept | Vallejo FD | Unknown |  | 12000 | Secondary | Overhead | Yes | 43734 | 0.57431 | Vegetation |  | Veg. contact |  |  |  | no-match | 2019-411 | 2019 | 9 | 26 | 13 | 47 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-26 13:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-26 | 14:12 | 36.9517 | -121.8278 | Vegetation | Shrub | 1 meter - < 3 meters | Cal Fire |  | 2287 |  | 21000 | Conductor | Overhead | Yes | 43734 | 0.59167 | Vegetation |  | Veg. contact |  |  |  | Branch (OverHanging) | 2019-352 | 2019 | 9 | 26 | 14 | 12 | 19-0104163 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 2856 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-26 14:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-26 | 17:54 | 38.0876 | -121.5266 |  | Urban | 0.25 - 10 Acres | Fire Dept | Unknown | 103958238 |  | 21000 | Pole | Overhead | Yes | 43734 | 0.74583 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-255 | 2019 | 9 | 26 | 17 | 54 | 19-0104275 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2556 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-26 17:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-27 | 10:30 | 36.5336 | -121.1464 | Vegetation | Barren/Other | 0.25 - 10 Acres | Cal Fire |  | 182492105 |  | 21000 | Conductor | Overhead | Yes | 43735 | 0.4375 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-359 | 2019 | 9 | 27 | 10 | 30 | 19-0104536 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20631 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-27 10:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-27 | 14:25 | 38.4845 | -121.7229 | Vehicle | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Unknown | 103959408 |  | 12000 | Pole | Overhead | Yes | 43735 | 0.60069 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-325 | 2019 | 9 | 27 | 14 | 25 | 19-0104713 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 29522 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-27 14:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-28 | 13:16 | 37.2553 | -119.5057 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 252531103 |  | 12000 | Conductor | Overhead | Yes | 43736 | 0.55278 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-36 | 2019 | 9 | 28 | 13 | 16 | 19-0104972 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1296 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-28 13:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-28 | 16:18 | 38.23 | -122.4593 |  | Urban | 0.25 - 10 Acres | Cal Fire |  | 103958771 |  | 12000 | Pole | Overhead | Yes | 43736 | 0.67917 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-04 | 2019 | 9 | 28 | 16 | 18 | 19-0105009 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1074 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-28 16:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-28 | 19:24 | 39.6135 | -121.7083 |  | Herbaceous | 100+ Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | Yes | 43736 | 0.80833 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-94 | 2019 | 9 | 28 | 19 | 24 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-09-28 19:24:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-29 | 13:30 | 39.5513 | -121.8104 |  | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 102171101 |  | 12000 | Conductor | Overhead | Yes | 43737 | 0.5625 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-247 | 2019 | 9 | 29 | 13 | 30 | 19-0105169 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 16704 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-29 13:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-29 | 15:04 | 36.2381 | -120.3958 |  | Herbaceous | 0.25 - 10 Acres | Cal Fire | Coalinga FD | 9000 |  | 12000 | Conductor | Overhead | Yes | 43737 | 0.62778 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-284 | 2019 | 9 | 29 | 15 | 4 | 19-0105188 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 8595 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-29 15:04:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-29 | 20:06 | 37.5448 | -121.8964 | Metallic Balloon | Urban | 0.25 - 10 Acres | Cal Fire |  | 8015 |  | 12000 | Insulator | Overhead | Yes | 43737 | 0.8375 | Contact - 3rd Party |  | Balloon contact |  | Human Error |  | Other/Unknown | 2019-208 | 2019 | 9 | 29 | 20 | 6 | 19-0105242 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 33476 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-29 20:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-29 | 20:29 | 36.2994 | -119.7694 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Lemoore FD | 253601105 |  | 12000 | Conductor | Overhead | Yes | 43737 | 0.85347 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-451 | 2019 | 9 | 29 | 20 | 29 | 19-0105204 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 19923 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-29 20:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-29 | 22:06 | 37.0642 | -119.9769 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire | Madera FD | 321533520550 |  | 12000 | Transformer | Overhead | Yes | 43737 | 0.92083 | Equipment - PG&E | Transformer |  |  |  |  | Other/Unknown | 2019-329 | 2019 | 9 | 29 | 22 | 6 | 19-0105270 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 24252 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-29 22:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-09-30 | 14:29 | 34.6139 | -120.1799 | Contact with High Voltage, 3rd party | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 183041102 |  | 12000 | Conductor | Overhead | Yes | 43738 | 0.60347 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-13 | 2019 | 9 | 30 | 14 | 29 | 19-0105582 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 4080 | 0 | NA | <25mph | <15mph | #REF! | 2019-09-30 14:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-02 | 17:17 | 38.4306 | -122.811 |  | Herbaceous | 0.25 - 10 Acres | Fire Dept | Unknown | 7Nr1002191710 |  | 12000 | Conductor | Overhead | Yes | 43740 | 0.72014 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-169 | 2019 | 10 | 2 | 17 | 17 | 19-0106778 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 444 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-02 17:17:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-02 | 19:15 | 36.9954 | -120 | Vehicle | Urban | 1 meter - < 3 meters | Cal Fire |  | 321463218071 |  | 12000 | Transformer | Overhead | Yes | 43740 | 0.80208 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-119 | 2019 | 10 | 2 | 19 | 15 | 19-0106784 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 5054 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-02 19:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-03 | 16:28 | 37.1978 | -120.0143 |  | Herbaceous | 10 - 100 Acres | Cal Fire |  | 101024245 |  | 12000 | Insulator | Overhead | No |  |  | Equipment - PG&E | Insulator |  |  |  |  | no-match | 2019-206 | 2019 | 10 | 3 | 16 | 28 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-03 16:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-04 | 19:07 | 40.4964 | -122.0448 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | Yes | 43742 | 0.79653 | Equipment - Overloaded | Other |  |  |  |  | no-match | 2019-257 | 2019 | 10 | 4 | 19 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-04 19:07:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-05 | 5:48 | 35.2084 | -119.0068 |  | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Kern County FD | 3310 |  | 12000 | Other | Overhead | Yes | 43743 | 0.24167 | Equipment - PG&E | Other |  |  |  |  | Other/Unknown | 2019-101 | 2019 | 10 | 5 | 5 | 48 | 19-0107809 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 3186 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-05 05:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-05 | 16:46 | 34.8695 | -120.2472 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire |  | 182811103 |  | 12000 | Conductor | Overhead | Yes | 43743 | 0.69861 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-430 | 2019 | 10 | 5 | 16 | 46 | 19-0107961 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 125120 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-05 16:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-06 | 20:30 | 37.7099 | -122.1758 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Alameda FD | 315155844491 |  | 12000 | Transformer | Overhead | Yes | 43744 | 0.85417 | Equipment - PG&E | Transformer |  |  |  |  | Other/Unknown | 2019-328 | 2019 | 10 | 6 | 20 | 30 | 19-0108128 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 692 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-06 20:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-07 | 9:27 | 38.1048 | -122.8266 |  | Urban | 1 meter - < 3 meters | Unknown |  | Unknown |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43745 | 0.39375 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | no-match | 2019-254 | 2019 | 10 | 7 | 9 | 27 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-07 09:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-07 | 18:47 | 37.71 | -120.5881 | Contact with High Voltage, 3rd party | Herbaceous | 10 - 100 Acres | Cal Fire |  | 163711708 |  | 17000 | Conductor | Overhead | Yes | 43745 | 0.78264 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-21 | 2019 | 10 | 7 | 18 | 47 | 19-0108473 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 94268 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-07 18:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-08 | 17:59 | 35.2979 | -120.4868 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 182541103 |  | 12000 | Conductor | Overhead | Yes | 43746 | 0.74931 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-207 | 2019 | 10 | 8 | 17 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-08 17:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-08 | 19:02 | 38.5896 | -121.701 |  | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Davis FD | 44167967 |  | 12000 | Recloser | Overhead | No |  |  | Equipment - PG&E | Recloser |  |  |  |  | no-match | 2019-226 | 2019 | 10 | 8 | 19 | 2 | No ILIS or TOTL available | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-08 19:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-10 | 3:26 | 38.3554 | -121.8698 |  | Agriculture | 0.25 - 10 Acres | Fire Dept | Vacaville FD | 63642105 |  | 21000 | Conductor | Overhead | Yes | 43748 | 0.14306 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-184 | 2019 | 10 | 10 | 3 | 26 | 19-0109874 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 38268 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-10 03:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-10 | 6:11 | 37.3932 | -121.8215 |  | Urban | 1 meter - < 3 meters | Fire Dept | San Jose FD | 83531103 |  | 12000 | Conductor | Overhead | Yes | 43748 | 0.25764 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-181 | 2019 | 10 | 10 | 6 | 11 | 19-0109887 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 288442 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-10 06:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-10 | 14:25 | 37.3115 | -121.0018 |  | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Newman FD | 162741106 |  | 12000 | Conductor | Overhead | Yes | 43748 | 0.60069 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-253 | 2019 | 10 | 10 | 14 | 25 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-10 14:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-10 | 16:29 | 37.4979 | -122.4627 |  | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 24101102 |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-221 | 2019 | 10 | 10 | 16 | 29 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-10 16:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-10 | 19:43 | 39.858 | -122.1972 |  | Herbaceous | 1 meter - < 3 meters | Cal Fire |  | 85203 |  | 12000 | Conductor | Overhead | Yes | 43748 | 0.82153 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-18 | 2019 | 10 | 10 | 19 | 43 | 19-0110281 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 9804 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-10 19:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-10 | 11:53 | 37.6888 | -122.4263 | Bird Found | Shrub | Structure Only | Cal Fire |  | Unknown |  | 115000 | Conductor | Overhead | No |  |  | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | no-match | 2019-426 | 2019 | 10 | 10 | 11 | 53 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-10 11:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-13 | 23:15 | 37.096 | -121.6468 | Vegetation | Urban | 1 meter - < 3 meters | Fire Dept | Morgan Hill FD | 083242105 |  | 21000 | Conductor | Overhead | Yes | 43751 | 0.96875 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-360 | 2019 | 10 | 13 | 23 | 15 | 19-0110996 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 6030 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-13 23:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-14 | 3:27 | 37.2886 | -120.2611 | Bird Found | Agriculture | 3 meters - 0.25 Acres | Employee |  | 5Tr1014190320 |  | 12000 | Conductor | Overhead | Yes | 43752 | 0.14375 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-54 | 2019 | 10 | 14 | 3 | 27 | 19-0111012 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 13391 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-14 03:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-15 | 0:41 | 37.3237 | -119.6173 |  | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | Circuit 254432102 |  | 21000 | Insulator | Overhead | Yes | 43753 | 0.028472 | Equipment - PG&E | Insulator |  |  |  |  | Other/Unknown | 2019-168 | 2019 | 10 | 15 | 0 | 41 | 19-0111571 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 741 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-15 00:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-17 | 19:44 | 37.6494 | -120.357 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 5Tr1017191903 |  | 12000 | Conductor | Overhead | Yes | 43755 | 0.82222 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-423 | 2019 | 10 | 17 | 19 | 44 | 19-0113175 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 10105 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-17 19:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-18 | 9:59 | 36.2166 | -120.4787 |  | Herbaceous | 10 - 100 Acres | Cal Fire |  | 4Tl1018190957 |  | 12000 | Booster | Overhead | Yes | 43756 | 0.41597 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-132 | 2019 | 10 | 18 | 9 | 59 | 19-0113385 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 24459 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-18 09:59:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-19 | 16:05 | 37.2133 | -121.7767 | Metallic Balloon | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 18073 |  | 12000 | Fuse | Overhead | Yes | 43757 | 0.67014 | Contact - 3rd Party |  | Balloon contact |  | Human Error |  | Other/Unknown | 2019-235 | 2019 | 10 | 19 | 16 | 5 | 19-0113733 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 1027 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-19 16:05:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-20 | 12:11 | 35.3764 | -118.9493 | Metallic Balloon | Urban | 1 meter - < 3 meters | Fire Dept | Unknown | 1101/2 |  | 12000 | Fuse | Overhead | Yes | 43758 | 0.50764 | Contact - 3rd Party |  | Balloon contact |  | Human Error |  | Other/Unknown | 2019-229 | 2019 | 10 | 20 | 12 | 11 | 19-0113818 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | 45771 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-20 12:11:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-20 | 14:23 | 34.8874 | -120.3832 |  | Barren/Other | 3 meters - 0.25 Acres | Fire Dept | Unknown | 7539 |  | 12000 | Fuse | Overhead | Yes | 43758 | 0.59931 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-71 | 2019 | 10 | 20 | 14 | 23 | 19-0113833 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 66 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-20 14:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-20 | 17:09 | 37.1585 | -122.1339 |  | Conifer Forest | 1 meter - < 3 meters | Employee |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match |  | 2019 | 10 | 20 | 17 | 9 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-20 17:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-22 | 15:06 | 36.7865 | -119.5598 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Fresno County FD | Unknown |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43760 | 0.62917 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | no-match | 2019-155 | 2019 | 10 | 22 | 15 | 6 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-22 15:06:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-22 | 14:44 | 35.7336 | -119.6897 | Bird Found | Urban | 0.25 - 10 Acres | Fire Dept | Unknown | 1139 |  | 21000 | Pole | Overhead | Yes | 43760 | 0.61389 | Contact - Animal - Other |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-133 | 2019 | 10 | 22 | 14 | 44 | 19-0114679 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 816 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-22 14:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-23 | 21:27 | 38.7959 | -122.7673 |  | Herbaceous | 100+ Acres | Cal Fire |  | 001/006 |  | 230000 | Jumper | Overhead | Yes | 43761 | 0.88819 | Under Investigation | Jumper |  |  |  | This ignition relates to the Kincade Fire, which is reported in compliance with D.19-05-037. The origin and cause of the Kincade Fire is under investigation by CAL FIRE and PG&E. At this time, PG&E has not formed a conclusion about the origin or cause of the Kincade Fire. | no-match |  | 2019 | 10 | 23 | 21 | 27 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-23 21:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-23 | 20:54 | 39.2035 | -121.9517 | Vegetation | Agriculture | 3 meters - 0.25 Acres | Fire Dept | Sacramento FD | 62021103 |  | 12000 | Conductor | Overhead | Yes | 43761 | 0.87083 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-364 | 2019 | 10 | 23 | 20 | 54 | 19-0115360 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1119 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-23 20:54:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-24 | 11:44 | 37.9754 | -122.322 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Richmond FD | 14371105 |  | 12000 | Conductor | Overhead | Yes | 43762 | 0.48889 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-436 | 2019 | 10 | 24 | 11 | 44 | No ILIS or TOTL available | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-24 11:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-24 | 7:38 | 36.9316 | -121.4759 | Vehicle | Barren/Other | 3 meters - 0.25 Acres | Fire Dept | Hollister FD | 103963645, 103963645 |  | 21000 | Pole | Overhead | Yes | 43762 | 0.31806 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-115 | 2019 | 10 | 24 | 7 | 38 | 19-0115405 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 46947 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-24 07:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-24 | 5:44 | 38.323 | -122.4758 | Vegetation | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 103946269 |  | 12000 | Pole | Overhead | Yes | 43762 | 0.23889 | Vegetation |  | Veg. contact | Pole |  |  | Other/Unknown | 2019-216 | 2019 | 10 | 24 | 5 | 44 | 19-0115396 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 281002 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-24 05:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-25 | 13:18 | 38.2143 | -121.9704 |  | Herbaceous | 0.25 - 10 Acres | Fire Dept | Suisun FD | 83999 |  | 21000 | Pole | Overhead | No |  |  | Contact - Animal - Other | Pole | Animal contact | Pole |  |  | no-match | 2019-231 | 2019 | 10 | 25 | 13 | 18 | No ILIS or TOTL available | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-25 13:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-25 | 11:37 | 35.321 | -119.3413 |  | Agriculture | 0.25 - 10 Acres | Fire Dept | Kern COunty FD | 103963804 |  | 12000 | Pole | Overhead | Yes | 43763 | 0.48403 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-270 | 2019 | 10 | 25 | 11 | 37 | 19-0116091 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 3230 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-25 11:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-26 | 23:27 | 40.1674 | -122.2467 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Red Bluff FD | 119312130404 |  | 12000 | Transformer | Overhead | Yes | 43764 | 0.97708 | Equipment - PG&E | Transformer |  |  |  |  | Other/Unknown | 2019-78 | 2019 | 10 | 26 | 23 | 27 | 19-0117061 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 4970 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-26 23:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-26 | 4:26 | 36.4892 | -119.7909 | Vehicle | Agriculture | 3 meters - 0.25 Acres | Fire Dept | unknown | 103960407 |  | 12000 | Pole | Overhead | Yes | 43764 | 0.18472 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-116 | 2019 | 10 | 26 | 4 | 26 | 19-0116761 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 58422 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-26 04:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 13:30 | 37.8997 | -122.0908 |  | Urban | 0.25 - 10 Acres | Fire Dept | Contra Costa FD | 100477289 |  | 12000 | Pole | Overhead | Yes | 43765 | 0.5625 | Equipment - PG&E | Pole |  |  |  |  | no-match | 2019-462 | 2019 | 10 | 27 | 13 | 30 | No ILIS or TOTL available | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 13:30:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 14:55 | 37.4345 | -121.9136 |  | Urban | 0.25 - 10 Acres | Fire Dept | Unknown | 689653 |  | 21000 | Conductor | Overhead | Yes | 43765 | 0.62153 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-438 | 2019 | 10 | 27 | 14 | 55 | 19-0117654 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 2076658 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 14:55:00 | #REF! | 0 | TRUE | <25mph
PG&E | 2019-10-27 | 14:55 | 37.5356 | -121.9516 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Unknown | 14351109 |  | 12000 | Conductor | Overhead | Yes | 43765 | 0.62153 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-409 | 2019 | 10 | 27 | 14 | 55 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 14:55:00 | #REF! | 0 | TRUE | <25mph
PG&E | 2019-10-27 | 14:34 | 38.7772 | -121.6883 | Vegetation | Urban | 0.25 - 10 Acres | Fire Dept | Knights Landing FD | 62721102 |  | 12000 | Conductor | Overhead | Yes | 43765 | 0.60694 | Vegetation |  | Veg. contact |  |  |  | Dead | 2019-366 | 2019 | 10 | 27 | 14 | 34 | 19-0117508 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 47943 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 14:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 17:12 | 37.3115 | -121.9996 | Vegetation | Urban | 1 meter - < 3 meters | Fire Dept | Santa Clara County FD | 83371114 |  | 12000 | Transformer | Overhead | Yes | 43765 | 0.71667 | Vegetation |  | Veg. contact |  |  |  | Other/Unknown | 2019-232 | 2019 | 10 | 27 | 17 | 12 | 19-0117569 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 13400 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 17:12:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 15:38 | 37.8909 | -122.0941 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Contra Costa County FD | Unknown | Yes | 12000 | Conductor | Overhead | No |  |  | Contact - 3rd Party | Conductor | Contact from Object - Other | Electric Facility | Human Error |  | no-match | 2019-240 | 2019 | 10 | 27 | 15 | 38 | No ILIS or TOTL available | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 15:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 15:28 | 36.785 | -121.6509 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 182961107 |  | 12000 | Conductor | Overhead | Yes | 43765 | 0.64444 | Vegetation |  | Veg. contact |  |  |  | Fell into (slight defect) | 2019-348 | 2019 | 10 | 27 | 15 | 28 | 19-0117555 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3172 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 15:28:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 16:15 | 37.3807 | -121.9017 | Metallic Balloon | Urban | 3 meters - 0.25 Acres | Fire Dept | Unknown | X2068 | Yes | 21000 | Conductor | Overhead | Yes | 43765 | 0.67708 | Contact - 3rd Party |  | Balloon contact |  | Human Error |  | Other/Unknown | 2019-237 | 2019 | 10 | 27 | 16 | 15 | 19-0117606 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 16:15:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 15:01 | 37.9383 | -121.2469 | Vegetation | Urban | 1 meter - < 3 meters | Fire Dept | Stockton FD | 163481114 |  | 12000 | Conductor | Overhead | Yes | 43765 | 0.62569 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-412 | 2019 | 10 | 27 | 15 | 1 | No ILIS or TOTL available | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 15:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 14:41 | 36.991 | -120.623 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Merced County FD | 254041101 |  | 12000 | Conductor | Overhead | Yes | 43765 | 0.61181 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-415 | 2019 | 10 | 27 | 14 | 41 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 14:41:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 14:48 | 37.2767 | -121.8146 | Vegetation | Urban | 0.25 - 10 Acres | Fire Dept | Unknown | 83912109 |  | 21000 | Conductor | Overhead | Yes | 43765 | 0.61667 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-414 | 2019 | 10 | 27 | 14 | 48 | 19-0117482 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 108547 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 14:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 13:32 | 37.9666 | -121.3462 |  | Urban | 1 meter - < 3 meters | Fire Dept | Stockton FD | Unknown |  | 12000 | Conductor | Overhead | Yes | 43765 | 0.56389 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-143 | 2019 | 10 | 27 | 13 | 32 | No ILIS or TOTL available | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 13:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 11:01 | 37.5973 | -122.0616 | Vegetation | Urban | 3 meters - 0.25 Acres | Self Extinguished |  | 100936457 |  | 12000 | Other | Overhead | Yes | 43765 | 0.45903 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-337 | 2019 | 10 | 27 | 11 | 1 | 19-0117344 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 48488 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 11:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 9:44 | 36.988 | -121.9395 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Unknown | 83252109 |  | 21000 | Conductor | Overhead | Yes | 43765 | 0.40556 | Other Fire: Non-PG&E related | [5 empty] | Other/Unknown | 2019-405 | 2019 | 10 | 27 | 9 | 44 | 19-0116039 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip failure | Conductor | 657272 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 09:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 6:34 | 38.7467 | -122.1492 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire | Esparato FD | 103779734 |  | 21000 | Conductor | Overhead | Yes | 43765 | 0.27361 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-446 | 2019 | 10 | 27 | 6 | 34 | 19-0117171 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 789429 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 06:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 7:27 | 37.9932 | -121.6412 |  | Urban | 10 - 100 Acres | Cal Fire | Contra Costa County FD | 014592112-2101053518{K504R} |  | 21000 | Line Recloser | Overhead | Yes | 43765 | 0.31042 | Equipment - PG&E | Line Recloser |  |  |  |  | Other/Unknown | 2019-262 | 2019 | 10 | 27 | 7 | 27 | 19-0117167 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1552280 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 07:27:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 14:56 | 38.1563 | -121.9761 |  | Urban | 100+ Acres | Fire Dept | Suisun FD | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-463 | 2019 | 10 | 27 | 14 | 56 | No ILIS or TOTL available | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 14:56:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 5:38 | 39.1968 | -121.9327 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | Unknown | 101633101 |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-363 | 2019 | 10 | 27 | 5 | 38 | No ILIS or TOTL available | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 05:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 3:16 | 39.5603 | -122.1068 | Vegetation | Agriculture | 0.25 - 10 Acres | Self Extinguished |  | 103017810 |  | 12000 | Pole | Overhead | Yes | 43765 | 0.13611 | Vegetation |  | Veg. contact | Pole |  |  | Branch (Not overhanging, Distance Unknown) | 2019-368 | 2019 | 10 | 27 | 3 | 16 | 19-0117124 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 8215 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 03:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 1:42 | 39.1737 | -122.1334 |  | Urban | 10 - 100 Acres | Fire Dept | Williams FD | 101629105 |  | 12000 | Pole | Overhead | Yes | 43765 | 0.070833 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-91 | 2019 | 10 | 27 | 1 | 42 | 19-0117070 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 545704 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 01:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 2:39 | 38.1666 | -121.5968 |  | Urban | 0.25 - 10 Acres | Fire Dept | Unknown | 62462223 |  | 21000 | Other | Overhead | Yes | 43765 | 0.11042 | Equipment - PG&E | Other |  |  |  |  | Other/Unknown | 2019-279 | 2019 | 10 | 27 | 2 | 39 | 19-0117150 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 196168 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 02:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 2:14 | 39.5268 | -122.3642 | Vegetation | Herbaceous | 10 - 100 Acres | Cal Fire |  | 100414823 |  | 21000 | Pole | Overhead | Yes | 43765 | 0.093056 | Vegetation |  | Veg. contact | Pole |  |  | Branch (Not overhanging, Distance Unknown) | 2019-350 | 2019 | 10 | 27 | 2 | 14 | 19-0117106 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 26316 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 02:14:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-27 | 5:35 | 38.2762 | -122.4614 |  | Urban | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-287 | 2019 | 10 | 27 | 5 | 35 | No ILIS or TOTL available | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-27 05:35:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-28 | 17:48 | 37.0309 | -121.7788 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 101682849 |  | 21000 | Conductor | Overhead | Yes | 43766 | 0.74167 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-389 | 2019 | 10 | 28 | 17 | 48 | 19-0118112 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 16698 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-28 17:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-28 | 18:46 | 38.5646 | -122.4642 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 43432104 |  | 21000 | Conductor | Overhead | Yes | 43766 | 0.78194 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-357 | 2019 | 10 | 28 | 18 | 46 | 19-0118147 | Tier 3 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 496944 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-28 18:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-28 | 7:09 | 37.7888 | -121.6212 |  | Herbaceous | 0.25 - 10 Acres | Fire Dept | Livermore FD | 163741102 |  | 12000 | Fuse | Underbuild | Yes | 43766 | 0.29792 | Equipment - PG&E | Fuse |  |  |  |  | Other/Unknown | 2019-447 | 2019 | 10 | 28 | 7 | 9 | 19-0118120 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 11047 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-28 07:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-28 | 16:51 | 38.856 | -121.7186 |  | Agriculture | 0.25 - 10 Acres | Fire Dept | Sutter County FD | 101593864 |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-271 | 2019 | 10 | 28 | 16 | 51 | No ILIS or TOTL available | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-28 16:51:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-28 | 13:00 | 39.3208 | -121.1273 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 100099164 |  | 12000 | Transformer | Overbuild | Yes | 43766 | 0.54167 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-398 | 2019 | 10 | 28 | 13 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-28 13:00:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-28 | 11:34 | 38.2115 | -121.3547 | Vegetation | Hardwood Forest | 10 - 100 Acres | Fire Dept | Woodbridge FD | 162081102 |  | 12000 | Conductor | Overhead | Yes | 43766 | 0.48194 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-339 | 2019 | 10 | 28 | 11 | 34 | 19-0117922 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 8955 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-28 11:34:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-29 | 20:40 | 37.2689 | -122.0176 | Vegetation | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 082841102-2100571264{8051} |  | 12000 | Cable | Overhead | Yes | 43767 | 0.86111 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-349 | 2019 | 10 | 29 | 20 | 40 | 19-0118769 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 8725 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-29 20:40:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-29 | 12:57 | 34.6203 | -120.1097 | Animal Found | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 6933 |  | 12000 | Other | Overhead | Yes | 43767 | 0.53958 | Contact - Animal - Other |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-300 | 2019 | 10 | 29 | 12 | 57 | 19-0118665 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 6660 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-29 12:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-29 | 3:29 | 37.0374 | -121.5207 | Animal Found | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 1471 |  | 21000 | Fuse | Overhead | Yes | 43767 | 0.14514 | Contact - Animal - Other |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-283 | 2019 | 10 | 29 | 3 | 29 | 19-0118370 | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 3294 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-29 03:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-30 | 12:03 | 35.4239 | -119.0193 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Unknown | 252721114 |  | 12000 | Conductor | Overhead | Yes | 43768 | 0.50208 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | no-match | 2019-136 | 2019 | 10 | 30 | 12 | 3 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-30 12:03:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-30 | 14:29 | 35.3939 | -118.995 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Unknown | 253371102 |  | 12000 | Secondary | Overhead | Yes | 43768 | 0.60347 | Vegetation |  | Veg. contact |  |  |  | no-match | 2019-259 | 2019 | 10 | 30 | 14 | 29 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-30 14:29:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-30 | 8:47 | 38.3612 | -121.9994 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Vacaville FD | Unknown |  | 12000 | Conductor | Overhead | Yes | 43768 | 0.36597 | Vegetation |  | Veg. contact |  |  |  | no-match | 2019-393 | 2019 | 10 | 30 | 8 | 47 | No ILIS or TOTL available | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-30 08:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-30 | 13:32 | 38.4792 | -122.0302 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 063681102 |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact |  |  |  | no-match | 2019-338 | 2019 | 10 | 30 | 13 | 32 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-30 13:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-30 | 10:02 | 35.4185 | -119.052 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Kern County FD | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-172 | 2019 | 10 | 30 | 10 | 2 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-30 10:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-31 | 21:21 | 39.661 | -120.6264 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Fire Dept | Sierra County FD | 152101101 |  | 12000 | Conductor | Overhead | Yes | 43769 | 0.88958 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-390 | 2019 | 10 | 31 | 21 | 21 | 19-0115942 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 7121279 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-31 21:21:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-31 | 17:23 | 38.0458 | -122.1905 |  | Herbaceous | 1 meter - < 3 meters | Fire Dept | Crockett FD | 13432207 |  | 21000 | Conductor | Overhead | Yes | 43769 | 0.72431 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-05 | 2019 | 10 | 31 | 17 | 23 | 19-0119756 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 138161 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-31 17:23:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-31 | 16:09 | 38.3845 | -122.1893 | Vegetation | Agriculture | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact |  |  |  | no-match | 2019-396 | 2019 | 10 | 31 | 16 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-10-31 16:09:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-10-31 | 14:57 | 37.3676 | -122.1335 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Fire Dept | Santa Clara County FD | 82161102 |  | 12000 | Conductor | Overhead | Yes | 43769 | 0.62292 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-395 | 2019 | 10 | 31 | 14 | 57 | 19-0119713 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Dead | 41751 | 0 | NA | <25mph | <15mph | #REF! | 2019-10-31 14:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-01 | 11:33 | 38.5801 | -122.5778 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire |  | 42711101 |  | 12000 | Conductor | Overhead | Yes | 43770 | 0.48125 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-367 | 2019 | 11 | 1 | 11 | 33 | 19-0118648 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3977180 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-01 11:33:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-01 | 22:43 | 34.7729 | -120.4288 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Santa Barbara County FD | Unknown |  | 12000 |  | Overhead | No |  |  | Unknown | [5 empty] | no-match | 2019-429 | 2019 | 11 | 1 | 22 | 43 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-11-01 22:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-01 | 11:57 | 37.653 | -121.6671 | Animal Found | Herbaceous | 1 meter - < 3 meters | Self Extinguished |  | 316624742194 |  | 12000 | Transformer | Overhead | Yes | 43770 | 0.49792 | Contact - Animal - Other |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-77 | 2019 | 11 | 1 | 11 | 57 | 19-0120017 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 10794 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-01 11:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-03 | 22:01 | 37.6584 | -122.0436 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | Hayward FD | 14091101 |  | 12000 | Conductor | Overhead | Yes | 43772 | 0.91736 | Equipment - Overloaded | Conductor |  |  |  |  | no-match | 2019-291 | 2019 | 11 | 3 | 22 | 1 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-11-03 22:01:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-03 | 18:26 | 36.2323 | -121.7622 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 182941102 |  | 12000 | Conductor | Overhead | Yes | 43772 | 0.76806 | Vegetation |  | Veg. contact |  |  |  | Fell into (Moderate-Severe defect) | 2019-371 | 2019 | 11 | 3 | 18 | 26 | 19-0120570 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 59211 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-03 18:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-04 | 9:48 | 38.6801 | -122.0559 | Metallic Balloon | Agriculture | 3 meters - 0.25 Acres | Cal Fire | Esparato FD | 63172101 |  | 21000 | Conductor | Overhead | No |  |  | Contact - 3rd Party |  | Balloon contact | Electric Facility | Human Error |  | no-match | 2019-31 | 2019 | 11 | 4 | 9 | 48 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-11-04 09:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-04 | 23:32 | 34.6619 | -120.0852 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 8145 |  | 12000 | Conductor | Overhead | Yes | 43773 | 0.98056 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-125 | 2019 | 11 | 4 | 23 | 32 | 19-0121150 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 20066 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-04 23:32:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-05 | 15:53 | 35.7067 | -120.7059 | Bird Found | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 4Bk1105191543 |  | 12000 | Conductor | Overhead | Yes | 43774 | 0.66181 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-47 | 2019 | 11 | 5 | 15 | 53 | 19-0121577 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 21982 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-05 15:53:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-06 | 18:13 | 36.0144 | -120.1299 | Bird Found | Urban | 1 meter - < 3 meters | Self Extinguished |  | 416659024996 |  | 21000 | Conductor | Overhead | Yes | 43775 | 0.75903 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-48 | 2019 | 11 | 6 | 18 | 13 | 19-0122227 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 1728 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-06 18:13:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-07 | 10:48 | 37.2948 | -120.8104 |  | Agriculture | 1 meter - < 3 meters | Cal Fire |  | 7258 |  | 12000 | Lightning Arrestor | Overhead | Yes | 43776 | 0.45 | Equipment - PG&E | Lightning Arrestor |  |  |  |  | Other/Unknown | 2019-151 | 2019 | 11 | 7 | 10 | 48 | 19-0122506 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 6722 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-07 10:48:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-08 | 7:22 | 37.9785 | -122.3086 |  | Urban | 0.25 - 10 Acres | Fire Dept | Richmond FD | 14371105 |  | 12000 | Conductor | Overhead | Yes | 43777 | 0.30694 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-07 | 2019 | 11 | 8 | 7 | 22 | 19-0122766 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 61161 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-08 07:22:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-09 | 22:02 | 37.2804 | -121.9042 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | San Jose FD | 82311101 |  | 12000 | Conductor | Overhead | Yes | 43778 | 0.91806 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-408 | 2019 | 11 | 9 | 22 | 2 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-11-09 22:02:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-10 | 9:47 | 35.0787 | -120.4974 |  | Herbaceous | 1 meter - < 3 meters | Cal Fire |  | 4Bx1110190931 |  | 12000 | Conductor | Overhead | Yes | 43779 | 0.40764 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-431 | 2019 | 11 | 10 | 9 | 47 | 19-0123396 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 19943 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-10 09:47:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-11 | 6:52 | 36.6822 | -119.1806 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 4Tj1111191656 |  | 12000 | Other | Overhead | Yes | 43780 | 0.28611 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-453 | 2019 | 11 | 11 | 6 | 52 | 19-0123468 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 109129 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-11 06:52:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-11 | 9:46 | 37.8782 | -120.4596 | Vehicle | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 101020184 |  | 17000 | Other | Overhead | Yes | 43780 | 0.40694 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-82 | 2019 | 11 | 11 | 9 | 46 | 19-0123520 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 38170 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-11 09:46:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-13 | 15:43 | 35.318 | -119.1661 |  | Agriculture | 1 meter - < 3 meters | Fire Dept | Kern County FD | 4Tx1113191536 |  | 21000 | Pole | Overhead | Yes | 43782 | 0.65486 | Contact - Animal - Bird |  | Animal contact | Pole | Animal Contact |  | Other/Unknown | 2019-130 | 2019 | 11 | 13 | 15 | 43 | 19-0124465 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 70516 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-13 15:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-13 | 17:26 | 36.7278 | -119.7746 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Unknown | C1176 |  | 12000 | Capacitor Bank | Overhead | Yes | 43782 | 0.72639 | Equipment - PG&E | Capacitor Bank |  |  |  |  | no-match | 2019-146 | 2019 | 11 | 13 | 17 | 26 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-11-13 17:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-15 | 2:55 | 35.4415 | -119.0204 |  | Urban | 1 meter - < 3 meters | Fire Dept | Bakersfield FD | 009/067 |  | 115000 |  | Overhead | No |  |  | Unknown | [5 empty] | no-match | 2019-158 | 2019 | 11 | 15 | 2 | 55 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-11-15 02:55:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-15 | 4:10 | 35.5088 | -119.0295 | Gun Shot | Herbaceous | 0.25 - 10 Acres | Fire Dept | Bakersfield FD | Kern-Kern Front 115Kv |  | 115000 | Conductor | Overhead | Yes | 43784 | 0.17361 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | no-match | 2019-234 | 2019 | 11 | 15 | 4 | 10 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-11-15 04:10:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-16 | 7:16 | 38.2921 | -122.6505 |  | Urban | 3 meters - 0.25 Acres | Fire Dept | Penngrove FD | 43491103 |  | 12000 | Conductor | Overhead | Yes | 43785 | 0.30278 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-06 | 2019 | 11 | 16 | 7 | 16 | 19-0125376 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 29487 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-16 07:16:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-17 | 7:38 | 39.3338 | -122.1824 | Vegetation | Agriculture | 1 meter - < 3 meters | Other | Customer | 062881105 |  | 12000 | Conductor | Underbuild | Yes | 43786 | 0.31806 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-260 | 2019 | 11 | 17 | 7 | 38 | 19-0125463 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 7800 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-17 07:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-18 | 15:38 | 35.4267 | -119.0653 | Equipment Failure/Involved, Overhead | Urban | 1 meter - < 3 meters | Fire Dept | Kern County FD | 252721116 |  | 12000 | Conductor | Overhead | Yes | 43787 | 0.65139 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-440 | 2019 | 11 | 18 | 15 | 38 | 19-0125902 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | Vehicle | 89757 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-18 15:38:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-20 | 12:31 | 38.4172 | -121.9608 | Vegetation | Urban | 0.25 - 10 Acres | Fire Dept | Vacaville FD | 063591105 |  | 12000 | Conductor | Overhead | Yes | 43789 | 0.52153 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-261 | 2019 | 11 | 20 | 12 | 31 | 19-0126843 | Non-HFTD | non-HFTD | Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | 890 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-20 12:31:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-21 | 10:25 | 36.9342 | -120.6989 |  | Water | 1 meter - < 3 meters | Employee |  | Mtr#1004462849 |  | 12000 | Other | Overhead | Yes | 43790 | 0.43403 | Equipment - PG&E | Other |  |  |  |  | Other/Unknown | 2019-149 | 2019 | 11 | 21 | 10 | 25 | 19-0127171 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 827 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-21 10:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-21 | 16:26 | 40.3231 | -123.9202 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 192311141 |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-416 | 2019 | 11 | 21 | 16 | 26 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-11-21 16:26:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-22 | 5:57 | 36.8448 | -119.7346 |  | Urban | 1 meter - < 3 meters | Fire Dept | Clovis FD | 255292109 |  | 21000 | Conductor | Overhead | Yes | 43791 | 0.24792 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-448 | 2019 | 11 | 22 | 5 | 57 | 19-0127470 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 12825 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-22 05:57:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-22 | 4:43 | 39.6736 | -121.3855 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 103751102 |  | 12000 | Conductor | Overhead | Yes | 43791 | 0.19653 | Vegetation |  | Veg. contact |  |  |  | Fell into (slight defect) | 2019-428 | 2019 | 11 | 22 | 4 | 43 | 19-0127475 | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3712 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-22 04:43:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-25 | 16:42 | 37.7176 | -120.6128 | Bird Found | Urban | 0.25 - 10 Acres | Cal Fire |  | 5Xr1125191811 |  | 17000 | Fuse | Overhead | Yes | 43794 | 0.69583 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-37 | 2019 | 11 | 25 | 16 | 42 | 19-0128628 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | 4694 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-25 16:42:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-26 | 14:18 | 35.4427 | -120.7567 |  | Urban | 0.25 - 10 Acres | Cal Fire |  | 511791771829 |  | 12000 | Other | Overhead | Yes | 43795 | 0.59583 | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-211 | 2019 | 11 | 26 | 14 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-11-26 14:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-27 | 15:39 | 40.6579 | -122.4211 |  | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 103521102-2101107406{2413} |  | 12000 | Fuse | Overhead | Yes | 43796 | 0.65208 | Other Fire: Non-PG&E related | [5 empty] | Other/Unknown |  | 2019 | 11 | 27 | 15 | 39 | 19-0130770 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip failure | Fuse | 8302 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-27 15:39:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-27 | 6:37 | 37.2717 | -122.3078 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 24101103 |  | 12000 | Conductor | Overhead | Yes | 43796 | 0.27569 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-362 | 2019 | 11 | 27 | 6 | 37 | 19-0130047 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 16680 | 0 | NA | <25mph | <15mph | #REF! | 2019-11-27 06:37:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-11-29 | 20:18 | 39.8503 | -121.6312 |  | Shrub | 1 meter - < 3 meters | Unknown |  | 40700248, 42578814, 42578813 |  | 60000 | Pole | Overhead | Yes | 43798 | 0.84583 | Equipment - PG&E | Pole |  |  |  |  | no-match | 2019-10 | 2019 | 11 | 29 | 20 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-11-29 20:18:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-12-12 | 13:44 | 37.9276 | -121.4316 |  | Urban | 1 meter - < 3 meters | Employee |  | 317315152121 |  | 12000 | Transformer | Overhead | Yes | 43811 | 0.57222 | Equipment - PG&E | Transformer |  |  |  |  | Other/Unknown | 2019-80 | 2019 | 12 | 12 | 13 | 44 | 19-0136247 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 1885 | 0 | NA | <25mph | <15mph | #REF! | 2019-12-12 13:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-12-17 | 13:44 | 36.3234 | -121.2117 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 103827940 |  | 21000 | Transformer | Overhead | Yes | 43816 | 0.57222 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-424 | 2019 | 12 | 17 | 13 | 44 | No ILIS or TOTL available | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Animal | Animal | N.A. | 0 | NA | <25mph | <15mph | #REF! | 2019-12-17 13:44:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-12-18 | 5:25 | 38.2817 | -120.517 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 101273893 |  | 12000 | Pole | Overhead | Yes | 43817 | 0.22569 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (No defect) | 2019-361 | 2019 | 12 | 18 | 5 | 25 | 19-0137065 | Tier 2 | HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3185 | 0 | NA | <25mph | <15mph | #REF! | 2019-12-18 05:25:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-12-23 | 22:49 | 36.9602 | -122.0497 | Equipment Failure/Involved, Fire, pole | Urban | 1 meter - < 3 meters | Fire Dept | Santa Cruz FD | 103822060 |  | 4000 | Pole | Underbuild | Yes | 43822 | 0.95069 | Contact - 3rd Party |  | Other | Pole | Human Error |  | Other/Unknown | 2019-285 | 2019 | 12 | 23 | 22 | 49 | 19-0137789 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 280173 | 0 | NA | <25mph | <15mph | #REF! | 2019-12-23 22:49:00 | #REF! | 0 | FALSE | <25mph
PG&E | 2019-12-25 | 0:58 | 36.6438 | -121.7984 |  | Hardwood Woodland | 1 meter - < 3 meters | Unknown |  | 101784201 |  | 21000 | Conductor |  | Yes | 43824 | 0.040278 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-449 | 2019 | 12 | 25 | 0 | 58 | 19-0137865 | Non-HFTD | non-HFTD | No Fire Weather RFW Applicable | #REF! | #REF! | Fire Less than 300 Acres | Equip Failure | #REF! | 6704 | 0 | NA | <25mph | <15mph | #REF! | 2019-12-25 00:58:00 | #REF! | 0 | #REF! | <25mph
Note on AP4: Based on the max wind gust speed in the hour of ignition. used wind gust speed factor of 1.6.
Note on AW4: Based on the max wind gust speed +/- 12 hours of ignition. Used wind gust speed factor of 1.6.
Note on AY4: based on mph_day_max
Note on AM2120: Chong, Yanping: was under investigation, Kincade

## Ign HFTD+Wind
CPUC Reportable Ignitions from 2015-2019 + 7 fires ¦ HFTD + Wind Station Analysis
Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations | [7 empty] | Used in the pivot | [7 empty] | Used in Pivot | Used for Tranche | Used in the Risk Input Sheet | Used in Pivot | Used in the Risk Input Sheet | Used in the Risk Input | Used in EO-WF-14 | [7 empty] | 1
Utility Name | Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | Notes (Optional): | Veg Subdriver | 0_Ignition ID | 0_Year | 0_Month | 0_Day | 0_Hour | 0_Minute | 0_Outage ID | 0_HFTD Zone | 0_HFTD | 0_RFW Applicable | 0_Transmission/Distribution | 0_Tranche | 0_Fire Greater than 300 Acres | 0_Driver | 0_Subdriver | 0_Customer Minutes Interrupted | 1_wg_mph | 1_we_sn | 1_Wind Categorization | 1_Wind Category | 1_Tranche | 2_dt_local | 2_wg_row | 2_wg_mph_day_max | 1_same date and time as other ignition | 2_Wind Category | 4m/1h stid | 4m/1h time | 4m/1h dist | 4m/1h gust mph | 4m/1h count | 8m/1h stid | 8m/1h time | 8m/1h dist | 8m/1h gust mph | 8m/1h count | 4m/2h stid | 4m/2h time | 4m/2h dist | 4m/2h gust mph | 4m/2h count | 8m/2h stid | 8m/2h time | 8m/2h dist | 8m/2h gust mph | 8m/2h count
PG&E | 2015-01-16 07:07 | 42020.2965 | 38.7753 | -122.7004 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 102167494 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0257 | 2015 | 1 | 16 | 7 | 7 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 19.4177 | 126_282 | <25mph | <15mph | HFTD - Distribution | 2015-01-16 07:07:00 | 4 | 24.2776 | FALSE | <25mph |  |  |  | 0 | 0 | HWKC1 | 7.87 | 2015-01-16T14:56:00Z | 11.01 | 1 |  |  |  | 0 | 0 | HWKC1 | 7.87 | 2015-01-16T14:56:00Z | 11.01 | 2
PG&E | 2015-01-26 03:51 | 42030.1604 | 37.0539 | -122.1587 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42030.1604 | 2015-01-26 03:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0258 | 2015 | 1 | 26 | 3 | 51 | 15-0007000 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7602 | 14.3078 | 149_187 | <25mph | <15mph | HFTD - Distribution | 2015-01-26 03:51:00 | 5 | 14.9656 | FALSE | <25mph |  |  |  | 0 | 0 | BNDC1 | 5.38 | 2015-01-26T11:50:00Z | 10 | 52 |  |  |  | 0 | 0 | BNDC1 | 5.38 | 2015-01-26T11:50:00Z | 10 | 97
PG&E | 2015-02-06 06:01 | 42041.2507 | 38.6059 | -121.0221 | Vegetation | Rural | < 3 meters | Fire Agency |  | 6661 Ryan Ranch Road, El Dorado Hills |  | 21000 | Conductor | Overhead | Yes | 42041.2507 | 2015-02-06 06:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0259 | 2015 | 2 | 6 | 6 | 1 | 15-0009876 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 51996 | 16.7927 | 199_272 | <25mph | <15mph | HFTD - Distribution | 2015-02-06 06:01:00 | 6 | 30.3484 | FALSE | 25-40mph | D4314 | 3.45 | 2015-02-06T13:58:00Z | 46.95 | 12 | BENC1 | 4.89 | 2015-02-06T13:59:00Z | 59.01 | 40 | D4314 | 3.45 | 2015-02-06T13:58:00Z | 46.95 | 24 | BENC1 | 4.89 | 2015-02-06T13:59:00Z | 59.01 | 79
PG&E | 2015-02-07 18:38 | 42042.7764 | 40.4674 | -123.6545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | mile marker 36.61, hwy 36, bridgeville |  | 12000 | Conductor | Overhead | Yes | 42042.7764 | 2015-02-07 18:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0262 | 2015 | 2 | 7 | 18 | 38 | 15-0011390 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 7691 | 20.9308 | 88_377 | <25mph | <15mph | HFTD - Distribution | 2015-02-07 18:38:00 | 9 | 24.639 | FALSE | <25mph |  |  |  | 0 | 0 | MDDC1 | 6.88 | 2015-02-08T01:53:00Z | 24 | 1 |  |  |  | 0 | 0 | MDDC1 | 6.88 | 2015-02-08T01:53:00Z | 24 | 2
PG&E | 2015-02-23 02:05 | 42058.0868 | 39.3027 | -121.0175 | Vegetation | Rural | < 3 meters | Fire Agency | NEVADA CITY FIRE | 100086316 |  | 12000 | Conductor | Overhead | Yes | 42058.0868 | 2015-02-23 02:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0267 | 2015 | 2 | 23 | 2 | 5 | 15-0014910 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 93279 | 24.5459 | 199_311 | <25mph | <15mph | HFTD - Distribution | 2015-02-23 02:05:00 | 14 | 25.6662 | FALSE | 25-40mph | E3651 | 2.92 | 2015-02-23T09:05:00Z | 14.99 | 13 | KGOO | 5.49 | 2015-02-23T09:40:00Z | 31.07 | 67 | E3651 | 2.92 | 2015-02-23T10:50:00Z | 16.98 | 25 | KGOO | 5.49 | 2015-02-23T09:40:00Z | 31.07 | 131
PG&E | 2015-02-23 13:25 | 42058.559 | 38.5046 | -122.7408 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RINCON VALLEY | BEHIND 4870 CARRIAGE LN SANTA ROSA |  | 12000 | Conductor | Overhead | Yes | 42058.559 | 2015-02-23 13:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0268 | 2015 | 2 | 23 | 13 | 25 | 15-0015168 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 85762 | 20.3218 | 124_267 | <25mph | <15mph | HFTD - Distribution | 2015-02-23 13:25:00 | 15 | 32.6885 | FALSE | 25-40mph | RSAC1 | 2.39 | 2015-02-23T20:29:00Z | 34 | 11 | RSAC1 | 2.39 | 2015-02-23T20:29:00Z | 34 | 73 | RSAC1 | 2.39 | 2015-02-23T20:29:00Z | 34 | 22 | RSAC1 | 2.39 | 2015-02-23T20:29:00Z | 34 | 145
PG&E | 2015-03-04 18:44 | 42067.7806 | 38.9995 | -122.7545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kelseyville FD | 102156367 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42067.7806 | 2015-03-04 18:44 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0271 | 2015 | 3 | 4 | 18 | 44 | 15-0017374 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29532 | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2015-03-04 18:44:00 | NA | 0 | FALSE | <25mph |  |  |  | 0 | 0 | KELC1 | 6.58 | 2015-03-05T01:57:00Z | 11.01 | 1 |  |  |  | 0 | 0 | KELC1 | 6.58 | 2015-03-05T01:57:00Z | 11.01 | 2
PG&E | 2015-03-07 13:35 | 42070.566 | 38.7091 | -122.6484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 14417 western mine rd, Middletown |  | 12000 | Conductor | Overhead | Yes | 42070.566 | 2015-03-07 13:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0272 | 2015 | 3 | 7 | 13 | 35 | 15-0018003 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2263 | 3.8777 | 128_279 | <25mph | <15mph | HFTD - Distribution | 2015-03-07 13:35:00 | 18 | 14.4715 | FALSE | <25mph |  |  |  | 0 | 0 | E2050 | 7.98 | 2015-03-07T21:33:00Z | 7 | 4 |  |  |  | 0 | 0 | E2050 | 7.98 | 2015-03-07T21:48:00Z | 8.99 | 8
PG&E | 2015-03-09 09:36 | 42072.4 | 38.7328 | -120.7524 | Building | Urban | Structure Only | Unknown |  | 101399208 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42072.4 | 2015-03-09 09:36 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0273 | 2015 | 3 | 9 | 9 | 36 | 15-0018212 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 35991 | 3.767 | 210_279 | <25mph | <15mph | HFTD - Distribution | 2015-03-09 09:36:00 | 19 | 14.4776 | FALSE | <25mph | E5691 | 2.49 | 2015-03-09T15:46:00Z | 2.01 | 19 | E6490 | 5.16 | 2015-03-09T16:31:00Z | 3 | 37 | E5691 | 2.49 | 2015-03-09T17:31:00Z | 3 | 37 | C6129 | 5.81 | 2015-03-09T17:29:00Z | 4.99 | 73
PG&E | 2015-03-14 02:30 | 42077.1042 | 38.9038 | -122.7579 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 9210 Wildcat Road, Kelseyville |  | 12000 | Conductor | Overhead | Yes | 42077.1042 | 2015-03-14 02:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0274 | 2015 | 3 | 14 | 2 | 30 | 15-0019556 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2280 | 8.9688 | 124_289 | <25mph | <15mph | HFTD - Distribution | 2015-03-14 02:30:00 | 20 | 8.9688 | FALSE | <25mph | KELC1 | 2.83 | 2015-03-14T08:57:00Z | 0 | 1 | E4393 | 6.32 | 2015-03-14T08:57:00Z | 4.99 | 5 | KELC1 | 2.83 | 2015-03-14T09:57:00Z | 0 | 2 | E4393 | 6.32 | 2015-03-14T08:57:00Z | 4.99 | 10
PG&E | 2015-03-15 22:47 | 42078.9493 | 38.3346 | -120.5325 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 103106530 |  | 12000 | Conductor | Overhead | Yes | 42078.9493 | 2015-03-15 22:47 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0279 | 2015 | 3 | 15 | 22 | 47 | 15-0019709 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 14520 | 7.4897 | 220_257 | <25mph | <15mph | HFTD - Distribution | 2015-03-15 22:47:00 | 25 | 18.5478 | FALSE | <25mph | D9396 | 3.65 | 2015-03-16T05:46:00Z | 2.01 | 11 | MTZC1 | 7.54 | 2015-03-16T04:56:00Z | 7 | 25 | D9396 | 3.65 | 2015-03-16T06:44:00Z | 2.01 | 20 | MTZC1 | 7.54 | 2015-03-16T04:56:00Z | 7 | 47
PG&E | 2015-03-21 10:46 | 42084.4486 | 40.1645 | -122.2894 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101546309 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42084.4486 | 2015-03-21 10:46 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0281 | 2015 | 3 | 21 | 10 | 46 | 15-0021120 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 10355 | 1.2543 | 145_359 | <25mph | <15mph | HFTD - Distribution | 2015-03-21 10:46:00 | 27 | 9.5396 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2015-04-02 09:44 | 42096.4056 | 39.6772 | -121.492 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100338726 |  | 12000 | Conductor | Overhead | Yes | 42096.4056 | 2015-04-02 09:44 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0284 | 2015 | 4 | 2 | 9 | 44 | 15-0023747 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 100204 | 15.7458 | 178_332 | <25mph | <15mph | HFTD - Distribution | 2015-04-02 09:44:00 | 30 | 15.7458 | FALSE | <25mph |  |  |  | 0 | 0 | JBGC1 | 4.06 | 2015-04-02T16:13:00Z | 37 | 12 |  |  |  | 0 | 0 | JBGC1 | 4.06 | 2015-04-02T16:13:00Z | 37 | 21
PG&E | 2015-04-04 16:49 | 42098.7007 | 38.8824 | -122.5914 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 20748 Jerusalem Grade Road, Middletown |  | 12000 | Other | Overhead | Yes | 42098.7007 | 2015-04-04 16:49 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0285 | 2015 | 4 | 4 | 16 | 49 | 15-0024208 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 20448 | 16.9925 | 131_288 | <25mph | <15mph | HFTD - Distribution | 2015-04-04 16:49:00 | 31 | 19.3597 | FALSE | <25mph |  |  |  | 0 | 0 | KELC1 | 6.51 | 2015-04-04T22:57:00Z | 22.01 | 13 |  |  |  | 0 | 0 | KELC1 | 6.51 | 2015-04-04T23:57:00Z | 25.99 | 26
PG&E | 2015-04-11 17:16 | 42105.7194 | 40.5462 | -122.2343 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101491414 |  | 12000 | Conductor | Overhead | Yes | 42105.7194 | 2015-04-11 17:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0286 | 2015 | 4 | 11 | 17 | 16 | 15-0026023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 11914 | 19.429 | 148_380 | <25mph | <15mph | HFTD - Distribution | 2015-04-11 17:16:00 | 32 | 19.429 | FALSE | <25mph | RRAC1 | 3.7 | 2015-04-11T23:24:00Z | 12.01 | 1 | C5599 | 6.52 | 2015-04-12T00:04:00Z | 14 | 9 | RRAC1 | 3.7 | 2015-04-11T23:24:00Z | 12.01 | 2 | C5599 | 6.52 | 2015-04-12T01:04:00Z | 20.98 | 18
PG&E | 2015-04-18 03:07 | 42112.1299 | 38.6858 | -121.0084 | Vegetation | Urban | < 3 meters | Fire Agency | carmeron park F.D. | around t-7464 |  | 21000 | Conductor | Overhead | Yes | 42112.1299 | 2015-04-18 03:07 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0293 | 2015 | 4 | 18 | 3 | 7 | 15-0027556 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 49438 | 9.1676 | 199_277 | <25mph | <15mph | HFTD - Distribution | 2015-04-18 03:07:00 | 39 | 10.9817 | FALSE | <25mph | D7401 | 0.28 | 2015-04-18T10:04:00Z | 8.99 | 33 | D7401 | 0.28 | 2015-04-18T10:04:00Z | 8.99 | 58 | D7401 | 0.28 | 2015-04-18T10:04:00Z | 8.99 | 65 | D7401 | 0.28 | 2015-04-18T10:04:00Z | 8.99 | 115
PG&E | 2015-04-27 12:54 | 42121.5375 | 35.4871 | -120.6756 | Vegetation | Rural | < 3 meters | Unknown |  | 103310601 |  | 21000 | Conductor | Overhead | Yes | 42121.5375 | 2015-04-27 12:54 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0301 | 2015 | 4 | 27 | 12 | 54 | 15-0029875 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 5836 | 7.5834 | 214_100 | <25mph | <15mph | HFTD - Distribution | 2015-04-27 12:54:00 | 47 | 19.0974 | FALSE | <25mph | E1179 | 1.84 | 2015-04-27T19:26:00Z | 8.99 | 8 | E2260 | 4.42 | 2015-04-27T19:11:00Z | 10.98 | 14 | E1179 | 1.84 | 2015-04-27T19:26:00Z | 8.99 | 16 | E2260 | 4.42 | 2015-04-27T20:32:00Z | 14 | 29
PG&E | 2015-04-30 00:26 | 42124.0181 | 37.2401 | -122.2472 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 1145 VERDE R |  | 12000 | Conductor | Overhead | Yes | 42124.0181 | 2015-04-30 00:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0304 | 2015 | 4 | 30 | 0 | 26 | 15-0030607 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1256 | 5.7566 | 145_197 | <25mph | <15mph | HFTD - Distribution | 2015-04-30 00:26:00 | 50 | 15.5915 | FALSE | <25mph |  |  |  | 0 | 0 | LAHC1 | 4.52 | 2015-04-30T07:07:00Z | 4.99 | 9 |  |  |  | 0 | 0 | LAHC1 | 4.52 | 2015-04-30T08:07:00Z | 5.99 | 17
PG&E | 2015-05-02 16:51 | 42126.7021 | 37.3284 | -119.643 | Vegetation | Rural | < 0.25 Acres | Fire Agency | MADERA COUNTY | 103768995 |  | 12000 | Conductor | Overhead | Yes | 42126.7021 | 2015-05-02 16:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0305 | 2015 | 5 | 2 | 16 | 51 | 15-0031285 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 79805 | 9.7158 | 259_202 | <25mph | <15mph | HFTD - Distribution | 2015-05-02 16:51:00 | 51 | 12.4769 | FALSE | <25mph | AT301 | 1.62 | 2015-05-02T23:51:00Z | 18.99 | 34 | AT301 | 1.62 | 2015-05-02T23:51:00Z | 18.99 | 60 | AT301 | 1.62 | 2015-05-02T23:56:00Z | 18.99 | 65 | AT301 | 1.62 | 2015-05-02T23:56:00Z | 18.99 | 119
PG&E | 2015-05-06 17:17 | 42130.7201 | 37.4273 | -119.8803 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | BOOSTER 8179 INDIAN PEEK N/O MIWUK | None | 21000 | Other | Overhead | Yes | 42130.7201 | 2015-05-06 17:17 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0307 | 2015 | 5 | 6 | 17 | 17 | 15-0032311 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 81600 | 12.4413 | 249_208 | <25mph | <15mph | HFTD - Distribution | 2015-05-06 17:17:00 | 53 | 13.2212 | FALSE | <25mph | C1522 | 2.85 | 2015-05-06T23:47:00Z | 13 | 6 | MIAC1 | 7.42 | 2015-05-06T23:59:00Z | 20 | 9 | C1522 | 2.85 | 2015-05-06T23:47:00Z | 13 | 11 | MIAC1 | 7.42 | 2015-05-06T23:59:00Z | 20 | 17
PG&E | 2015-05-09 13:10 | 42133.5486 | 39.2343 | -121.2468 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100000103 | None | 21000 | Conductor | Overhead | Yes | 42133.5486 | 2015-05-09 13:10 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0311 | 2015 | 5 | 9 | 13 | 10 | 15-0033085 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 382926 | 12.172 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 13:10:00 | 57 | 17.071 | FALSE | <25mph | E2572 | 3.27 | 2015-05-09T19:28:00Z | 7 | 12 | E2572 | 3.27 | 2015-05-09T19:28:00Z | 7 | 12 | E2572 | 3.27 | 2015-05-09T19:28:00Z | 7 | 12 | E2572 | 3.27 | 2015-05-09T19:28:00Z | 7 | 12
PG&E | 2015-05-09 21:37 | 42133.9007 | 39.2848 | -121.0219 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100004095 | Pacific Bell | 12000 | Fuse | Overhead | Yes | 42133.9007 | 2015-05-09 21:37 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0312 | 2015 | 5 | 9 | 21 | 37 | 15-0033109 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 11 | 9.2188 | 198_310 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 21:37:00 | 58 | 15.4234 | FALSE | <25mph | E5439 | 3.42 | 2015-05-10T04:00:00Z | 4 | 28 | RRRC1 | 5.26 | 2015-05-10T04:13:00Z | 5.99 | 66 | E5439 | 3.42 | 2015-05-10T04:00:00Z | 4 | 56 | RRRC1 | 5.26 | 2015-05-10T05:13:00Z | 5.99 | 130
PG&E | 2015-05-21 09:23 | 42145.391 | 38.5996 | -122.9935 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 4 SPANS LOAD SIDE 2993 |  | 12000 | Conductor | Overhead | Yes | 42145.391 | 2015-05-21 09:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0324 | 2015 | 5 | 21 | 9 | 23 | 15-0035686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2850 | 1.6525 | 114_273 | <25mph | <15mph | HFTD - Distribution | 2015-05-21 09:23:00 | 70 | 15.124 | FALSE | <25mph |  |  |  | 0 | 0 | D3481 | 5.82 | 2015-05-21T16:22:00Z | 4 | 31 |  |  |  | 0 | 0 | D3481 | 5.82 | 2015-05-21T17:17:00Z | 7 | 63
PG&E | 2015-05-27 21:44 | 42151.9056 | 39.169 | -120.9612 | Vegetation | Rural | < 0.25 Acres | Fire Agency | PEARDALE F.D. | 100077687 |  | 12000 | Conductor | Overhead | Yes | 42151.9056 | 2015-05-27 21:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0329 | 2015 | 5 | 27 | 21 | 44 | 15-0036850 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10828 | 3.691 | 201_303 | <25mph | <15mph | HFTD - Distribution | 2015-05-27 21:44:00 | 75 | 11.9096 | FALSE | <25mph |  |  |  | 0 | 0 | E5439 | 7.11 | 2015-05-28T04:20:00Z | 2.01 | 62 |  |  |  | 0 | 0 | SETC1 | 4.24 | 2015-05-28T05:28:00Z | 5.99 | 119
PG&E | 2015-05-30 12:52 | 42154.5361 | 38.7371 | -120.8122 | Vegetation | Urban | < 3 meters | Fire Agency | el dorado co fire district | across from 2669 hwy 49 |  | 12000 | Fuse | Overhead | Yes | 42154.5361 | 2015-05-30 12:52 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0334 | 2015 | 5 | 30 | 12 | 52 | 15-0037405 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 115 | 11.152 | 208_280 | <25mph | <15mph | HFTD - Distribution | 2015-05-30 12:52:00 | 80 | 12.3322 | FALSE | <25mph | E5691 | 1.7 | 2015-05-30T19:47:00Z | 10 | 29 | E5691 | 1.7 | 2015-05-30T19:47:00Z | 10 | 47 | C6129 | 3.5 | 2015-05-30T20:49:00Z | 11.99 | 57 | C6129 | 3.5 | 2015-05-30T20:49:00Z | 11.99 | 93
PG&E | 2015-06-03 09:33 | 42158.3979 | 39.6896 | -121.6216 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42158.3979 | 2015-06-03 09:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0341 | 2015 | 6 | 3 | 9 | 33 | 15-0038091 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 28146 | 6.3564 | 173_332 | <25mph | <15mph | HFTD - Distribution | 2015-06-03 09:33:00 | 87 | 12.6567 | FALSE | <25mph |  |  |  | 0 | 0 | JBGC1 | 7.74 | 2015-06-03T16:13:00Z | 8.99 | 12 |  |  |  | 0 | 0 | CICC1 | 6.93 | 2015-06-03T16:54:00Z | 10 | 25
PG&E | 2015-06-04 13:17 | 42159.5535 | 39.2694 | -123.7841 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42159.5535 | 2015-06-04 13:17 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0344 | 2015 | 6 | 4 | 13 | 17 | 15-0038501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20525 | 22.1312 | 81_311 | <25mph | <15mph | HFTD - Distribution | 2015-06-04 13:17:00 | 90 | 22.6218 | FALSE | <25mph | KLLR | 1.7 | 2015-06-04T19:55:00Z | 16.11 | 7 | KLLR | 1.7 | 2015-06-04T19:55:00Z | 16.11 | 9 | KLLR | 1.7 | 2015-06-04T20:55:00Z | 17.25 | 14 | KLLR | 1.7 | 2015-06-04T20:55:00Z | 17.25 | 18
PG&E | 2015-06-04 20:00 | 42159.8333 | 38.6916 | -120.8606 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101412760 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42159.8333 | 2015-06-04 20:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0347 | 2015 | 6 | 4 | 20 | 0 | 15-0038597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 9640 | 2.0731 | 205_277 | <25mph | <15mph | HFTD - Distribution | 2015-06-04 20:00:00 | 93 | 11.0268 | FALSE | <25mph | E6490 | 1.72 | 2015-06-05T02:01:00Z | 7 | 25 | D4464 | 6.46 | 2015-06-05T02:16:00Z | 8.01 | 60 | E6490 | 1.72 | 2015-06-05T02:01:00Z | 7 | 49 | D4464 | 6.46 | 2015-06-05T02:16:00Z | 8.01 | 119
PG&E | 2015-06-05 01:25 | 42160.059 | 38.3461 | -122.3998 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | 4870 REDWOOD |  | 21000 | Conductor | Overhead | Yes | 42160.059 | 2015-06-05 01:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0348 | 2015 | 6 | 5 | 1 | 25 | 15-0038607 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 53842 | 2.8209 | 139_258 | <25mph | <15mph | HFTD - Distribution | 2015-06-05 01:25:00 | 94 | 16.3328 | FALSE | <25mph |  |  |  | 0 | 0 | E6860 | 6.98 | 2015-06-05T08:07:00Z | 1.01 | 23 |  |  |  | 0 | 0 | E6860 | 6.98 | 2015-06-05T09:22:00Z | 1.01 | 45
PG&E | 2015-06-05 14:40 | 42160.6111 | 37.9578 | -120.4519 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101012484 |  | 17000 | Conductor | Overhead | Yes | 42160.6111 | 2015-06-05 14:40 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0350 | 2015 | 6 | 5 | 14 | 40 | 15-0038686 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 14319 | 9.5876 | 223_237 | <25mph | <15mph | HFTD - Distribution | 2015-06-05 14:40:00 | 96 | 16.2954 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2015-06-06 15:38 | 42161.6514 | 39.0409 | -123.4019 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 11480 ANDERSON VALLEY WAY @ BRIDGE |  | 12000 | Conductor | Overhead | Yes | 42161.6514 | 2015-06-06 15:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0355 | 2015 | 6 | 6 | 15 | 38 | 15-0039056 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 1748 | 19.2204 | 97_298 | <25mph | <15mph | HFTD - Distribution | 2015-06-06 15:38:00 | 101 | 19.2204 | FALSE | <25mph | E4777 | 3.27 | 2015-06-06T22:26:00Z | 14 | 2 | BNVC1 | 4.68 | 2015-06-06T21:50:00Z | 17 | 7 | E4777 | 3.27 | 2015-06-06T22:40:00Z | 14 | 3 | BNVC1 | 4.68 | 2015-06-06T22:50:00Z | 21 | 13
PG&E | 2015-06-08 14:18 | 42163.5958 | 38.1796 | -120.959 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 102048579 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42163.5958 | 2015-06-08 14:18 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0360 | 2015 | 6 | 8 | 14 | 18 | 15-0039368 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 65168 | 7.0021 | 201_249 | <25mph | <15mph | HFTD - Distribution | 2015-06-08 14:18:00 | 106 | 9.7763 | FALSE | <25mph |  |  |  | 0 | 0 | CMAC1 | 5.88 | 2015-06-08T20:59:00Z | 12.01 | 1 |  |  |  | 0 | 0 | CMAC1 | 5.88 | 2015-06-08T21:59:00Z | 12.01 | 2
PG&E | 2015-06-08 16:15 | 42163.6771 | 39.8236 | -123.6093 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 2 spans loadside 1741 |  | 12000 | Conductor | Overhead | Yes | 42163.6771 | 2015-06-08 16:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0362 | 2015 | 6 | 8 | 16 | 15 | 15-0039481 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1740 | 14.8206 | 89_341 | <25mph | <15mph | HFTD - Distribution | 2015-06-08 16:15:00 | 108 | 15.1524 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2015-06-09 15:24 | 42164.6417 | 38.3651 | -122.2541 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | load side 2987 | Yes | 21000 | Conductor | Overhead | Yes | 42164.6417 | 2015-06-09 15:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0368 | 2015 | 6 | 9 | 15 | 24 | 15-0039825 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 651298 | 15.2247 | 145_259 | <25mph | <15mph | HFTD - Distribution | 2015-06-09 15:24:00 | 114 | 15.4726 | FALSE | <25mph |  |  |  | 0 | 0 | ATLC1 | 7.61 | 2015-06-09T21:29:00Z | 48 | 21 |  |  |  | 0 | 0 | ATLC1 | 7.61 | 2015-06-09T22:29:00Z | 53.02 | 41
PG&E | 2015-06-09 16:20 | 42164.6806 | 38.3822 | -122.4316 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102269716 | Pacific Bell | 21000 | Unknown | Overhead | Yes | 42164.6806 | 2015-06-09 16:20 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0369 | 2015 | 6 | 9 | 16 | 20 | 15-0039860 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 4184 | 20.783 | 138_260 | <25mph | <15mph | HFTD - Distribution | 2015-06-09 16:20:00 | 115 | 24.1918 | FALSE | <25mph |  |  |  | 0 | 0 | E7241 | 7.11 | 2015-06-09T22:38:00Z | 17.98 | 18 |  |  |  | 0 | 0 | E7241 | 7.11 | 2015-06-09T22:38:00Z | 17.98 | 38
PG&E | 2015-06-12 13:07 | 42167.5465 | 40.4077 | -122.4104 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS STREET FROM 4139 OLD HAPPY VALLEY RD |  | 12000 | Lightning Arrestor | Overhead | No |  |  | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | no-match | 0378 | 2015 | 6 | 12 | 13 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Lightning Arrestor | N.A. | 9.7698 | 140_372 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 13:07:00 | 124 | 24.3549 | FALSE | <25mph |  |  |  | 0 | 0 | E7114 | 7.46 | 2015-06-12T19:27:00Z | 14.99 | 8 |  |  |  | 0 | 0 | E7114 | 7.46 | 2015-06-12T20:15:00Z | 20 | 16
PG&E | 2015-06-12 23:32 | 42167.9806 | 39.2308 | -121.1559 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 10903 PROSPECTOR RD ROUGH AND READY | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42167.9806 | 2015-06-12 23:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0380 | 2015 | 6 | 12 | 23 | 32 | 15-0040789 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 20 | 12.2901 | 193_307 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 23:32:00 | 126 | 14.4252 | FALSE | <25mph | E2572 | 1.63 | 2015-06-13T06:29:00Z | 5.99 | 18 | E5439 | 5.49 | 2015-06-13T06:25:00Z | 8.99 | 65 | E2572 | 1.63 | 2015-06-13T06:34:00Z | 5.99 | 35 | RRRC1 | 5.44 | 2015-06-13T07:13:00Z | 12.01 | 129
PG&E | 2015-06-15 15:35 | 42170.6493 | 37.1852 | -121.7595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Jose city | 100618215 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42170.6493 | 2015-06-15 15:35 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0384 | 2015 | 6 | 15 | 15 | 35 | 15-0041178 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 345 | 20.7397 | 166_194 | <25mph | <15mph | HFTD - Distribution | 2015-06-15 15:35:00 | 130 | 21.599 | FALSE | <25mph |  |  |  | 0 | 0 | C9520 | 5.63 | 2015-06-15T21:46:00Z | 11.99 | 42 |  |  |  | 0 | 0 | C2789 | 6.18 | 2015-06-15T23:35:00Z | 14 | 84
PG&E | 2015-06-21 13:31 | 42176.5632 | 37.375 | -119.6116 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103204866 |  | 0 – 750 | Conductor | Overhead | No |  |  | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0399 | 2015 | 6 | 21 | 13 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 11.8124 | 260_205 | <25mph | <15mph | HFTD - Distribution | 2015-06-21 13:31:00 | 145 | 12.2407 | FALSE | <25mph | D7171 | 3.95 | 2015-06-21T19:55:00Z | 16.98 | 25 | MIAC1 | 7.96 | 2015-06-21T19:59:00Z | 22.01 | 69 | AT301 | 3.85 | 2015-06-21T21:27:00Z | 18.99 | 49 | MIAC1 | 7.96 | 2015-06-21T19:59:00Z | 22.01 | 133
PG&E | 2015-06-22 11:58 | 42177.4986 | 39.1737 | -121.0667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | SENTINAL WY |  | 12000 | Conductor | Overhead | Yes | 42177.4986 | 2015-06-22 11:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0400 | 2015 | 6 | 22 | 11 | 58 | 15-0042502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 148438 | 10.8591 | 197_304 | <25mph | <15mph | HFTD - Distribution | 2015-06-22 11:58:00 | 146 | 12.4713 | FALSE | <25mph | AS856 | 3.16 | 2015-06-22T18:58:00Z | 10 | 25 | E5439 | 4.77 | 2015-06-22T18:56:00Z | 10.98 | 85 | AS856 | 3.16 | 2015-06-22T19:58:00Z | 11.99 | 49 | AS856 | 3.16 | 2015-06-22T19:58:00Z | 11.99 | 170
PG&E | 2015-06-24 19:05 | 42179.7951 | 39.9921 | -123.9258 | Vegetation | Rural | < 3 meters | Customer |  | 4 spans load side 8207 |  | 12000 | Conductor | Overhead | Yes | 42179.7951 | 2015-06-24 19:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0406 | 2015 | 6 | 24 | 19 | 5 | 15-0043176 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1080 | 19.6004 | 76_351 | <25mph | <15mph | HFTD - Distribution | 2015-06-24 19:05:00 | 152 | 20.8753 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2015-06-27 12:48 | 42182.5333 | 37.9474 | -120.4274 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101034512 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.5333 | 2015-06-27 12:48 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0414 | 2015 | 6 | 27 | 12 | 48 | 15-0043755 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 150075 | 11.0891 | 224_236 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 12:48:00 | 159 | 19.6587 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 | KO22 | 5.72 | 2015-06-27T19:55:00Z | 16.11 | 1
PG&E | 2015-06-27 18:51 | 42182.7854 | 37.9911 | -120.438 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | MORMON CREEK 100' FROM S/OF HWY 49 |  | 17000 | Conductor | Overhead | Yes | 42182.7854 | 2015-06-27 18:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0415 | 2015 | 6 | 27 | 18 | 51 | 15-0043784 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 5249 | 11.3463 | 224_239 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 18:51:00 | 160 | 14.5222 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2015-06-27 21:15 | 42182.8854 | 39.2699 | -121.0403 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 16151 INDAIN FLAT RD |  | 12000 | Conductor | Overhead | Yes | 42182.8854 | 2015-06-27 21:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0416 | 2015 | 6 | 27 | 21 | 15 | 15-0043789 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4210 | 5.8168 | 198_309 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 21:15:00 | 161 | 11.6482 | FALSE | <25mph | E5439 | 2.06 | 2015-06-28T04:15:00Z | 2.01 | 40 | RRRC1 | 4.73 | 2015-06-28T04:13:00Z | 7 | 49 | E5439 | 2.06 | 2015-06-28T05:15:00Z | 4 | 72 | RRRC1 | 4.73 | 2015-06-28T04:13:00Z | 7 | 88
PG&E | 2015-06-27 22:28 | 42182.9361 | 38.1194 | -120.6218 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 101281699 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.9361 | 2015-06-27 22:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0417 | 2015 | 6 | 27 | 22 | 28 | 15-0043798 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 517 | 14.2862 | 216_246 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 22:28:00 | 162 | 15.5829 | FALSE | <25mph | C9085 | 3.92 | 2015-06-28T05:15:00Z | 1.01 | 2 | C9085 | 3.92 | 2015-06-28T05:15:00Z | 1.01 | 2 | C9085 | 3.92 | 2015-06-28T06:05:00Z | 1.01 | 5 | C9085 | 3.92 | 2015-06-28T06:05:00Z | 1.01 | 5
PG&E | 2015-06-28 02:50 | 42183.1181 | 35.491 | -120.731 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 13505 Santa Lucia Rd. Atascadero |  | 12000 | Conductor | Overhead | Yes | 42183.1181 | 2015-06-28 02:50 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0418 | 2015 | 6 | 28 | 2 | 50 | 15-0043807 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 12323 | 9.9634 | 212_101 | <25mph | <15mph | HFTD - Distribution | 2015-06-28 02:50:00 | 163 | 24.8049 | FALSE | <25mph | E6394 | 1.17 | 2015-06-28T09:37:00Z | 0 | 4 | E2260 | 6.83 | 2015-06-28T09:01:00Z | 3 | 6 | E6394 | 1.17 | 2015-06-28T10:22:00Z | 3 | 8 | E6394 | 1.17 | 2015-06-28T10:22:00Z | 3 | 15
PG&E | 2015-06-28 21:07 | 42183.8799 | 39.7405 | -121.4974 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | DEADWOOD RD, JARBO GAP |  | 12000 | Conductor | Overhead | Yes | 42183.8799 | 2015-06-28 21:07 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0424 | 2015 | 6 | 28 | 21 | 7 | 15-0043869 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 45683 | 12.2547 | 178_335 | <25mph | <15mph | HFTD - Distribution | 2015-06-28 21:07:00 | 169 | 17.5682 | FALSE | <25mph | JBGC1 | 0.55 | 2015-06-29T03:13:00Z | 4.99 | 1 | JBGC1 | 0.55 | 2015-06-29T03:13:00Z | 4.99 | 2 | JBGC1 | 0.55 | 2015-06-29T04:13:00Z | 5.99 | 2 | JBGC1 | 0.55 | 2015-06-29T04:13:00Z | 5.99 | 7
PG&E | 2015-06-30 18:18 | 42185.7625 | 36.2199 | -121.7534 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | loadside of 88973 | unknown | 12000 | Conductor | Overhead | Yes | 42185.7625 | 2015-06-30 18:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0432 | 2015 | 6 | 30 | 18 | 18 | 15-0044405 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 158 | 5.7006 | 166_141 | <25mph | <15mph | HFTD - Distribution | 2015-06-30 18:18:00 | 177 | 8.2628 | FALSE | <25mph | PPSC1 | 2.3 | 2015-07-01T01:04:00Z | 8.99 | 1 | PPSC1 | 2.3 | 2015-07-01T01:04:00Z | 8.99 | 3 | PPSC1 | 2.3 | 2015-07-01T01:04:00Z | 8.99 | 2 | PPSC1 | 2.3 | 2015-07-01T01:04:00Z | 8.99 | 8
PG&E | 2015-07-01 09:17 | 42186.3868 | 38.5715 | -122.5443 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42186.3868 | 2015-07-01 09:17 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0433 | 2015 | 7 | 1 | 9 | 17 | 15-0044529 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 85168 | 0.56943 | 133_271 | <25mph | <15mph | HFTD - Distribution | 2015-07-01 09:17:00 | 178 | 20.9979 | FALSE | <25mph | E2050 | 3.6 | 2015-07-01T16:14:00Z | 3 | 4 | E2050 | 3.6 | 2015-07-01T16:14:00Z | 3 | 21 | E2050 | 3.6 | 2015-07-01T17:15:00Z | 4.99 | 8 | E2050 | 3.6 | 2015-07-01T17:15:00Z | 4.99 | 33
PG&E | 2015-07-01 12:57 | 42186.5396 | 39.4146 | -121.379 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42186.5396 | 2015-07-01 12:57 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0434 | 2015 | 7 | 1 | 12 | 57 | 15-0044609 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 12.6482 | 183_317 | <25mph | <15mph | HFTD - Distribution | 2015-07-01 12:57:00 | 179 | 18.7031 | FALSE | <25mph | BNGC1 | 2.37 | 2015-07-01T19:51:00Z | 15.99 | 1 | BNGC1 | 2.37 | 2015-07-01T19:51:00Z | 15.99 | 1 | BNGC1 | 2.37 | 2015-07-01T20:51:00Z | 17 | 2 | BNGC1 | 2.37 | 2015-07-01T20:51:00Z | 17 | 2
PG&E | 2015-07-03 03:23 | 42188.141 | 35.6785 | -120.9567 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 1 soan 1 conducter 1 span loade side transformer formtr 1008493290 |  | 21000 | Conductor | Overhead | Yes | 42188.141 | 2015-07-03 03:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0438 | 2015 | 7 | 3 | 3 | 23 | 15-0045239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 978 | 7.7054 | 202_111 | <25mph | <15mph | HFTD - Distribution | 2015-07-03 03:23:00 | 183 | 16.8894 | FALSE | <25mph | TABC1 | 2.38 | 2015-07-03T10:07:00Z | 1.01 | 1 | D4060 | 6.58 | 2015-07-03T10:19:00Z | 2.01 | 5 | TABC1 | 2.38 | 2015-07-03T11:07:00Z | 3 | 2 | TABC1 | 2.38 | 2015-07-03T11:07:00Z | 3 | 10
PG&E | 2015-07-04 01:14 | 42189.0514 | 38.9566 | -121.0434 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100037226 |  | 12000 | Other | Overhead | Yes | 42189.0514 | 2015-07-04 01:14 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0441 | 2015 | 7 | 4 | 1 | 14 | 15-0045440 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 53865 | 7.3476 | 198_292 | <25mph | <15mph | HFTD - Distribution | 2015-07-04 01:14:00 | 186 | 12.3228 | FALSE | <25mph |  |  |  | 0 | 0 | D8862 | 5.23 | 2015-07-04T07:21:00Z | 5.99 | 25 |  |  |  | 0 | 0 | D8862 | 5.23 | 2015-07-04T07:21:00Z | 5.99 | 49
PG&E | 2015-07-05 09:42 | 42190.4042 | 35.5323 | -120.7371 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 0 – 750 | Conductor | Overhead | No |  |  | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0444 | 2015 | 7 | 5 | 9 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 11.0729 | 211_103 | <25mph | <15mph | HFTD - Distribution | 2015-07-05 09:42:00 | 189 | 25.4306 | FALSE | 25-40mph | E6394 | 1.7 | 2015-07-05T16:08:00Z | 12.01 | 4 | E6394 | 1.7 | 2015-07-05T16:08:00Z | 12.01 | 4 | E6394 | 1.7 | 2015-07-05T16:54:00Z | 13 | 8 | E6394 | 1.7 | 2015-07-05T16:54:00Z | 13 | 8
PG&E | 2015-07-05 21:21 | 42190.8896 | 38.6524 | -120.6278 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | one span east of c/o 1055 |  | 21000 | Conductor | Overhead | Yes | 42190.8896 | 2015-07-05 21:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0445 | 2015 | 7 | 5 | 21 | 21 | 15-0045605 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 22374 | 5.6191 | 215_275 | <25mph | <15mph | HFTD - Distribution | 2015-07-05 21:21:00 | 190 | 12.9317 | FALSE | <25mph |  |  |  | 0 | 0 | GZFC1 | 5.69 | 2015-07-06T04:17:00Z | 3 | 1 |  |  |  | 0 | 0 | GZFC1 | 5.69 | 2015-07-06T04:17:00Z | 3 | 2
PG&E | 2015-07-07 10:42 | 42192.4458 | 39.1138 | -121.0655 | Vegetation | Rural | < 0.25 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42192.4458 | 2015-07-07 10:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0448 | 2015 | 7 | 7 | 10 | 42 | 15-0045985 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 46738 | 10.1548 | 197_300 | <25mph | <15mph | HFTD - Distribution | 2015-07-07 10:42:00 | 193 | 12.5396 | FALSE | <25mph | C5488 | 3.42 | 2015-07-07T17:40:00Z | 4.99 | 4 | E1789 | 4.22 | 2015-07-07T17:18:00Z | 7 | 55 | C5488 | 3.42 | 2015-07-07T18:20:00Z | 7 | 9 | E1789 | 4.22 | 2015-07-07T18:42:00Z | 8.01 | 115
PG&E | 2015-07-07 15:27 | 42192.6438 | 35.155 | -120.5442 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 303corraltos cyn rd | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42192.6438 | 2015-07-07 15:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0449 | 2015 | 7 | 7 | 15 | 27 | 15-0046127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 98566 | 24.1391 | 220_82 | <25mph | <15mph | HFTD - Distribution | 2015-07-07 15:27:00 | 194 | 24.1391 | FALSE | <25mph | C9814 | 3.58 | 2015-07-07T22:23:00Z | 10 | 6 | KSBP | 7.64 | 2015-07-07T21:56:00Z | 34.52 | 7 | C9814 | 3.58 | 2015-07-07T23:03:00Z | 10 | 12 | KSBP | 7.64 | 2015-07-07T21:56:00Z | 34.52 | 14
PG&E | 2015-07-08 11:23 | 42193.4743 | 39.224 | -121.0635 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 100094468 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42193.4743 | 2015-07-08 11:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0451 | 2015 | 7 | 8 | 11 | 23 | 15-0046274 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 22064 | 9.2756 | 197_306 | <25mph | <15mph | HFTD - Distribution | 2015-07-08 11:23:00 | 196 | 10.6981 | FALSE | <25mph | E6355 | 2.74 | 2015-07-08T18:19:00Z | 8.99 | 46 | RRRC1 | 6.2 | 2015-07-08T18:13:00Z | 12.01 | 89 | E6355 | 2.74 | 2015-07-08T19:20:00Z | 8.99 | 91 | RRRC1 | 6.2 | 2015-07-08T19:13:00Z | 12.01 | 174
PG&E | 2015-07-12 17:04 | 42197.7111 | 37.4713 | -122.4256 | Vegetation | Rural | < 0.25 Acres | Fire Agency | COUNTY FIRE | 1 s w c509 |  | 12000 | Conductor | Overhead | Yes | 42197.7111 | 2015-07-12 17:04 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown | Jumper | Other/Unknown | 0456 | 2015 | 7 | 12 | 17 | 4 | 15-0047023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 117853 | 14.8289 | 137_210 | <25mph | <15mph | HFTD - Distribution | 2015-07-12 17:04:00 | 201 | 14.9925 | FALSE | <25mph | D9259 | 3.49 | 2015-07-12T23:43:00Z | 5.99 | 4 | PUGC1 | 7 | 2015-07-12T23:18:00Z | 25.99 | 48 | D9259 | 3.49 | 2015-07-13T00:28:00Z | 5.99 | 8 | PUGC1 | 7 | 2015-07-12T23:18:00Z | 25.99 | 99
PG&E | 2015-07-15 09:00 | 42200.375 | 36.997 | -121.7381 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101795728 |  | 21000 | Conductor | Overhead | Yes | 42200.375 | 2015-07-15 09:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0463 | 2015 | 7 | 15 | 9 | 0 | 15-0047650 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3800 | 8.5113 | 167_184 | <25mph | <15mph | HFTD - Distribution | 2015-07-15 09:00:00 | 208 | 13.379 | FALSE | <25mph | CTOC1 | 3.71 | 2015-07-15T15:27:00Z | 3 | 1 | E4962 | 6.01 | 2015-07-15T15:52:00Z | 4.99 | 32 | CTOC1 | 3.71 | 2015-07-15T15:27:00Z | 3 | 2 | C4503 | 7.38 | 2015-07-15T16:55:00Z | 7 | 65
PG&E | 2015-07-16 19:11 | 42201.7993 | 37.1989 | -119.7712 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 20334 ROAD 400 |  | 12000 | Conductor | Overhead | Yes | 42201.7993 | 2015-07-16 19:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0465 | 2015 | 7 | 16 | 19 | 11 | 15-0048064 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 8.6422 | 254_195 | <25mph | <15mph | HFTD - Distribution | 2015-07-16 19:11:00 | 210 | 13.1745 | FALSE | <25mph | D7022 | 1.32 | 2015-07-17T01:21:00Z | 11.01 | 20 | D7022 | 1.32 | 2015-07-17T01:21:00Z | 11.01 | 20 | D7022 | 1.32 | 2015-07-17T01:21:00Z | 11.01 | 38 | D7022 | 1.32 | 2015-07-17T01:21:00Z | 11.01 | 38
PG&E | 2015-07-18 17:00 | 42203.7083 | 38.8383 | -123.6297 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | off HWY 1 PA |  | 12000 | Conductor | Overhead | Yes | 42203.7083 | 2015-07-18 17:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0470 | 2015 | 7 | 18 | 17 | 0 | 15-0048394 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 51806 | 18.0824 | 86_287 | <25mph | <15mph | HFTD - Distribution | 2015-07-18 17:00:00 | 215 | 27.3037 | FALSE | 25-40mph |  |  |  | 0 | 0 | ANVC1 | 6.68 | 2015-07-18T23:36:00Z | 14.99 | 10 |  |  |  | 0 | 0 | ANVC1 | 6.68 | 2015-07-18T23:36:00Z | 14.99 | 20
PG&E | 2015-07-22 14:21 | 42207.5979 | 38.7935 | -120.714 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | s\ 3204 stope dr |  | 12000 | Conductor | Overhead | Yes | 42207.5979 | 2015-07-22 14:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0478 | 2015 | 7 | 22 | 14 | 21 | 15-0049908 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 149206 | 14.9339 | 212_283 | <25mph | <15mph | HFTD - Distribution | 2015-07-22 14:21:00 | 223 | 15.8107 | FALSE | <25mph | E3165 | 1.79 | 2015-07-22T20:38:00Z | 10 | 5 | BDMC1 | 7.66 | 2015-07-22T20:36:00Z | 17 | 24 | E3165 | 1.79 | 2015-07-22T21:39:00Z | 14 | 11 | BDMC1 | 7.66 | 2015-07-22T20:36:00Z | 17 | 51
PG&E | 2015-07-24 14:30 | 42209.6042 | 36.6913 | -119.0312 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46970 DUNLAP RD | YES | 0 – 750 | Transformer | Overhead | Yes | 42209.6042 | 2015-07-24 14:30 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0482 | 2015 | 7 | 24 | 14 | 30 | 15-0050401 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 281 | 12.3885 | 287_168 | <25mph | <15mph | HFTD - Distribution | 2015-07-24 14:30:00 | 227 | 13.0893 | FALSE | <25mph | PHRC1 | 0.81 | 2015-07-24T20:58:00Z | 14.99 | 1 | PHRC1 | 0.81 | 2015-07-24T20:58:00Z | 14.99 | 11 | PHRC1 | 0.81 | 2015-07-24T21:58:00Z | 15.99 | 2 | PHRC1 | 0.81 | 2015-07-24T21:58:00Z | 15.99 | 24
PG&E | 2015-07-26 12:25 | 42211.5174 | 39.1586 | -121.0634 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 15499 ALLISON RANCH RD |  | 12000 | Conductor | Overhead | Yes | 42211.5174 | 2015-07-26 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0485 | 2015 | 7 | 26 | 12 | 25 | 15-0050558 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2224 | 13.0644 | 197_303 | <25mph | <15mph | HFTD - Distribution | 2015-07-26 12:25:00 | 230 | 13.6917 | FALSE | <25mph | E1789 | 3.9 | 2015-07-26T19:24:00Z | 12.01 | 10 | E1789 | 3.9 | 2015-07-26T19:24:00Z | 12.01 | 68 | E1789 | 3.9 | 2015-07-26T19:54:00Z | 12.01 | 20 | E6355 | 6.63 | 2015-07-26T20:21:00Z | 12.01 | 133
PG&E | 2015-07-30 17:56 | 42215.7472 | 37.9021 | -120.4739 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101019808 |  | 17000 | Conductor | Overhead | Yes | 42215.7472 | 2015-07-30 17:56 | Contact From Object | N.A. | Other | Electric Facility | Unknown | osprey nest | Other/Unknown | 0499 | 2015 | 7 | 30 | 17 | 56 | 15-0051764 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 615 | 11.6086 | 222_234 | <25mph | <15mph | HFTD - Distribution | 2015-07-30 17:56:00 | 244 | 16.9062 | FALSE | <25mph |  |  |  | 0 | 0 | GNSC1 | 4.96 | 2015-07-31T00:03:00Z | 18.99 | 1 |  |  |  | 0 | 0 | GNSC1 | 4.96 | 2015-07-31T00:03:00Z | 18.99 | 2
PG&E | 2015-07-30 19:11 | 42215.7993 | 37.8102 | -120.1287 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE |  |  | 17000 | Conductor | Overhead | Yes | 42215.7993 | 2015-07-30 19:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0500 | 2015 | 7 | 30 | 19 | 11 | 15-0051772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26776 | 10.007 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2015-07-30 19:11:00 | 245 | 11.7658 | FALSE | <25mph | SEWC1 | 1.66 | 2015-07-31T01:16:00Z | 14.99 | 5 | SEWC1 | 1.66 | 2015-07-31T01:16:00Z | 14.99 | 7 | SEWC1 | 1.66 | 2015-07-31T01:16:00Z | 14.99 | 10 | SEWC1 | 1.66 | 2015-07-31T01:16:00Z | 14.99 | 14
PG&E | 2015-07-31 22:45 | 42216.9479 | 38.3805 | -120.5628 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS FROM 1958 QUAIL LN WEST POINT | None | 12000 | Conductor | Overhead | Yes | 42216.9479 | 2015-07-31 22:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0503 | 2015 | 7 | 31 | 22 | 45 | 15-0052033 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 33559 | 6.4734 | 218_260 | <25mph | <15mph | HFTD - Distribution | 2015-07-31 22:45:00 | 248 | 15.0324 | FALSE | <25mph | AT450 | 2.7 | 2015-08-01T05:19:00Z | 3 | 3 | C9148 | 7.8 | 2015-08-01T04:48:00Z | 7 | 20 | AT450 | 2.7 | 2015-08-01T06:45:00Z | 4 | 5 | C9148 | 7.8 | 2015-08-01T04:48:00Z | 7 | 38
PG&E | 2015-08-01 14:30 | 42217.6042 | 34.9524 | -120.2952 | Vegetation | Rural | 10 - 99 Acres | Unknown |  | 101868639 |  | 12000 | Conductor | Overhead | Yes | 42217.6042 | 2015-08-01 14:30 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0505 | 2015 | 8 | 1 | 14 | 30 | 15-0052506 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 1528 | 14.5808 | 232_71 | <25mph | <15mph | HFTD - Distribution | 2015-08-01 14:30:00 | 250 | 15.69 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2015-08-02 16:24 | 42218.6833 | 37.6317 | -120.1547 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101076992 |  | 21000 | Conductor | Overhead | Yes | 42218.6833 | 2015-08-02 16:24 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0508 | 2015 | 8 | 2 | 16 | 24 | 15-0064792 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 13.5475 | 236_219 | <25mph | <15mph | HFTD - Distribution | 2015-08-02 16:24:00 | 253 | 15.2166 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2015-08-03 00:07 | 42219.0049 | 40.5056 | -122.347 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | COTTONWOOD FIRE DEPT | 101503428 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42219.0049 | 2015-08-03 00:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0509 | 2015 | 8 | 3 | 0 | 7 | 15-0052184 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 10427 | 9.7241 | 143_378 | <25mph | <15mph | HFTD - Distribution | 2015-08-03 00:07:00 | 254 | 13.2206 | FALSE | <25mph | RRAC1 | 2.97 | 2015-08-03T06:24:00Z | 8.01 | 7 | RRAC1 | 2.97 | 2015-08-03T06:24:00Z | 8.01 | 15 | RRAC1 | 2.97 | 2015-08-03T06:24:00Z | 8.01 | 14 | RRAC1 | 2.97 | 2015-08-03T06:24:00Z | 8.01 | 30
PG&E | 2015-08-03 17:53 | 42219.7451 | 39.3361 | -121.1894 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Pole 000/008 |  | 60000 | Conductor | Overhead | Yes | 42219.7451 | 2015-08-03 17:53 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0510 | 2015 | 8 | 3 | 17 | 53 | TM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 11.0618 | 191_313 | <25mph | <15mph | HFTD - Transmission | 2015-08-03 17:53:00 | 255 | 11.5241 | FALSE | <25mph |  |  |  | 0 | 0 | RRRC1 | 4.47 | 2015-08-04T00:13:00Z | 14 | 30 |  |  |  | 0 | 0 | RRRC1 | 4.47 | 2015-08-04T01:13:00Z | 14.99 | 60
PG&E | 2015-08-04 16:05 | 42220.6701 | 40.0822 | -121.1538 | Vegetation | Rural | < 0.25 Acres | Fire Agency | USFS | 100441220 | None | 0 – 750 | Fuse | Overhead | Yes | 42220.6701 | 2015-08-04 16:05 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0511 | 2015 | 8 | 4 | 16 | 5 | 15-0052743 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 4591 | 11.3093 | 193_354 | <25mph | <15mph | HFTD - Distribution | 2015-08-04 16:05:00 | 256 | 18.1222 | FALSE | <25mph |  |  |  | 0 | 0 | TR180 | 5.53 | 2015-08-04T22:59:00Z | 14 | 1 |  |  |  | 0 | 0 | TR180 | 5.53 | 2015-08-04T22:59:00Z | 14 | 2
PG&E | 2015-08-04 17:57 | 42220.7479 | 37.5879 | -120.229 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Str. 007/019 |  | 70000 | Conductor | Overhead | Yes | 42220.7479 | 2015-08-04 17:57 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0512 | 2015 | 8 | 4 | 17 | 57 | LB-2015-028 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 10.9398 | 233_216 | <25mph | <15mph | HFTD - Transmission | 2015-08-04 17:57:00 | 257 | 10.9398 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2015-08-07 06:32 | 42223.2722 | 37.84 | -122.1823 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100498058 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42223.2722 | 2015-08-07 06:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0517 | 2015 | 8 | 7 | 6 | 32 | 15-0053493 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.7497 | 148_230 | <25mph | <15mph | HFTD - Distribution | 2015-08-07 06:32:00 | 261 | 20.6611 | FALSE | <25mph | ONOC1 | 2.72 | 2015-08-07T12:33:00Z | 14 | 60 | LTRC1 | 6.31 | 2015-08-07T13:28:00Z | 24.99 | 155 | ONOC1 | 2.72 | 2015-08-07T12:33:00Z | 14 | 120 | LTRC1 | 6.31 | 2015-08-07T13:28:00Z | 24.99 | 305
PG&E | 2015-08-08 07:42 | 42224.3208 | 39.2007 | -121.2137 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100076217 | Pacific Bell | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0519 | 2015 | 8 | 8 | 7 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 14.1661 | 190_305 | <25mph | <15mph | HFTD - Distribution | 2015-08-08 07:42:00 | 263 | 14.9803 | FALSE | <25mph | E2572 | 2.41 | 2015-08-08T13:53:00Z | 1.01 | 13 | E1789 | 5.79 | 2015-08-08T14:12:00Z | 4.99 | 42 | E2572 | 2.41 | 2015-08-08T15:38:00Z | 1.01 | 20 | E1789 | 5.79 | 2015-08-08T15:42:00Z | 4.99 | 77
PG&E | 2015-08-12 17:38 | 42228.7347 | 40.2153 | -123.8681 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 1 SP LD SD METER 1007960761 |  | 12000 | Conductor | Overhead | Yes | 42228.7347 | 2015-08-12 17:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0525 | 2015 | 8 | 12 | 17 | 38 | 15-0054643 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 14640 | 10.9518 | 79_363 | <25mph | <15mph | HFTD - Distribution | 2015-08-12 17:38:00 | 269 | 13.2342 | FALSE | <25mph |  |  |  | 0 | 0 | ERCC1 | 5.81 | 2015-08-13T00:28:00Z | 15.99 | 1 |  |  |  | 0 | 0 | ERCC1 | 5.81 | 2015-08-13T00:28:00Z | 15.99 | 2
PG&E | 2015-08-13 03:46 | 42229.1569 | 37.2072 | -119.7343 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 44365 SAVAGE RD COARSEGOLD |  | 21000 | Conductor | Overhead | Yes | 42229.1569 | 2015-08-13 03:46 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0526 | 2015 | 8 | 13 | 3 | 46 | 15-0054655 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 7600 | 7.8941 | 255_196 | <25mph | <15mph | HFTD - Distribution | 2015-08-13 03:46:00 | 270 | 10.403 | FALSE | <25mph | D7022 | 2.54 | 2015-08-13T10:41:00Z | 0 | 6 | E5766 | 4.34 | 2015-08-13T10:42:00Z | 0 | 18 | D7022 | 2.54 | 2015-08-13T11:41:00Z | 0 | 12 | E5766 | 4.34 | 2015-08-13T11:42:00Z | 0 | 36
PG&E | 2015-08-14 15:09 | 42230.6312 | 40.9829 | -121.7802 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101514540 |  | 21000 | Conductor | Overhead | Yes | 42230.6312 | 2015-08-14 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0530 | 2015 | 8 | 14 | 15 | 9 | 15-0055136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3072 | 14.8278 | 167_404 | <25mph | <15mph | HFTD - Distribution | 2015-08-14 15:09:00 | 274 | 16.5644 | FALSE | <25mph |  |  |  | 0 | 0 | AS418 | 7.42 | 2015-08-14T21:31:00Z | 17 | 6 |  |  |  | 0 | 0 | AS418 | 7.42 | 2015-08-14T23:01:00Z | 17 | 12
PG&E | 2015-08-14 17:44 | 42230.7389 | 37.8894 | -120.4933 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | ENTRANCE TO 14650 HWY 108, JAMESTOWN |  | 17000 | Conductor | Overhead | Yes | 42230.7389 | 2015-08-14 17:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0531 | 2015 | 8 | 14 | 17 | 44 | 15-0055160 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 1726 | 11.4655 | 222_233 | <25mph | <15mph | HFTD - Distribution | 2015-08-14 17:44:00 | 275 | 13.236 | FALSE | <25mph | GNSC1 | 3.85 | 2015-08-15T00:03:00Z | 17 | 1 | GNSC1 | 3.85 | 2015-08-15T00:03:00Z | 17 | 8 | GNSC1 | 3.85 | 2015-08-15T00:03:00Z | 17 | 2 | GNSC1 | 3.85 | 2015-08-15T00:03:00Z | 17 | 15
PG&E | 2015-08-15 13:41 | 42231.5701 | 37.9607 | -122.5709 | Vegetation | Urban | < 0.25 Acres | Fire Agency | COUNTY FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42231.5701 | 2015-08-15 13:41 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0533 | 2015 | 8 | 15 | 13 | 41 | 15-0055217 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 5973 | 6.6199 | 131_237 | <25mph | <15mph | HFTD - Distribution | 2015-08-15 13:41:00 | 277 | 12.8653 | FALSE | <25mph | MDEC1 | 2.44 | 2015-08-15T20:36:00Z | 8.01 | 5 | NBRC1 | 5.44 | 2015-08-15T20:33:00Z | 13 | 10 | MDEC1 | 2.44 | 2015-08-15T21:36:00Z | 12.01 | 10 | NBRC1 | 5.44 | 2015-08-15T21:33:00Z | 14 | 20
PG&E | 2015-08-16 07:35 | 42232.316 | 35.4572 | -120.6567 | Vegetation | Rural | < 3 meters | Utility: PG&E |  | 8932 SAN GABRIEL RD. SW C/O OF LOT, Atascadero | None | 0 – 750 | Conductor | Overhead | Yes | 42232.316 | 2015-08-16 07:35 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0534 | 2015 | 8 | 16 | 7 | 35 | 15-0055284 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.0129 | 215_99 | <25mph | <15mph | HFTD - Distribution | 2015-08-16 07:35:00 | 278 | 16.9932 | FALSE | <25mph | E1179 | 1.71 | 2015-08-16T14:13:00Z | 2.01 | 4 | E1179 | 1.71 | 2015-08-16T14:13:00Z | 2.01 | 9 | E2260 | 2.13 | 2015-08-16T15:10:00Z | 2.01 | 11 | E2260 | 2.13 | 2015-08-16T15:10:00Z | 2.01 | 19
PG&E | 2015-08-17 08:37 | 42233.359 | 37.0757 | -122.023 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101800237 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0537 | 2015 | 8 | 17 | 8 | 37 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 1.4249 | 154_188 | <25mph | <15mph | HFTD - Distribution | 2015-08-17 08:37:00 | 281 | 11.7495 | FALSE | <25mph | E5965 | 3.61 | 2015-08-17T15:35:00Z | 4 | 32 | AR172 | 6.98 | 2015-08-17T15:30:00Z | 4.99 | 145 | E5965 | 3.61 | 2015-08-17T16:35:00Z | 7 | 63 | E5965 | 3.61 | 2015-08-17T16:35:00Z | 7 | 286
PG&E | 2015-08-17 17:33 | 42233.7312 | 38.8337 | -123.5533 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 14 spans load side 2345 |  | 12000 | Conductor | Overhead | Yes | 42233.7312 | 2015-08-17 17:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0539 | 2015 | 8 | 17 | 17 | 33 | 15-0055664 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 676 | 5.6157 | 90_286 | <25mph | <15mph | HFTD - Distribution | 2015-08-17 17:33:00 | 283 | 9.4465 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2015-08-17 20:57 | 42233.8729 | 36.6867 | -119.0612 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46371 ORCHARD DRIVE |  | 12000 | Conductor | Overhead | Yes | 42233.8729 | 2015-08-17 20:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0540 | 2015 | 8 | 17 | 20 | 57 | 15-0055696 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 34398 | 8.6424 | 285_168 | <25mph | <15mph | HFTD - Distribution | 2015-08-17 20:57:00 | 284 | 13.6283 | FALSE | <25mph | PHRC1 | 2.47 | 2015-08-18T02:58:00Z | 5.99 | 1 | PHRC1 | 2.47 | 2015-08-18T02:58:00Z | 5.99 | 2 | PHRC1 | 2.47 | 2015-08-18T03:58:00Z | 8.99 | 2 | PHRC1 | 2.47 | 2015-08-18T03:58:00Z | 8.99 | 14
PG&E | 2015-08-19 06:20 | 42235.2639 | 39.2831 | -123.2931 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | MTR#50001225 | None | 12000 | Conductor | Overhead | Yes | 42235.2639 | 2015-08-19 06:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0545 | 2015 | 8 | 19 | 6 | 20 | 15-0055982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5403 | 1.4303 | 102_311 | <25mph | <15mph | HFTD - Distribution | 2015-08-19 06:20:00 | 289 | 19.8186 | FALSE | <25mph | AU552 | 3.69 | 2015-08-19T12:42:00Z | 5.99 | 12 | AU552 | 3.69 | 2015-08-19T12:42:00Z | 5.99 | 40 | AU552 | 3.69 | 2015-08-19T12:42:00Z | 5.99 | 24 | AU552 | 3.69 | 2015-08-19T12:42:00Z | 5.99 | 78
PG&E | 2015-08-22 20:38 | 42238.8597 | 38.7748 | -120.8564 | Vegetation | Rural | < 3 meters | Self Extinguished |  | at base of co pole 21721 - 720 Woodridge Rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42238.8597 | 2015-08-22 20:38 | Contact From Object | N.A. | Vegetation | Communication Facility | Unknown | tree hit phone lines | Fell into (Moderate-Severe defect) | 0549 | 2015 | 8 | 22 | 20 | 38 | 15-0056766 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26513 | 9.2929 | 206_282 | <25mph | <15mph | HFTD - Distribution | 2015-08-22 20:38:00 | 293 | 10.7008 | FALSE | <25mph | E5691 | 3.87 | 2015-08-23T03:21:00Z | 4 | 12 | E5691 | 3.87 | 2015-08-23T03:21:00Z | 4 | 45 | E5691 | 3.87 | 2015-08-23T03:21:00Z | 4 | 24 | E5691 | 3.87 | 2015-08-23T03:21:00Z | 4 | 89
PG&E | 2015-08-24 22:48 | 42240.95 | 37.896 | -122.6011 | Vegetation | Rural | < 3 meters | Fire Agency | marin county fire | 200' east of pan toll rd 50' north of panoramic hwy |  | 12000 | Unknown | Overhead | Yes | 42240.95 | 2015-08-24 22:48 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0552 | 2015 | 8 | 24 | 22 | 48 | 15-0057082 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 1128 | 8.5935 | 130_234 | <25mph | <15mph | HFTD - Distribution | 2015-08-24 22:48:00 | 296 | 14.2171 | FALSE | <25mph | MDEC1 | 2.32 | 2015-08-25T05:36:00Z | 13 | 5 | MDEC1 | 2.32 | 2015-08-25T05:36:00Z | 13 | 9 | MDEC1 | 2.32 | 2015-08-25T06:36:00Z | 14.99 | 10 | MDEC1 | 2.32 | 2015-08-25T06:36:00Z | 14.99 | 18
PG&E | 2015-08-26 12:04 | 42242.5028 | 37.9638 | -122.5243 | Vegetation | Urban | < 0.25 Acres | Fire Agency | srfd | 102242504 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42242.5028 | 2015-08-26 12:04 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0555 | 2015 | 8 | 26 | 12 | 4 | 15-0057475 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 28873 | 7.5325 | 133_237 | <25mph | <15mph | HFTD - Distribution | 2015-08-26 12:04:00 | 299 | 14.8961 | FALSE | <25mph | D7094 | 3.73 | 2015-08-26T18:29:00Z | 4.99 | 4 | MDEC1 | 4.24 | 2015-08-26T18:36:00Z | 14 | 20 | D7094 | 3.73 | 2015-08-26T19:30:00Z | 7 | 8 | MDEC1 | 4.24 | 2015-08-26T18:36:00Z | 14 | 41
PG&E | 2015-08-26 23:49 | 42242.9924 | 36.3897 | -121.3653 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101756678 | None | 21000 | Conductor | Overhead | Yes | 42242.9924 | 2015-08-26 23:49 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0557 | 2015 | 8 | 26 | 23 | 49 | 15-0057613 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 8445 | 14.6722 | 183_150 | <25mph | <15mph | HFTD - Distribution | 2015-08-26 23:49:00 | 301 | 28.5279 | FALSE | 25-40mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2015-08-27 03:30 | 42243.1458 | 37.8448 | -122.1992 | Vegetation | Urban | < 0.25 Acres | Unknown |  | 100487196 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42243.1458 | 2015-08-27 03:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0558 | 2015 | 8 | 27 | 3 | 30 | 15-0057619 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 176351 | 8.4259 | 147_231 | <25mph | <15mph | HFTD - Distribution | 2015-08-27 03:30:00 | 302 | 13.0131 | FALSE | <25mph | E4855 | 1.92 | 2015-08-27T10:15:00Z | 7 | 59 | LTRC1 | 7.26 | 2015-08-27T10:28:00Z | 14.99 | 137 | E4855 | 1.92 | 2015-08-27T10:15:00Z | 7 | 112 | LTRC1 | 7.26 | 2015-08-27T10:28:00Z | 14.99 | 271
PG&E | 2015-08-28 11:48 | 42244.4917 | 38.8513 | -121.1469 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100055373 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0562 | 2015 | 8 | 28 | 11 | 48 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 8.8306 | 193_286 | <25mph | <15mph | HFTD - Distribution | 2015-08-28 11:48:00 | 306 | 13.8724 | FALSE | <25mph |  |  |  | 0 | 0 | PLTC1 | 7.53 | 2015-08-28T17:56:00Z | 10 | 16 |  |  |  | 0 | 0 | PLTC1 | 7.53 | 2015-08-28T18:56:00Z | 13 | 30
PG&E | 2015-08-28 12:02 | 42244.5014 | 37.9047 | -122.2058 | Vegetation | Rural | < 0.25 Acres | Fire Agency | EB MUD | 103623279 |  | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0563 | 2015 | 8 | 28 | 12 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 10.0355 | 147_234 | <25mph | <15mph | HFTD - Distribution | 2015-08-28 12:02:00 | 307 | 16.9223 | FALSE | <25mph | E5555 | 3.43 | 2015-08-28T18:54:00Z | 10 | 32 | E5555 | 3.43 | 2015-08-28T18:54:00Z | 10 | 123 | LBNL1 | 3.01 | 2015-08-28T19:45:00Z | 11.61 | 66 | E6179 | 6.07 | 2015-08-28T19:49:00Z | 13 | 251
PG&E | 2015-08-29 03:30 | 42245.1458 | 38.6302 | -122.8327 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Dirt road across from 3204 Rio Lindo Rd, Healdsburg |  | 12000 | Conductor | Overhead | Yes | 42245.1458 | 2015-08-29 03:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0566 | 2015 | 8 | 29 | 3 | 30 | 15-0058127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4780 | 9.2134 | 120_274 | <25mph | <15mph | HFTD - Distribution | 2015-08-29 03:30:00 | 310 | 15.1029 | FALSE | <25mph | D2144 | 1.2 | 2015-08-29T10:00:00Z | 3 | 9 | HWKC1 | 7.25 | 2015-08-29T09:56:00Z | 4.99 | 27 | D2144 | 1.2 | 2015-08-29T10:00:00Z | 3 | 15 | HWKC1 | 7.25 | 2015-08-29T10:56:00Z | 12.01 | 52
PG&E | 2015-08-30 17:05 | 42246.7118 | 38.4039 | -120.5559 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | centennial mine rd |  | 12000 | Conductor | Overhead | Yes | 42246.7118 | 2015-08-30 17:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0567 | 2015 | 8 | 30 | 17 | 5 | 15-0058273 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 40298 | 10.8566 | 219_261 | <25mph | <15mph | HFTD - Distribution | 2015-08-30 17:05:00 | 311 | 12.2451 | FALSE | <25mph | AT450 | 1.93 | 2015-08-30T23:45:00Z | 12.01 | 13 | C9148 | 6.15 | 2015-08-30T23:49:00Z | 14.99 | 27 | AT450 | 1.93 | 2015-08-30T23:45:00Z | 12.01 | 25 | C9148 | 6.15 | 2015-08-30T23:49:00Z | 14.99 | 53
PG&E | 2015-08-31 14:28 | 42247.6028 | 36.5325 | -121.1462 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 29401 Hwy 25 |  | 21000 | Conductor | Overhead | Yes | 42247.6028 | 2015-08-31 14:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0568 | 2015 | 8 | 31 | 14 | 28 | 15-0058455 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25668 | 4.8975 | 193_158 | <25mph | <15mph | HFTD - Distribution | 2015-08-31 14:28:00 | 312 | 19.6836 | FALSE | <25mph |  |  |  | 0 | 0 | PCLC1 | 4.27 | 2015-08-31T20:37:00Z | 13 | 1 |  |  |  | 0 | 0 | PCLC1 | 4.27 | 2015-08-31T20:37:00Z | 13 | 2
PG&E | 2015-09-04 07:49 | 42251.3257 | 40.2318 | -122.3643 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | E/O FRONTIER RD & N/O WAGON WAY |  | 12000 | Conductor | Overhead | Yes | 42251.3257 | 2015-09-04 07:49 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0577 | 2015 | 9 | 4 | 7 | 49 | 15-0059323 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 9563 | 2.343 | 142_362 | <25mph | <15mph | HFTD - Distribution | 2015-09-04 07:49:00 | 321 | 17.9748 | FALSE | <25mph | D6527 | 1.77 | 2015-09-04T13:53:00Z | 4.99 | 1 | E7114 | 5.07 | 2015-09-04T14:49:00Z | 24 | 4 | D6527 | 1.77 | 2015-09-04T13:53:00Z | 4.99 | 1 | E7114 | 5.07 | 2015-09-04T15:21:00Z | 30 | 7
PG&E | 2015-09-06 19:27 | 42253.8104 | 34.6195 | -120.2534 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Santa Barbara County Fire | meter# 1008400678 | Verizon | 12000 | Conductor | Overhead | Yes | 42253.8104 | 2015-09-06 19:27 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0582 | 2015 | 9 | 6 | 19 | 27 | 15-0059612 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 863 | 14.7315 | 234_53 | <25mph | <15mph | HFTD - Distribution | 2015-09-06 19:27:00 | 326 | 17.7534 | FALSE | <25mph |  |  |  | 0 | 0 | C9206 | 6.79 | 2015-09-07T02:01:00Z | 4.99 | 8 |  |  |  | 0 | 0 | C9206 | 6.79 | 2015-09-07T02:01:00Z | 4.99 | 15
PG&E | 2015-09-09 10:47 | 42256.4493 | 37.1041 | -121.8853 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100520291 |  | 12000 | Conductor | Overhead | Yes | 42256.4493 | 2015-09-09 10:47 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0587 | 2015 | 9 | 9 | 10 | 47 | 15-0060074 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 142401 | 4.2376 | 161_190 | <25mph | <15mph | HFTD - Distribution | 2015-09-09 10:47:00 | 331 | 18.9097 | FALSE | <25mph | E6085 | 0.69 | 2015-09-09T17:16:00Z | 8.01 | 10 | E6085 | 0.69 | 2015-09-09T17:16:00Z | 8.01 | 101 | E6085 | 0.69 | 2015-09-09T18:31:00Z | 10 | 20 | C2789 | 6.89 | 2015-09-09T18:40:00Z | 11.01 | 197
PG&E | 2015-09-10 05:42 | 42257.2375 | 37.4609 | -121.8434 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100619766 | None | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0588 | 2015 | 9 | 10 | 5 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 1.7354 | 163_209 | <25mph | <15mph | HFTD - Distribution | 2015-09-10 05:42:00 | 333 | 13.8129 | FALSE | <25mph | E3968 | 2.89 | 2015-09-10T12:37:00Z | 2.01 | 12 | RSPC1 | 6.56 | 2015-09-10T12:28:00Z | 7 | 16 | E3968 | 2.89 | 2015-09-10T12:37:00Z | 2.01 | 25 | RSPC1 | 6.56 | 2015-09-10T13:28:00Z | 7 | 33
PG&E | 2015-09-10 16:24 | 42257.6833 | 38.5049 | -122.3535 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103159970 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42257.6833 | 2015-09-10 16:24 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0589 | 2015 | 9 | 10 | 16 | 24 | 15-0060610 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 130124 | 14.3548 | 141_267 | <25mph | <15mph | HFTD - Distribution | 2015-09-10 16:24:00 | 334 | 16.5969 | FALSE | <25mph |  |  |  | 0 | 0 | ATLC1 | 5.22 | 2015-09-10T22:29:00Z | 28.99 | 1 |  |  |  | 0 | 0 | ATLC1 | 5.22 | 2015-09-10T22:29:00Z | 28.99 | 2
PG&E | 2015-09-10 18:39 | 42257.7771 | 40.7569 | -123.7958 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 096/004 |  | 115000 | Conductor | Overhead | Yes | 42257.7771 | 2015-09-10 18:39 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0590 | 2015 | 9 | 10 | 18 | 39 | RM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 2.2423 | 82_393 | <25mph | <15mph | HFTD - Transmission | 2015-09-10 18:39:00 | 335 | 12.4043 | FALSE | <25mph |  |  |  | 0 | 0 | KNNC1 | 7.39 | 2015-09-11T00:55:00Z | 8.99 | 1 |  |  |  | 0 | 0 | KNNC1 | 7.39 | 2015-09-11T00:55:00Z | 8.99 | 2
PG&E | 2015-09-11 08:15 | 42258.3438 | 38.1094 | -122.87 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102293992 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42258.3438 | 2015-09-11 08:15 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0592 | 2015 | 9 | 11 | 8 | 15 | 15-0060698 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 32419 | 6.2068 | 118_246 | <25mph | <15mph | HFTD - Distribution | 2015-09-11 08:15:00 | 337 | 16.9176 | FALSE | <25mph | PREC1 | 3.64 | 2015-09-11T15:05:00Z | 8.99 | 1 | PTRCA | 4.48 | 2015-09-11T15:10:00Z | 12.91 | 7 | PREC1 | 3.64 | 2015-09-11T16:05:00Z | 10 | 2 | PTRCA | 4.48 | 2015-09-11T16:10:00Z | 13.4 | 14
PG&E | 2015-09-12 09:51 | 42259.4104 | 39.1164 | -121.0693 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | TOP OF AVALON PLACE, GRASS VALLEY TOWER NUMBER 19/152 40689729 |  | 115000 | Conductor | Overhead | Yes | 42259.4104 | 2015-09-12 09:51 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0594 | 2015 | 9 | 12 | 9 | 51 | VD-2015-079 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.5014 | 196_301 | <25mph | <15mph | HFTD - Transmission | 2015-09-12 09:51:00 | 339 | 14.0472 | FALSE | <25mph | E1789 | 3.95 | 2015-09-12T16:48:00Z | 7 | 8 | E1789 | 3.95 | 2015-09-12T16:48:00Z | 7 | 41 | E1789 | 3.95 | 2015-09-12T16:48:00Z | 7 | 16 | E1789 | 3.95 | 2015-09-12T16:48:00Z | 7 | 83
PG&E | 2015-09-12 11:09 | 42259.4646 | 38.603 | -120.6741 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101394996 |  | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0595 | 2015 | 9 | 12 | 11 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.0719 | 214_272 | <25mph | <15mph | HFTD - Distribution | 2015-09-12 11:09:00 | 340 | 13.2134 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2015-09-18 17:05 | 42265.7118 | 37.8992 | -120.4551 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101019893 |  | 17000 | Conductor | Overhead | Yes | 42265.7118 | 2015-09-18 17:05 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0602 | 2015 | 9 | 18 | 17 | 5 | 15-0062207 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 35222 | 9.055 | 223_234 | <25mph | <15mph | HFTD - Distribution | 2015-09-18 17:05:00 | 347 | 11.0018 | FALSE | <25mph |  |  |  | 0 | 0 | GNSC1 | 5.2 | 2015-09-19T00:03:00Z | 14.99 | 1 |  |  |  | 0 | 0 | GNSC1 | 5.2 | 2015-09-19T00:03:00Z | 14.99 | 2
PG&E | 2015-09-19 09:51 | 42266.4104 | 38.4755 | -122.9069 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FORESTVILLE | 103334444 |  | 12000 | Conductor | Overhead | Yes | 42266.4104 | 2015-09-19 09:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0603 | 2015 | 9 | 19 | 9 | 51 | 15-0062267 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 488 | 1.1332 | 117_266 | <25mph | <15mph | HFTD - Distribution | 2015-09-19 09:51:00 | 348 | 13.7107 | FALSE | <25mph | D4623 | 2.94 | 2015-09-19T16:36:00Z | 1.01 | 7 | E5234 | 7.03 | 2015-09-19T16:28:00Z | 5.99 | 81 | D4623 | 2.94 | 2015-09-19T17:51:00Z | 3 | 13 | E5234 | 7.03 | 2015-09-19T16:28:00Z | 5.99 | 171
PG&E | 2015-09-20 18:53 | 42267.7868 | 39.8638 | -121.6599 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42267.7868 | 2015-09-20 18:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0604 | 2015 | 9 | 20 | 18 | 53 | 15-0062407 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 3479 | 4.6718 | 171_342 | <25mph | <15mph | HFTD - Distribution | 2015-09-20 18:53:00 | 349 | 13.083 | FALSE | <25mph | C8878 | 0.76 | 2015-09-21T01:53:00Z | 4 | 16 | CSTC1 | 5.81 | 2015-09-21T01:51:00Z | 10 | 19 | C8878 | 0.76 | 2015-09-21T02:33:00Z | 4 | 33 | CSTC1 | 5.81 | 2015-09-21T01:51:00Z | 10 | 38
PG&E | 2015-09-21 04:06 | 42268.1708 | 38.6587 | -121.0404 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 1of3@13833 |  | 21000 | Conductor | Overhead | Yes | 42268.1708 | 2015-09-21 04:06 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0605 | 2015 | 9 | 21 | 4 | 6 | 15-0062450 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | 162824 | 13.8981 | 198_275 | <25mph | <15mph | HFTD - Distribution | 2015-09-21 04:06:00 | 350 | 14.8386 | FALSE | <25mph | D4464 | 3.9 | 2015-09-21T10:25:00Z | 5.99 | 20 | BENC1 | 7.43 | 2015-09-21T10:59:00Z | 8.99 | 46 | D4464 | 3.9 | 2015-09-21T11:40:00Z | 7 | 37 | BENC1 | 7.43 | 2015-09-21T11:59:00Z | 8.99 | 79
PG&E | 2015-09-21 14:23 | 42268.5993 | 40.4786 | -123.771 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | mile marker 29.1, e of hairpin turn |  | 12000 | Conductor | Overhead | Yes | 42268.5993 | 2015-09-21 14:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0606 | 2015 | 9 | 21 | 14 | 23 | 15-0062556 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 13197 | 13.8607 | 83_377 | <25mph | <15mph | HFTD - Distribution | 2015-09-21 14:23:00 | 351 | 13.9527 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2015-09-24 04:30 | 42271.1875 | 38.6769 | -123.314 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Str. 041/007 |  | 60000 | Conductor | Overhead | Yes | 42271.1875 | 2015-09-24 04:30 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0613 | 2015 | 9 | 24 | 4 | 30 | FU-2015-057 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 22680 | 6.5939 | 100_277 | <25mph | <15mph | HFTD - Transmission | 2015-09-24 04:30:00 | 358 | 13.8122 | FALSE | <25mph |  |  |  | 0 | 0 | D2695 | 7.76 | 2015-09-24T11:12:00Z | 8.99 | 4 |  |  |  | 0 | 0 | D2695 | 7.76 | 2015-09-24T11:12:00Z | 8.99 | 8
PG&E | 2015-09-24 13:56 | 42271.5806 | 39.3508 | -121.2454 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 9692 Rices-Texas Hill rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42271.5806 | 2015-09-24 13:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0614 | 2015 | 9 | 24 | 13 | 56 | 15-0063159 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 51917 | 10.3419 | 189_313 | <25mph | <15mph | HFTD - Distribution | 2015-09-24 13:56:00 | 359 | 13.3743 | FALSE | <25mph |  |  |  | 0 | 0 | RRRC1 | 7.59 | 2015-09-24T20:13:00Z | 10 | 2 |  |  |  | 0 | 0 | BNGC1 | 7.8 | 2015-09-24T21:51:00Z | 12.01 | 4
PG&E | 2015-09-25 17:28 | 42272.7278 | 38.7169 | -120.7693 | Vegetation | Rural | < 0.25 Acres | Fire Agency | el dorado F D | 101405928 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42272.7278 | 2015-09-25 17:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0616 | 2015 | 9 | 25 | 17 | 28 | 15-0063666 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 111180 | 8.3925 | 209_279 | <25mph | <15mph | HFTD - Distribution | 2015-09-25 17:28:00 | 361 | 11.4196 | FALSE | <25mph | E5691 | 2.8 | 2015-09-25T23:45:00Z | 7 | 16 | C6129 | 4.54 | 2015-09-25T23:39:00Z | 12.01 | 40 | E5691 | 2.8 | 2015-09-25T23:45:00Z | 7 | 28 | C6129 | 4.54 | 2015-09-25T23:39:00Z | 12.01 | 76
PG&E | 2015-09-28 09:42 | 42275.4042 | 37.9623 | -122.1765 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100458692 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42275.4042 | 2015-09-28 09:42 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0619 | 2015 | 9 | 28 | 9 | 42 | 15-0066062 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 2125 | 9.6053 | 148_237 | <25mph | <15mph | HFTD - Distribution | 2015-09-28 09:42:00 | 364 | 19.5931 | FALSE | <25mph | PLEC1 | 3.75 | 2015-09-28T16:28:00Z | 14.99 | 6 | UPBC1 | 6.07 | 2015-09-28T15:42:00Z | 20.98 | 147 | PLEC1 | 3.75 | 2015-09-28T16:28:00Z | 14.99 | 7 | MZXC1 | 5.72 | 2015-09-28T17:18:00Z | 20.98 | 286
PG&E | 2015-09-30 17:25 | 42277.7257 | 38.5747 | -120.682 | Vegetation | Rural | < 0.25 Acres | Fire Agency | el dorado county | 7901 shenandoah ln |  | 21000 | Conductor | Overhead | Yes | 42277.7257 | 2015-09-30 17:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0625 | 2015 | 9 | 30 | 17 | 25 | 15-0066934 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 28912 | 2.1463 | 213_271 | <25mph | <15mph | HFTD - Distribution | 2015-09-30 17:25:00 | 370 | 8.8317 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2015-10-03 07:27 | 42280.3104 | 39.0633 | -122.6237 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 2323 new long valley rd | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0631 | 2015 | 10 | 3 | 7 | 27 | No ILIS or TOTL available | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 6.9412 | 130_298 | <25mph | <15mph | HFTD - Distribution | 2015-10-03 07:27:00 | 376 | 21.7099 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2015-10-03 21:11 | 42280.8826 | 39.7358 | -121.6855 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | honey run rd at cutouts 16015 |  | 12000 | Conductor | Overhead | Yes | 42280.8826 | 2015-10-03 21:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0632 | 2015 | 10 | 3 | 21 | 11 | 15-0067708 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 10499 | 20.0626 | 170_335 | <25mph | <15mph | HFTD - Distribution | 2015-10-03 21:11:00 | 377 | 26.1472 | FALSE | 25-40mph | PDEC1 | 3.46 | 2015-10-04T04:00:00Z | 14 | 1 | E4833 | 6.49 | 2015-10-04T03:45:00Z | 18.99 | 7 | PDEC1 | 3.46 | 2015-10-04T05:00:00Z | 15.99 | 2 | E4833 | 6.49 | 2015-10-04T03:45:00Z | 18.99 | 15
PG&E | 2015-10-04 01:03 | 42281.0437 | 39.7923 | -121.5803 | Vegetation | Urban | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42281.0437 | 2015-10-04 01:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0634 | 2015 | 10 | 4 | 1 | 3 | 15-0067711 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2697 | 33.2768 | 175_338 | 25-40mph | 30-45mph | HFTD - Distribution | 2015-10-04 01:03:00 | 378 | 33.2768 | FALSE | 25-40mph | E4833 | 1.69 | 2015-10-04T07:12:00Z | 18.01 | 13 | JBGC1 | 6.22 | 2015-10-04T07:13:00Z | 53.02 | 27 | E4833 | 1.69 | 2015-10-04T07:12:00Z | 18.01 | 25 | JBGC1 | 6.22 | 2015-10-04T07:13:00Z | 53.02 | 52
PG&E | 2015-10-04 01:32 | 42281.0639 | 39.2279 | -121.3774 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | in field at 6275 sandstonel ln |  | 12000 | Conductor | Overhead | Yes | 42281.0639 | 2015-10-04 01:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0635 | 2015 | 10 | 4 | 1 | 32 | 15-0067743 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 4021 | 16.6384 | 183_307 | <25mph | <15mph | HFTD - Distribution | 2015-10-04 01:32:00 | 379 | 28.3725 | FALSE | 25-40mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2015-10-07 15:04 | 42284.6277 | 35.3079 | -120.8328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101924901 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42284.6277 | 2015-10-07 15:04 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0640 | 2015 | 10 | 7 | 15 | 3 | 15-0068730 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 77896 | 15.4357 | 207_90 | <25mph | <15mph | HFTD - Distribution | 2015-10-07 15:03:00 | 384 | 16.4418 | FALSE | <25mph | E1668 | 0.48 | 2015-10-07T22:00:00Z | 15.99 | 5 | E1668 | 0.48 | 2015-10-07T22:00:00Z | 15.99 | 7 | E6113 | 0.7 | 2015-10-07T22:46:00Z | 18.01 | 11 | E6113 | 0.7 | 2015-10-07T22:46:00Z | 18.01 | 14
PG&E | 2015-10-09 06:32 | 42286.2722 | 38.364 | -122.9173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 320 Freestone St, Frestone | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0642 | 2015 | 10 | 9 | 6 | 32 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 2.6818 | 117_260 | <25mph | <15mph | HFTD - Distribution | 2015-10-09 06:32:00 | 386 | 15.5803 | FALSE | <25mph | D2849 | 3.33 | 2015-10-09T13:22:00Z | 3 | 22 | D2849 | 3.33 | 2015-10-09T13:22:00Z | 3 | 49 | D2849 | 3.33 | 2015-10-09T13:22:00Z | 3 | 44 | D2849 | 3.33 | 2015-10-09T13:22:00Z | 3 | 99
PG&E | 2015-10-16 09:43 | 42293.4049 | 39.187 | -123.2015 | Vegetation | Rural | < 3 meters | Unknown |  | 102196855 |  | 12000 | Conductor | Overhead | Yes | 42293.4049 | 2015-10-16 09:43 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0653 | 2015 | 10 | 16 | 9 | 43 | 15-0070948 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 65228 | 2.2696 | 105_305 | <25mph | <15mph | HFTD - Distribution | 2015-10-16 09:43:00 | 397 | 16.8813 | FALSE | <25mph | E7513 | 1.34 | 2015-10-16T16:08:00Z | 3 | 13 | E7513 | 1.34 | 2015-10-16T16:08:00Z | 3 | 25 | E7513 | 1.34 | 2015-10-16T17:38:00Z | 4 | 25 | E7513 | 1.34 | 2015-10-16T17:38:00Z | 4 | 49
PG&E | 2015-10-25 05:50 | 42302.2431 | 37.7843 | -121.7683 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | cutouts 9504 |  | 21000 | Conductor | Overhead | Yes | 42302.2431 | 2015-10-25 05:50 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0657 | 2015 | 10 | 25 | 5 | 50 | 15-0073203 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 10710 | 23.3456 | 166_227 | <25mph | <15mph | HFTD - Distribution | 2015-10-25 05:50:00 | 401 | 23.3456 | FALSE | <25mph | VAQC1 | 1.86 | 2015-10-25T12:45:00Z | 15.99 | 2 | VAQC1 | 1.86 | 2015-10-25T12:45:00Z | 15.99 | 2 | VAQC1 | 1.86 | 2015-10-25T13:45:00Z | 18.99 | 4 | VAQC1 | 1.86 | 2015-10-25T13:45:00Z | 18.99 | 4
PG&E | 2015-10-30 04:29 | 42307.1868 | 39.5059 | -123.7672 | Vegetation | Rural | < 3 meters | Fire Agency | local fire | in field next to hwy / 1 span SS of Fuse 4617 |  | 12000 | Conductor | Overhead | Yes | 42307.1868 | 2015-10-30 04:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0661 | 2015 | 10 | 30 | 4 | 29 | 15-0074188 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 273183 | 4.1098 | 82_324 | <25mph | <15mph | HFTD - Distribution | 2015-10-30 04:29:00 | 405 | 16.2052 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2015-10-30 17:13 | 42307.7174 | 38.3166 | -120.7226 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 7600 HWY 49, Jackson | None | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0662 | 2015 | 10 | 30 | 17 | 13 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 8.0122 | 211_256 | <25mph | <15mph | HFTD - Distribution | 2015-10-30 17:13:00 | 406 | 12.822 | FALSE | <25mph |  |  |  | 0 | 0 | MTZC1 | 6.34 | 2015-10-30T23:56:00Z | 11.01 | 1 |  |  |  | 0 | 0 | MTZC1 | 6.34 | 2015-10-30T23:56:00Z | 11.01 | 2
PG&E | 2015-10-31 07:45 | 42308.3229 | 38.1157 | -120.8931 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal FIRE | 103763040 |  | 12000 | Conductor | Overhead | Yes | 42308.3229 | 2015-10-31 07:45 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0663 | 2015 | 10 | 31 | 7 | 45 | 15-0074424 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 314565 | 11.8471 | 204_245 | <25mph | <15mph | HFTD - Distribution | 2015-10-31 07:45:00 | 407 | 12.187 | FALSE | <25mph |  |  |  | 0 | 0 | CMAC1 | 7.6 | 2015-10-31T13:59:00Z | 12.01 | 1 |  |  |  | 0 | 0 | CMAC1 | 7.6 | 2015-10-31T14:59:00Z | 13 | 2
PG&E | 2015-11-09 05:55 | 42317.2465 | 34.9984 | -120.3634 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42317.2465 | 2015-11-09 05:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0673 | 2015 | 11 | 9 | 5 | 55 | 15-0076534 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 205393 | 8.4294 | 228_73 | <25mph | <15mph | HFTD - Distribution | 2015-11-09 05:55:00 | 417 | 17.7768 | FALSE | <25mph |  |  |  | 0 | 0 | AU609 | 7.47 | 2015-11-09T13:07:00Z | 2.01 | 4 |  |  |  | 0 | 0 | AU609 | 7.47 | 2015-11-09T13:07:00Z | 2.01 | 7
PG&E | 2015-11-15 16:30 | 42323.6875 | 37.0007 | -121.885 | Vegetation | Rural | < 3 meters | Customer |  | 101691004 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42323.6875 | 2015-11-15 16:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0676 | 2015 | 11 | 15 | 16 | 30 | 15-0077978 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 25920 | 24.6094 | 161_184 | <25mph | <15mph | HFTD - Distribution | 2015-11-15 16:30:00 | 420 | 25.3186 | FALSE | 25-40mph | E7291 | 2.82 | 2015-11-16T00:21:00Z | 32.01 | 33 | E7291 | 2.82 | 2015-11-16T00:21:00Z | 32.01 | 123 | E7291 | 2.82 | 2015-11-16T00:21:00Z | 32.01 | 62 | E7291 | 2.82 | 2015-11-16T00:21:00Z | 32.01 | 232
PG&E | 2015-11-21 10:36 | 42329.4417 | 38.0679 | -120.1872 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101045952 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42329.4417 | 2015-11-21 10:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0677 | 2015 | 11 | 21 | 10 | 36 | 15-0079868 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18350 | 7.816 | 235_243 | <25mph | <15mph | HFTD - Distribution | 2015-11-21 10:36:00 | 421 | 16.6927 | FALSE | <25mph | MOUC1 | 3.29 | 2015-11-21T18:02:00Z | 17 | 1 | MOUC1 | 3.29 | 2015-11-21T18:02:00Z | 17 | 1 | MOUC1 | 3.29 | 2015-11-21T19:02:00Z | 18.01 | 2 | MOUC1 | 3.29 | 2015-11-21T19:02:00Z | 18.01 | 2
PG&E | 2015-12-01 12:03 | 42339.5021 | 35.6744 | -120.9932 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal FIRE | 101860660 |  | 21000 | Conductor | Overhead | Yes | 42339.5021 | 2015-12-01 12:03 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0680 | 2015 | 12 | 1 | 12 | 3 | 15-0081983 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 42427 | 6.9865 | 200_111 | <25mph | <15mph | HFTD - Distribution | 2015-12-01 12:03:00 | 424 | 12.3916 | FALSE | <25mph |  |  |  | 0 | 0 | TABC1 | 4.07 | 2015-12-01T19:07:00Z | 8.99 | 1 |  |  |  | 0 | 0 | TABC1 | 4.07 | 2015-12-01T19:07:00Z | 8.99 | 2
PG&E | 2015-12-03 12:10 | 42341.5069 | 40.0277 | -120.9652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | usfs | spanish creek campground |  | 12000 | Conductor | Overhead | Yes | 42341.5069 | 2015-12-03 12:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0683 | 2015 | 12 | 3 | 12 | 10 | 15-0082505 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 196854 | 26.293 | 201_351 | 25-40mph | 15-30mph | HFTD - Distribution | 2015-12-03 12:10:00 | 427 | 26.9543 | FALSE | 25-40mph | CHAC1 | 3.2 | 2015-12-03T19:47:00Z | 47 | 2 | CHAC1 | 3.2 | 2015-12-03T19:47:00Z | 47 | 3 | CHAC1 | 3.2 | 2015-12-03T20:47:00Z | 59.01 | 4 | CHAC1 | 3.2 | 2015-12-03T20:47:00Z | 59.01 | 6
PG&E | 2015-12-08 12:41 | 42346.5285 | 38.2489 | -120.5228 | Other | Rural | Structure Only | Unknown |  | 7026 Railroad Flat Road, Mountain Ranch |  | 12000 | Conductor | Overhead | Yes | 42346.5285 | 2015-12-08 12:41 | Contact From Object | N.A. | Other | Electric Facility | Human Error | AT&T work error | Other/Unknown | 0684 | 2015 | 12 | 8 | 12 | 41 | 15-0083435 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1120 | 3.9918 | 220_253 | <25mph | <15mph | HFTD - Distribution | 2015-12-08 12:41:00 | 428 | 10.4116 | FALSE | <25mph | ESPC1 | 3.04 | 2015-12-08T20:13:00Z | 5.99 | 6 | ESPC1 | 3.04 | 2015-12-08T20:13:00Z | 5.99 | 6 | ESPC1 | 3.04 | 2015-12-08T21:13:00Z | 10 | 13 | ESPC1 | 3.04 | 2015-12-08T21:13:00Z | 10 | 13
PG&E | 2015-12-31 19:12 | 42369.8 | 37.1568 | -121.9868 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LOS GATOS MONTE SERENO SARATOGA | 100518215 | Verizon | 21000 | Conductor | Overhead | Yes | 42369.8 | 2015-12-31 19:12 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0689 | 2015 | 12 | 31 | 19 | 12 | 15-0087962 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7979 | 7.4149 | 156_193 | <25mph | <15mph | HFTD - Distribution | 2015-12-31 19:12:00 | 433 | 10.9251 | FALSE | <25mph | D8979 | 2.76 | 2016-01-01T02:57:00Z | 10 | 23 | E6085 | 6.01 | 2016-01-01T02:32:00Z | 10 | 176 | D8979 | 2.76 | 2016-01-01T04:08:00Z | 12.01 | 45 | D8979 | 2.76 | 2016-01-01T04:08:00Z | 12.01 | 346
PG&E | 2016-01-21 21:32 | 42390.8972 | 40.553 | -124.1116 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100994021 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42390.8972 | 2016-01-21 21:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0690 | 2016 | 1 | 21 | 21 | 32 | 16-0007239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 6468 | 26.2481 | 69_382 | 25-40mph | 15-30mph | HFTD - Distribution | 2016-01-21 21:32:00 | 434 | 29.6828 | FALSE | 25-40mph | KFOT | 1.14 | 2016-01-22T05:15:00Z | 36.82 | 28 | KFOT | 1.14 | 2016-01-22T05:15:00Z | 36.82 | 28 | KFOT | 1.14 | 2016-01-22T05:35:00Z | 48.34 | 55 | KFOT | 1.14 | 2016-01-22T05:35:00Z | 48.34 | 55
PG&E | 2016-01-23 15:41 | 42392.6535 | 39.9486 | -122.3728 | Vegetation | RURAL | < 0.25 Acres | Self Extinguished | N.A. | 101524077 |  | 12000 | Conductor | Overhead | Yes | 42392.6535 | 2016-01-23 15:41 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0691 | 2016 | 1 | 23 | 15 | 41 | 16-0007778 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 133520 | 6.2464 | 141_347 | <25mph | <15mph | HFTD - Distribution | 2016-01-23 15:41:00 | 435 | 27.5908 | FALSE | 25-40mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-02-05 20:50 | 42405.8681 | 40.0156 | -122.4333 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | TEHAMA COUNTY & LOCAL VOLUNTEER | 101529688 | None | 12000 | Conductor | Overhead | Yes | 42405.8681 | 2016-02-05 20:50 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0693 | 2016 | 2 | 5 | 20 | 50 | 16-0011034 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 11424 | 8.9717 | 139_351 | <25mph | <15mph | HFTD - Distribution | 2016-02-05 20:50:00 | 437 | 11.0459 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-02-08 03:55 | 42408.1632 | 39.7852 | -121.5056 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100337507 |  | 12000 | Conductor | Overhead | Yes | 42408.1632 | 2016-02-08 03:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0694 | 2016 | 2 | 8 | 3 | 55 | 16-0011201 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 87046 | 36.3276 | 178_337 | 25-40mph | 30-45mph | HFTD - Distribution | 2016-02-08 03:55:00 | 438 | 40.0336 | FALSE | 40-55mph | JBGC1 | 3.52 | 2016-02-08T11:13:00Z | 45.99 | 1 | JBGC1 | 3.52 | 2016-02-08T11:13:00Z | 45.99 | 23 | JBGC1 | 3.52 | 2016-02-08T12:13:00Z | 57 | 2 | JBGC1 | 3.52 | 2016-02-08T12:13:00Z | 57 | 46
PG&E | 2016-04-03 12:01 | 42463.5007 | 38.6804 | -123.125 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101968191 |  | 12000 | Conductor | Overhead | Yes | 42463.5007 | 2016-04-03 12:01 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0702 | 2016 | 4 | 3 | 12 | 1 | 16-0025794 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 3528 | 7.1346 | 108_277 | <25mph | <15mph | HFTD - Distribution | 2016-04-03 12:01:00 | 446 | 15.3303 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-04-08 13:14 | 42468.5514 | 39.0429 | -121.1002 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100086751 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42468.5514 | 2016-04-08 13:14 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0705 | 2016 | 4 | 8 | 13 | 14 | 16-0027237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 11817 | 10.7666 | 195_296 | <25mph | <15mph | HFTD - Distribution | 2016-04-08 13:14:00 | 449 | 10.7666 | FALSE | <25mph | C0713 | 3.59 | 2016-04-08T19:24:00Z | 8.01 | 17 | E1789 | 7.22 | 2016-04-08T20:00:00Z | 8.99 | 40 | C0713 | 3.59 | 2016-04-08T20:34:00Z | 10 | 33 | C0713 | 3.59 | 2016-04-08T20:34:00Z | 10 | 80
PG&E | 2016-04-13 19:28 | 42473.8111 | 40.4954 | -124.1219 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103659313 |  | 12000 | Conductor | Overhead | Yes | 42473.8111 | 2016-04-13 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0706 | 2016 | 4 | 13 | 19 | 28 | 16-0028421 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 688 | 19.0823 | 68_379 | <25mph | <15mph | HFTD - Distribution | 2016-04-13 19:28:00 | 450 | 22.9769 | FALSE | <25mph |  |  |  | 0 | 0 | KFOT | 4.03 | 2016-04-14T01:55:00Z | 32.21 | 30 |  |  |  | 0 | 0 | KFOT | 4.03 | 2016-04-14T01:55:00Z | 32.21 | 58
PG&E | 2016-04-21 09:25 | 42481.3924 | 39.293 | -123.769 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 103312287 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0711 | 2016 | 4 | 21 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 8.8774 | 81_312 | <25mph | <15mph | HFTD - Distribution | 2016-04-21 09:25:00 | 455 | 20.2474 | FALSE | <25mph | E6025 | 0.21 | 2016-04-21T16:15:00Z | 3 | 4 | E6025 | 0.21 | 2016-04-21T16:15:00Z | 3 | 4 | E6025 | 0.21 | 2016-04-21T17:15:00Z | 4.99 | 8 | E6025 | 0.21 | 2016-04-21T17:15:00Z | 4.99 | 8
PG&E | 2016-04-30 | 17:59 | 38.3142 | -120.9015 | Vegetation | RURAL | < 3 meters | Fire Agency | Kern County FD |  |  | 12000 | Conductor | Overhead | Yes | 42490 | 0.74931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0719 | 2016 | 4 | 30 | 17 | 59 | 16-0032910 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 722 | 19.7396 | 204_256 | <25mph | <15mph | HFTD - Distribution | 2016-04-30 17:59:00 | 465 | 19.7396 | FALSE | <25mph |  |  |  | 0 | 0 | CMAC1 | 6.54 | 2016-04-30T06:59:00Z | 23 | 3 |  |  |  | 0 | 0 | CFAC1 | 4.81 | 2016-04-30T07:05:00Z | 28.99 | 6
PG&E | 2016-05-12 20:15 | 42502.8438 | 35.1922 | -120.4563 | Vegetation | RURAL | < 3 meters | Self Extinguished | N.A. | 101857280 |  | 12000 | Conductor | Overhead | Yes | 42502.8438 | 2016-05-12 20:15 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0727 | 2016 | 5 | 12 | 20 | 15 | 16-0035728 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 54088 | 8.5669 | 224_84 | <25mph | <15mph | HFTD - Distribution | 2016-05-12 20:15:00 | 471 | 14.182 | FALSE | <25mph |  |  |  | 0 | 0 | AU609 | 7.02 | 2016-05-13T02:21:00Z | 10 | 11 |  |  |  | 0 | 0 | AU609 | 7.02 | 2016-05-13T02:21:00Z | 10 | 25
PG&E | 2016-05-15 15:54 | 42505.6625 | 36.7948 | -119.3966 | Vegetation | RURAL | 100 - 299 Acres | Fire Agency | Cal Fire | 100729685 | None | 12000 | Conductor | Overhead | Yes | 42505.6625 | 2016-05-15 15:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0730 | 2016 | 5 | 15 | 15 | 54 | 16-0036136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 180310 | 10.5903 | 270_173 | <25mph | <15mph | HFTD - Distribution | 2016-05-15 15:54:00 | 474 | 14.7659 | FALSE | <25mph |  |  |  | 0 | 0 | FCHC1 | 7.54 | 2016-05-15T22:00:00Z | 12.01 | 1 |  |  |  | 0 | 0 | FCHC1 | 7.54 | 2016-05-15T23:00:00Z | 15.99 | 2
PG&E | 2016-05-18 | 18:24 | 39.7381 | -123.1587 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42508 | 0.76667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0735 | 2016 | 5 | 18 | 18 | 24 | 16-0036911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1482 | 13.4862 | 108_336 | <25mph | <15mph | HFTD - Distribution | 2016-05-18 18:24:00 | 480 | 21.4181 | FALSE | <25mph | C3111 | 2.79 | 2016-05-18T06:56:00Z | 0 | 2 | EELC1 | 7.26 | 2016-05-18T06:45:00Z | 13 | 3 | C3111 | 2.79 | 2016-05-18T07:57:00Z | 0 | 6 | EELC1 | 7.26 | 2016-05-18T06:45:00Z | 13 | 8
PG&E | 2016-05-19 01:42 | 42509.0708 | 34.6645 | -120.4 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Santa Barbara County FD | 101916587 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42509.0708 | 2016-05-19 01:42 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | no-match | 0738 | 2016 | 5 | 19 | 1 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 6.9523 | 227_55 | <25mph | <15mph | HFTD - Distribution | 2016-05-19 01:42:00 | 482 | 22.8605 | FALSE | <25mph |  |  |  | 0 | 0 | D4531 | 5.16 | 2016-05-19T08:04:00Z | 4 | 3 |  |  |  | 0 | 0 | D4531 | 5.16 | 2016-05-19T09:19:00Z | 4 | 7
PG&E | 2016-05-19 18:54 | 42509.7875 | 38.8168 | -123.5843 | Vegetation | RURAL | < 3 meters | Fire Agency | Gualala Firw | 102183917 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42509.7875 | 2016-05-19 18:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0740 | 2016 | 5 | 19 | 18 | 54 | 16-0037247 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 4510 | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2016-05-19 18:54:00 | NA | 0 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-05-20 15:01 | 15:01 | 39.0559 | -123.4581 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102198323 |  | 12000 | Conductor | Overhead | Yes | 42510.6257 | 0.62569 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0741 | 2016 | 5 | 20 | 15 | 1 | 16-0037479 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2720 | 20.9117 | 94_299 | <25mph | <15mph | HFTD - Distribution | 2016-05-20 15:01:00 | 484 | 20.9117 | FALSE | <25mph | E1763 | 3.93 | 2016-05-20T21:19:00Z | 11.01 | 4 | BNVC1 | 7.56 | 2016-05-20T21:50:00Z | 25.99 | 6 | E1763 | 3.93 | 2016-05-20T22:18:00Z | 12.01 | 8 | BNVC1 | 7.56 | 2016-05-20T22:50:00Z | 27 | 15
PG&E | 2016-05-24 12:36 | 42514.525 | 38.0811 | -120.668 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101278239 |  | 12000 | Conductor | Overhead | Yes | 42514.525 | 2016-05-24 12:36 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0747 | 2016 | 5 | 24 | 12 | 36 | 16-0038096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 10678 | 12.6931 | 214_243 | <25mph | <15mph | HFTD - Distribution | 2016-05-24 12:36:00 | 490 | 15.0493 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-05-29 14:19 | 42519.5965 | 40.5795 | -122.4694 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103156596 | Yes | 12000 | Conductor | Overhead | Yes | 42519.5965 | 2016-05-29 14:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0751 | 2016 | 5 | 29 | 14 | 19 | 16-0039619 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3860 | 1.6611 | 138_382 | <25mph | <15mph | HFTD - Distribution | 2016-05-29 14:19:00 | 494 | 20.6013 | FALSE | <25mph | MMOC1 | 1.91 | 2016-05-29T21:00:00Z | 8.01 | 5 | E6886 | 6.63 | 2016-05-29T20:41:00Z | 8.01 | 13 | MMOC1 | 1.91 | 2016-05-29T22:00:00Z | 8.01 | 10 | C5599 | 7.38 | 2016-05-29T21:31:00Z | 8.99 | 26
PG&E | 2016-05-31 04:02 | 42521.1681 | 35.7984 | -120.9743 | Vegetation | RURAL | < 0.25 Acres | Utility: PG&E | N.A. | 101863413 |  | 12000 | Conductor | Overhead | Yes | 42521.1681 | 2016-05-31 04:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0754 | 2016 | 5 | 31 | 4 | 2 | 16-0039748 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 51888 | 1.5922 | 201_118 | <25mph | <15mph | HFTD - Distribution | 2016-05-31 04:02:00 | 497 | 16.9662 | FALSE | <25mph | E9175 | 3.45 | 2016-05-31T10:42:00Z | 1.01 | 13 | E9175 | 3.45 | 2016-05-31T10:42:00Z | 1.01 | 17 | E9175 | 3.45 | 2016-05-31T11:22:00Z | 1.01 | 25 | E9175 | 3.45 | 2016-05-31T11:22:00Z | 1.01 | 33
PG&E | 2016-06-03 | 42524.5111 | 38.6435 | -120.6959 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | cal-fire and usfs | 103119737 |  | 21000 | Conductor | Overhead | Yes | 42524 | 2016-06-03 12:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0764 | 2016 | 6 | 3 | 12 | 16 | 16-0040808 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 101354 | 7.6436 | 213_274 | <25mph | <15mph | HFTD - Distribution | 2016-06-03 12:16:00 | 507 | 11.74 | FALSE | <25mph |  |  |  | 0 | 0 | E6490 | 7.82 | 2016-06-03T06:56:00Z | 0 | 16 |  |  |  | 0 | 0 | E6490 | 7.82 | 2016-06-03T07:56:00Z | 2.01 | 32
PG&E | 2016-06-04 | 22:15 | 38.5117 | -122.9373 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42525 | 0.92708 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0768 | 2016 | 6 | 4 | 22 | 15 | 16-0041119 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7220 | 6.1483 | 116_268 | <25mph | <15mph | HFTD - Distribution | 2016-06-04 22:15:00 | 514 | 16.4728 | FALSE | <25mph | D9841 | 2.58 | 2016-06-04T06:52:00Z | 0 | 11 | E9070 | 7.35 | 2016-06-04T06:25:00Z | 5.99 | 75 | D9841 | 2.58 | 2016-06-04T07:52:00Z | 0 | 21 | E9070 | 7.35 | 2016-06-04T07:25:00Z | 5.99 | 142
PG&E | 2016-06-05 15:44 | 42526.6556 | 40.3441 | -123.71 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101009790 |  | 60000 | Conductor | Overhead | Yes | 42526.6556 | 2016-06-05 15:44 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0774 | 2016 | 6 | 5 | 15 | 44 | HM-2016-016 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 14.708 | 85_370 | <25mph | <15mph | HFTD - Transmission | 2016-06-05 15:44:00 | 516 | 17.5828 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-06-06 | 42527.825 | 38.9129 | -121.1192 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire/placer fire | 100050264 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42527 | 2016-06-06 19:48 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0775 | 2016 | 6 | 6 | 19 | 48 | 16-0041497 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 2039 | 14.8039 | 194_289 | <25mph | <15mph | HFTD - Distribution | 2016-06-06 19:48:00 | 518 | 15.3816 | FALSE | <25mph | D8862 | 3.32 | 2016-06-06T06:49:00Z | 4 | 4 | D8862 | 3.32 | 2016-06-06T06:49:00Z | 4 | 4 | D8862 | 3.32 | 2016-06-06T07:04:00Z | 5.99 | 8 | D8862 | 3.32 | 2016-06-06T07:04:00Z | 5.99 | 8
PG&E | 2016-06-10 15:51 | 42531.6604 | 39.9934 | -123.7883 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100992291 |  | 12000 | Conductor | Overhead | Yes | 42531.6604 | 2016-06-10 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0788 | 2016 | 6 | 10 | 15 | 51 | 16-0042501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | N.A. | 22.4156 | 82_351 | <25mph | <15mph | HFTD - Distribution | 2016-06-10 15:51:00 | 531 | 22.7996 | FALSE | <25mph |  |  |  | 0 | 0 | AV037 | 5.5 | 2016-06-10T22:23:00Z | 8.99 | 3 |  |  |  | 0 | 0 | AV037 | 5.5 | 2016-06-10T23:13:00Z | 11.01 | 7
PG&E | 2016-06-10 15:57 | 42531.6646 | 38.1792 | -120.6657 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103809655 |  | 12000 | Conductor | Overhead | Yes | 42531.6646 | 2016-06-10 15:57 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0789 | 2016 | 6 | 10 | 15 | 57 | 16-0042508 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 13.31 | 214_249 | <25mph | <15mph | HFTD - Distribution | 2016-06-10 15:57:00 | 532 | 14.6453 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-06-11 | 42532.8229 | 39.3265 | -121.3921 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101292512 |  | 0 – 750 | Transformer | Overhead | Yes | 42532 | 2016-06-11 19:45 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0790 | 2016 | 6 | 11 | 19 | 45 | 16-0042611 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 642 | 8.1809 | 183_312 | <25mph | <15mph | HFTD - Distribution | 2016-06-11 19:45:00 | 533 | 16.0839 | FALSE | <25mph | BNGC1 | 3.76 | 2016-06-11T06:51:00Z | 1.01 | 1 | BNGC1 | 3.76 | 2016-06-11T06:51:00Z | 1.01 | 1 | BNGC1 | 3.76 | 2016-06-11T07:51:00Z | 4 | 2 | BNGC1 | 3.76 | 2016-06-11T07:51:00Z | 4 | 2
PG&E | 2016-06-12 | 42533.4319 | 38.0491 | -120.3976 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101042514 |  | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0792 | 2016 | 6 | 12 | 10 | 22 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 13.4105 | 226_242 | <25mph | <15mph | HFTD - Distribution | 2016-06-12 10:22:00 | 536 | 13.7918 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-06-12 | 42533.5514 | 37.5096 | -120.0462 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101083986 |  | 0 – 750 | Conductor | Overhead | Yes | 42533 | 2016-06-12 13:14 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0795 | 2016 | 6 | 12 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.8806 | 241_212 | <25mph | <15mph | HFTD - Distribution | 2016-06-12 13:14:00 | 539 | 13.4596 | FALSE | <25mph | MPOC1 | 3.28 | 2016-06-12T06:07:00Z | 11.01 | 1 | MPOC1 | 3.28 | 2016-06-12T06:07:00Z | 11.01 | 1 | MPOC1 | 3.28 | 2016-06-12T06:07:00Z | 11.01 | 2 | MPOC1 | 3.28 | 2016-06-12T06:07:00Z | 11.01 | 2
PG&E | 2016-06-12 01:45 | 1:45 | 37.4643 | -122.3459 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Unknown | 100265854 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42533.0729 | 0.072917 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0796 | 2016 | 6 | 12 | 1 | 45 | 16-0042637 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 19836 | 11.0705 | 141_210 | <25mph | <15mph | HFTD - Distribution | 2016-06-12 01:45:00 | 534 | 17.9563 | FALSE | <25mph | PUGC1 | 2.7 | 2016-06-12T08:18:00Z | 8.01 | 8 | AU981 | 5.46 | 2016-06-12T08:44:00Z | 20 | 85 | PUGC1 | 2.7 | 2016-06-12T08:18:00Z | 8.01 | 17 | E2649 | 7.02 | 2016-06-12T09:44:00Z | 24 | 171
PG&E | 2016-06-15 | 42536.5479 | 38.4433 | -120.7568 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103169620 |  | 12000 | Conductor | Overhead | Yes | 42536 | 2016-06-15 13:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0801 | 2016 | 6 | 15 | 13 | 9 | 16-0043476 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 23963 | 15.7348 | 210_263 | <25mph | <15mph | HFTD - Distribution | 2016-06-15 13:09:00 | 543 | 16.8625 | FALSE | <25mph |  |  |  | 0 | 0 | MTZC1 | 6.74 | 2016-06-15T06:56:00Z | 4.99 | 1 |  |  |  | 0 | 0 | MTZC1 | 6.74 | 2016-06-15T07:56:00Z | 5.99 | 2
PG&E | 2016-06-19 | 42540.5049 | 39.3811 | -123.7737 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102187888 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 12:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0807 | 2016 | 6 | 19 | 12 | 7 | 16-0044317 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6100 | 11.4602 | 81_317 | <25mph | <15mph | HFTD - Distribution | 2016-06-19 12:07:00 | 550 | 15.3844 | FALSE | <25mph |  |  |  | 0 | 0 | E6025 | 6.3 | 2016-06-19T06:30:00Z | 3 | 5 |  |  |  | 0 | 0 | E6025 | 6.3 | 2016-06-19T06:30:00Z | 3 | 9
PG&E | 2016-06-19 | 42540.7215 | 38.4508 | -122.3546 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire--napa fire | 102256859 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 17:19 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0808 | 2016 | 6 | 19 | 17 | 19 | 16-0044337 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 672 | 13.296 | 141_264 | <25mph | <15mph | HFTD - Distribution | 2016-06-19 17:19:00 | 552 | 13.7776 | FALSE | <25mph |  |  |  | 0 | 0 | ATLC1 | 5.13 | 2016-06-19T06:29:00Z | 11.01 | 1 |  |  |  | 0 | 0 | ATLC1 | 5.13 | 2016-06-19T06:29:00Z | 11.01 | 2
PG&E | 2016-06-20 | 42541.6979 | 41.0697 | -123.6789 | Vegetation | RURAL | < 3 meters | Fire Agency | Hoopa FD | 101011420 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42541 | 2016-06-20 16:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0811 | 2016 | 6 | 20 | 16 | 45 | 16-0044577 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7361 | 15.1157 | 88_410 | <25mph | <15mph | HFTD - Distribution | 2016-06-20 16:45:00 | 554 | 15.1157 | FALSE | <25mph | HOAC1 | 1.56 | 2016-06-20T06:40:00Z | 3 | 1 | HOAC1 | 1.56 | 2016-06-20T06:40:00Z | 3 | 1 | HOAC1 | 1.56 | 2016-06-20T06:40:00Z | 3 | 2 | HOAC1 | 1.56 | 2016-06-20T06:40:00Z | 3 | 2
PG&E | 2016-06-21 | 20:49 | 35.5352 | -120.8457 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101900832 |  | 12000 | Conductor | Overhead | Yes | 42542 | 0.86736 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0812 | 2016 | 6 | 21 | 20 | 49 | 16-0044904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7806 | 8.2716 | 207_103 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 20:49:00 | 558 | 17.6234 | FALSE | <25mph |  |  |  | 0 | 0 | E6394 | 6.56 | 2016-06-21T06:59:00Z | 1.01 | 4 |  |  |  | 0 | 0 | E6394 | 6.56 | 2016-06-21T07:59:00Z | 1.01 | 8
PG&E | 2016-06-21 | 42542.4229 | 39.0294 | -121.2927 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100024816 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | no-match | 0813 | 2016 | 6 | 21 | 10 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 5.0939 | 187_296 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 10:09:00 | 555 | 12.3682 | FALSE | <25mph |  |  |  | 0 | 0 | E5440 | 6.7 | 2016-06-21T06:47:00Z | 7 | 28 |  |  |  | 0 | 0 | E5440 | 6.7 | 2016-06-21T06:47:00Z | 7 | 56
PG&E | 2016-06-21 | 42542.7035 | 38.4233 | -122.5448 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | KENWOOD FIRE XST | 102036904 | Yes | 0 – 750 | Conductor | Overhead | Yes | 42542 | 2016-06-21 16:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0814 | 2016 | 6 | 21 | 16 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 14.0146 | 133_263 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 16:53:00 | 556 | 14.0381 | FALSE | <25mph |  |  |  | 0 | 0 | E1582 | 5.25 | 2016-06-21T06:33:00Z | 4 | 14 |  |  |  | 0 | 0 | E1582 | 5.25 | 2016-06-21T06:33:00Z | 4 | 28
PG&E | 2016-06-24 | 42545.6097 | 40.22 | -122.283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101526647 | PACIFIC BELL | 0 – 750 | Unknown | Overhead | Yes | 42545 | 2016-06-24 14:38 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0821 | 2016 | 6 | 24 | 14 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 11.9685 | 145_362 | <25mph | <15mph | HFTD - Distribution | 2016-06-24 14:38:00 | 564 | 17.4582 | FALSE | <25mph |  |  |  | 0 | 0 | KRBL | 5.07 | 2016-06-24T06:54:00Z | 23.02 | 1 |  |  |  | 0 | 0 | KRBL | 5.07 | 2016-06-24T06:54:00Z | 23.02 | 1
PG&E | 2016-06-26 | 42547.6931 | 39.5042 | -121.4475 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100375810 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42547 | 2016-06-26 16:38 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0823 | 2016 | 6 | 26 | 16 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 9.04 | 180_322 | <25mph | <15mph | HFTD - Distribution | 2016-06-26 16:38:00 | 567 | 14.524 | FALSE | <25mph | TT309 | 3.14 | 2016-06-26T06:45:00Z | 8.01 | 1 | TT309 | 3.14 | 2016-06-26T06:45:00Z | 8.01 | 1 | TT309 | 3.14 | 2016-06-26T06:45:00Z | 8.01 | 2 | TT309 | 3.14 | 2016-06-26T06:45:00Z | 8.01 | 2
PG&E | 2016-06-26 11:06 | 42547.4625 | 40.4832 | -122.0466 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101483777 | FRONTIER | 12000 | Conductor | Overhead | Yes | 42547.4625 | 2016-06-26 11:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0826 | 2016 | 6 | 26 | 11 | 6 | 16-0045846 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 15520 | 6.1274 | 155_376 | <25mph | <15mph | HFTD - Distribution | 2016-06-26 11:06:00 | 566 | 14.8861 | FALSE | <25mph | AR225 | 3.09 | 2016-06-26T17:25:00Z | 8.01 | 10 | AR225 | 3.09 | 2016-06-26T17:25:00Z | 8.01 | 10 | AR225 | 3.09 | 2016-06-26T18:45:00Z | 8.01 | 22 | AR225 | 3.09 | 2016-06-26T18:45:00Z | 8.01 | 22
PG&E | 2016-06-30 | 0:03 | 39.8157 | -121.5994 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42551 | 0.0020833 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0832 | 2016 | 6 | 30 | 0 | 3 | 16-0046763 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 299100 | 7.8781 | 174_339 | <25mph | <15mph | HFTD - Distribution | 2016-06-30 00:03:00 | 575 | 11.8323 | FALSE | <25mph | C4565 | 1.82 | 2016-06-30T06:40:00Z | 3 | 2 | C4565 | 1.82 | 2016-06-30T06:40:00Z | 3 | 15 | C4565 | 1.82 | 2016-06-30T07:30:00Z | 3 | 5 | C4565 | 1.82 | 2016-06-30T07:30:00Z | 3 | 31
PG&E | 2016-06-30 | 42551.7181 | 40.0353 | -122.5694 | Vegetation | RURAL | 300 - 999 Acres | Fire Agency | Cal Fire | 101528146 |  | 12000 | Conductor | Overhead | Yes | 2016-06-30 | 2016-06-30 17:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0833 | 2016 | 6 | 30 | 17 | 14 | 16-0047210 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Fell into (slight defect) | 4520 | 9.1425 | 133_352 | <25mph | <15mph | HFTD - Distribution | 2016-06-30 17:14:00 | 577 | 19.2749 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-06-30 14:20 | 42551.5972 | 37.9927 | -120.3996 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Cal Fire | 102327111 | PACIFIC BELL | 17000 | Conductor | Overhead | Yes | 42551.5972 | 2016-06-30 14:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0834 | 2016 | 6 | 30 | 14 | 20 | 16-0047073 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 278 | 11.2101 | 226_239 | <25mph | <15mph | HFTD - Distribution | 2016-06-30 14:20:00 | 576 | 13.117 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-07-03 15:00 | 42554.625 | 38.0348 | -120.3809 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101050507 |  | 17000 | Conductor | Overhead | Yes | 42554.625 | 2016-07-03 15:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0837 | 2016 | 7 | 3 | 15 | 0 | 16-0047689 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38812 | 10.6263 | 226_241 | <25mph | <15mph | HFTD - Distribution | 2016-07-03 15:00:00 | 580 | 12.5395 | FALSE | <25mph |  |  |  | 0 | 0 | MOUC1 | 7.53 | 2016-07-03T21:02:00Z | 14.99 | 1 |  |  |  | 0 | 0 | MOUC1 | 7.53 | 2016-07-03T22:02:00Z | 17 | 2
PG&E | 2016-07-08 10:49 | 42559.4507 | 38.3373 | -122.1211 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 102291118 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42559.4507 | 2016-07-08 10:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0842 | 2016 | 7 | 8 | 10 | 49 | 16-0048647 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 19469 | 8.3702 | 151_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-08 10:49:00 | 585 | 20.6133 | FALSE | <25mph |  |  |  | 0 | 0 | E6079 | 6.28 | 2016-07-08T17:23:00Z | 14.99 | 12 |  |  |  | 0 | 0 | E6079 | 6.28 | 2016-07-08T17:23:00Z | 14.99 | 23
PG&E | 2016-07-12 14:18 | 42563.5958 | 35.3471 | -120.3813 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101879190 |  | 21000 | Conductor | Overhead | Yes | 42563.5958 | 2016-07-12 14:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0848 | 2016 | 7 | 12 | 14 | 18 | 16-0049403 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 18883 | 13.3171 | 227_93 | <25mph | <15mph | HFTD - Distribution | 2016-07-12 14:18:00 | 591 | 15.2041 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-07-15 05:19 | 42566.2215 | 35.1839 | -120.5018 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101846594 |  | 12000 | Conductor | Overhead | Yes | 42566.2215 | 2016-07-15 05:19 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0851 | 2016 | 7 | 15 | 5 | 19 | 16-0050086 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 62404 | 2.6454 | 222_84 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 05:19:00 | 594 | 14.1102 | FALSE | <25mph |  |  |  | 0 | 0 | D6295 | 5.2 | 2016-07-15T12:11:00Z | 0 | 8 |  |  |  | 0 | 0 | D6295 | 5.2 | 2016-07-15T13:01:00Z | 0 | 15
PG&E | 2016-07-15 14:09 | 42566.5896 | 38.6965 | -120.8598 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412774 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.5896 | 2016-07-15 14:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0852 | 2016 | 7 | 15 | 14 | 9 | 16-0050274 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 11253 | 10.7453 | 205_277 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 14:09:00 | 595 | 14.2057 | FALSE | <25mph | C6129 | 0.59 | 2016-07-15T20:39:00Z | 12.01 | 31 | C6129 | 0.59 | 2016-07-15T20:39:00Z | 12.01 | 65 | C6129 | 0.59 | 2016-07-15T20:39:00Z | 12.01 | 61 | C6129 | 0.59 | 2016-07-15T20:39:00Z | 12.01 | 130
PG&E | 2016-07-15 14:26 | 42566.6014 | 38.1366 | -122.7092 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | NOVATO FIRE AND OTHERS | 102013570 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.6014 | 2016-07-15 14:26 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0853 | 2016 | 7 | 15 | 14 | 26 | 16-0050269 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 758 | 13.1533 | 125_247 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 14:26:00 | 596 | 15.659 | FALSE | <25mph |  |  |  | 0 | 0 | BBEC1 | 7.51 | 2016-07-15T21:11:00Z | 13 | 25 |  |  |  | 0 | 0 | BBEC1 | 7.51 | 2016-07-15T21:11:00Z | 13 | 50
PG&E | 2016-07-16 00:58 | 42567.0403 | 36.4379 | -121.9198 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101669758 |  | 12000 | Other | Overhead | Yes | 42567.0403 | 2016-07-16 00:58 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0855 | 2016 | 7 | 16 | 0 | 58 | 16-0050335 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 8976 | 11.1025 | 159_153 | <25mph | <15mph | HFTD - Distribution | 2016-07-16 00:58:00 | 598 | 18.5622 | FALSE | <25mph |  |  |  | 0 | 0 | E6019 | 7.86 | 2016-07-16T07:42:00Z | 4.99 | 4 |  |  |  | 0 | 0 | E6019 | 7.86 | 2016-07-16T08:27:00Z | 4.99 | 8
PG&E | 2016-07-16 08:19 | 42567.3465 | 37.4828 | -119.87 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101079104 | None | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0856 | 2016 | 7 | 16 | 8 | 19 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 2.1905 | 249_211 | <25mph | <15mph | HFTD - Distribution | 2016-07-16 08:19:00 | 599 | 13.487 | FALSE | <25mph |  |  |  | 0 | 0 | MPOC1 | 6.57 | 2016-07-16T15:07:00Z | 8.01 | 10 |  |  |  | 0 | 0 | MPOC1 | 6.57 | 2016-07-16T15:07:00Z | 8.01 | 19
PG&E | 2016-07-16 20:26 | 42567.8514 | 38.4944 | -122.4944 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Cal Fire | 102265740 | None | 12000 | Conductor | Overhead | Yes | 42567.8514 | 2016-07-16 20:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0857 | 2016 | 7 | 16 | 20 | 26 | 16-0050320 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 13240 | 11.277 | 135_267 | <25mph | <15mph | HFTD - Distribution | 2016-07-16 20:26:00 | 600 | 15.7774 | FALSE | <25mph | TR110 | 3.79 | 2016-07-17T02:49:00Z | 5.99 | 1 | E1582 | 7.62 | 2016-07-17T03:03:00Z | 8.01 | 7 | TR110 | 3.79 | 2016-07-17T02:49:00Z | 5.99 | 2 | E1582 | 7.62 | 2016-07-17T03:03:00Z | 8.01 | 14
PG&E | 2016-07-20 19:15 | 42571.8021 | 37.7712 | -121.8104 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100898986 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42571.8021 | 2016-07-20 19:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0865 | 2016 | 7 | 20 | 19 | 15 | 16-0051308 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3013 | 17.1873 | 164_226 | <25mph | <15mph | HFTD - Distribution | 2016-07-20 19:15:00 | 608 | 18.9944 | FALSE | <25mph | LVMC1 | 3.62 | 2016-07-21T02:02:00Z | 18.01 | 1 | VAQC1 | 4.3 | 2016-07-21T01:45:00Z | 20 | 57 | LVMC1 | 3.62 | 2016-07-21T03:02:00Z | 18.99 | 2 | VAQC1 | 4.3 | 2016-07-21T02:45:00Z | 24 | 115
PG&E | 2016-07-21 21:45 | 42572.9062 | 40.8566 | -122.3387 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101455670 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0870 | 2016 | 7 | 21 | 21 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.7351 | 143_397 | <25mph | <15mph | HFTD - Distribution | 2016-07-21 21:45:00 | 613 | 15.1303 | FALSE | <25mph |  |  |  | 0 | 0 | SLFC1 | 6.48 | 2016-07-22T04:19:00Z | 15.99 | 5 |  |  |  | 0 | 0 | SLFC1 | 6.48 | 2016-07-22T04:19:00Z | 15.99 | 10
PG&E | 2016-07-24 16:24 | 42575.6833 | 38.0105 | -122.1941 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | CCD | 103049639 |  | 115000 | Conductor | Overhead | Yes | 42575.6833 | 2016-07-24 16:24 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0876 | 2016 | 7 | 24 | 16 | 24 | PS-2016-013 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 0 | 18.9534 | 148_240 | <25mph | <15mph | HFTD - Transmission | 2016-07-24 16:24:00 | 619 | 23.7155 | FALSE | <25mph | E6179 | 3.92 | 2016-07-24T23:20:00Z | 12.01 | 12 | DPXC1 | 4.78 | 2016-07-24T22:48:00Z | 22.12 | 80 | E6179 | 3.92 | 2016-07-25T00:20:00Z | 14.99 | 24 | DPXC1 | 4.78 | 2016-07-24T22:48:00Z | 22.12 | 156
PG&E | 2016-07-25 15:32 | 42576.6472 | 38.3522 | -120.7107 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42576.6472 | 2016-07-25 15:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0878 | 2016 | 7 | 25 | 15 | 32 | 16-0052398 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 19951 | 10.4912 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-25 15:32:00 | 621 | 14.4675 | FALSE | <25mph |  |  |  | 0 | 0 | MTZC1 | 4.1 | 2016-07-25T21:56:00Z | 8.99 | 2 |  |  |  | 0 | 0 | MTZC1 | 4.1 | 2016-07-25T22:56:00Z | 11.01 | 4
PG&E | 2016-07-27 11:53 | 42578.4951 | 37.8649 | -120.5134 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101041792 |  | 17000 | Conductor | Overhead | Yes | 42578.4951 | 2016-07-27 11:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0880 | 2016 | 7 | 27 | 11 | 53 | 16-0052942 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 14734 | 9.7065 | 221_232 | <25mph | <15mph | HFTD - Distribution | 2016-07-27 11:53:00 | 622 | 14.5426 | FALSE | <25mph | GNSC1 | 2.2 | 2016-07-27T18:03:00Z | 10 | 1 | GNSC1 | 2.2 | 2016-07-27T18:03:00Z | 10 | 8 | GNSC1 | 2.2 | 2016-07-27T19:03:00Z | 10 | 2 | GNSC1 | 2.2 | 2016-07-27T19:03:00Z | 10 | 16
PG&E | 2016-07-27 17:05 | 42578.7118 | 38.5392 | -122.7656 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102029945 |  | 60000 | Conductor | Overhead | Yes | 42578.7118 | 2016-07-27 17:05 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0882 | 2016 | 7 | 27 | 17 | 5 | FU-2016-047 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 18.1446 | 123_269 | <25mph | <15mph | HFTD - Transmission | 2016-07-27 17:05:00 | 625 | 18.1446 | FALSE | <25mph | E6724 | 1.55 | 2016-07-27T23:20:00Z | 14 | 19 | E6724 | 1.55 | 2016-07-27T23:20:00Z | 14 | 89 | E6724 | 1.55 | 2016-07-28T00:30:00Z | 14 | 37 | E6724 | 1.55 | 2016-07-28T00:30:00Z | 14 | 166
PG&E | 2016-07-28 02:41 | 42579.1118 | 35.3674 | -120.3977 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101849904 |  | 21000 | Conductor | Overhead | Yes | 42579.1118 | 2016-07-28 02:41 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0883 | 2016 | 7 | 28 | 2 | 41 | 16-0053127 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 22592 | 6.4781 | 227_94 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 02:41:00 | 626 | 16.1822 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-07-28 08:12 | 42579.3417 | 37.8207 | -120.1388 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101037043 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0884 | 2016 | 7 | 28 | 8 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 1.7128 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 08:12:00 | 627 | 11.4062 | FALSE | <25mph | SEWC1 | 2.5 | 2016-07-28T14:16:00Z | 10 | 5 | SEWC1 | 2.5 | 2016-07-28T14:16:00Z | 10 | 5 | SEWC1 | 2.5 | 2016-07-28T14:16:00Z | 10 | 10 | SEWC1 | 2.5 | 2016-07-28T14:16:00Z | 10 | 10
PG&E | 2016-07-28 12:58 | 42579.5403 | 37.2371 | -119.8157 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103323932 |  | 21000 | Conductor | Overhead | Yes | 42579.5403 | 2016-07-28 12:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0885 | 2016 | 7 | 28 | 12 | 58 | 16-0053313 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 15215 | 9.4729 | 252_197 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 12:58:00 | 628 | 14.0324 | FALSE | <25mph | E5766 | 0.77 | 2016-07-28T19:25:00Z | 8.01 | 12 | E5766 | 0.77 | 2016-07-28T19:25:00Z | 8.01 | 12 | E5766 | 0.77 | 2016-07-28T19:25:00Z | 8.01 | 12 | E5766 | 0.77 | 2016-07-28T19:25:00Z | 8.01 | 12
PG&E | 2016-07-28 13:19 | 42579.5549 | 39.7127 | -123.4973 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102195566 |  | 12000 | Conductor | Overhead | Yes | 42579.5549 | 2016-07-28 13:19 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0886 | 2016 | 7 | 28 | 13 | 19 | 16-0053369 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 4447 | 11.1949 | 93_335 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 13:19:00 | 629 | 12.238 | FALSE | <25mph | LAYC1 | 0.97 | 2016-07-28T19:29:00Z | 7 | 1 | LAYC1 | 0.97 | 2016-07-28T19:29:00Z | 7 | 1 | LAYC1 | 0.97 | 2016-07-28T20:29:00Z | 10 | 2 | LAYC1 | 0.97 | 2016-07-28T20:29:00Z | 10 | 2
PG&E | 2016-07-28 14:24 | 42579.6 | 37.8232 | -120.1356 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101037045 |  | 17000 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Guy/Span Wire | N.A. | N.A. | Unknown |  | no-match | 0888 | 2016 | 7 | 28 | 14 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Guy/Span Wire | N.A. | 10.9021 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 14:24:00 | 631 | 11.4062 | FALSE | <25mph | SEWC1 | 2.46 | 2016-07-28T21:16:00Z | 14.99 | 5 | SEWC1 | 2.46 | 2016-07-28T21:16:00Z | 14.99 | 5 | SEWC1 | 2.46 | 2016-07-28T22:16:00Z | 15.99 | 9 | SEWC1 | 2.46 | 2016-07-28T22:16:00Z | 15.99 | 9
PG&E | 2016-07-29 | 18:16 | 38.5769 | -122.6187 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Selma Fire Department |  |  | 12000 | Conductor | Overhead | Yes | 42580 | 0.76111 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0890 | 2016 | 7 | 29 | 18 | 16 | 16-0053726 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 177834 | 13.7145 | 130_271 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 18:16:00 | 635 | 15.1116 | FALSE | <25mph | E2050 | 1.89 | 2016-07-29T06:56:00Z | 0 | 15 | E2362 | 7.38 | 2016-07-29T06:20:00Z | 4 | 26 | E2050 | 1.89 | 2016-07-29T07:56:00Z | 0 | 30 | E2362 | 7.38 | 2016-07-29T06:20:00Z | 4 | 50
PG&E | 2016-07-29 01:31 | 42580.0632 | 41.0396 | -123.674 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Hoopa FD | 100962351 |  | 12000 | Conductor | Overhead | Yes | 42580.0632 | 2016-07-29 01:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0891 | 2016 | 7 | 29 | 1 | 31 | 16-0053478 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1418 | 4.1421 | 88_408 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 01:31:00 | 633 | 13.6696 | FALSE | <25mph | HOAC1 | 0.58 | 2016-07-29T07:40:00Z | 3 | 1 | HOAC1 | 0.58 | 2016-07-29T07:40:00Z | 3 | 1 | HOAC1 | 0.58 | 2016-07-29T08:40:00Z | 4 | 2 | HOAC1 | 0.58 | 2016-07-29T08:40:00Z | 4 | 2
PG&E | 2016-07-31 12:11 | 42582.5076 | 38.7827 | -120.9168 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101417359 |  | 21000 | Conductor | Overhead | Yes | 42582.5076 | 2016-07-31 12:11 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0895 | 2016 | 7 | 31 | 12 | 11 | 16-0053949 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 10.9662 | 203_282 | <25mph | <15mph | HFTD - Distribution | 2016-07-31 12:11:00 | 638 | 14.1387 | FALSE | <25mph |  |  |  | 0 | 0 | PLTC1 | 6.02 | 2016-07-31T18:56:00Z | 12.01 | 43 |  |  |  | 0 | 0 | PLTC1 | 6.02 | 2016-07-31T18:56:00Z | 12.01 | 81
PG&E | 2016-08-01 | 42583.5347 | 38.9044 | -121.1274 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100078299 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42583 | 2016-08-01 12:50 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0896 | 2016 | 8 | 1 | 12 | 50 | 16-0054142 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 855 | 9.1677 | 194_289 | <25mph | <15mph | HFTD - Distribution | 2016-08-01 12:50:00 | 639 | 14.2258 | FALSE | <25mph | D8862 | 3.4 | 2016-08-01T06:23:00Z | 4 | 4 | LICC1 | 7.66 | 2016-08-01T06:13:00Z | 8.99 | 5 | D8862 | 3.4 | 2016-08-01T06:23:00Z | 4 | 8 | LICC1 | 7.66 | 2016-08-01T07:13:00Z | 11.01 | 10
PG&E | 2016-08-01 | 42583.7701 | 38.6956 | -120.9283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412720 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0898 | 2016 | 8 | 1 | 18 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2359 | 203_277 | <25mph | <15mph | HFTD - Distribution | 2016-08-01 18:29:00 | 641 | 12.0255 | FALSE | <25mph | D4464 | 2.83 | 2016-08-01T06:05:00Z | 4 | 17 | D4464 | 2.83 | 2016-08-01T06:05:00Z | 4 | 73 | D4464 | 2.83 | 2016-08-01T06:05:00Z | 4 | 31 | BENC1 | 7.25 | 2016-08-01T07:59:00Z | 4.99 | 136
PG&E | 2016-08-02 | 42584.6771 | 37.0312 | -119.4395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Fresno County FD | 100675986 |  | 12000 | Conductor | Overhead | Yes | 42584 | 2016-08-02 16:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0900 | 2016 | 8 | 2 | 16 | 15 | 16-0054552 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 265566 | 14.0604 | 268_186 | <25mph | <15mph | HFTD - Distribution | 2016-08-02 16:15:00 | 643 | 14.6638 | FALSE | <25mph |  |  |  | 0 | 0 | MTQC1 | 4.04 | 2016-08-02T06:52:00Z | 4 | 5 |  |  |  | 0 | 0 | MTQC1 | 4.04 | 2016-08-02T07:52:00Z | 4 | 11
PG&E | 2016-08-03 | 42585.1931 | 38.8474 | -120.812 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire garden valley fire | 103809676 |  | 21000 | Conductor | Overhead | Yes | 42585 | 2016-08-03 04:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0901 | 2016 | 8 | 3 | 4 | 38 | 16-0054597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2751 | 9.4989 | 208_286 | <25mph | <15mph | HFTD - Distribution | 2016-08-03 04:38:00 | 644 | 11.5219 | FALSE | <25mph | D5266 | 2.62 | 2016-08-03T06:44:00Z | 3 | 13 | BDMC1 | 6.95 | 2016-08-03T06:36:00Z | 5.99 | 31 | D5266 | 2.62 | 2016-08-03T07:54:00Z | 3 | 22 | BDMC1 | 6.95 | 2016-08-03T07:36:00Z | 7 | 63
PG&E | 2016-08-03 | 42585.5285 | 39.3269 | -120.6033 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100001032 |  | 12000 | Conductor | Overhead | Yes | 42585 | 2016-08-03 12:41 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0902 | 2016 | 8 | 3 | 12 | 41 | 16-0054769 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 20554 | 9.0542 | 216_312 | <25mph | <15mph | HFTD - Distribution | 2016-08-03 12:41:00 | 645 | 12.3394 | FALSE | <25mph | CISCO | 2.6 | 2016-08-03T06:00:00Z | 7.9 | 12 | CISCO | 2.6 | 2016-08-03T06:00:00Z | 7.9 | 16 | CISCO | 2.6 | 2016-08-03T07:30:00Z | 10.11 | 22 | CISCO | 2.6 | 2016-08-03T07:30:00Z | 10.11 | 30
PG&E | 2016-08-05 | 42587.5292 | 38.4048 | -120.5292 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101244628 |  | 12000 | Conductor | Overhead | Yes | 42587 | 2016-08-05 12:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0906 | 2016 | 8 | 5 | 12 | 42 | 16-0055368 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 363 | 12.0247 | 220_261 | <25mph | <15mph | HFTD - Distribution | 2016-08-05 12:42:00 | 649 | 12.7612 | FALSE | <25mph | AT450 | 0.53 | 2016-08-05T07:00:00Z | 0 | 13 | MTZC1 | 6.75 | 2016-08-05T06:56:00Z | 8.99 | 24 | AT450 | 0.53 | 2016-08-05T08:00:00Z | 0 | 25 | MTZC1 | 6.75 | 2016-08-05T07:56:00Z | 8.99 | 47
PG&E | 2016-08-05 | 42587.6153 | 40.4797 | -123.7803 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103572261 |  | 12000 | Conductor | Overhead | Yes | 42587 | 2016-08-05 14:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0907 | 2016 | 8 | 5 | 14 | 46 | 16-0055425 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 7019 | 13.7408 | 83_377 | <25mph | <15mph | HFTD - Distribution | 2016-08-05 14:46:00 | 650 | 14.7579 | FALSE | <25mph |  |  |  | 0 | 0 | E8593 | 4.09 | 2016-08-05T07:00:00Z | 5.99 | 13 |  |  |  | 0 | 0 | E8593 | 4.09 | 2016-08-05T07:30:00Z | 7 | 25
PG&E | 2016-08-07 | 42589.5972 | 37.2316 | -122.1552 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire/woodside fire | 103413747 |  | 12000 | Conductor | Overhead | Yes | 42589 | 2016-08-07 14:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0910 | 2016 | 8 | 7 | 14 | 20 | 16-0055597 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29869 | 12.3369 | 149_197 | <25mph | <15mph | HFTD - Distribution | 2016-08-07 14:20:00 | 653 | 12.9748 | FALSE | <25mph | E6800 | 0.63 | 2016-08-07T06:51:00Z | 4 | 4 | BNDC1 | 7.02 | 2016-08-07T06:50:00Z | 14.99 | 59 | E6800 | 0.63 | 2016-08-07T07:36:00Z | 4 | 8 | BNDC1 | 7.02 | 2016-08-07T07:50:00Z | 14.99 | 116
PG&E | 2016-08-08 | 42590.6556 | 37.1382 | -121.9672 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100519919 |  | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0912 | 2016 | 8 | 8 | 15 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 8.8992 | 157_192 | <25mph | <15mph | HFTD - Distribution | 2016-08-08 15:44:00 | 655 | 10.1741 | FALSE | <25mph | D9791 | 1.67 | 2016-08-08T07:00:00Z | 0 | 27 | E6085 | 4.45 | 2016-08-08T06:06:00Z | 5.99 | 135 | D8979 | 1.09 | 2016-08-08T07:42:00Z | 1.01 | 55 | E6085 | 4.45 | 2016-08-08T06:06:00Z | 5.99 | 267
PG&E | 2016-08-09 | 42591.8063 | 38.9187 | -120.9525 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | El Dorado County FD | 100038028 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0915 | 2016 | 8 | 9 | 19 | 21 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.2678 | 201_290 | <25mph | <15mph | HFTD - Distribution | 2016-08-09 19:21:00 | 658 | 10.7446 | FALSE | <25mph |  |  |  | 0 | 0 | D8862 | 6.76 | 2016-08-09T06:14:00Z | 4.99 | 17 |  |  |  | 0 | 0 | D8862 | 6.76 | 2016-08-09T06:14:00Z | 4.99 | 34
PG&E | 2016-08-10 | 42592.3583 | 37.0575 | -121.9556 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 101680487 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0917 | 2016 | 8 | 10 | 8 | 36 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 6.3982 | 157_187 | <25mph | <15mph | HFTD - Distribution | 2016-08-10 08:36:00 | 659 | 9.833 | FALSE | <25mph | AR172 | 3.97 | 2016-08-10T07:00:00Z | 4.99 | 43 | C8539 | 7.1 | 2016-08-10T06:56:00Z | 4.99 | 172 | AR172 | 3.97 | 2016-08-10T07:15:00Z | 4.99 | 84 | E5038 | 6.34 | 2016-08-10T07:31:00Z | 4.99 | 340
PG&E | 2016-08-12 | 42594.4222 | 38.8751 | -122.4223 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 102168360 |  | 12000 | Conductor | Overhead | Yes | 42594 | 2016-08-12 10:08 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0922 | 2016 | 8 | 12 | 10 | 8 | 16-0056982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 1368 | 5.1025 | 138_288 | <25mph | <15mph | HFTD - Distribution | 2016-08-12 10:08:00 | 665 | 17.0718 | FALSE | <25mph | KNXC1 | 0.95 | 2016-08-12T06:09:00Z | 3 | 1 | KNXC1 | 0.95 | 2016-08-12T06:09:00Z | 3 | 9 | KNXC1 | 0.95 | 2016-08-12T07:09:00Z | 4 | 2 | KNXC1 | 0.95 | 2016-08-12T07:09:00Z | 4 | 18
PG&E | 2016-08-13 | 14:31 | 37.4642 | -119.8589 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire |  |  | 21000 | Conductor | Overhead | Yes | 42595 | 0.60486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0923 | 2016 | 8 | 13 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.5527 | 249_210 | <25mph | <15mph | HFTD - Distribution | 2016-08-13 14:31:00 | 667 | 11.4441 | FALSE | <25mph | E9110 | 3.11 | 2016-08-13T06:44:00Z | 5.99 | 3 | E9110 | 3.11 | 2016-08-13T06:44:00Z | 5.99 | 7 | E9110 | 3.11 | 2016-08-13T07:59:00Z | 5.99 | 7 | E9110 | 3.11 | 2016-08-13T07:59:00Z | 5.99 | 15
PG&E | 2016-08-13 | 42595.5833 | 39.2009 | -121.213 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100011376 | PACIFIC BELL | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0924 | 2016 | 8 | 13 | 14 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 9.674 | 190_305 | <25mph | <15mph | HFTD - Distribution | 2016-08-13 14:00:00 | 666 | 11.9455 | FALSE | <25mph | E2572 | 2.38 | 2016-08-13T06:48:00Z | 1.01 | 11 | E1789 | 5.78 | 2016-08-13T07:00:00Z | 4.99 | 36 | E2572 | 2.38 | 2016-08-13T06:48:00Z | 1.01 | 21 | E1789 | 5.78 | 2016-08-13T07:18:00Z | 7 | 70
PG&E | 2016-08-15 | 42597.6549 | 37.8784 | -120.4488 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101020079 |  | 17000 | Conductor | Overhead | Yes | 42597 | 2016-08-15 15:43 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0928 | 2016 | 8 | 15 | 15 | 43 | 16-0057465 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 122905 | 10.0906 | 223_232 | <25mph | <15mph | HFTD - Distribution | 2016-08-15 15:43:00 | 671 | 12.9875 | FALSE | <25mph |  |  |  | 0 | 0 | GNSC1 | 4.26 | 2016-08-15T06:03:00Z | 11.01 | 1 |  |  |  | 0 | 0 | GNSC1 | 4.26 | 2016-08-15T06:03:00Z | 11.01 | 2
PG&E | 2016-08-16 | 42598.5542 | 40.3417 | -123.8803 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | miranda/fruitland vol, calfire | 100990019 | None | 12000 | Conductor | Overhead | Yes | 42598 | 2016-08-16 13:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0929 | 2016 | 8 | 16 | 13 | 18 | 16-0057668 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 137 | 16.9792 | 78_370 | <25mph | <15mph | HFTD - Distribution | 2016-08-16 13:18:00 | 672 | 18.3145 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-08-17 | 42599.516 | 41.2495 | -123.7671 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103315791 |  | 12000 | Conductor | Overhead | Yes | 42599 | 2016-08-17 12:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0932 | 2016 | 8 | 17 | 12 | 23 | 16-0058002 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 16544 | 13.4388 | 84_420 | <25mph | <15mph | HFTD - Distribution | 2016-08-17 12:23:00 | 675 | 14.3475 | FALSE | <25mph |  |  |  | 0 | 0 | TS777 | 6.47 | 2016-08-17T06:04:00Z | 3 | 2 |  |  |  | 0 | 0 | NTCC1 | 5.46 | 2016-08-17T07:45:00Z | 4 | 4
PG&E | 2016-08-17 | 42599.7757 | 37.3078 | -119.6511 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101020932 |  | 21000 | Conductor | Overhead | Yes | 42599 | 2016-08-17 18:37 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0934 | 2016 | 8 | 17 | 18 | 37 | 16-0058019 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 59379 | 5.4346 | 259_201 | <25mph | <15mph | HFTD - Distribution | 2016-08-17 18:37:00 | 677 | 11.1875 | FALSE | <25mph | D7171 | 3.9 | 2016-08-17T06:09:00Z | 5.99 | 26 | BSNC1 | 5.02 | 2016-08-17T06:48:00Z | 8.01 | 57 | D7171 | 3.9 | 2016-08-17T06:09:00Z | 5.99 | 54 | BSNC1 | 5.02 | 2016-08-17T07:48:00Z | 8.01 | 114
PG&E | 2016-08-19 | 42601.6826 | 39.2235 | -123.755 | Vegetation | RURAL | < 3 meters | Fire Agency | Albion-Little River FD | 102206661 |  | 12000 | Conductor | Overhead | Yes | 42601 | 2016-08-19 16:23 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0938 | 2016 | 8 | 19 | 16 | 23 | 16-0058677 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 95106 | 9.7374 | 82_308 | <25mph | <15mph | HFTD - Distribution | 2016-08-19 16:23:00 | 681 | 11.9986 | FALSE | <25mph |  |  |  | 0 | 0 | E6025 | 4.66 | 2016-08-19T07:00:00Z | 0 | 4 |  |  |  | 0 | 0 | E6025 | 4.66 | 2016-08-19T08:00:00Z | 1.01 | 7
PG&E | 2016-08-21 | 42603.5431 | 38.4445 | -122.2496 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102291451 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42603 | 2016-08-21 13:02 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0940 | 2016 | 8 | 21 | 13 | 2 | 16-0058847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 12780 | 10.3444 | 145_264 | <25mph | <15mph | HFTD - Distribution | 2016-08-21 13:02:00 | 683 | 21.5044 | FALSE | <25mph | ATLC1 | 2.26 | 2016-08-21T06:29:00Z | 2.01 | 1 | ATLC1 | 2.26 | 2016-08-21T06:29:00Z | 2.01 | 1 | ATLC1 | 2.26 | 2016-08-21T07:29:00Z | 4 | 2 | ATLC1 | 2.26 | 2016-08-21T07:29:00Z | 4 | 3
PG&E | 2016-08-22 | 42604.6736 | 37.9666 | -120.2395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Toulumne City FD | 101043683 |  | 17000 | Conductor | Overhead | Yes | 42604 | 2016-08-22 16:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0941 | 2016 | 8 | 22 | 16 | 10 | 16-0059149 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 78534 | 13.4322 | 233_237 | <25mph | <15mph | HFTD - Distribution | 2016-08-22 16:10:00 | 684 | 13.7297 | FALSE | <25mph |  |  |  | 0 | 0 | MOUC1 | 6.67 | 2016-08-22T06:02:00Z | 13 | 5 |  |  |  | 0 | 0 | MOUC1 | 6.67 | 2016-08-22T07:02:00Z | 14 | 10
PG&E | 2016-08-24 | 42606.5076 | 36.4633 | -121.712 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101750810 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42606 | 2016-08-24 12:11 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0943 | 2016 | 8 | 24 | 12 | 11 | 16-0059702 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 232770 | 12.4663 | 168_154 | <25mph | <15mph | HFTD - Distribution | 2016-08-24 12:11:00 | 686 | 13.9556 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-08-25 | 42607.5028 | 36.9726 | -119.3816 | Vegetation | RURAL | < 3 meters | Utility: PG&E | N.A. | 100651318 | PONDEROSA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0945 | 2016 | 8 | 25 | 12 | 4 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.3948 | 271_183 | <25mph | <15mph | HFTD - Distribution | 2016-08-25 12:04:00 | 689 | 15.1668 | FALSE | <25mph |  |  |  | 0 | 0 | MTQC1 | 5.65 | 2016-08-25T06:52:00Z | 4.99 | 6 |  |  |  | 0 | 0 | TRMC1 | 5.94 | 2016-08-25T07:52:00Z | 4.99 | 13
PG&E | 2016-08-30 | 42612.6674 | 36.5941 | -121.9212 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Unknown | 101734977 |  | 21000 | Conductor | Overhead | Yes | 42612 | 2016-08-30 16:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0951 | 2016 | 8 | 30 | 16 | 1 | 16-0061130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 199327 | 14.6893 | 159_162 | <25mph | <15mph | HFTD - Distribution | 2016-08-30 16:01:00 | 694 | 14.6893 | FALSE | <25mph | E8505 | 2.6 | 2016-08-30T06:15:00Z | 20 | 48 | E8505 | 2.6 | 2016-08-30T06:15:00Z | 20 | 52 | E8505 | 2.6 | 2016-08-30T06:15:00Z | 20 | 91 | E8505 | 2.6 | 2016-08-30T06:15:00Z | 20 | 99
PG&E | 2016-08-31 | 42613.6194 | 35.1918 | -120.4697 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101942860 |  | 12000 | Conductor | Overhead | Yes | 42613 | 2016-08-31 14:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0955 | 2016 | 8 | 31 | 14 | 52 | 16-0061423 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 156294 | 16.7717 | 224_84 | <25mph | <15mph | HFTD - Distribution | 2016-08-31 14:52:00 | 697 | 16.7717 | FALSE | <25mph |  |  |  | 0 | 0 | C9687 | 6.31 | 2016-08-31T06:30:00Z | 4.99 | 13 |  |  |  | 0 | 0 | C9687 | 6.31 | 2016-08-31T06:30:00Z | 4.99 | 23
PG&E | 2016-09-12 | 4:24 | 36.3999 | -121.902 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire Hwy 1 Carmel Hill | 101669614 |  | 12000 | Conductor | Overhead | Yes | 42625 | 0.18333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0973 | 2016 | 9 | 12 | 4 | 24 | 16-0063826 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 130604 | 5.4712 | 159_151 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 04:24:00 | 715 | 8.1881 | FALSE | <25mph |  |  |  | 0 | 0 | TR419 | 7.81 | 2016-09-12T06:15:00Z | 14 | 1 |  |  |  | 0 | 0 | TR419 | 7.81 | 2016-09-12T07:15:00Z | 15.99 | 2
PG&E | 2016-09-12 | 12:38 | 38.7832 | -120.6006 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101421708 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42625 | 0.52639 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0974 | 2016 | 9 | 12 | 12 | 38 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 15.5165 | 217_282 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 12:38:00 | 716 | 15.5342 | FALSE | <25mph |  |  |  | 0 | 0 | E3165 | 7.91 | 2016-09-12T06:37:00Z | 4 | 6 |  |  |  | 0 | 0 | E3165 | 7.91 | 2016-09-12T06:37:00Z | 4 | 12
PG&E | 2016-09-12 15:08 | 42625.6306 | 39.5256 | -123.7655 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102185070 |  | 12000 | Conductor | Overhead | Yes | 42625.6306 | 2016-09-12 15:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0977 | 2016 | 9 | 12 | 15 | 8 | 16-0064050 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 428 | 9.2458 | 82_325 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 15:08:00 | 717 | 9.2458 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-09-13 10:45 | 42626.4479 | 40.2958 | -122.1318 | Vegetation | RURAL | 300 - 999 Acres | Fire Agency | Cal Fire | 103702175 |  | 60000 | Conductor | Overhead | Yes | 2016-09-13 10:45 | 2016-09-13 10:45 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0979 | 2016 | 9 | 13 | 10 | 45 | INT-08528 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Animal | Animal | 0 | 12.3995 | 152_366 | <25mph | <15mph | HFTD - Transmission | 2016-09-13 10:45:00 | 721 | 18.1659 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-09-15 | 15:56 | 37.1102 | -121.9509 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100520198 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42628 | 0.66389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0982 | 2016 | 9 | 15 | 15 | 56 | 16-0065001 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 28900 | 4.729 | 158_190 | <25mph | <15mph | HFTD - Distribution | 2016-09-15 15:56:00 | 724 | 12.2674 | FALSE | <25mph | D8979 | 1.17 | 2016-09-15T06:16:00Z | 7 | 56 | D8979 | 1.17 | 2016-09-15T06:16:00Z | 7 | 108 | D8979 | 1.17 | 2016-09-15T07:18:00Z | 8.01 | 107 | E9039 | 4.03 | 2016-09-15T07:56:00Z | 8.99 | 204
PG&E | 2016-09-16 20:56 | 42629.8722 | 39.8387 | -121.7023 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 100441760 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42629.8722 | 2016-09-16 20:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0983 | 2016 | 9 | 16 | 20 | 56 | 16-0065273 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 314427 | 11.5178 | 170_340 | <25mph | <15mph | HFTD - Distribution | 2016-09-16 20:56:00 | 725 | 12.6422 | FALSE | <25mph | C8878 | 3.59 | 2016-09-17T03:53:00Z | 0 | 12 | CSTC1 | 4.21 | 2016-09-17T03:51:00Z | 7 | 14 | C8878 | 3.59 | 2016-09-17T03:53:00Z | 0 | 12 | CSTC1 | 4.21 | 2016-09-17T04:51:00Z | 7 | 16
PG&E | 2016-09-18 | 14:33 | 37.1619 | -122.1347 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire & Boulder Creek Fire Dept. | 103410909 | Yes | 12000 | Conductor | Overhead | Yes | 42631 | 0.60625 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0986 | 2016 | 9 | 18 | 14 | 33 | 16-0065437 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 54983 | 5.897 | 150_193 | <25mph | <15mph | HFTD - Distribution | 2016-09-18 14:33:00 | 728 | 11.3228 | FALSE | <25mph | BNDC1 | 2.99 | 2016-09-18T06:50:00Z | 7 | 23 | BNDC1 | 2.99 | 2016-09-18T06:50:00Z | 7 | 49 | BNDC1 | 2.99 | 2016-09-18T06:50:00Z | 7 | 43 | BNDC1 | 2.99 | 2016-09-18T06:50:00Z | 7 | 94
PG&E | 2016-09-20 | 8:25 | 40.0044 | -123.7871 | Vegetation | RURAL | < 3 meters | Self Extinguished | N.A. | 100992643 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42633 | 0.35069 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0990 | 2016 | 9 | 20 | 8 | 25 | 16-0065910 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 798 | 11.2567 | 82_351 | <25mph | <15mph | HFTD - Distribution | 2016-09-20 08:25:00 | 732 | 20.9022 | FALSE | <25mph |  |  |  | 0 | 0 | AV037 | 4.73 | 2016-09-20T06:23:00Z | 4 | 3 |  |  |  | 0 | 0 | AV037 | 4.73 | 2016-09-20T07:03:00Z | 4 | 7
PG&E | 2016-09-21 | 10:01 | 39.1173 | -121.071 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100014315 | PACIFIC BELL | 115000 | Conductor | Overhead | Yes | 42634 | 0.41736 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0991 | 2016 | 9 | 21 | 10 | 1 | INT-08560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 18.3543 | 196_301 | <25mph | <15mph | HFTD - Transmission | 2016-09-21 10:01:00 | 734 | 24.3978 | FALSE | <25mph | E1789 | 3.84 | 2016-09-21T06:54:00Z | 13 | 29 | E1789 | 3.84 | 2016-09-21T06:54:00Z | 13 | 87 | E1789 | 3.84 | 2016-09-21T06:54:00Z | 13 | 57 | E1789 | 3.84 | 2016-09-21T06:54:00Z | 13 | 165
PG&E | 2016-09-22 | 13:53 | 40.224 | -122.3417 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101539450 | None | 12000 | Conductor | Overhead | Yes | 42635 | 0.57847 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0996 | 2016 | 9 | 22 | 13 | 53 | 16-0066692 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 14706 | 14.6017 | 143_362 | <25mph | <15mph | HFTD - Distribution | 2016-09-22 13:53:00 | 739 | 20.1469 | FALSE | <25mph |  |  |  | 0 | 0 | E7114 | 6.08 | 2016-09-22T06:24:00Z | 14 | 4 |  |  |  | 0 | 0 | E7114 | 6.08 | 2016-09-22T07:54:00Z | 18.01 | 8
PG&E | 2016-09-23 05:23 | 15:23 | 39.3784 | -121.0922 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100091491 | None | 12000 | Conductor | Overhead | Yes | 42636.2243 | 0.64097 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0999 | 2016 | 9 | 23 | 15 | 23 | 16-0067089 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 80185 | 10.9717 | 195_315 | <25mph | <15mph | HFTD - Distribution | 2016-09-23 15:23:00 | 741 | 11.3047 | FALSE | <25mph | E3651 | 3.67 | 2016-09-23T12:20:00Z | 0 | 12 | RRRC1 | 5.34 | 2016-09-23T12:13:00Z | 8.01 | 13 | E3651 | 3.67 | 2016-09-23T13:20:00Z | 0 | 24 | RRRC1 | 5.34 | 2016-09-23T12:13:00Z | 8.01 | 26
PG&E | 2016-09-25 | 19:19 | 37.0993 | -122.1155 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire ben lomond fire | 101670837 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42638 | 0.80486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1003 | 2016 | 9 | 25 | 19 | 19 | 16-0067346 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1497 | 2.1111 | 150_190 | <25mph | <15mph | HFTD - Distribution | 2016-09-25 19:19:00 | 746 | 9.8702 | FALSE | <25mph | BNDC1 | 3.83 | 2016-09-25T06:50:00Z | 8.99 | 28 | BNDC1 | 3.83 | 2016-09-25T06:50:00Z | 8.99 | 47 | BNDC1 | 3.83 | 2016-09-25T07:50:00Z | 10 | 55 | BNDC1 | 3.83 | 2016-09-25T07:50:00Z | 10 | 96
PG&E | 2016-09-25 10:35 | 42638.441 | 38.8019 | -122.8176 | Vegetation | RURAL | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103613996 |  | 115000 | Other | Overhead | Yes | 2016-09-25 10:35 | 2016-09-25 10:35 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1004 | 2016 | 9 | 25 | 10 | 35 | INT-08572 | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Equip Failure - Other | 0 | 28.1055 | 121_284 | 25-40mph | 15-30mph | HFTD - Transmission | 2016-09-25 10:35:00 | 743 | 28.9174 | FALSE | 25-40mph |  |  |  | 0 | 0 | HWKC1 | 4.73 | 2016-09-25T16:56:00Z | 35.99 | 2 |  |  |  | 0 | 0 | HWKC1 | 4.73 | 2016-09-25T17:56:00Z | 35.99 | 4
PG&E | 2016-09-26 | 10:40 | 38.0157 | -122.6889 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | marin county fire | 102252082 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42639 | 0.44444 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1005 | 2016 | 9 | 26 | 10 | 40 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 4.5159 | 126_240 | <25mph | <15mph | HFTD - Distribution | 2016-09-26 10:40:00 | 747 | 11.2091 | FALSE | <25mph | WDAC1 | 2.97 | 2016-09-26T06:51:00Z | 12.01 | 2 | WDAC1 | 2.97 | 2016-09-26T06:51:00Z | 12.01 | 27 | WDAC1 | 2.97 | 2016-09-26T06:51:00Z | 12.01 | 4 | WDAC1 | 2.97 | 2016-09-26T06:51:00Z | 12.01 | 56
PG&E | 2016-09-28 | 14:00 | 35.2145 | -118.5625 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire |  |  | 0 – 750 | Conductor | Overhead | Yes | 42641 | 0.58333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1008 | 2016 | 9 | 28 | 14 | 0 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.8467 | 310_87 | <25mph | <15mph | HFTD - Distribution | 2016-09-28 14:00:00 | 750 | 26.957 | FALSE | 25-40mph | HFLC1 | 3.31 | 2016-09-28T06:13:00Z | 15.99 | 7 | HFLC1 | 3.31 | 2016-09-28T06:13:00Z | 15.99 | 28 | HFLC1 | 3.31 | 2016-09-28T06:13:00Z | 15.99 | 15 | HFLC1 | 3.31 | 2016-09-28T06:13:00Z | 15.99 | 58
PG&E | 2016-10-01 15:29 | 15:19 | 39.4384 | -120.816 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | State goverment forestry | 100112411 |  | 12000 | Conductor | Overhead | Yes | 42644.6455 | 0.63819 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1011 | 2016 | 10 | 1 | 15 | 19 | 16-0068934 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6157 | 14.1505 | 207_318 | <25mph | <15mph | HFTD - Distribution | 2016-10-01 15:19:00 | 753 | 14.2966 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-10-02 16:41 | 16:41 | 39.8888 | -121.6648 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103358082 |  | 12000 | Other | Overhead | Yes | 42645.6954 | 0.69514 | Other | N.A. | N.A. | N.A. | Weather | lightning strike | Other/Unknown | 1013 | 2016 | 10 | 2 | 16 | 41 | 16-0069050 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 339550 | 8.5152 | 171_343 | <25mph | <15mph | HFTD - Distribution | 2016-10-02 16:41:00 | 755 | 17.2989 | FALSE | <25mph | C8878 | 1.4 | 2016-10-02T23:28:00Z | 1.01 | 12 | CSTC1 | 5.65 | 2016-10-02T22:51:00Z | 18.01 | 19 | C8878 | 1.4 | 2016-10-03T00:38:00Z | 14 | 24 | CSTC1 | 5.65 | 2016-10-02T23:51:00Z | 28.01 | 42
PG&E | 2016-10-08 15:05 | 15:04 | 38.6686 | -120.9091 | Vegetation | RURAL | < 0.25 Acres | Customer | N.A. | 101380856 |  | 0 – 750 | Capacitor Bank | Overhead | Yes | 42651.6284 | 0.62778 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1021 | 2016 | 10 | 8 | 15 | 4 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 10.4532 | 203_276 | <25mph | <15mph | HFTD - Distribution | 2016-10-08 15:04:00 | 762 | 14.8776 | FALSE | <25mph | C6129 | 3.74 | 2016-10-08T21:09:00Z | 12.01 | 18 | C6129 | 3.74 | 2016-10-08T21:09:00Z | 12.01 | 64 | C6129 | 3.74 | 2016-10-08T21:09:00Z | 12.01 | 36 | C6129 | 3.74 | 2016-10-08T21:09:00Z | 12.01 | 126
PG&E | 2016-10-08 16:31 | 16:31 | 39.0099 | -122.6145 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102152342 |  | 0 – 750 | Transformer | Overhead | Yes | 42651.6884 | 0.68819 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1022 | 2016 | 10 | 8 | 16 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 1.265 | 130_295 | <25mph | <15mph | HFTD - Distribution | 2016-10-08 16:31:00 | 763 | 12.9101 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-10-09 18:52 | 18:52 | 38.656 | -120.9725 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101376768 |  | 12000 | Conductor | Overhead | Yes | 42652.7862 | 0.78611 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1024 | 2016 | 10 | 9 | 18 | 52 | 16-0070676 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 98361 | 11.3582 | 201_275 | <25mph | <15mph | HFTD - Distribution | 2016-10-09 18:52:00 | 765 | 14.948 | FALSE | <25mph | D7401 | 2.79 | 2016-10-10T01:03:00Z | 1.01 | 8 | BENC1 | 4.97 | 2016-10-10T00:59:00Z | 8.01 | 63 | D7401 | 2.79 | 2016-10-10T02:03:00Z | 1.01 | 16 | BENC1 | 4.97 | 2016-10-10T00:59:00Z | 8.01 | 126
PG&E | 2016-10-11 23:17 | 23:16 | 39.0201 | -120.8294 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire.foresthill fire | 100025501 |  | 60000 | Conductor | Overhead | Yes | 42654.9701 | 0.96944 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error |  | no-match | 1028 | 2016 | 10 | 11 | 23 | 16 | INT-08640 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 0 | 7.6312 | 207_295 | <25mph | <15mph | HFTD - Transmission | 2016-10-11 23:16:00 | 769 | 11.1078 | FALSE | <25mph | AU268 | 0.89 | 2016-10-12T06:04:00Z | 2.01 | 6 | FSHC1 | 7.19 | 2016-10-12T05:33:00Z | 3 | 7 | AU268 | 0.89 | 2016-10-12T06:49:00Z | 2.01 | 9 | FSHC1 | 7.19 | 2016-10-12T06:33:00Z | 3 | 11
PG&E | 2016-10-13 23:23 | 23:14 | 40.4901 | -122.3729 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | SHASTA COUNTY FIRE | 101502366 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42656.9745 | 0.96806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1029 | 2016 | 10 | 13 | 23 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 30.3025 | 142_377 | 25-40mph | 30-45mph | HFTD - Distribution | 2016-10-13 23:14:00 | 770 | 30.3025 | FALSE | 25-40mph | E6886 | 3.41 | 2016-10-14T05:33:00Z | 41 | 4 | KRDD | 4.3 | 2016-10-14T05:55:00Z | 50.64 | 17 | E6886 | 3.41 | 2016-10-14T06:48:00Z | 47 | 8 | KRDD | 4.3 | 2016-10-14T06:53:00Z | 56.39 | 39
PG&E | 2016-10-14 01:33 | 1:32 | 40.5007 | -121.9162 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101489328 |  | 12000 | Conductor | Overhead | Yes | 42657.0644 | 0.063889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1031 | 2016 | 10 | 14 | 1 | 32 | 16-0071832 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 213622 | 38.071 | 161_377 | 25-40mph | 30-45mph | HFTD - Distribution | 2016-10-14 01:32:00 | 772 | 39.405 | FALSE | 25-40mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-10-14 04:33 | 4:32 | 40.5228 | -121.6813 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101513661 |  | 12000 | Conductor | Overhead | Yes | 42657.1893 | 0.18889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1032 | 2016 | 10 | 14 | 4 | 32 | 16-0071897 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 38950 | 28.7152 | 171_378 | 25-40mph | 15-30mph | HFTD - Distribution | 2016-10-14 04:32:00 | 773 | 31.1927 | FALSE | 25-40mph |  |  |  | 0 | 0 | VIOC1 | 5.45 | 2016-10-14T10:52:00Z | 31 | 1 |  |  |  | 0 | 0 | VIOC1 | 5.45 | 2016-10-14T10:52:00Z | 31 | 2
PG&E | 2016-10-14 19:45 | 19:44 | 39.6245 | -121.5382 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100435570 |  | 0 – 750 | Conductor | Overhead | Yes | 42657.8228 | 0.82222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1036 | 2016 | 10 | 14 | 19 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.5623 | 177_329 | <25mph | <15mph | HFTD - Distribution | 2016-10-14 19:44:00 | 777 | 22.2526 | FALSE | <25mph |  |  |  | 0 | 0 | CICC1 | 5.69 | 2016-10-15T01:54:00Z | 18.99 | 1 |  |  |  | 0 | 0 | CICC1 | 5.69 | 2016-10-15T01:54:00Z | 18.99 | 2
PG&E | 2016-10-19 10:42 | 10:42 | 38.5098 | -122.45 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | st helena | 102242552 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42662.4459 | 0.44583 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1040 | 2016 | 10 | 19 | 10 | 42 | 16-0073955 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 693 | 4.5329 | 137_268 | <25mph | <15mph | HFTD - Distribution | 2016-10-19 10:42:00 | 781 | 13.4953 | FALSE | <25mph |  |  |  | 0 | 0 | AT925 | 4.5 | 2016-10-19T17:15:00Z | 8.01 | 12 |  |  |  | 0 | 0 | AT925 | 4.5 | 2016-10-19T18:40:00Z | 10 | 24
PG&E | 2016-10-23 18:44 | 18:10 | 38.021 | -120.5991 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101272943 |  | 115000 | Conductor | Overhead | Yes | 42666.7804 | 0.75694 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1043 | 2016 | 10 | 23 | 18 | 10 | INT-08709 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 0 | 9.2045 | 217_240 | <25mph | <15mph | HFTD - Transmission | 2016-10-23 18:10:00 | 784 | 15.0974 | FALSE | <25mph |  |  |  | 0 | 0 | E2861 | 6.79 | 2016-10-24T01:26:00Z | 3 | 10 |  |  |  | 0 | 0 | E2861 | 6.79 | 2016-10-24T02:29:00Z | 3 | 20
PG&E | 2016-11-09 | 9:06 | 37.4532 | -119.6413 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | US FOREST SERVICE | 101017062 |  | 12000 | Conductor | Overhead | Yes | 42683 | 0.37917 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1046 | 2016 | 11 | 9 | 9 | 6 | 16-0078863 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1586 | 6.3162 | 259_209 | <25mph | <15mph | HFTD - Distribution | 2016-11-09 09:06:00 | 787 | 14.6769 | FALSE | <25mph | TR172 | 1.09 | 2016-11-09T07:45:00Z | 8.99 | 5 | TR172 | 1.09 | 2016-11-09T07:45:00Z | 8.99 | 25 | TR172 | 1.09 | 2016-11-09T08:45:00Z | 12.01 | 8 | TR172 | 1.09 | 2016-11-09T08:45:00Z | 12.01 | 47
PG&E | 2016-11-14 | 13:15 | 35.4577 | -120.4619 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101895511 |  | 21000 | Conductor | Overhead | Yes | 42688 | 0.55208 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1048 | 2016 | 11 | 14 | 13 | 15 | 16-0079725 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 19590 | 5.0739 | 224_99 | <25mph | <15mph | HFTD - Distribution | 2016-11-14 13:15:00 | 789 | 19.5654 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2016-11-15 | 17:27 | 39.7275 | -121.6557 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100327525 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42689 | 0.72708 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 1049 | 2016 | 11 | 15 | 17 | 27 | 16-0080083 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 69231 | 9.6883 | 172_334 | <25mph | <15mph | HFTD - Distribution | 2016-11-15 17:27:00 | 790 | 16.6369 | FALSE | <25mph | PDEC1 | 2.44 | 2016-11-15T08:00:00Z | 2.01 | 2 | PDEC1 | 2.44 | 2016-11-15T08:00:00Z | 2.01 | 2 | PDEC1 | 2.44 | 2016-11-15T09:00:00Z | 2.01 | 3 | PDEC1 | 2.44 | 2016-11-15T09:00:00Z | 2.01 | 3
PG&E | 2016-11-20 | 11:04 | 39.6326 | -123.7823 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102200173 |  | 12000 | Conductor | Overhead | Yes | 42694 | 0.46111 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1050 | 2016 | 11 | 20 | 11 | 4 | 16-0081252 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 87261 | 8.4994 | 81_331 | <25mph | <15mph | HFTD - Distribution | 2016-11-20 11:04:00 | 791 | 16.1898 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2017-04-04 13:36 | 13:29 | 35.6885 | -120.7653 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101945026 | None | 12000 | Conductor | Overhead | Yes | 42829.567 | 0.56181 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1064 | 2017 | 4 | 4 | 13 | 29 | 17-0036460 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 167151 | 3.61 | 210_111 | <25mph | <15mph | HFTD - Distribution | 2017-04-04 13:29:00 | 804 | 8.6409 | FALSE | <25mph |  |  |  | 0 | 0 | D4060 | 7.1 | 2017-04-04T20:22:00Z | 5.99 | 3 |  |  |  | 0 | 0 | D4060 | 7.1 | 2017-04-04T20:22:00Z | 5.99 | 3
PG&E | 2017-04-25 12:39 | 12:38 | 38.6583 | -120.9762 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101376746 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 42850.5271 | 0.52639 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1072 | 2017 | 4 | 25 | 12 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 9.948 | 200_275 | <25mph | <15mph | HFTD - Distribution | 2017-04-25 12:38:00 | 812 | 10.5664 | FALSE | <25mph | D7401 | 2.53 | 2017-04-25T18:45:00Z | 10 | 3 | C6129 | 7.33 | 2017-04-25T19:24:00Z | 20 | 56 | D7401 | 2.53 | 2017-04-25T18:45:00Z | 10 | 5 | C6129 | 7.33 | 2017-04-25T19:24:00Z | 20 | 102
PG&E | 2017-04-28 16:21 | 15:49 | 38.7679 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chris paper fire investigator, 530/677-1868. incident #caaeuo11821 | 101409833 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42853.6815 | 0.65903 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1077 | 2017 | 4 | 28 | 15 | 49 | 17-0043771 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 82614 | 19.7837 | 201_281 | <25mph | <15mph | HFTD - Distribution | 2017-04-28 15:49:00 | 817 | 25.4223 | FALSE | 25-40mph |  |  |  | 0 | 0 | D7401 | 6.46 | 2017-04-28T22:51:00Z | 25.99 | 53 |  |  |  | 0 | 0 | D7401 | 6.46 | 2017-04-28T22:51:00Z | 25.99 | 104
PG&E | 2017-04-29 15:29 | 15:07 | 37.0349 | -119.5242 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100678661 | Unknown | 12000 | Conductor | Overhead | Yes | 42854.6453 | 0.62986 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1078 | 2017 | 4 | 29 | 15 | 7 | 17-0043911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 7.6275 | 265_186 | <25mph | <15mph | HFTD - Distribution | 2017-04-29 15:07:00 | 818 | 19.1329 | FALSE | <25mph | PRHC1 | 2.76 | 2017-04-29T22:27:00Z | 10 | 1 | PRHC1 | 2.76 | 2017-04-29T22:27:00Z | 10 | 1 | PRHC1 | 2.76 | 2017-04-29T23:27:00Z | 13 | 2 | PRHC1 | 2.76 | 2017-04-29T23:27:00Z | 13 | 2
PG&E | 2017-04-30 09:35 | 9:32 | 35.6349 | -118.9563 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 661-324-6551 | 100216308 | Unknown | 21000 | Conductor | Overhead | Yes | 42855.3995 | 0.39722 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1079 | 2017 | 4 | 30 | 9 | 32 | 17-0043980 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 3065 | 15.1229 | 291_110 | <25mph | <15mph | HFTD - Distribution | 2017-04-30 09:32:00 | 819 | 20.0476 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2017-05-05 15:52 | 15:52 | 40.3776 | -123.0019 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101501566 | None | 12000 | Conductor | Overhead | Yes | 42860.6614 | 15:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1084 | 2017 | 5 | 5 | 15 | 52 | 17-0045707 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 56893 | 24.5621 | 115_371 | <25mph | <15mph | HFTD - Distribution | 2017-05-05 15:52:00 | 824 | 35.0644 | FALSE | 25-40mph |  |  |  | 0 | 0 | YOBC1 | 4.35 | 2017-05-05T22:35:00Z | 5.99 | 1 |  |  |  | 0 | 0 | YOBC1 | 4.35 | 2017-05-05T23:35:00Z | 7 | 2
PG&E | 2017-05-06 11:23 | 11:18 | 40.7951 | -124.029 | Vegetation | Rural | < 3 Meters | Fire Agency | chief rick harden 7074423352 | 103661154 | Unknown | 12000 | Conductor | Overhead | Yes | 42861.4744 | 0.47083 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1086 | 2017 | 5 | 6 | 11 | 18 | 17-0045785 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 113630 | 26.2788 | 73_395 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-05-06 11:18:00 | 826 | 28.8261 | FALSE | 25-40mph |  |  |  | 0 | 0 | D8223 | 6.16 | 2017-05-06T17:35:00Z | 27 | 35 |  |  |  | 0 | 0 | D8223 | 6.16 | 2017-05-06T19:10:00Z | 30 | 76
PG&E | 2017-05-09 18:41 | 18:26 | 40.8689 | -123.5156 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | todd wright fire chief. 5307392493 | 103796045 | Unknown | 12000 | Conductor | Overhead | Yes | 42864.7782 | 0.76806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1092 | 2017 | 5 | 9 | 18 | 26 | 17-0046642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 108117 | 15.9566 | 94_399 | <25mph | <15mph | HFTD - Distribution | 2017-05-09 18:26:00 | 832 | 17.9691 | FALSE | <25mph |  |  |  | 0 | 0 | LYEC1 | 5.31 | 2017-05-10T00:46:00Z | 10 | 1 |  |  |  | 0 | 0 | LYEC1 | 5.31 | 2017-05-10T00:46:00Z | 10 | 2
PG&E | 2017-05-14 | 11:59 | 38.0798 | -122.8665 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102247059 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42869 | 0.49931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1095 | 2017 | 5 | 14 | 11 | 59 | 17-0047802 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 377483 | 24.3878 | 118_244 | <25mph | <15mph | HFTD - Distribution | 2017-05-14 11:59:00 | 835 | 24.3878 | FALSE | <25mph |  |  |  | 0 | 0 | PTRCA | 4.65 | 2017-05-14T06:30:00Z | 27.2 | 12 |  |  |  | 0 | 0 | PTRCA | 4.65 | 2017-05-14T06:30:00Z | 27.2 | 18
PG&E | 2017-05-15 | 3:05 | 35.6261 | -120.8962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101873299 | Unknown | 21000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1097 | 2017 | 5 | 15 | 3 | 5 | 17-0047837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 337188 | 4.016 | 204_108 | <25mph | <15mph | HFTD - Distribution | 2017-05-15 03:05:00 | 837 | 18.5139 | FALSE | <25mph | TABC1 | 2.62 | 2017-05-15T06:07:00Z | 3 | 1 | TABC1 | 2.62 | 2017-05-15T06:07:00Z | 3 | 1 | TABC1 | 2.62 | 2017-05-15T07:07:00Z | 3 | 2 | TABC1 | 2.62 | 2017-05-15T07:07:00Z | 3 | 2
PG&E | 2017-05-15 16:14 | 16:00 | 37.1766 | -119.8189 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SHAUN FAIRBANKS 559-683-4823 | 101108423 | SIERRA | 21000 | Conductor | Overhead | Yes | 42870.6767 | 0.66667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1099 | 2017 | 5 | 15 | 16 | 0 | 17-0048096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20007 | 15.7465 | 251_194 | <25mph | <15mph | HFTD - Distribution | 2017-05-15 16:00:00 | 839 | 20.7849 | FALSE | <25mph |  |  |  | 0 | 0 | E5766 | 4.44 | 2017-05-15T22:22:00Z | 5.99 | 11 |  |  |  | 0 | 0 | E5766 | 4.44 | 2017-05-15T22:22:00Z | 5.99 | 23
PG&E | 2017-05-24 16:25 | 16:24 | 38.834 | -121.1197 | Vegetation | Rural | < 3 Meters | Fire Agency | Fire Capt | 103838109 | None | 12000 | Conductor | Overhead | Yes | 42879.6837 | 16:24 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | no-match | 1111 | 2017 | 5 | 24 | 16 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 20.975 | 194_285 | <25mph | <15mph | HFTD - Distribution | 2017-05-24 16:24:00 | 851 | 20.975 | FALSE | <25mph |  |  |  | 0 | 0 | PLTC1 | 5.95 | 2017-05-24T22:56:00Z | 15.99 | 21 |  |  |  | 0 | 0 | PLTC1 | 5.95 | 2017-05-24T23:56:00Z | 15.99 | 40
PG&E | 2017-05-25 15:05 | 15:05 | 36.5217 | -121.8473 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Buddy Bloxham 831-236-5659 | 101778611 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42880.6288 | 0.62847 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1113 | 2017 | 5 | 25 | 15 | 5 | 17-0050761 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 13965 | 25.8899 | 162_158 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-05-25 15:05:00 | 853 | 26.2648 | FALSE | 25-40mph |  |  |  | 0 | 0 | E8505 | 7.82 | 2017-05-25T21:07:00Z | 31 | 34 |  |  |  | 0 | 0 | KMRY | 4.75 | 2017-05-25T22:54:00Z | 32.21 | 77
PG&E | 2017-05-25 17:36 | 16:55 | 38.3986 | -122.9876 | Vegetation | Rural | < 3 Meters | Utility: PG&E | N.A. | 101974034 | Unknown | 12000 | Conductor | Overhead | Yes | 42880.7334 | 0.70486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1114 | 2017 | 5 | 25 | 16 | 55 | 17-0050815 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 2644 | 12.6436 | 114_262 | <25mph | <15mph | HFTD - Distribution | 2017-05-25 16:55:00 | 854 | 13.2306 | FALSE | <25mph | D2849 | 1.17 | 2017-05-26T00:17:00Z | 10 | 12 | DUTWW | 7.06 | 2017-05-26T00:00:00Z | 17.81 | 55 | D2849 | 1.17 | 2017-05-26T00:17:00Z | 10 | 23 | DUTWW | 7.06 | 2017-05-26T01:00:00Z | 17.81 | 109
PG&E | 2017-05-29 18:30 | 18:29 | 39.2245 | -121.3753 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101304842 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1115 | 2017 | 5 | 29 | 18 | 29 | 17-0051324 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 616 | 7.4398 | 183_307 | <25mph | <15mph | HFTD - Distribution | 2017-05-29 18:29:00 | 855 | 10.3518 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2017-06-03 13:35 | 13:26 | 38.9017 | -121.2056 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100043664 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42889.5662 | 0.55972 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1122 | 2017 | 6 | 3 | 13 | 26 | 17-0052543 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29512 | 13.2044 | 191_289 | <25mph | <15mph | HFTD - Distribution | 2017-06-03 13:26:00 | 862 | 14.9142 | FALSE | <25mph | LICC1 | 3.58 | 2017-06-03T20:13:00Z | 8.99 | 1 | LICC1 | 3.58 | 2017-06-03T20:13:00Z | 8.99 | 19 | LICC1 | 3.58 | 2017-06-03T20:13:00Z | 8.99 | 2 | AR944 | 7.74 | 2017-06-03T20:45:00Z | 8.99 | 36
PG&E | 2017-06-08 15:19 | 15:08 | 34.6058 | -120.0214 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SHAWN STEINER | 101947678 | Unknown | 12000 | Conductor | Overhead | Yes | 42894.6382 | 0.63056 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1136 | 2017 | 6 | 8 | 15 | 8 | 17-0053783 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 41311 | 18.6266 | 244_52 | <25mph | <15mph | HFTD - Distribution | 2017-06-08 15:08:00 | 875 | 20.2983 | FALSE | <25mph | KIZA | 3.08 | 2017-06-08T21:55:00Z | 19.57 | 2 | SXWC1 | 5.38 | 2017-06-08T22:09:00Z | 23 | 18 | KIZA | 3.08 | 2017-06-08T23:15:00Z | 20.71 | 5 | SXWC1 | 5.38 | 2017-06-08T23:09:00Z | 24 | 39
PG&E | 2017-06-10 07:38 | 07:37 | 35.4359 | -120.4957 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101890429 | Unknown | 21000 | Conductor | Overhead | Yes | 42896.3177 | 07:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1140 | 2017 | 6 | 10 | 7 | 37 | 17-0054182 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 34397 | 9.2577 | 222_98 | <25mph | <15mph | HFTD - Distribution | 2017-06-10 07:37:00 | 879 | 18.05 | FALSE | <25mph |  |  |  | 0 | 0 | E2260 | 7.67 | 2017-06-10T14:14:00Z | 4 | 5 |  |  |  | 0 | 0 | E2260 | 7.67 | 2017-06-10T15:26:00Z | 12.01 | 10
PG&E | 2017-06-13 | 14:30 | 37.8526 | -122.1853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Tower 005/035c | Unknown | 115000 | Conductor | Overhead | Yes | 42899 | 0.60417 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1143 | 2017 | 6 | 13 | 14 | 30 | INT-09744 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | Balloons | 0 | 10.6352 | 148_231 | <25mph | <15mph | HFTD - Transmission | 2017-06-13 14:30:00 | 882 | 14.5193 | FALSE | <25mph | LBNL1 | 3.84 | 2017-06-13T07:00:00Z | 14.05 | 45 | LBNL1 | 3.84 | 2017-06-13T07:00:00Z | 14.05 | 123 | LBNL1 | 3.84 | 2017-06-13T07:00:00Z | 14.05 | 93 | LTRC1 | 6.59 | 2017-06-13T07:28:00Z | 17 | 258
PG&E | 2017-06-15 04:31 | 2:58 | 40.299 | -122.4318 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101511631 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42901.1885 | 0.12361 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | Other/Unknown | 1145 | 2017 | 6 | 15 | 2 | 58 | 17-0055359 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1762 | 9.755 | 139_366 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 02:58:00 | 884 | 19.4408 | FALSE | <25mph | E7114 | 1.68 | 2017-06-15T10:47:00Z | 3 | 4 | E7114 | 1.68 | 2017-06-15T10:47:00Z | 3 | 4 | E7114 | 1.68 | 2017-06-15T10:47:00Z | 3 | 7 | E7114 | 1.68 | 2017-06-15T10:47:00Z | 3 | 7
PG&E | 2017-06-15 08:08 | 7:39 | 39.2276 | -121.2348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE CHIEF | 103676075 | Unknown | 21000 | Conductor | Overhead | Yes | 42901.3391 | 0.31875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1147 | 2017 | 6 | 15 | 7 | 39 | 17-0055387 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 740 | 10.5195 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 07:39:00 | 886 | 12.4202 | FALSE | <25mph | E2572 | 2.6 | 2017-06-15T15:03:00Z | 1.01 | 11 | E1789 | 7.9 | 2017-06-15T15:06:00Z | 4 | 25 | E2572 | 2.6 | 2017-06-15T16:03:00Z | 2.01 | 21 | E1789 | 7.9 | 2017-06-15T16:00:00Z | 5.99 | 48
PG&E | 2017-06-15 15:04 | 15:01 | 39.3913 | -123.3054 | Vegetation | Rural | < 0.25 Acres | Fire Agency | STEPHEN | 103838176 | YES | 12000 | Conductor | Overhead | Yes | 42901.6279 | 0.62569 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1148 | 2017 | 6 | 15 | 15 | 1 | 17-0055557 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 180469 | 19.6681 | 101_317 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 15:01:00 | 887 | 19.7788 | FALSE | <25mph | E4027 | 2.73 | 2017-06-15T21:48:00Z | 17 | 22 | AU552 | 4.26 | 2017-06-15T22:04:00Z | 20 | 36 | E4027 | 2.73 | 2017-06-15T23:03:00Z | 17 | 39 | AU552 | 4.26 | 2017-06-15T23:01:00Z | 20 | 65
PG&E | 2017-06-16 19:15 | 19:14 | 38.3443 | -122.7812 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101970801 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42902.8019 | 19:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1155 | 2017 | 6 | 16 | 19 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 20.0158 | 122_259 | <25mph | <15mph | HFTD - Distribution | 2017-06-16 19:14:00 | 894 | 22.0101 | FALSE | <25mph | AR323 | 3.41 | 2017-06-17T01:49:00Z | 15.99 | 12 | BTOWW | 5.5 | 2017-06-17T01:45:00Z | 22.1 | 44 | AR323 | 3.41 | 2017-06-17T01:49:00Z | 15.99 | 24 | BTOWW | 5.5 | 2017-06-17T01:45:00Z | 22.1 | 92
PG&E | 2017-06-16 22:30 | 22:30 | 38.0373 | -122.1847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101424286 | Unknown | 21000 | Conductor | Overhead | Yes | 42902.9378 | 22:30 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1156 | 2017 | 6 | 16 | 22 | 30 | 17-0055882 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 12000 | 25.2975 | 148_241 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-06-16 22:30:00 | 895 | 25.6656 | FALSE | 25-40mph | UPBC1 | 3.49 | 2017-06-17T05:00:00Z | 32.97 | 21 | UPBC1 | 3.49 | 2017-06-17T05:00:00Z | 32.97 | 63 | UPBC1 | 3.49 | 2017-06-17T05:00:00Z | 32.97 | 41 | UPBC1 | 3.49 | 2017-06-17T05:00:00Z | 32.97 | 122
PG&E | 2017-06-20 15:19 | 11:51 | 40.3156 | -124.0611 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101006039 | Unknown | 12000 | Conductor | Overhead | Yes | 42906.638 | 0.49375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1180 | 2017 | 6 | 20 | 11 | 51 | 17-0057001 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 9256 | 16.7606 | 71_369 | <25mph | <15mph | HFTD - Distribution | 2017-06-20 11:51:00 | 917 | 17.2398 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 0.4 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 14.8685 | 222_261 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 09:36:00 | 925 | 23.4839 | FALSE | <25mph | AT450 | 2.61 | 2017-06-22T17:04:00Z | 4 | 16 | ULBC1 | 6.95 | 2017-06-22T16:33:00Z | 8.99 | 34 | AT450 | 2.61 | 2017-06-22T18:04:00Z | 5.99 | 27 | ULBC1 | 6.95 | 2017-06-22T16:33:00Z | 8.99 | 59
PG&E | 2017-06-22 17:54 | 18:07 | 38.7583 | -120.7176 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101401088 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.7461 | 0.75486 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1188 | 2017 | 6 | 22 | 18 | 7 | 17-0057857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 8517 | 11.5365 | 212_281 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 18:07:00 | 927 | 16.1873 | FALSE | <25mph | E5691 | 3.88 | 2017-06-23T00:37:00Z | 7 | 22 | E6490 | 7.72 | 2017-06-23T00:14:00Z | 7 | 35 | E5691 | 3.88 | 2017-06-23T00:37:00Z | 7 | 42 | E6490 | 7.72 | 2017-06-23T00:14:00Z | 7 | 67
PG&E | 2017-06-23 13:01 | 13:00 | 39.3051 | -122.4862 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 100329817 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42909.5421 | 13:00 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | no-match | 1190 | 2017 | 6 | 23 | 13 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 8.6467 | 136_311 | <25mph | <15mph | HFTD - Distribution | 2017-06-23 13:00:00 | 929 | 13.2674 | FALSE | <25mph |  |  |  | 0 | 0 | SYWC1 | 6.32 | 2017-06-23T19:26:00Z | 11.01 | 1 |  |  |  | 0 | 0 | SYWC1 | 6.32 | 2017-06-23T20:26:00Z | 11.01 | 2
PG&E | 2017-06-24 10:32 | 10:31 | 38.9438 | -121.0447 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100090318 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42910.439 | 0.43819 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1193 | 2017 | 6 | 24 | 10 | 31 | 17-0058318 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 582 | 9.5424 | 198_291 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 10:31:00 | 932 | 10.7882 | FALSE | <25mph |  |  |  | 0 | 0 | PLTC1 | 7.98 | 2017-06-24T16:56:00Z | 10 | 22 |  |  |  | 0 | 0 | PLTC1 | 7.98 | 2017-06-24T17:56:00Z | 10 | 43
PG&E | 2017-06-24 15:06 | 14:51 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 42910.6292 | 0.61875 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1194 | 2017 | 6 | 24 | 14 | 51 | 17-0058332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 21296 | 10.4286 | 210_259 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 14:51:00 | 933 | 10.7263 | FALSE | <25mph |  |  |  | 0 | 0 | MTZC1 | 6.33 | 2017-06-24T21:56:00Z | 8.99 | 1 |  |  |  | 0 | 0 | MTZC1 | 6.33 | 2017-06-24T21:56:00Z | 8.99 | 2
PG&E | 2017-06-24 22:27 | 22:27 | 38.2908 | -120.849 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CONTACT BOBBY BOWMAN | 101238865 | None | 12000 | Conductor | Overhead | Yes | 42910.9354 | 0.93542 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1195 | 2017 | 6 | 24 | 22 | 27 | 17-0058399 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 4529 | 5.1717 | 206_255 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 22:27:00 | 934 | 13.7168 | FALSE | <25mph |  |  |  | 0 | 0 | CFAC1 | 7.57 | 2017-06-25T05:05:00Z | 10 | 10 |  |  |  | 0 | 0 | CFAC1 | 7.57 | 2017-06-25T05:05:00Z | 10 | 24
PG&E | 2017-06-25 02:47 | 0:23 | 39.4043 | -123.3869 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102193088 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42911.1159 | 0.015972 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1197 | 2017 | 6 | 25 | 0 | 23 | 17-0058406 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 23100 | 15.6787 | 98_318 | <25mph | <15mph | HFTD - Distribution | 2017-06-25 00:23:00 | 935 | 19.8426 | FALSE | <25mph | AT319 | 3.31 | 2017-06-25T09:44:00Z | 4 | 24 | AU552 | 7.7 | 2017-06-25T09:46:00Z | 4.99 | 54 | AT319 | 3.31 | 2017-06-25T09:44:00Z | 4 | 48 | AU552 | 7.7 | 2017-06-25T10:45:00Z | 4.99 | 104
PG&E | 2017-06-27 09:28 | 9:23 | 37.9559 | -122.6176 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | marin county fire | 102260068 | UNFILED | 12000 | Conductor | Overhead | Yes | 42913.3944 | 0.39097 | Other | N.A. | N.A. | N.A. | Unknown |  | Fell into (slight defect) | 1203 | 2017 | 6 | 27 | 9 | 23 | 17-0058882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 3920 | 16.1278 | 129_237 | <25mph | <15mph | HFTD - Distribution | 2017-06-27 09:23:00 | 942 | 18.7182 | FALSE | <25mph | MDEC1 | 2.55 | 2017-06-27T15:36:00Z | 24 | 18 | MDEC1 | 2.55 | 2017-06-27T15:36:00Z | 24 | 24 | MDEC1 | 2.55 | 2017-06-27T15:36:00Z | 24 | 35 | MDEC1 | 2.55 | 2017-06-27T15:36:00Z | 24 | 47
PG&E | 2017-06-30 01:20 | 01:20 | 39.821 | -121.5883 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103840463 | YES | 12000 | Conductor | Overhead | Yes | 42916.0559 | 01:20 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1210 | 2017 | 6 | 30 | 1 | 20 | 17-0059647 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 2888 | 7.4054 | 174_339 | <25mph | <15mph | HFTD - Distribution | 2017-06-30 01:20:00 | 948 | 9.8944 | FALSE | <25mph | C4565 | 1.69 | 2017-06-30T07:43:00Z | 3 | 6 | JBGC1 | 7.9 | 2017-06-30T08:13:00Z | 10 | 20 | C4565 | 1.69 | 2017-06-30T07:43:00Z | 3 | 12 | JBGC1 | 7.9 | 2017-06-30T09:13:00Z | 11.01 | 40
PG&E | 2017-06-30 23:55 | 23:54 | 38.5794 | -122.8835 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 101958804 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42916.9965 | 23:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1211 | 2017 | 6 | 30 | 23 | 54 | 17-0059922 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2025 | 14.1552 | 118_272 | <25mph | <15mph | HFTD - Distribution | 2017-06-30 23:54:00 | 950 | 23.4555 | FALSE | <25mph | R08WW | 2.5 | 2017-07-01T06:00:00Z | 7.29 | 9 | DRYWW | 4.93 | 2017-07-01T06:00:00Z | 7.61 | 41 | R08WW | 2.5 | 2017-07-01T06:00:00Z | 7.29 | 18 | DRYWW | 4.93 | 2017-07-01T07:00:00Z | 9.19 | 82
PG&E | 2017-07-01 | 12:02 | 39.8209 | -121.6418 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 003/039 | Unknown | 60000 | Conductor | Overhead | Yes | 42917 | 0.50139 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1212 | 2017 | 7 | 1 | 12 | 2 | INT-09792 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.6345 | 172_339 | <25mph | <15mph | HFTD - Transmission | 2017-07-01 12:02:00 | 954 | 9.664 | FALSE | <25mph | C4565 | 2.41 | 2017-07-01T06:53:00Z | 2.01 | 18 | CSTC1 | 7.61 | 2017-07-01T06:51:00Z | 11.01 | 21 | C4565 | 2.41 | 2017-07-01T07:53:00Z | 3 | 36 | CSTC1 | 7.61 | 2017-07-01T06:51:00Z | 11.01 | 41
PG&E | 2017-07-01 04:43 | 3:12 | 38.1952 | -122.9197 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103855493 | Unknown | 12000 | Conductor | Overhead | Yes | 42917.1963 | 0.13333 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1214 | 2017 | 7 | 1 | 3 | 12 | 17-0059935 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 41370 | 14.0388 | 116_251 | <25mph | <15mph | HFTD - Distribution | 2017-07-01 03:12:00 | 951 | 27.9197 | FALSE | 25-40mph |  |  |  | 0 | 0 | PRWC1 | 7.17 | 2017-07-01T10:50:00Z | 27.98 | 13 |  |  |  | 0 | 0 | PRWC1 | 7.17 | 2017-07-01T10:50:00Z | 27.98 | 26
PG&E | 2017-07-02 | 13:28 | 39.8605 | -121.6274 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 000/017c | Unknown | 60000 | Conductor | Overhead | Yes | 42918 | 0.56111 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1216 | 2017 | 7 | 2 | 13 | 28 | INT-09794 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 10.1141 | 173_342 | <25mph | <15mph | HFTD - Transmission | 2017-07-02 13:28:00 | 956 | 11.4462 | FALSE | <25mph | C4565 | 1.76 | 2017-07-02T06:43:00Z | 2.01 | 18 | CSTC1 | 7.55 | 2017-07-02T06:51:00Z | 8.99 | 21 | C4565 | 1.76 | 2017-07-02T07:33:00Z | 2.01 | 36 | CSTC1 | 7.55 | 2017-07-02T06:51:00Z | 8.99 | 41
PG&E | 2017-07-03 20:28 | 20:26 | 38.7923 | -120.9438 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101388730 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42919.853 | 0.85139 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1218 | 2017 | 7 | 3 | 20 | 26 | 17-0060336 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 8134 | 10.0527 | 202_283 | <25mph | <15mph | HFTD - Distribution | 2017-07-03 20:26:00 | 957 | 12.5378 | FALSE | <25mph |  |  |  | 0 | 0 | PLTC1 | 4.45 | 2017-07-04T02:56:00Z | 7 | 25 |  |  |  | 0 | 0 | PLTC1 | 4.45 | 2017-07-04T03:56:00Z | 7 | 50
PG&E | 2017-07-04 20:17 | 20:16 | 40.4228 | -122.3975 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SCOTT CORN 530-448-2414 | 101481860 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42920.8451 | 20:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1221 | 2017 | 7 | 4 | 20 | 16 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 13.3568 | 141_373 | <25mph | <15mph | HFTD - Distribution | 2017-07-04 20:16:00 | 960 | 18.8443 | FALSE | <25mph |  |  |  | 0 | 0 | E6886 | 4.89 | 2017-07-05T02:19:00Z | 11.01 | 4 |  |  |  | 0 | 0 | E6886 | 4.89 | 2017-07-05T02:19:00Z | 11.01 | 8
PG&E | 2017-07-05 12:11 | 11:58 | 39.2105 | -121.2266 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVE ROBERTSON 530 906 4892 | 100010286 | Unknown | 21000 | Conductor | Overhead | Yes | 42921.5077 | 0.49861 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1223 | 2017 | 7 | 5 | 11 | 58 | 17-0060605 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 10231 | 9.71 | 190_306 | <25mph | <15mph | HFTD - Distribution | 2017-07-05 11:58:00 | 962 | 14.0848 | FALSE | <25mph |  |  |  | 0 | 0 | E1789 | 6.76 | 2017-07-05T18:54:00Z | 8.01 | 16 |  |  |  | 0 | 0 | E1789 | 6.76 | 2017-07-05T19:30:00Z | 11.01 | 32
PG&E | 2017-07-07 | 15:09 | 40.9054 | -122.3806 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101455950 | Unknown | 12000 | Conductor | Overhead | Yes | 42923 | 0.63125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1229 | 2017 | 7 | 7 | 15 | 9 | 17-0061903 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.0906 | 142_400 | <25mph | <15mph | HFTD - Distribution | 2017-07-07 15:09:00 | 969 | 11.4161 | FALSE | <25mph | CTANT | 2.76 | 2017-07-07T06:45:00Z | 13.04 | 11 | CTANT | 2.76 | 2017-07-07T06:45:00Z | 13.04 | 11 | CTANT | 2.76 | 2017-07-07T07:45:00Z | 15.52 | 20 | CTANT | 2.76 | 2017-07-07T07:45:00Z | 15.52 | 20
PG&E | 2017-07-07 20:49 | 14:31 | 37.499 | -119.799 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVEN WARD OFFICE 209-966-3542 CELL559-706-8811 | 103855637 | Unknown | 21000 | Conductor | Overhead | Yes | 42923.8675 | 0.60486 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1230 | 2017 | 7 | 7 | 14 | 31 | 17-0061288 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 554306 | 11.2535 | 252_212 | <25mph | <15mph | HFTD - Distribution | 2017-07-07 14:31:00 | 968 | 22.3608 | FALSE | <25mph | JSDC1 | 3.81 | 2017-07-08T03:47:00Z | 7 | 1 | C1522 | 5.09 | 2017-07-08T03:01:00Z | 7 | 8 | JSDC1 | 3.81 | 2017-07-08T04:47:00Z | 8.01 | 2 | C1522 | 5.09 | 2017-07-08T04:31:00Z | 8.99 | 17
PG&E | 2017-07-08 19:23 | 18:49 | 40.2935 | -122.4089 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | TOM STROING, RED BLUFF | 101526269 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42924.8076 | 0.78403 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1234 | 2017 | 7 | 8 | 18 | 49 | 17-0061469 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 157484 | 8.2983 | 140_366 | <25mph | <15mph | HFTD - Distribution | 2017-07-08 18:49:00 | 973 | 15.6109 | FALSE | <25mph | E7114 | 0.65 | 2017-07-09T01:29:00Z | 35.99 | 4 | E7114 | 0.65 | 2017-07-09T01:29:00Z | 35.99 | 4 | E7114 | 0.65 | 2017-07-09T01:29:00Z | 35.99 | 8 | E7114 | 0.65 | 2017-07-09T01:29:00Z | 35.99 | 8
PG&E | 2017-07-10 12:34 | 12:32 | 40.2603 | -123.8253 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103139646 | Unknown | 12000 | Conductor | Overhead | Yes | 42926.5237 | 0.52222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1238 | 2017 | 7 | 10 | 12 | 32 | 17-0061771 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 5910 | 19.8597 | 80_365 | <25mph | <15mph | HFTD - Distribution | 2017-07-10 12:32:00 | 977 | 21.4861 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2017-07-10 18:00 | 17:00 | 37.3768 | -122.3597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | David Hibdon 831-254-1763 | 100270370 | Unknown | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1240 | 2017 | 7 | 10 | 17 | 0 | 17-0061857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3322 | 11.4741 | 140_205 | <25mph | <15mph | HFTD - Distribution | 2017-07-10 17:00:00 | 979 | 11.9313 | FALSE | <25mph | E4551 | 0.89 | 2017-07-11T00:03:00Z | 5.99 | 1 | PUGC1 | 7.47 | 2017-07-11T00:18:00Z | 14.99 | 17 | E4551 | 0.89 | 2017-07-11T00:03:00Z | 5.99 | 1 | PUGC1 | 7.47 | 2017-07-11T01:18:00Z | 18.01 | 30
PG&E | 2017-07-11 22:13 | 22:12 | 37.0122 | -121.9497 | Vegetation | Rural | < 3 Meters | Fire Agency | CAPT PHIL CRAMBLET 831-479-6842 | 101676689 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42927.9254 | 22:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1244 | 2017 | 7 | 11 | 22 | 12 | 17-0062198 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 714 | 7.2694 | 158_185 | <25mph | <15mph | HFTD - Distribution | 2017-07-11 22:12:00 | 983 | 9.7577 | FALSE | <25mph | E5038 | 3.28 | 2017-07-12T04:30:00Z | 11.01 | 44 | C8539 | 5.04 | 2017-07-12T04:21:00Z | 14 | 153 | E5038 | 3.28 | 2017-07-12T04:30:00Z | 11.01 | 84 | C8539 | 5.04 | 2017-07-12T04:21:00Z | 14 | 311
PG&E | 2017-07-12 | 16:04 | 40.6531 | -122.3343 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 000/001 | Unknown | 60000 | Conductor | Overhead | Yes | 42928 | 0.66944 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1245 | 2017 | 7 | 12 | 16 | 4 | INT-09837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 13.5069 | 143_386 | <25mph | <15mph | HFTD - Transmission | 2017-07-12 16:04:00 | 987 | 13.828 | FALSE | <25mph | C5599 | 3.4 | 2017-07-12T06:46:00Z | 0 | 4 | C5599 | 3.4 | 2017-07-12T06:46:00Z | 0 | 4 | C5599 | 3.4 | 2017-07-12T07:46:00Z | 0 | 7 | C5599 | 3.4 | 2017-07-12T07:46:00Z | 0 | 7
PG&E | 2017-07-12 15:09 | 15:09 | 37.1491 | -122.0037 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 103565794 | Unknown | 21000 | Conductor | Overhead | Yes | 42928.6313 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1248 | 2017 | 7 | 12 | 15 | 9 | 17-0062439 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24690 | 9.5326 | 155_192 | <25mph | <15mph | HFTD - Distribution | 2017-07-12 15:09:00 | 986 | 9.5326 | FALSE | <25mph | D8979 | 3.17 | 2017-07-12T21:47:00Z | 8.01 | 19 | LSGC1 | 4.79 | 2017-07-12T21:32:00Z | 14.99 | 117 | D8979 | 3.17 | 2017-07-12T22:17:00Z | 8.99 | 32 | LSGC1 | 4.79 | 2017-07-12T22:32:00Z | 15.99 | 200
PG&E | 2017-07-12 20:22 | 20:21 | 40.0808 | -123.8339 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103841917 | Unknown | 12000 | Conductor | Overhead | Yes | 42928.8485 | 20:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1249 | 2017 | 7 | 12 | 20 | 21 | 17-0062445 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 4616 | 11.5535 | 80_355 | <25mph | <15mph | HFTD - Distribution | 2017-07-12 20:21:00 | 988 | 18.1059 | FALSE | <25mph | AV037 | 2.72 | 2017-07-13T02:33:00Z | 11.01 | 3 | AV037 | 2.72 | 2017-07-13T02:33:00Z | 11.01 | 4 | AV037 | 2.72 | 2017-07-13T02:33:00Z | 11.01 | 6 | ERCC1 | 4.01 | 2017-07-13T03:28:00Z | 12.01 | 8
PG&E | 2017-07-15 14:35 | 14:34 | 39.6231 | -121.5328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | russ fowler | 100404385 | Unknown | 12000 | Conductor | Overhead | Yes | 42931.6076 | 14:34 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1254 | 2017 | 7 | 15 | 14 | 34 | 17-0063126 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 54372 | 7.6156 | 177_329 | <25mph | <15mph | HFTD - Distribution | 2017-07-15 14:34:00 | 993 | 11.3229 | FALSE | <25mph |  |  |  | 0 | 0 | CICC1 | 5.91 | 2017-07-15T20:54:00Z | 12.01 | 1 |  |  |  | 0 | 0 | CICC1 | 5.91 | 2017-07-15T21:54:00Z | 12.01 | 2
PG&E | 2017-07-16 10:40 | 10:39 | 40.3414 | -123.8786 | Vegetation | Rural | < 3 Meters | Fire Agency | 707-726-1280 | 100990019 | Unknown | 12000 | Conductor | Overhead | Yes | 42932.4443 | 10:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1258 | 2017 | 7 | 16 | 10 | 39 | 17-0063223 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 198 | 15.2311 | 78_370 | <25mph | <15mph | HFTD - Distribution | 2017-07-16 10:39:00 | 997 | 19.5024 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2017-07-16 11:59 | 11:59 | 36.6669 | -121.7515 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101761892 | None | 21000 | Fuse | Overhead | Yes | 42932.4994 | 11:59 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1259 | 2017 | 7 | 16 | 11 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 22.4318 | 166_166 | <25mph | <15mph | HFTD - Distribution | 2017-07-16 11:59:00 | 998 | 30.0095 | FALSE | 25-40mph | E6666 | 1.85 | 2017-07-16T18:50:00Z | 14.99 | 12 | E6666 | 1.85 | 2017-07-16T18:50:00Z | 14.99 | 16 | E6666 | 1.85 | 2017-07-16T19:50:00Z | 15.99 | 22 | E6666 | 1.85 | 2017-07-16T19:50:00Z | 15.99 | 30
PG&E | 2017-07-16 12:10 | 12:10 | 35.6613 | -120.922 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101942626 | Unknown | 21000 | Conductor | Overhead | Yes | 42932.5072 | 12:10 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1260 | 2017 | 7 | 16 | 12 | 10 | 17-0063242 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 1304 | 7.6377 | 203_110 | <25mph | <15mph | HFTD - Distribution | 2017-07-16 12:10:00 | 999 | 17.3186 | FALSE | <25mph | TABC1 | 0.35 | 2017-07-16T19:07:00Z | 7 | 1 | D4060 | 6.39 | 2017-07-16T18:30:00Z | 7 | 17 | TABC1 | 0.35 | 2017-07-16T20:07:00Z | 8.99 | 2 | D4060 | 6.39 | 2017-07-16T20:00:00Z | 10 | 33
PG&E | 2017-07-18 | 11:30 | 38.0484 | -120.5565 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 012/071 | Unknown | 115000 | Conductor | Overhead | Yes | 42934 | 0.47917 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1265 | 2017 | 7 | 18 | 11 | 30 | INT-09873 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 55499 | 7.0574 | 219_242 | <25mph | <15mph | HFTD - Transmission | 2017-07-18 11:30:00 | 1005 | 15.7901 | FALSE | <25mph |  |  |  | 0 | 0 | C9085 | 5.13 | 2017-07-18T06:53:00Z | 2.01 | 65 |  |  |  | 0 | 0 | C9085 | 5.13 | 2017-07-18T06:53:00Z | 2.01 | 122
PG&E | 2017-07-18 | 21:40 | 38.0031 | -122.2093 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | Pole 000/002 to 000/003 | Unknown | 60000 | Conductor | Overhead | Yes | 42934 | 0.90278 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1266 | 2017 | 7 | 18 | 21 | 40 | INT-09875 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 0 | 11.7142 | 147_239 | <25mph | <15mph | HFTD - Transmission | 2017-07-18 21:40:00 | 1007 | 20.8699 | FALSE | <25mph | E4251 | 2.95 | 2017-07-18T06:15:00Z | 12.01 | 4 | E9944 | 7.08 | 2017-07-18T06:21:00Z | 15.99 | 75 | E4251 | 2.95 | 2017-07-18T06:15:00Z | 12.01 | 9 | MZXC1 | 5.07 | 2017-07-18T07:24:00Z | 18.99 | 146
PG&E | 2017-07-19 | 5:52 | 37.0905 | -119.6047 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Tower 003/001 | Unknown | 115000 | Conductor | Overhead | Yes | 42935 | 0.24444 | Contact From Object | N.A. | Other | Electric Facility | Unknown |  | no-match | 1269 | 2017 | 7 | 19 | 5 | 52 | INT-09877 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 0 | 0.36815 | 261_189 | <25mph | <15mph | HFTD - Transmission | 2017-07-19 05:52:00 | 1008 | 14.3689 | FALSE | <25mph |  |  |  | 0 | 0 | PRHC1 | 5.59 | 2017-07-19T06:27:00Z | 3 | 1 |  |  |  | 0 | 0 | PRHC1 | 5.59 | 2017-07-19T07:27:00Z | 3 | 2
PG&E | 2017-07-20 13:46 | 13:45 | 35.0804 | -120.5538 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | PAUL LEE 805 903-3416 INC # 8291 | 101941116 | Unknown | 12000 | Conductor | Overhead | Yes | 42936.5736 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1275 | 2017 | 7 | 20 | 13 | 45 | 17-0064321 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 45999 | 13.843 | 220_78 | <25mph | <15mph | HFTD - Distribution | 2017-07-20 13:45:00 | 1013 | 14.6968 | FALSE | <25mph | D6295 | 2.82 | 2017-07-20T20:33:00Z | 12.01 | 9 | D6295 | 2.82 | 2017-07-20T20:33:00Z | 12.01 | 28 | D6295 | 2.82 | 2017-07-20T20:33:00Z | 12.01 | 17 | D6295 | 2.82 | 2017-07-20T20:33:00Z | 12.01 | 54
PG&E | 2017-07-22 12:26 | 12:25 | 40.8795 | -123.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Josh , comander chief of forest service. | 100980577 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.518 | 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1279 | 2017 | 7 | 22 | 12 | 25 | 17-0064721 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 23227 | 10.7493 | 84_399 | <25mph | <15mph | HFTD - Distribution | 2017-07-22 12:25:00 | 1018 | 13.5476 | FALSE | <25mph |  |  |  | 0 | 0 | BHTC1 | 5.5 | 2017-07-22T18:46:00Z | 7 | 1 |  |  |  | 0 | 0 | BHTC1 | 5.5 | 2017-07-22T19:46:00Z | 8.01 | 2
PG&E | 2017-07-22 14:38 | 14:38 | 37.2994 | -122.1631 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100265488 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.6101 | 14:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1280 | 2017 | 7 | 22 | 14 | 38 | 17-0064738 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49181 | 4.6185 | 148_201 | <25mph | <15mph | HFTD - Distribution | 2017-07-22 14:38:00 | 1019 | 12.5156 | FALSE | <25mph | E0516 | 3.56 | 2017-07-22T21:33:00Z | 8.99 | 14 | C6623 | 4.81 | 2017-07-22T21:23:00Z | 12.01 | 87 | E0516 | 3.56 | 2017-07-22T21:49:00Z | 10 | 29 | C6623 | 4.81 | 2017-07-22T21:23:00Z | 12.01 | 168
PG&E | 2017-07-23 09:22 | 09:22 | 40.642 | -122.2302 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT? | 101459708 | FRONTIER COMMUNICATI | 12000 | Conductor | Overhead | Yes | 42939.3906 | 09:22 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1282 | 2017 | 7 | 23 | 9 | 22 | 17-0064801 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 184712 | 3.9314 | 148_385 | <25mph | <15mph | HFTD - Distribution | 2017-07-23 09:22:00 | 1021 | 13.6933 | FALSE | <25mph |  |  |  | 0 | 0 | C5599 | 5.97 | 2017-07-23T15:31:00Z | 2.01 | 8 |  |  |  | 0 | 0 | C5599 | 5.97 | 2017-07-23T17:02:00Z | 4 | 15
PG&E | 2017-07-23 18:25 | 18:25 | 39.6723 | -123.5336 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103823226 | Unknown | 12000 | Conductor | Overhead | Yes | 42939.7676 | 18:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1284 | 2017 | 7 | 23 | 18 | 25 | 17-0064854 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 12864 | 11.8402 | 92_333 | <25mph | <15mph | HFTD - Distribution | 2017-07-23 18:25:00 | 1023 | 16.2282 | FALSE | <25mph | LAYC1 | 3.32 | 2017-07-24T00:29:00Z | 11.01 | 1 | LAYC1 | 3.32 | 2017-07-24T00:29:00Z | 11.01 | 7 | LAYC1 | 3.32 | 2017-07-24T00:29:00Z | 11.01 | 2 | LAYC1 | 3.32 | 2017-07-24T00:29:00Z | 11.01 | 14
PG&E | 2017-07-24 14:02 | 14:01 | 37.2635 | -122.3364 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike klink 650-879-0121 | 100322130 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42940.5845 | 14:01 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1286 | 2017 | 7 | 24 | 14 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 18.4533 | 141_199 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 14:01:00 | 1025 | 18.6394 | FALSE | <25mph |  |  |  | 0 | 0 | LAHC1 | 5.31 | 2017-07-24T20:07:00Z | 13 | 1 |  |  |  | 0 | 0 | LAHC1 | 5.31 | 2017-07-24T20:07:00Z | 13 | 2
PG&E | 2017-07-24 19:31 | 19:31 | 38.3519 | -120.7103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.8134 | 19:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1288 | 2017 | 7 | 24 | 19 | 31 | 17-0065145 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14281 | 10.3402 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 19:31:00 | 1027 | 12.2366 | FALSE | <25mph |  |  |  | 0 | 0 | MTZC1 | 4.1 | 2017-07-25T01:56:00Z | 7 | 1 |  |  |  | 0 | 0 | MTZC1 | 4.1 | 2017-07-25T01:56:00Z | 7 | 2
PG&E | 2017-07-24 21:45 | 21:45 | 35.6024 | -120.9211 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101860186 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.9063 | 21:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1289 | 2017 | 7 | 24 | 21 | 45 | 17-0065191 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 21231 | 19.4445 | 203_107 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 21:45:00 | 1028 | 30.0108 | FALSE | 25-40mph | TABC1 | 3.74 | 2017-07-25T04:07:00Z | 3 | 1 | TABC1 | 3.74 | 2017-07-25T04:07:00Z | 3 | 1 | TABC1 | 3.74 | 2017-07-25T05:07:00Z | 4 | 2 | TABC1 | 3.74 | 2017-07-25T05:07:00Z | 4 | 2
PG&E | 2017-07-25 15:52 | 15:51 | 38.3779 | -122.5388 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102031447 | Unknown | 12000 | Conductor | Overhead | Yes | 42941.6609 | 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1290 | 2017 | 7 | 25 | 15 | 51 | 17-0065437 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 18584 | 12.338 | 133_260 | <25mph | <15mph | HFTD - Distribution | 2017-07-25 15:51:00 | 1029 | 16.6773 | FALSE | <25mph | KENWW | 2.06 | 2017-07-25T22:00:00Z | 15.3 | 4 | KENWW | 2.06 | 2017-07-25T22:00:00Z | 15.3 | 11 | F11WW | 3.22 | 2017-07-25T23:00:00Z | 15.5 | 10 | F11WW | 3.22 | 2017-07-25T23:00:00Z | 15.5 | 24
PG&E | 2017-07-25 19:13 | 19:12 | 39.5997 | -121.4449 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100403612 | Unknown | 12000 | Conductor | Overhead | Yes | 42941.8004 | 19:12 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1291 | 2017 | 7 | 25 | 19 | 12 | 17-0065453 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 68452 | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2017-07-25 19:12:00 | NA | 0 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2017-07-28 | 14:02 | 40.9997 | -121.9579 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101512624 | Unknown | 12000 | Conductor | Overhead | Yes | 42944 | 0.58472 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1293 | 2017 | 7 | 28 | 14 | 2 | 17-0066367 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 46581 | 11.7167 | 159_405 | <25mph | <15mph | HFTD - Distribution | 2017-07-28 14:02:00 | 1031 | 11.7167 | FALSE | <25mph | OMTC1 | 1.45 | 2017-07-28T06:26:00Z | 2.01 | 1 | OMTC1 | 1.45 | 2017-07-28T06:26:00Z | 2.01 | 1 | OMTC1 | 1.45 | 2017-07-28T06:26:00Z | 2.01 | 2 | OMTC1 | 1.45 | 2017-07-28T06:26:00Z | 2.01 | 2
PG&E | 2017-07-28 19:21 | 19:20 | 35.7276 | -120.9903 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Luis Obispo CDF | 101945496 | None | 21000 | Conductor | Overhead | Yes | 42944.8062 | 19:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1295 | 2017 | 7 | 28 | 19 | 20 | 17-0066392 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 8300 | 11.4004 | 200_114 | <25mph | <15mph | HFTD - Distribution | 2017-07-28 19:20:00 | 1033 | 13.3732 | FALSE | <25mph | E9175 | 1.53 | 2017-07-29T02:10:00Z | 7 | 12 | TABC1 | 6.16 | 2017-07-29T02:07:00Z | 10 | 13 | E9175 | 1.53 | 2017-07-29T02:10:00Z | 7 | 20 | TABC1 | 6.16 | 2017-07-29T02:07:00Z | 10 | 22
PG&E | 2017-07-29 13:28 | 13:28 | 35.4523 | -120.3834 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101889516 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42945.5612 | 13:28 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1297 | 2017 | 7 | 29 | 13 | 28 | 17-0066472 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 1962 | 15.5786 | 227_99 | <25mph | <15mph | HFTD - Distribution | 2017-07-29 13:28:00 | 1035 | 23.5205 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2017-07-30 09:47 | 09:46 | 38.9132 | -122.6179 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike wink | 102151066 | None | 0 – 750 | Conductor | Overhead | Yes | 42946.4075 | 09:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1302 | 2017 | 7 | 30 | 9 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.2785 | 130_290 | <25mph | <15mph | HFTD - Distribution | 2017-07-30 09:46:00 | 1040 | 13.7198 | FALSE | <25mph |  |  |  | 0 | 0 | KELC1 | 4.76 | 2017-07-30T15:57:00Z | 8.01 | 8 |  |  |  | 0 | 0 | KELC1 | 4.76 | 2017-07-30T16:57:00Z | 10 | 17
PG&E | 2017-07-31 14:42 | 14:41 | 38.7967 | -121.1329 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103782414 | Unknown | 12000 | Conductor | Overhead | Yes | 42947.6123 | 14:41 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1305 | 2017 | 7 | 31 | 14 | 41 | 17-0066797 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 210 | 10.6525 | 194_283 | <25mph | <15mph | HFTD - Distribution | 2017-07-31 14:41:00 | 1043 | 12.727 | FALSE | <25mph | D2336 | 3.3 | 2017-07-31T20:45:00Z | 4 | 1 | PLTC1 | 7.08 | 2017-07-31T20:56:00Z | 11.01 | 15 | D2336 | 3.3 | 2017-07-31T21:57:00Z | 7 | 6 | D7393 | 6.59 | 2017-07-31T22:23:00Z | 11.01 | 34
PG&E | 2017-08-02 | 9:42 | 39.2274 | -123.1081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 5/0 | None | 60000 | Conductor | Overhead | Yes | 42949 | 0.40417 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1307 | 2017 | 8 | 2 | 9 | 42 | INT-09925 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 4.0697 | 109_308 | <25mph | <15mph | HFTD - Transmission | 2017-08-02 09:42:00 | 1047 | 15.4312 | FALSE | <25mph |  |  |  | 0 | 0 | COWC1 | 7.26 | 2017-08-02T06:01:00Z | 14 | 11 |  |  |  | 0 | 0 | COWC1 | 7.26 | 2017-08-02T06:01:00Z | 14 | 23
PG&E | 2017-08-02 06:01 | 5:54 | 40.7986 | -123.3961 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 100974913 | Unknown | 12000 | Conductor | Overhead | Yes | 42949.251 | 0.24583 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1308 | 2017 | 8 | 2 | 5 | 54 | 17-0067270 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 5832 | 11.2488 | 99_395 | <25mph | <15mph | HFTD - Distribution | 2017-08-02 05:54:00 | 1045 | 15.9988 | FALSE | <25mph |  |  |  | 0 | 0 | UDWC1 | 7.47 | 2017-08-02T12:24:00Z | 1.01 | 1 |  |  |  | 0 | 0 | UDWC1 | 7.47 | 2017-08-02T13:24:00Z | 1.01 | 2
PG&E | 2017-08-03 11:01 | 10:53 | 39.0732 | -121.0868 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100072742 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42950.4588 | 0.45347 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1312 | 2017 | 8 | 3 | 10 | 53 | 17-0067679 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 127440 | 9.5869 | 196_298 | <25mph | <15mph | HFTD - Distribution | 2017-08-03 10:53:00 | 1050 | 11.8038 | FALSE | <25mph | C5488 | 3.14 | 2017-08-03T17:57:00Z | 5.99 | 5 | E1789 | 5.51 | 2017-08-03T18:00:00Z | 7 | 48 | C5488 | 3.14 | 2017-08-03T18:38:00Z | 7 | 8 | E1789 | 5.51 | 2017-08-03T19:00:00Z | 7 | 91
PG&E | 2017-08-05 08:33 | 08:33 | 38.4583 | -120.8695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JEFF MICHEL- 530 409 2223 | 101236223 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42952.3565 | 08:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1317 | 2017 | 8 | 5 | 8 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 6.5905 | 205_264 | <25mph | <15mph | HFTD - Distribution | 2017-08-05 08:33:00 | 1055 | 14.6063 | FALSE | <25mph |  |  |  | 0 | 0 | CFAC1 | 6.33 | 2017-08-05T15:05:00Z | 7 | 10 |  |  |  | 0 | 0 | CFAC1 | 6.33 | 2017-08-05T15:05:00Z | 7 | 17
PG&E | 2017-08-05 18:13 | 18:08 | 39.0968 | -123.2147 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102196629 | Unknown | 12000 | Conductor | Overhead | Yes | 42952.7592 | 0.75556 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1318 | 2017 | 8 | 5 | 18 | 8 | 17-0068200 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 134239 | 10.1139 | 105_301 | <25mph | <15mph | HFTD - Distribution | 2017-08-05 18:08:00 | 1056 | 16.2126 | FALSE | <25mph | KUKI | 2.28 | 2017-08-06T00:56:00Z | 17.27 | 12 | COWC1 | 7.84 | 2017-08-06T01:01:00Z | 23 | 26 | KUKI | 2.28 | 2017-08-06T01:25:00Z | 19.57 | 13 | COWC1 | 7.84 | 2017-08-06T02:01:00Z | 32.01 | 40
PG&E | 2017-08-06 11:38 | 11:38 | 36.5857 | -121.7121 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101747125 | Unknown | 12000 | Conductor | Overhead | Yes | 42953.4849 | 11:38 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1321 | 2017 | 8 | 6 | 11 | 38 | 17-0068279 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 87172 | 7.0101 | 168_161 | <25mph | <15mph | HFTD - Distribution | 2017-08-06 11:38:00 | 1059 | 12.123 | FALSE | <25mph |  |  |  | 0 | 0 | E8875 | 7.87 | 2017-08-06T18:20:00Z | 12.01 | 16 |  |  |  | 0 | 0 | E6666 | 7.23 | 2017-08-06T19:30:00Z | 15.99 | 32
PG&E | 2017-08-08 04:23 | 4:10 | 38.4949 | -122.6685 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 102025742 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42955.1829 | 0.17361 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1325 | 2017 | 8 | 8 | 4 | 10 | 17-0068642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 2750 | 5.2658 | 127_267 | <25mph | <15mph | HFTD - Distribution | 2017-08-08 04:10:00 | 1062 | 14.7124 | FALSE | <25mph | RSAC1 | 2.6 | 2017-08-08T10:29:00Z | 5.99 | 16 | D9840 | 5.11 | 2017-08-08T10:31:00Z | 5.99 | 63 | C3628 | 3.62 | 2017-08-08T11:46:00Z | 5.99 | 31 | D9840 | 5.11 | 2017-08-08T10:31:00Z | 5.99 | 120
PG&E | 2017-08-08 11:28 | 11:27 | 37.0445 | -121.6343 | Vegetation | Urban | < 3 Meters | Utility: PG&E | N.A. | 100613200 | VERIZON CALIFORNIA | 21000 | Capacitor Bank | Overhead | Yes | 42955.4775 | 11:27 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | Other/Unknown | 1326 | 2017 | 8 | 8 | 11 | 27 | 17-0068774 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | 34192 | 1.9101 | 172_186 | <25mph | <15mph | HFTD - Distribution | 2017-08-08 11:27:00 | 1063 | 18.8418 | FALSE | <25mph |  |  |  | 0 | 0 | C4787 | 5.95 | 2017-08-08T18:13:00Z | 7 | 43 |  |  |  | 0 | 0 | C4787 | 5.95 | 2017-08-08T18:48:00Z | 8.01 | 85
PG&E | 2017-08-08 20:35 | 20:35 | 37.2637 | -119.7103 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TROY CHEEK1-209-966-3621 | 103793352 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42955.8578 | 20:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1327 | 2017 | 8 | 8 | 20 | 35 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.9357 | 256_199 | <25mph | <15mph | HFTD - Distribution | 2017-08-08 20:35:00 | 1065 | 11.9714 | FALSE | <25mph |  |  |  | 0 | 0 | D7171 | 6.79 | 2017-08-09T02:39:00Z | 5.99 | 32 |  |  |  | 0 | 0 | D7171 | 6.79 | 2017-08-09T03:39:00Z | 7 | 69
PG&E | 2017-08-09 11:29 | 11:29 | 38.6532 | -120.6273 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101402496 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42956.4786 | 11:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1328 | 2017 | 8 | 9 | 11 | 29 | 17-0069107 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 54216 | 9.4272 | 216_275 | <25mph | <15mph | HFTD - Distribution | 2017-08-09 11:29:00 | 1066 | 11.5652 | FALSE | <25mph |  |  |  | 0 | 0 | GZFC1 | 5.69 | 2017-08-09T18:17:00Z | 8.01 | 3 |  |  |  | 0 | 0 | GZFC1 | 5.69 | 2017-08-09T19:17:00Z | 11.01 | 5
PG&E | 2017-08-12 09:09 | 09:08 | 34.6689 | -120.0286 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103391912 | Unknown | 12000 | Conductor | Overhead | Yes | 42959.3812 | 09:08 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | wire cut | Other/Unknown | 1330 | 2017 | 8 | 12 | 9 | 8 | 17-0069829 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 26070 | 3.5662 | 244_55 | <25mph | <15mph | HFTD - Distribution | 2017-08-12 09:08:00 | 1068 | 23.4799 | FALSE | <25mph | SXWC1 | 1.34 | 2017-08-12T15:09:00Z | 4 | 7 | SXWC1 | 1.34 | 2017-08-12T15:09:00Z | 4 | 14 | UCSE | 1.88 | 2017-08-12T17:00:00Z | 7.2 | 14 | AP901 | 5.95 | 2017-08-12T17:00:00Z | 8.99 | 32
PG&E | 2017-08-14 | 6:14 | 40.1164 | -123.8064 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100986364 | Unknown | 12000 | Conductor | Overhead | Yes | 42961 | 0.25972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1332 | 2017 | 8 | 14 | 6 | 14 | 17-0070003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 959989 | 9.3352 | 81_357 | <25mph | <15mph | HFTD - Distribution | 2017-08-14 06:14:00 | 1070 | 20.8696 | FALSE | <25mph | ERCC1 | 1.77 | 2017-08-14T06:28:00Z | 11.01 | 2 | ERCC1 | 1.77 | 2017-08-14T06:28:00Z | 11.01 | 2 | ERCC1 | 1.77 | 2017-08-14T06:28:00Z | 11.01 | 7 | ERCC1 | 1.77 | 2017-08-14T06:28:00Z | 11.01 | 7
PG&E | 2017-08-14 | 23:52 | 37.1272 | -122.1689 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 015/127 | None | 60000 | Conductor | Overhead | Yes | 42961 | 0.99444 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1333 | 2017 | 8 | 14 | 23 | 52 | INT-09976 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 1790869 | 16.3701 | 148_191 | <25mph | <15mph | HFTD - Transmission | 2017-08-14 23:52:00 | 1072 | 18.2518 | FALSE | <25mph | BNDC1 | 0.33 | 2017-08-14T06:50:00Z | 18.01 | 21 | BNDC1 | 0.33 | 2017-08-14T06:50:00Z | 18.01 | 31 | BNDC1 | 0.33 | 2017-08-14T06:50:00Z | 18.01 | 48 | BNDC1 | 0.33 | 2017-08-14T06:50:00Z | 18.01 | 68
PG&E | 2017-08-14 07:56 | 07:56 | 39.1794 | -120.9761 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100083743 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42961.3308 | 07:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1334 | 2017 | 8 | 14 | 7 | 56 | 17-0070063 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3012 | 6.4958 | 200_304 | <25mph | <15mph | HFTD - Distribution | 2017-08-14 07:56:00 | 1071 | 15.2686 | FALSE | <25mph | D8321 | 3.61 | 2017-08-14T14:50:00Z | 2.01 | 14 | E5439 | 6.04 | 2017-08-14T14:50:00Z | 8.01 | 69 | D8321 | 3.61 | 2017-08-14T15:40:00Z | 4 | 30 | AT999 | 5.18 | 2017-08-14T15:32:00Z | 11.01 | 144
PG&E | 2017-08-15 19:29 | 19:28 | 39.5037 | -121.2783 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 100396172 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42962.8116 | 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1335 | 2017 | 8 | 15 | 19 | 28 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.8405 | 188_322 | <25mph | <15mph | HFTD - Distribution | 2017-08-15 19:28:00 | 1073 | 9.7276 | FALSE | <25mph |  |  |  | 0 | 0 | PKCC1 | 4.51 | 2017-08-16T02:10:00Z | 13 | 2 |  |  |  | 0 | 0 | PKCC1 | 4.51 | 2017-08-16T02:10:00Z | 13 | 4
PG&E | 2017-08-17 | 15:15 | 39.3703 | -121.0484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | PHIL MICHAEL 265-2894 INCIENT # CA NEV 21642 | 100083029 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42964 | 0.63542 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1338 | 2017 | 8 | 17 | 15 | 15 | 17-0071121 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 32850 | 10.6037 | 197_315 | <25mph | <15mph | HFTD - Distribution | 2017-08-17 15:15:00 | 1076 | 10.6037 | FALSE | <25mph | E3651 | 2.23 | 2017-08-17T07:00:00Z | 0 | 13 | RRRC1 | 5.9 | 2017-08-17T06:13:00Z | 5.99 | 14 | E3651 | 2.23 | 2017-08-17T08:00:00Z | 0 | 25 | RRRC1 | 5.9 | 2017-08-17T06:13:00Z | 5.99 | 27
PG&E | 2017-08-19 | 21:16 | 40.5752 | -122.2985 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464623 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42966 | 0.88611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1341 | 2017 | 8 | 19 | 21 | 16 | 17-0071522 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 19044 | 8.8981 | 145_381 | <25mph | <15mph | HFTD - Distribution | 2017-08-19 21:16:00 | 1079 | 13.341 | FALSE | <25mph | C5599 | 2.67 | 2017-08-19T06:47:00Z | 0 | 4 | RRAC1 | 4.12 | 2017-08-19T06:24:00Z | 4.99 | 11 | C5599 | 2.67 | 2017-08-19T07:16:00Z | 3 | 8 | RRAC1 | 4.12 | 2017-08-19T07:24:00Z | 4.99 | 22
PG&E | 2017-08-26 | 20:53 | 38.7066 | -121.0193 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101382231 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42973 | 0.87014 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1350 | 2017 | 8 | 26 | 20 | 53 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.4442 | 199_278 | <25mph | <15mph | HFTD - Distribution | 2017-08-26 20:53:00 | 1088 | 14.1326 | FALSE | <25mph | E4740 | 2.39 | 2017-08-26T07:00:00Z | 2.01 | 33 | FSLC1 | 6.06 | 2017-08-26T06:05:00Z | 5.37 | 58 | D7401 | 1.71 | 2017-08-26T07:54:00Z | 4.99 | 65 | FSLC1 | 6.06 | 2017-08-26T07:20:00Z | 5.59 | 115
PG&E | 2017-08-27 | 20:04 | 38.9165 | -121.151 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-477-0641 x7, log 22629 | 100077184 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42974 | 0.83611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1352 | 2017 | 8 | 27 | 20 | 4 | 17-0073228 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 905 | 9.7822 | 193_290 | <25mph | <15mph | HFTD - Distribution | 2017-08-27 20:04:00 | 1090 | 16.757 | FALSE | <25mph |  |  |  | 0 | 0 | D8862 | 4.91 | 2017-08-27T06:02:00Z | 8.99 | 8 |  |  |  | 0 | 0 | D8862 | 4.91 | 2017-08-27T07:47:00Z | 8.99 | 14
PG&E | 2017-08-28 | 9:14 | 38.7443 | -122.6491 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 103781085 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42975 | 0.38472 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1356 | 2017 | 8 | 28 | 9 | 14 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 4.693 | 128_281 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 09:14:00 | 1094 | 16.6198 | FALSE | <25mph |  |  |  | 0 | 0 | LKRC1 | 6.54 | 2017-08-28T06:05:00Z | 8.99 | 1 |  |  |  | 0 | 0 | LKRC1 | 6.54 | 2017-08-28T06:05:00Z | 8.99 | 2
PG&E | 2017-08-28 | 10:07 | 39.0472 | -120.7859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | FORESTHILL | 100019525 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 0.42153 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1357 | 2017 | 8 | 28 | 10 | 7 | 17-0073379 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 10077 | 5.9792 | 209_297 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 10:07:00 | 1095 | 13.4783 | FALSE | <25mph | AU268 | 3.78 | 2017-08-28T06:44:00Z | 2.01 | 5 | AU268 | 3.78 | 2017-08-28T06:44:00Z | 2.01 | 6 | AU268 | 3.78 | 2017-08-28T07:47:00Z | 2.01 | 8 | AU268 | 3.78 | 2017-08-28T07:47:00Z | 2.01 | 10
PG&E | 2017-08-28 | 14:06 | 38.634 | -122.4194 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102253236 | Unknown | 21000 | Conductor | Overhead | Yes | 42975 | 0.5875 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1359 | 2017 | 8 | 28 | 14 | 6 | 17-0073526 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 1896 | 12.4455 | 138_274 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 14:06:00 | 1097 | 13.1602 | FALSE | <25mph |  |  |  | 0 | 0 | AT925 | 4.29 | 2017-08-28T06:57:00Z | 1.01 | 12 |  |  |  | 0 | 0 | AT925 | 4.29 | 2017-08-28T07:58:00Z | 1.01 | 24
PG&E | 2017-08-28 | 14:59 | 40.2853 | -123.8728 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 100990599 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 0.62431 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1361 | 2017 | 8 | 28 | 14 | 59 | 17-0073546 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2688 | 17.8816 | 78_367 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 14:59:00 | 1099 | 23.0594 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2017-08-29 | 12:49 | 37.4507 | -119.6454 | Vegetation | Rural | > 5000 Acres | Fire Agency | USFS | 101017368 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-29 | 0.53403 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1366 | 2017 | 8 | 29 | 12 | 49 | 17-0073823 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | 3rd Party | 3rd Party - Unknown | 5894785 | 7.4398 | 259_209 | <25mph | <15mph | HFTD - Distribution | 2017-08-29 12:49:00 | 1104 | 13.5545 | FALSE | <25mph | D0826 | 0.24 | 2017-08-29T06:01:00Z | 3 | 4 | MIAC1 | 5.9 | 2017-08-29T06:59:00Z | 8.99 | 28 | D0826 | 0.24 | 2017-08-29T06:01:00Z | 3 | 8 | MIAC1 | 5.9 | 2017-08-29T06:59:00Z | 8.99 | 59
PG&E | 2017-08-29 | 15:54 | 38.302 | -122.5431 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 911 | 102026119 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 42976 | 0.6625 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1367 | 2017 | 8 | 29 | 15 | 54 | 17-0073928 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 485 | 16.1777 | 133_256 | <25mph | <15mph | HFTD - Distribution | 2017-08-29 15:54:00 | 1105 | 18.0049 | FALSE | <25mph | F11WW | 3.32 | 2017-08-29T06:00:00Z | 2.1 | 2 | KENWW | 7.3 | 2017-08-29T06:00:00Z | 6.4 | 21 | F11WW | 3.32 | 2017-08-29T06:00:00Z | 2.1 | 3 | KENWW | 7.3 | 2017-08-29T06:00:00Z | 6.4 | 38
PG&E | 2017-08-30 | 18:21 | 40.6243 | -122.3039 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CASHU008896 | 103151338 | YES | 12000 | Conductor | Overhead | Yes | 42977 | 0.76458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1369 | 2017 | 8 | 30 | 18 | 21 | 17-0074287 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 76344 | 5.8461 | 145_384 | <25mph | <15mph | HFTD - Distribution | 2017-08-30 18:21:00 | 1107 | 16.2636 | FALSE | <25mph | C5599 | 2.06 | 2017-08-30T06:47:00Z | 1.01 | 8 | RRAC1 | 7.52 | 2017-08-30T06:24:00Z | 7 | 9 | C5599 | 2.06 | 2017-08-30T07:46:00Z | 3 | 17 | RRAC1 | 7.52 | 2017-08-30T06:24:00Z | 7 | 19
PG&E | 2017-08-30 | 22:37 | 38.9993 | -120.9887 | Vegetation | Rural | < 3 Meters | Fire Agency | Andy 530-889-0111 | 100026238 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42977 | 0.94236 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1370 | 2017 | 8 | 30 | 22 | 37 | 17-0074333 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 3750 | 7.3126 | 200_294 | <25mph | <15mph | HFTD - Distribution | 2017-08-30 22:37:00 | 1108 | 12.9461 | FALSE | <25mph | D9434 | 3.56 | 2017-08-30T06:53:00Z | 2.01 | 15 | AT999 | 7.28 | 2017-08-30T06:33:00Z | 3 | 37 | D9434 | 3.56 | 2017-08-30T07:53:00Z | 3 | 34 | C5488 | 5.56 | 2017-08-30T07:44:00Z | 4 | 82
PG&E | 2017-08-31 | 6:42 | 35.616 | -120.8577 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Derrick | 101860075 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 0.27917 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1372 | 2017 | 8 | 31 | 6 | 42 | 17-0074386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1620 | 12.088 | 206_107 | <25mph | <15mph | HFTD - Distribution | 2017-08-31 06:42:00 | 1110 | 13.8216 | FALSE | <25mph |  |  |  | 0 | 0 | TABC1 | 4.66 | 2017-08-31T06:07:00Z | 2.01 | 1 |  |  |  | 0 | 0 | TABC1 | 4.66 | 2017-08-31T06:07:00Z | 2.01 | 2
PG&E | 2017-08-31 | 11:33 | 37.1379 | -121.9966 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100519201 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 0.48125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1373 | 2017 | 8 | 31 | 11 | 33 | 17-0074457 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 99153 | 14.3205 | 156_192 | <25mph | <15mph | HFTD - Distribution | 2017-08-31 11:33:00 | 1111 | 14.3569 | FALSE | <25mph | D8979 | 2.5 | 2017-08-31T06:03:00Z | 4.99 | 19 | D3546 | 7.44 | 2017-08-31T06:10:00Z | 7 | 105 | D8979 | 2.5 | 2017-08-31T06:03:00Z | 4.99 | 37 | D3546 | 7.44 | 2017-08-31T06:10:00Z | 7 | 206
PG&E | 2017-09-01 | 8:00 | 37.3757 | -119.8886 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101067028 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42979 | 0.33333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1378 | 2017 | 9 | 1 | 8 | 0 | 17-0074724 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 680 | 5.98 | 248_205 | <25mph | <15mph | HFTD - Distribution | 2017-09-01 08:00:00 | 1116 | 14.9658 | FALSE | <25mph |  |  |  | 0 | 0 | E9110 | 4.96 | 2017-09-01T06:35:00Z | 8.01 | 6 |  |  |  | 0 | 0 | E9110 | 4.96 | 2017-09-01T07:50:00Z | 8.99 | 12
PG&E | 2017-09-01 | 17:48 | 36.6518 | -121.7249 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MCFD | 103155761 | Unknown | 12000 | Conductor | Overhead | Yes | 42979 | 0.74167 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1382 | 2017 | 9 | 1 | 17 | 48 | 17-0074898 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 8152 | 14.5474 | 167_165 | <25mph | <15mph | HFTD - Distribution | 2017-09-01 17:48:00 | 1120 | 19.9505 | FALSE | <25mph | E6666 | 3.59 | 2017-09-01T06:25:00Z | 5.99 | 4 | E6666 | 3.59 | 2017-09-01T06:25:00Z | 5.99 | 12 | E6666 | 3.59 | 2017-09-01T07:55:00Z | 8.01 | 9 | E6666 | 3.59 | 2017-09-01T07:55:00Z | 8.01 | 27
PG&E | 2017-09-02 | 12:01 | 37.6645 | -121.9223 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 100956020 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42980 | 0.50069 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1384 | 2017 | 9 | 2 | 12 | 1 | 17-0075132 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 7152 | 6.3171 | 159_221 | <25mph | <15mph | HFTD - Distribution | 2017-09-02 12:01:00 | 1122 | 21.2394 | FALSE | <25mph | AU719 | 3.94 | 2017-09-02T06:56:00Z | 2.01 | 13 | D3560 | 6.84 | 2017-09-02T07:00:00Z | 8.01 | 31 | AU719 | 3.94 | 2017-09-02T07:56:00Z | 3 | 26 | D3560 | 6.84 | 2017-09-02T07:45:00Z | 8.99 | 65
PG&E | 2017-09-03 | 12:52 | 37.2162 | -119.4807 | Vegetation | Rural | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103345573 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-09-03 | 0.53611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1388 | 2017 | 9 | 3 | 12 | 52 | 17-0075546 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 2362 | 10.0918 | 266_196 | <25mph | <15mph | HFTD - Distribution | 2017-09-03 12:52:00 | 1126 | 25.526 | FALSE | 25-40mph | NFRC1 | 1.81 | 2017-09-03T06:55:00Z | 11.01 | 5 | NFRC1 | 1.81 | 2017-09-03T06:55:00Z | 11.01 | 5 | C6459 | 2.52 | 2017-09-03T08:00:00Z | 12.01 | 9 | C6459 | 2.52 | 2017-09-03T08:00:00Z | 12.01 | 9
PG&E | 2017-09-03 | 17:52 | 37.4956 | -119.8367 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101086621 | Unknown | 21000 | Transformer | Overhead | Yes | 42981 | 0.74444 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 1389 | 2017 | 9 | 3 | 17 | 52 | 17-0075617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 4512 | 13.9592 | 250_212 | <25mph | <15mph | HFTD - Distribution | 2017-09-03 17:52:00 | 1127 | 22.0754 | FALSE | <25mph | JSDC1 | 3.33 | 2017-09-03T06:47:00Z | 5.99 | 1 | E9110 | 4.74 | 2017-09-03T06:40:00Z | 8.99 | 6 | JSDC1 | 3.33 | 2017-09-03T07:47:00Z | 5.99 | 2 | E9110 | 4.74 | 2017-09-03T07:55:00Z | 10 | 17
PG&E | 2017-09-04 | 3:29 | 39.8317 | -121.8444 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102300100 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1392 | 2017 | 9 | 4 | 3 | 29 | 17-0075723 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 214974 | 9.8341 | 164_340 | <25mph | <15mph | HFTD - Distribution | 2017-09-04 03:29:00 | 1130 | 13.8789 | FALSE | <25mph |  |  |  | 0 | 0 | D8204 | 5.42 | 2017-09-04T06:37:00Z | 8.99 | 14 |  |  |  | 0 | 0 | D8204 | 5.42 | 2017-09-04T07:13:00Z | 8.99 | 34
PG&E | 2017-09-05 | 6:58 | 39.6727 | -123.5128 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 102194697 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 42983 | 0.29028 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1395 | 2017 | 9 | 5 | 6 | 58 | 17-0075976 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10528 | 9.1824 | 93_333 | <25mph | <15mph | HFTD - Distribution | 2017-09-05 06:58:00 | 1133 | 14.0364 | FALSE | <25mph | LAYC1 | 2.53 | 2017-09-05T06:29:00Z | 7 | 1 | LAYC1 | 2.53 | 2017-09-05T06:29:00Z | 7 | 8 | LAYC1 | 2.53 | 2017-09-05T07:29:00Z | 7 | 2 | LAYC1 | 2.53 | 2017-09-05T07:29:00Z | 7 | 15
PG&E | 2017-09-06 | 19:26 | 40.8392 | -122.3635 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103643183 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 0.80972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1399 | 2017 | 9 | 6 | 19 | 26 | 17-0076501 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 23830 | 6.5088 | 142_396 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 19:26:00 | 1137 | 12.365 | FALSE | <25mph | CTANT | 1.93 | 2017-09-06T06:00:00Z | 8.08 | 5 | SLFC1 | 6.48 | 2017-09-06T06:19:00Z | 12.01 | 11 | CTANT | 1.93 | 2017-09-06T06:00:00Z | 8.08 | 9 | SLFC1 | 6.48 | 2017-09-06T07:19:00Z | 18.01 | 20
PG&E | 2017-09-06 | 20:08 | 37.2925 | -122.294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100256917 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 0.83889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1400 | 2017 | 9 | 6 | 20 | 8 | 17-0076502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4914 | 6.7999 | 143_200 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 20:08:00 | 1138 | 13.6021 | FALSE | <25mph | LAHC1 | 2.3 | 2017-09-06T06:07:00Z | 4 | 1 | LAHC1 | 2.3 | 2017-09-06T06:07:00Z | 4 | 7 | LAHC1 | 2.3 | 2017-09-06T07:07:00Z | 4 | 2 | LAHC1 | 2.3 | 2017-09-06T07:07:00Z | 4 | 13
PG&E | 2017-09-08 | 4:47 | 38.7478 | -120.859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101391575 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42986 | 0.19931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1401 | 2017 | 9 | 8 | 4 | 47 | 17-0076889 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 39736 | 2.1381 | 205_280 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 04:47:00 | 1139 | 10.5203 | FALSE | <25mph | E5691 | 3.77 | 2017-09-08T06:56:00Z | 0 | 37 | E3165 | 7.16 | 2017-09-08T06:32:00Z | 3 | 78 | E5691 | 3.77 | 2017-09-08T07:56:00Z | 0 | 73 | E3165 | 7.16 | 2017-09-08T06:32:00Z | 3 | 154
PG&E | 2017-09-08 | 17:21 | 38.6039 | -120.9275 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101379094 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42986 | 0.72292 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1402 | 2017 | 9 | 8 | 17 | 21 | 17-0077122 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 8504 | 10.5347 | 203_272 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 17:21:00 | 1140 | 11.5767 | FALSE | <25mph | BENC1 | 0.96 | 2017-09-08T06:59:00Z | 7 | 14 | BENC1 | 0.96 | 2017-09-08T06:59:00Z | 7 | 59 | BENC1 | 0.96 | 2017-09-08T06:59:00Z | 7 | 27 | BENC1 | 0.96 | 2017-09-08T06:59:00Z | 7 | 116
PG&E | 2017-09-08 | 21:14 | 37.9604 | -120.3764 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | John Lite 209-984-5623 | 101042521 | Unknown | 17000 | Conductor | Overhead | Yes | 42986 | 0.88472 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1403 | 2017 | 9 | 8 | 21 | 14 | 17-0077137 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49858 | 11.2644 | 227_237 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 21:14:00 | 1141 | 11.9927 | FALSE | <25mph |  |  |  | 0 | 0 | F0305 | 6.4 | 2017-09-08T07:00:00Z | 0 | 17 |  |  |  | 0 | 0 | F0305 | 6.4 | 2017-09-08T08:00:00Z | 0 | 33
PG&E | 2017-09-11 | 7:18 | 37.0008 | -121.6667 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100621936 | VERIZON CALIFORNIA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1407 | 2017 | 9 | 11 | 7 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.0313 | 170_184 | <25mph | <15mph | HFTD - Distribution | 2017-09-11 07:18:00 | 1145 | 32.6801 | FALSE | 25-40mph | AU710 | 3.82 | 2017-09-11T06:15:00Z | 3 | 5 | C4787 | 7.93 | 2017-09-11T06:33:00Z | 11.01 | 40 | AU710 | 3.82 | 2017-09-11T08:00:00Z | 3 | 9 | C4787 | 7.93 | 2017-09-11T06:33:00Z | 11.01 | 79
PG&E | 2017-09-11 | 8:50 | 36.9515 | -121.842 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101790954 | PACIFIC BELL | 21000 | Fuse | Overhead | Yes | 42989 | 0.36806 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | no-match | 1408 | 2017 | 9 | 11 | 8 | 50 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | N.A. | 9.6414 | 162_181 | <25mph | <15mph | HFTD - Distribution | 2017-09-11 08:50:00 | 1146 | 17.9559 | FALSE | <25mph | CTOC1 | 3.41 | 2017-09-11T06:27:00Z | 4.99 | 32 | CTOC1 | 3.41 | 2017-09-11T06:27:00Z | 4.99 | 63 | E7291 | 2.85 | 2017-09-11T07:39:00Z | 7 | 65 | E7291 | 2.85 | 2017-09-11T07:39:00Z | 7 | 124
PG&E | 2017-09-12 | 9:24 | 39.741 | -121.6079 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 911 | 100330302 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42990 | 0.39167 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1410 | 2017 | 9 | 12 | 9 | 24 | 17-0078149 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 402890 | 5.7135 | 174_335 | <25mph | <15mph | HFTD - Distribution | 2017-09-12 09:24:00 | 1148 | 23.672 | FALSE | <25mph | PDEC1 | 1.25 | 2017-09-12T06:00:00Z | 8.99 | 2 | JBGC1 | 6.33 | 2017-09-12T06:13:00Z | 23 | 9 | PDEC1 | 1.25 | 2017-09-12T06:00:00Z | 8.99 | 3 | JBGC1 | 6.33 | 2017-09-12T06:13:00Z | 23 | 17
PG&E | 2017-09-14 | 14:06 | 40.2942 | -123.8174 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100989497 | Unknown | 12000 | Conductor | Overhead | Yes | 42992 | 0.5875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1414 | 2017 | 9 | 14 | 14 | 6 | 17-0079010 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 19722 | 23.1884 | 81_367 | <25mph | <15mph | HFTD - Distribution | 2017-09-14 14:06:00 | 1152 | 23.1884 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2017-09-15 | 14:55 | 39.7461 | -121.4885 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100335239 | Unknown | 12000 | Conductor | Overhead | Yes | 42993 | 0.62153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1415 | 2017 | 9 | 15 | 14 | 55 | 17-0079388 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 8834 | 10.5756 | 179_335 | <25mph | <15mph | HFTD - Distribution | 2017-09-15 14:55:00 | 1153 | 16.2937 | FALSE | <25mph | JBGC1 | 0.7 | 2017-09-15T06:13:00Z | 3 | 1 | JBGC1 | 0.7 | 2017-09-15T06:13:00Z | 3 | 3 | JBGC1 | 0.7 | 2017-09-15T07:13:00Z | 7 | 2 | JBGC1 | 0.7 | 2017-09-15T07:13:00Z | 7 | 5
PG&E | 2017-09-17 | 17:38 | 38.9946 | -121.0261 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100029537 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42995 | 0.73472 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Branch (OverHanging) | 1417 | 2017 | 9 | 17 | 17 | 38 | 17-0079585 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 28509 | 11.5169 | 198_294 | <25mph | <15mph | HFTD - Distribution | 2017-09-17 17:38:00 | 1155 | 15.8476 | FALSE | <25mph | C0713 | 1.74 | 2017-09-17T06:54:00Z | 0 | 9 | AT999 | 7.97 | 2017-09-17T06:52:00Z | 3 | 18 | C0713 | 1.74 | 2017-09-17T07:54:00Z | 0 | 19 | AT999 | 7.97 | 2017-09-17T07:07:00Z | 3 | 37
PG&E | 2017-09-18 | 13:01 | 39.3889 | -121.4054 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 103795057 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42996 | 0.54236 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1418 | 2017 | 9 | 18 | 13 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 17.7047 | 182_316 | <25mph | <15mph | HFTD - Distribution | 2017-09-18 13:01:00 | 1156 | 19.5678 | FALSE | <25mph | BNGC1 | 1.17 | 2017-09-18T06:51:00Z | 4.99 | 1 | TT309 | 5.6 | 2017-09-18T06:45:00Z | 7 | 2 | BNGC1 | 1.17 | 2017-09-18T07:51:00Z | 7 | 2 | TT309 | 5.6 | 2017-09-18T06:45:00Z | 7 | 4
PG&E | 2017-09-18 | 23:50 | 37.9088 | -120.4865 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | incident comander geoff marshall 209-419-4407 | 101040882 | Unknown | 17000 | Conductor | Overhead | Yes | 42996 | 0.99306 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1422 | 2017 | 9 | 18 | 23 | 50 | 17-0079858 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 382303 | 9.0814 | 222_234 | <25mph | <15mph | HFTD - Distribution | 2017-09-18 23:50:00 | 1160 | 16.9339 | FALSE | <25mph |  |  |  | 0 | 0 | GNSC1 | 5.23 | 2017-09-18T06:03:00Z | 4.99 | 1 |  |  |  | 0 | 0 | GNSC1 | 5.23 | 2017-09-18T07:03:00Z | 4.99 | 2
PG&E | 2017-09-20 | 2:06 | 37.2597 | -122.3222 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100322388 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42998 | 0.0875 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1424 | 2017 | 9 | 20 | 2 | 6 | 17-0080179 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 36593 | 8.989 | 141_198 | <25mph | <15mph | HFTD - Distribution | 2017-09-20 02:06:00 | 1162 | 20.1127 | FALSE | <25mph |  |  |  | 0 | 0 | LAHC1 | 4.84 | 2017-09-20T06:07:00Z | 4 | 1 |  |  |  | 0 | 0 | LAHC1 | 4.84 | 2017-09-20T07:07:00Z | 4 | 2
PG&E | 2017-09-23 | 14:17 | 40.6509 | -122.2974 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DARREN STEWART 448-2421 | 101467221 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43001 | 0.59514 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1429 | 2017 | 9 | 23 | 14 | 17 | 17-0081216 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 98820 | 17.9072 | 145_386 | <25mph | <15mph | HFTD - Distribution | 2017-09-23 14:17:00 | 1167 | 24.6958 | FALSE | <25mph | C5599 | 3.73 | 2017-09-23T06:16:00Z | 4.99 | 4 | C5599 | 3.73 | 2017-09-23T06:16:00Z | 4.99 | 10 | C5599 | 3.73 | 2017-09-23T06:16:00Z | 4.99 | 8 | C5599 | 3.73 | 2017-09-23T06:16:00Z | 4.99 | 20
PG&E | 2017-09-24 | 16:42 | 38.3869 | -122.9667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DOUG JONES | 101973946 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43002 | 0.69583 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1432 | 2017 | 9 | 24 | 16 | 42 | 17-0081329 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 22574 | 19.6154 | 114_261 | <25mph | <15mph | HFTD - Distribution | 2017-09-24 16:42:00 | 1170 | 19.6154 | FALSE | <25mph | D2849 | 0.23 | 2017-09-24T07:00:00Z | 1.01 | 13 | BGAC1 | 6.8 | 2017-09-24T06:05:00Z | 7 | 71 | D2849 | 0.23 | 2017-09-24T07:55:00Z | 1.01 | 25 | BGAC1 | 6.8 | 2017-09-24T06:05:00Z | 7 | 147
PG&E | 2017-09-27 | 12:12 | 39.4845 | -121.3545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | bill lopez cell 530 521-8052 | 100429924 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 43005 | 0.50833 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1436 | 2017 | 9 | 27 | 12 | 12 | 17-0082180 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 6370 | 7.6613 | 184_321 | <25mph | <15mph | HFTD - Distribution | 2017-09-27 12:12:00 | 1174 | 27.61 | FALSE | 25-40mph | TT309 | 3.08 | 2017-09-27T06:45:00Z | 4 | 1 | BNGC1 | 7.37 | 2017-09-27T06:51:00Z | 7 | 2 | TT309 | 3.08 | 2017-09-27T07:45:00Z | 4 | 2 | BNGC1 | 7.37 | 2017-09-27T06:51:00Z | 7 | 4
PG&E | 2017-09-27 | 19:06 | 40.7592 | -123.995 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103660812 | Unknown | 12000 | Conductor | Overhead | Yes | 43005 | 0.79583 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1437 | 2017 | 9 | 27 | 19 | 6 | 17-0082303 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 35394 | 10.6184 | 74_393 | <25mph | <15mph | HFTD - Distribution | 2017-09-27 19:06:00 | 1175 | 13.0154 | FALSE | <25mph |  |  |  | 0 | 0 | KNNC1 | 4.42 | 2017-09-27T06:55:00Z | 10 | 11 |  |  |  | 0 | 0 | KNNC1 | 4.42 | 2017-09-27T07:55:00Z | 10 | 21
PG&E | 2017-10-02 | 14:56 | 38.9102 | -120.9185 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100110800 | None | 21000 | Other | Overhead | Yes | 43010 | 0.62222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1447 | 2017 | 10 | 2 | 14 | 56 | 17-0083516 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 160 | 17.2967 | 203_289 | <25mph | <15mph | HFTD - Distribution | 2017-10-02 14:56:00 | 1185 | 22.7009 | FALSE | <25mph |  |  |  | 0 | 0 | E6476 | 6.41 | 2017-10-02T06:55:00Z | 10 | 14 |  |  |  | 0 | 0 | E6476 | 6.41 | 2017-10-02T06:55:00Z | 10 | 31
PG&E | 2017-10-02 | 16:05 | 38.7182 | -120.9756 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101375963 | Unknown | 21000 | Conductor | Overhead | Yes | 43010 | 0.67014 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1448 | 2017 | 10 | 2 | 16 | 5 | 17-0083539 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4797 | 14.669 | 201_279 | <25mph | <15mph | HFTD - Distribution | 2017-10-02 16:05:00 | 1186 | 17.4155 | FALSE | <25mph | D7401 | 3.14 | 2017-10-02T06:03:00Z | 4 | 70 | E4740 | 4.79 | 2017-10-02T06:50:00Z | 4 | 92 | D7401 | 3.14 | 2017-10-02T06:03:00Z | 4 | 147 | E4740 | 4.79 | 2017-10-02T07:50:00Z | 4.99 | 190
PG&E | 2017-10-04 | 23:42 | 38.6554 | -120.9934 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101375442 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 43012 | 0.9875 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1452 | 2017 | 10 | 4 | 23 | 42 | 17-0084323 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7553 | 12.9958 | 200_275 | <25mph | <15mph | HFTD - Distribution | 2017-10-04 23:42:00 | 1190 | 14.755 | FALSE | <25mph | D7401 | 2.11 | 2017-10-04T06:24:00Z | 8.01 | 20 | D7401 | 2.11 | 2017-10-04T06:24:00Z | 8.01 | 106 | D7401 | 2.11 | 2017-10-04T06:24:00Z | 8.01 | 39 | D7401 | 2.11 | 2017-10-04T06:24:00Z | 8.01 | 207
PG&E | 2017-10-08 | 19:44 | 39.7446 | -121.597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100330456 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 0.82222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1464 | 2017 | 10 | 8 | 19 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 33.2724 | 174_335 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-08 19:44:00 | 1202 | 34.7906 | FALSE | 25-40mph | PDEC1 | 1.6 | 2017-10-08T07:00:00Z | 1.01 | 2 | JBGC1 | 5.77 | 2017-10-08T06:13:00Z | 11.01 | 9 | PDEC1 | 1.6 | 2017-10-08T08:00:00Z | 1.01 | 3 | JBGC1 | 5.77 | 2017-10-08T07:13:00Z | 13 | 17
PG&E | 2017-10-08 | 20:35 | 39.6315 | -121.4225 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100347747 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 0.85764 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1465 | 2017 | 10 | 8 | 20 | 35 | 17-0085196 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 181992 | 24.0056 | 181_329 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 20:35:00 | 1203 | 27.1605 | FALSE | 25-40mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2017-10-08 | 21:10 | 39.4554 | -121.0498 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100099226 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 0.88194 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (Not overhanging, > 12ft) | 1466 | 2017 | 10 | 8 | 21 | 10 | 17-0085261 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 255784 | 21.8939 | 197_319 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 21:10:00 | 1204 | 34.69 | FALSE | 25-40mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2017-10-08 | 21:46 | 39.2595 | -120.9965 | Vegetation | Urban | < 0.25 Acres | Fire Agency | PHILLIP NUNNICK 530 273-3158 INCENDENT # 26264 | 100072730 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 43016 | 0.90694 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1467 | 2017 | 10 | 8 | 21 | 46 | 17-0085308 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 12650 | 28.1852 | 200_308 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-10-08 21:46:00 | 1205 | 31.7744 | FALSE | 25-40mph | E9947 | 1.53 | 2017-10-08T06:34:00Z | 3 | 26 | RRRC1 | 7.14 | 2017-10-08T06:13:00Z | 8.01 | 59 | E9947 | 1.53 | 2017-10-08T06:34:00Z | 3 | 52 | RRRC1 | 7.14 | 2017-10-08T07:13:00Z | 8.99 | 117
PG&E | 2017-10-08 | 22:19 | 39.7371 | -121.6464 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 103319605 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43016 | 0.92986 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1468 | 2017 | 10 | 8 | 22 | 19 | 17-0085504 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 42839 | 9.4272 | 172_335 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 22:19:00 | 1208 | 31.7535 | FALSE | 25-40mph | PDEC1 | 1.62 | 2017-10-08T07:00:00Z | 1.01 | 2 | C4565 | 7.55 | 2017-10-08T06:43:00Z | 3 | 8 | PDEC1 | 1.62 | 2017-10-08T08:00:00Z | 1.01 | 3 | C4565 | 7.55 | 2017-10-08T07:53:00Z | 3 | 15
PG&E | 2017-10-08 | 22:54 | 35.5528 | -118.9681 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | span 7/87-7/88, Vedder Tap | Unknown | 115000 | Conductor | Overhead | Yes | 43016 | 0.95417 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1470 | 2017 | 10 | 8 | 22 | 54 | INT-10231 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 66311 | 16.3809 | 291_105 | <25mph | <15mph | HFTD - Transmission | 2017-10-08 22:54:00 | 1210 | 17.6011 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2017-10-08 | 22:58 | 39.3642 | -121.1131 | Vegetation | Rural | < 3 Meters | Fire Agency | INCIDENT NUMBER 26268 | 100068104 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43016 | 0.95694 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Fell into (No defect) | 1471 | 2017 | 10 | 8 | 22 | 58 | 17-0085355 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 198802 | 15.5554 | 195_314 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 22:58:00 | 1211 | 22.0344 | FALSE | <25mph | E3651 | 3.94 | 2017-10-08T06:45:00Z | 3 | 13 | RRRC1 | 4.2 | 2017-10-08T06:13:00Z | 8.01 | 20 | E3651 | 3.94 | 2017-10-08T06:45:00Z | 3 | 25 | RRRC1 | 4.2 | 2017-10-08T07:13:00Z | 8.99 | 39
PG&E | 2017-10-09 | 1:02 | 38.7037 | -120.6725 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101408485 | Unknown | 21000 | Other | Overhead | Yes | 43017 | 0.043056 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1473 | 2017 | 10 | 9 | 1 | 2 | 17-0085324 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 419843 | 26.702 | 214_278 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-10-09 01:02:00 | 1216 | 29.779 | FALSE | 25-40mph | AV185 | 3.98 | 2017-10-09T06:00:00Z | 15.99 | 3 | KPVF | 4.58 | 2017-10-09T06:55:00Z | 33.38 | 28 | AV185 | 3.98 | 2017-10-09T07:30:00Z | 18.99 | 5 | KPVF | 4.58 | 2017-10-09T06:55:00Z | 33.38 | 55
PG&E | 2017-10-09 | 1:45 | 38.8576 | -122.7221 | Vegetation | Rural | < 0.25 Acres | Fire Agency | wink | 103570679 | Unknown | 12000 | Conductor | Overhead | Yes | 43017 | 0.072917 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Other/Unknown | 1477 | 2017 | 10 | 9 | 1 | 45 | 17-0085344 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 219653 | 32.3097 | 125_287 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-09 01:45:00 | 1220 | 32.3097 | FALSE | 25-40mph | LKRC1 | 3.67 | 2017-10-09T06:05:00Z | 34.99 | 2 | LKRC1 | 3.67 | 2017-10-09T06:05:00Z | 34.99 | 2 | LKRC1 | 3.67 | 2017-10-09T07:05:00Z | 48 | 4 | LKRC1 | 3.67 | 2017-10-09T07:05:00Z | 48 | 4
PG&E | 2017-10-10 | 13:36 | 38.931 | -123.3023 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 102214553 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43018 | 0.56667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1481 | 2017 | 10 | 10 | 13 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.7263 | 101_291 | <25mph | <15mph | HFTD - Distribution | 2017-10-10 13:36:00 | 1224 | 17.0479 | FALSE | <25mph |  |  |  | 0 | 0 | E4371 | 5.14 | 2017-10-10T06:02:00Z | 10 | 8 |  |  |  | 0 | 0 | BNVC1 | 4.62 | 2017-10-10T07:50:00Z | 13 | 17
PG&E | 2017-10-11 | 11:57 | 38.5015 | -123.0237 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101974930 | Unknown | 12000 | Conductor | Overhead | Yes | 43019 | 0.49792 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1484 | 2017 | 10 | 11 | 11 | 57 | 17-0086350 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 226925 | 16.5068 | 112_268 | <25mph | <15mph | HFTD - Distribution | 2017-10-11 11:57:00 | 1227 | 19.0479 | FALSE | <25mph | D9841 | 2.93 | 2017-10-11T06:47:00Z | 0 | 31 | R30WW | 7.7 | 2017-10-11T06:00:00Z | 2.51 | 39 | D9841 | 2.93 | 2017-10-11T07:47:00Z | 0 | 61 | R30WW | 7.7 | 2017-10-11T08:00:00Z | 3.2 | 75
PG&E | 2017-10-13 | 10:27 | 37.0561 | -122.0206 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Scotts Valley Fire Dept. | 101677721 | Unknown | 21000 | Conductor | Overhead | Yes | 43021 | 0.43542 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Grow Into | 1487 | 2017 | 10 | 13 | 10 | 27 | 17-0087093 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Grow Into | 201996 | 10.1261 | 155_187 | <25mph | <15mph | HFTD - Distribution | 2017-10-13 10:27:00 | 1230 | 15.0293 | FALSE | <25mph | C5272 | 2.36 | 2017-10-13T06:52:00Z | 4 | 38 | E6085 | 7.97 | 2017-10-13T06:50:00Z | 10 | 171 | C5272 | 2.36 | 2017-10-13T06:52:00Z | 4 | 75 | E6085 | 7.97 | 2017-10-13T07:35:00Z | 11.01 | 340
PG&E | 2017-10-13 | 22:19 | 39.7648 | -121.6307 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100325368 | PACIFIC BELL | 0 – 750 | Transformer | Overhead | Yes | 43021 | 0.92986 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1489 | 2017 | 10 | 13 | 22 | 19 | 17-0087321 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 7056 | 20.0116 | 173_336 | <25mph | <15mph | HFTD - Distribution | 2017-10-13 22:19:00 | 1232 | 26.6486 | FALSE | 25-40mph | PDEC1 | 0.84 | 2017-10-13T07:00:00Z | 2.01 | 2 | JBGC1 | 7.79 | 2017-10-13T06:13:00Z | 11.01 | 21 | PDEC1 | 0.84 | 2017-10-13T07:00:00Z | 2.01 | 3 | JBGC1 | 7.79 | 2017-10-13T07:13:00Z | 13 | 41
PG&E | 2017-10-16 | 12:10 | 36.5831 | -121.9368 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101781248 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43024 | 0.50694 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | Other/Unknown | 1493 | 2017 | 10 | 16 | 12 | 10 | 17-0087767 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 6313 | 5.0415 | 158_161 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:10:00 | 1236 | 13.6905 | FALSE | <25mph | E6019 | 2.26 | 2017-10-16T06:15:00Z | 12.01 | 22 | E6019 | 2.26 | 2017-10-16T06:15:00Z | 12.01 | 26 | E6019 | 2.26 | 2017-10-16T07:30:00Z | 12.01 | 42 | E6019 | 2.26 | 2017-10-16T07:30:00Z | 12.01 | 50
PG&E | 2017-10-16 | 12:20 | 37.72 | -122.0687 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100900970 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43024 | 0.51389 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | no-match | 1494 | 2017 | 10 | 16 | 12 | 20 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 7.2864 | 153_224 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:20:00 | 1237 | 12.1708 | FALSE | <25mph | E9856 | 0.77 | 2017-10-16T06:58:00Z | 4.99 | 6 | OKSC1 | 6.18 | 2017-10-16T06:33:00Z | 12.01 | 54 | E9856 | 0.77 | 2017-10-16T07:43:00Z | 4.99 | 16 | LTRC1 | 7.87 | 2017-10-16T07:28:00Z | 15.99 | 112
PG&E | 2017-10-16 | 12:26 | 36.6641 | -121.0995 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Nick Shawkey E4462 209-402-1645 Cover Engine from Tuolumne Calaveras Unit | 101689865 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43024 | 0.51806 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1495 | 2017 | 10 | 16 | 12 | 26 | 17-0087754 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 519 | 1.3904 | 195_165 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:26:00 | 1238 | 14.8173 | FALSE | <25mph |  |  |  | 0 | 0 | E1697 | 6.85 | 2017-10-16T06:58:00Z | 4 | 4 |  |  |  | 0 | 0 | E1697 | 6.85 | 2017-10-16T07:43:00Z | 5.99 | 8
PG&E | 2017-10-20 | 6:18 | 39.2922 | -121.0157 | Vegetation | Rural | < 3 Meters | Fire Agency | PHILLIP NUNNINK INCIDENT # 27272 | 100087647 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43028 | 0.2625 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1499 | 2017 | 10 | 20 | 6 | 18 | 17-0088957 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 102410 | 6.1464 | 199_310 | <25mph | <15mph | HFTD - Distribution | 2017-10-20 06:18:00 | 1242 | 23.0997 | FALSE | <25mph | E9947 | 3.74 | 2017-10-20T06:59:00Z | 11.01 | 20 | RRRC1 | 5.48 | 2017-10-20T06:13:00Z | 22.01 | 73 | E3651 | 3.59 | 2017-10-20T08:00:00Z | 14.99 | 40 | KGOO | 4.76 | 2017-10-20T07:55:00Z | 35.68 | 145
PG&E | 2017-10-20 | 13:45 | 34.5532 | -120.5303 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 101921492 | Unknown | 12000 | Conductor | Overhead | Yes | 43028 | 0.57292 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1502 | 2017 | 10 | 20 | 13 | 45 | 17-0089249 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 173 | 31.847 | 221_49 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-20 13:45:00 | 1245 | 35.5655 | FALSE | 25-40mph |  |  |  | 0 | 0 | E2332 | 4.19 | 2017-10-20T06:04:00Z | 23 | 21 |  |  |  | 0 | 0 | E2332 | 4.19 | 2017-10-20T06:04:00Z | 23 | 37
PG&E | 2017-10-21 | 15:08 | 39.064 | -122.7765 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102155186 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43029 | 0.63056 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1504 | 2017 | 10 | 21 | 15 | 8 | 17-0089392 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 13374 | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2017-10-21 15:08:00 | NA | 0 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2017-10-23 | 21:24 | 37.3713 | -122.348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100270421 | Unknown | 12000 | Conductor | Overhead | Yes | 43031 | 0.89167 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1507 | 2017 | 10 | 23 | 21 | 24 | 17-0089820 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1768 | 13.1103 | 140_205 | <25mph | <15mph | HFTD - Distribution | 2017-10-23 21:24:00 | 1249 | 22.0037 | FALSE | <25mph | E4551 | 1.61 | 2017-10-23T06:48:00Z | 3 | 6 | LAHC1 | 6.84 | 2017-10-23T06:07:00Z | 7 | 18 | E4551 | 1.61 | 2017-10-23T07:58:00Z | 4 | 12 | E4863 | 4.38 | 2017-10-23T07:49:00Z | 8.99 | 36
PG&E | 2017-10-28 | 15:26 | 39.4516 | -123.3838 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102209084 | Unknown | 12000 | Conductor | Overhead | Yes | 43036 | 0.64306 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | no-match | 1510 | 2017 | 10 | 28 | 15 | 26 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 10.3107 | 98_320 | <25mph | <15mph | HFTD - Distribution | 2017-10-28 15:26:00 | 1252 | 11.7696 | FALSE | <25mph | E4027 | 3.28 | 2017-10-28T06:58:00Z | 0 | 12 | AT319 | 5.75 | 2017-10-28T06:58:00Z | 2.01 | 24 | E4027 | 3.28 | 2017-10-28T07:58:00Z | 0 | 24 | AT319 | 5.75 | 2017-10-28T07:48:00Z | 2.01 | 48
PG&E | 2017-10-31 | 21:02 | 39.1119 | -122.9163 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Structure 020/003 | Unknown | 60000 | Conductor | Overhead | Yes | 43039 | 0.87639 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | no-match | 1513 | 2017 | 10 | 31 | 21 | 2 | INT-10325 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | 50730 | 1.8727 | 117_301 | <25mph | <15mph | HFTD - Transmission | 2017-10-31 21:02:00 | 1255 | 9.8895 | FALSE | <25mph |  |  |  | 0 | 0 | E5780 | 6.35 | 2017-10-31T06:56:00Z | 3 | 12 |  |  |  | 0 | 0 | E5780 | 6.35 | 2017-10-31T07:57:00Z | 4 | 24
PG&E | 2017-11-08 07:12 | 07:11 | 37.7367 | -120.3459 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101191714 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43047.2998 | 07:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1516 | 2017 | 11 | 8 | 7 | 11 | 17-0093414 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 1573 | 10.744 | 228_225 | <25mph | <15mph | HFTD - Distribution | 2017-11-08 07:11:00 | 1258 | 18.072 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2017-11-11 12:17 | 11:57 | 35.1191 | -120.3936 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Jordan Dayley ph#929-3911,engine#3467 | 101931190 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43050.5115 | 0.49792 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1518 | 2017 | 11 | 11 | 11 | 57 | 17-0094408 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29093 | 8.6182 | 227_80 | <25mph | <15mph | HFTD - Distribution | 2017-11-11 11:57:00 | 1260 | 14.1707 | FALSE | <25mph | AU609 | 1.13 | 2017-11-11T19:50:00Z | 12.01 | 3 | AU609 | 1.13 | 2017-11-11T19:50:00Z | 12.01 | 9 | AU609 | 1.13 | 2017-11-11T19:50:00Z | 12.01 | 5 | F0412 | 7.06 | 2017-11-11T21:15:00Z | 13 | 17
PG&E | 2017-11-20 08:33 | 08:32 | 38.7584 | -120.8439 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101389405 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43059.3562 | 08:32 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1522 | 2017 | 11 | 20 | 8 | 32 | 17-0096436 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 12376 | 9.7427 | 206_281 | <25mph | <15mph | HFTD - Distribution | 2017-11-20 08:32:00 | 1264 | 12.0384 | FALSE | <25mph | E5691 | 2.94 | 2017-11-20T16:29:00Z | 0 | 12 | E3165 | 6.09 | 2017-11-20T16:06:00Z | 5.99 | 109 | E5691 | 2.94 | 2017-11-20T17:29:00Z | 0 | 24 | E3165 | 6.09 | 2017-11-20T16:06:00Z | 5.99 | 219
PG&E | 2017-11-29 17:35 | 17:34 | 38.6841 | -120.6546 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 101419450 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 43068.7326 | 17:34 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1533 | 2017 | 11 | 29 | 17 | 34 | 17-0098456 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 582825 | 2.2539 | 214_277 | <25mph | <15mph | HFTD - Distribution | 2017-11-29 17:34:00 | 1275 | 13.1335 | FALSE | <25mph |  |  |  | 0 | 0 | GZFC1 | 7.93 | 2017-11-30T01:17:00Z | 3 | 8 |  |  |  | 0 | 0 | GZFC1 | 7.93 | 2017-11-30T02:17:00Z | 3 | 17
PG&E | 2017-12-07 12:26 | 12:25 | 34.7115 | -120.1772 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 015/220 | Unknown | 115000 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1534 | 2017 | 12 | 7 | 12 | 25 | 17-0097211 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 4.373 | 237_58 | <25mph | <15mph | HFTD - Transmission | 2017-12-07 12:25:00 | 1276 | 13.3077 | FALSE | <25mph | TT480 | 2.15 | 2017-12-07T20:20:00Z | 25.99 | 1 | SXWC1 | 7.67 | 2017-12-07T20:09:00Z | 27 | 9 | TT480 | 2.15 | 2017-12-07T20:20:00Z | 25.99 | 2 | SXWC1 | 7.67 | 2017-12-07T20:09:00Z | 27 | 23
PG&E | 2017-12-14 | 17:16 | 34.5878 | -120.3566 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101911004 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 43083 | 0.71944 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1538 | 2017 | 12 | 14 | 17 | 16 | 17-0101672 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2896 | 2.7073 | 229_51 | <25mph | <15mph | HFTD - Distribution | 2017-12-14 17:16:00 | 1280 | 11.3138 | FALSE | <25mph |  |  |  | 0 | 0 | E2332 | 7.61 | 2017-12-14T08:00:00Z | 15.99 | 7 |  |  |  | 0 | 0 | E2332 | 7.61 | 2017-12-14T08:56:00Z | 22.01 | 24
PG&E | 2017-12-16 | 11:51 | 38.8171 | -122.7041 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Shawn Ohare | 102167231 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43085 | 0.49375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1540 | 2017 | 12 | 16 | 11 | 51 | 17-0102101 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26120 | 34.3488 | 126_285 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-12-16 11:51:00 | 1282 | 35.345 | FALSE | 25-40mph | LKRC1 | 2.09 | 2017-12-16T07:05:00Z | 17 | 1 | KELC1 | 6.55 | 2017-12-16T07:57:00Z | 23 | 2 | LKRC1 | 2.09 | 2017-12-16T08:05:00Z | 18.99 | 2 | KELC1 | 6.55 | 2017-12-16T07:57:00Z | 23 | 4
PG&E | 2017-12-19 | 19:45 | 40.7271 | -122.3263 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101457738 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43088 | 0.82292 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1545 | 2017 | 12 | 19 | 19 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 12.0712 | 144_390 | <25mph | <15mph | HFTD - Distribution | 2017-12-19 19:45:00 | 1287 | 14.9625 | FALSE | <25mph |  |  |  | 0 | 0 | F0355 | 7.84 | 2017-12-19T07:51:00Z | 0 | 6 |  |  |  | 0 | 0 | F0355 | 7.84 | 2017-12-19T08:51:00Z | 0 | 12
PG&E | 2017-12-20 07:55 | 07:54 | 37.4012 | -122.3606 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100318864 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43089.3298 | 07:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1546 | 2017 | 12 | 20 | 7 | 54 | 17-0102756 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6602 | 16.1413 | 140_206 | <25mph | <15mph | HFTD - Distribution | 2017-12-20 07:54:00 | 1288 | 21.2088 | FALSE | <25mph | E4863 | 2.73 | 2017-12-20T15:28:00Z | 17 | 3 | E4863 | 2.73 | 2017-12-20T15:28:00Z | 17 | 13 | E4863 | 2.73 | 2017-12-20T16:38:00Z | 17 | 6 | E4863 | 2.73 | 2017-12-20T16:38:00Z | 17 | 19
PG&E | 2017-12-20 14:04 | 14:03 | 35.6646 | -121.244 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103857828 | Unknown | 12000 | Fuse | Overhead | No |  |  | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1547 | 2017 | 12 | 20 | 14 | 3 | 17-0102828 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 31041 | 28.5755 | 189_110 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-12-20 14:03:00 | 1289 | 28.5755 | FALSE | 25-40mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2017-12-29 | 16:31 | 37.8517 | -122.1586 | Vegetation | Rural | < 3 Meters | Fire Agency | 925-933-1313 | 100488954 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1552 | 2017 | 12 | 29 | 16 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 4.4772 | 149_231 | <25mph | <15mph | HFTD - Distribution | 2017-12-29 16:31:00 | 1294 | 9.6531 | FALSE | <25mph | E5555 | 3.67 | 2017-12-29T07:01:00Z | 23 | 31 | E5555 | 3.67 | 2017-12-29T07:01:00Z | 23 | 135 | E5555 | 3.67 | 2017-12-29T07:01:00Z | 23 | 61 | E5555 | 3.67 | 2017-12-29T07:01:00Z | 23 | 263
PG&E | 2018-01-16 | 14:25 | 34.5703 | -119.9645 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101921689 | Verizon | 12000 | Conductor | Overhead | Yes | 43116 | 0.60069 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1556 | 2018 | 1 | 16 | 14 | 25 | 18-0006506 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 23519 | 5.0963 | 247_50 | <25mph | <15mph | HFTD - Distribution | 2018-01-16 14:25:00 | 1298 | 9.8389 | FALSE | <25mph |  |  |  | 0 | 0 | RHWC1 | 7.32 | 2018-01-16T07:06:00Z | 21 | 6 |  |  |  | 0 | 0 | RHWC1 | 7.32 | 2018-01-16T08:06:00Z | 21 | 11
PG&E | 2018-02-07 | 5:44 | 40.6543 | -122.5198 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 103922730 | Unknown | 12000 | Conductor | Overhead | Yes | 43138 | 0.23889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1558 | 2018 | 2 | 7 | 5 | 44 | 18-0012073 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 9610 | 17.8768 | 136_386 | <25mph | <15mph | HFTD - Distribution | 2018-02-07 05:44:00 | 1300 | 25.5948 | FALSE | 25-40mph | AU138 | 3.45 | 2018-02-07T07:44:00Z | 10 | 5 | MMOC1 | 5.95 | 2018-02-07T08:00:00Z | 27 | 9 | AU138 | 3.45 | 2018-02-07T07:44:00Z | 10 | 9 | MMOC1 | 5.95 | 2018-02-07T09:00:00Z | 28.99 | 15
PG&E | 2018-02-07 | 9:16 | 38.0369 | -120.2096 | Vegetation | Rural | < 3 meters | Fire Agency | Jason Podesta 209-586-3362 | 101038120 | AT&T | 17000 | Conductor | Overhead | Yes | 43138 | 0.38611 | Contact From Object | N.A. | Other | Electric Facility | Human Error | third-party caused | Other/Unknown | 1559 | 2018 | 2 | 7 | 9 | 16 | 18-0012146 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 78738 | 9.6764 | 234_241 | <25mph | <15mph | HFTD - Distribution | 2018-02-07 09:16:00 | 1301 | 13.44 | FALSE | <25mph | MOUC1 | 2.73 | 2018-02-07T07:02:00Z | 18.99 | 1 | MOUC1 | 2.73 | 2018-02-07T07:02:00Z | 18.99 | 1 | MOUC1 | 2.73 | 2018-02-07T08:02:00Z | 20 | 2 | MOUC1 | 2.73 | 2018-02-07T08:02:00Z | 20 | 2
PG&E | 2018-02-12 | 20:20 | 39.9395 | -121.6494 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430947 | Unknown | 12000 | Conductor | Overhead | Yes | 43143 | 0.84722 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1561 | 2018 | 2 | 12 | 20 | 20 | 18-0013604 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 149212 | 10.1876 | 172_346 | <25mph | <15mph | HFTD - Distribution | 2018-02-12 20:20:00 | 1303 | 14.6044 | FALSE | <25mph |  |  |  | 0 | 0 | CSTC1 | 7.88 | 2018-02-12T07:51:00Z | 5.99 | 19 |  |  |  | 0 | 0 | CSTC1 | 7.88 | 2018-02-12T08:51:00Z | 14.99 | 38
PG&E | 2018-02-26 | 16:33 | 35.5302 | -118.9695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100208194 | Unknown | 21000 | Conductor | Overhead | Yes | 43157 | 0.68958 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1563 | 2018 | 2 | 26 | 16 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 13.4301 | 291_104 | <25mph | <15mph | HFTD - Distribution | 2018-02-26 16:33:00 | 1305 | 20.5649 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-03-03 | 12:15 | 39.1213 | -121.055 | Building | Urban | Structure Only | Unknown | N.A. | 100095928 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43162 | 0.51042 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1564 | 2018 | 3 | 3 | 12 | 15 | 18-0019280 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 15750 | 9.9978 | 197_301 | <25mph | <15mph | HFTD - Distribution | 2018-03-03 12:15:00 | 1306 | 11.8211 | FALSE | <25mph | C5488 | 3.59 | 2018-03-03T07:00:00Z | 10 | 22 | C5488 | 3.59 | 2018-03-03T07:00:00Z | 10 | 77 | C5488 | 3.59 | 2018-03-03T07:00:00Z | 10 | 43 | C5488 | 3.59 | 2018-03-03T07:00:00Z | 10 | 148
PG&E | 2018-03-06 | 17:57 | 38.2811 | -120.8965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-647-5220 | 101238429 | AT&T | 12000 | Conductor | Overhead | Yes | 43165 | 0.74792 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1566 | 2018 | 3 | 6 | 17 | 57 | 18-0020396 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 142000 | 3.9357 | 204_254 | <25mph | <15mph | HFTD - Distribution | 2018-03-06 17:57:00 | 1308 | 12.1612 | FALSE | <25mph |  |  |  | 0 | 0 | CFAC1 | 7.07 | 2018-03-06T07:05:00Z | 13 | 4 |  |  |  | 0 | 0 | CFAC1 | 7.07 | 2018-03-06T08:05:00Z | 14 | 8
PG&E | 2018-03-26 | 17:06 | 38.7304 | -122.6215 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102166450 | AT&T | 12000 | Conductor | Overhead | Yes | 43185 | 0.7125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1569 | 2018 | 3 | 26 | 17 | 6 | 18-0026824 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3255 | 19.5124 | 130_280 | <25mph | <15mph | HFTD - Distribution | 2018-03-26 17:06:00 | 1311 | 20.9229 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-04-27 | 12:48 | 39.1717 | -120.8652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | incident # 9960 ph # 530-8850111 | 100075314 | Unknown | 12000 | Conductor | Overhead | Yes | 43217 | 0.53333 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Dead | 1577 | 2018 | 4 | 27 | 12 | 48 | 18-0036310 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 28650 | 12.9115 | 205_304 | <25mph | <15mph | HFTD - Distribution | 2018-04-27 12:48:00 | 1319 | 12.9115 | FALSE | <25mph | SETC1 | 1.33 | 2018-04-27T06:28:00Z | 2.01 | 1 | AT999 | 7.76 | 2018-04-27T06:02:00Z | 4 | 14 | SETC1 | 1.33 | 2018-04-27T07:28:00Z | 2.01 | 2 | AT999 | 7.76 | 2018-04-27T07:32:00Z | 4 | 27
PG&E | 2018-05-09 | 14:00 | 38.5908 | -123.3423 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CASE# 18CALNU 005865 | 101998286 | Unknown | 12000 | Conductor | Overhead | Yes | 43229 | 0.58333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1584 | 2018 | 5 | 9 | 14 | 0 | 18-0039683 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 29522 | 27.1689 | 98_273 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-05-09 14:00:00 | 1326 | 27.3091 | FALSE | 25-40mph | E7021 | 3.81 | 2018-05-09T06:56:00Z | 0 | 6 | HIRWW | 5.18 | 2018-05-09T07:00:00Z | 7.9 | 8 | E7021 | 3.81 | 2018-05-09T07:36:00Z | 8.01 | 12 | E7021 | 3.81 | 2018-05-09T07:36:00Z | 8.01 | 15
PG&E | 2018-05-11 | 10:13 | 38.387 | -122.9856 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101973909 | Unknown | 12000 | Conductor | Overhead | Yes | 43231 | 0.42569 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1585 | 2018 | 5 | 11 | 10 | 13 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.6545 | 114_261 | <25mph | <15mph | HFTD - Distribution | 2018-05-11 10:13:00 | 1327 | 21.7544 | FALSE | <25mph | D2849 | 0.89 | 2018-05-11T06:52:00Z | 3 | 12 | BGAC1 | 6.17 | 2018-05-11T06:05:00Z | 25.99 | 55 | D2849 | 0.89 | 2018-05-11T06:52:00Z | 3 | 24 | BGAC1 | 6.17 | 2018-05-11T06:05:00Z | 25.99 | 106
PG&E | 2018-05-11 | 15:51 | 40.3385 | -123.9137 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100989912 | Unknown | 12000 | Conductor | Overhead | Yes | 43231 | 0.66042 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1587 | 2018 | 5 | 11 | 15 | 51 | 18-0040389 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 5926 | 23.9859 | 77_370 | <25mph | <15mph | HFTD - Distribution | 2018-05-11 15:51:00 | 1329 | 23.9859 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-05-11 | 17:43 | 38.8218 | -120.9295 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Douglas Ferro. cell-530-708-2715. office-530-677-6192 | 101388939 | AT&T | 21000 | Conductor | Overhead | Yes | 43231 | 0.73819 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1588 | 2018 | 5 | 11 | 17 | 43 | 18-0040415 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 53784 | 23.6414 | 202_284 | <25mph | <15mph | HFTD - Distribution | 2018-05-11 17:43:00 | 1330 | 24.2639 | FALSE | <25mph |  |  |  | 0 | 0 | PLTC1 | 4.34 | 2018-05-11T06:56:00Z | 2.01 | 19 |  |  |  | 0 | 0 | PLTC1 | 4.34 | 2018-05-11T07:56:00Z | 3 | 38
PG&E | 2018-05-19 | 19:44 | 40.2665 | -122.2727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103899310 | Unknown | 12000 | Conductor | Overhead | Yes | 43239 | 0.82222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1599 | 2018 | 5 | 19 | 19 | 44 | 18-0042559 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 31980 | 15.59 | 146_364 | <25mph | <15mph | HFTD - Distribution | 2018-05-19 19:44:00 | 1341 | 18.253 | FALSE | <25mph |  |  |  | 0 | 0 | E7114 | 7.1 | 2018-05-19T06:14:00Z | 3 | 4 |  |  |  | 0 | 0 | E7114 | 7.1 | 2018-05-19T08:00:00Z | 3 | 8
PG&E | 2018-05-28 | 6:30 | 40.4382 | -122.3001 | Building | Rural | Structure Only | Unknown | N.A. | 101495757 | Unknown | 0 – 750 | conductor | Overhead | Yes | 43248 | 0.27083 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1610 | 2018 | 5 | 28 | 6 | 30 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 17.501 | 145_374 | <25mph | <15mph | HFTD - Distribution | 2018-05-28 06:30:00 | 1352 | 26.4092 | FALSE | 25-40mph | AP525 | 2.99 | 2018-05-28T06:55:00Z | 0 | 6 | RRAC1 | 5.38 | 2018-05-28T06:24:00Z | 5.99 | 11 | AP525 | 2.99 | 2018-05-28T07:55:00Z | 0 | 12 | RRAC1 | 5.38 | 2018-05-28T07:24:00Z | 5.99 | 22
PG&E | 2018-06-04 | 9:25 | 35.4593 | -120.4921 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101895513 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43255 | 0.39236 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1624 | 2018 | 6 | 4 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 12.0315 | 222_99 | <25mph | <15mph | HFTD - Distribution | 2018-06-04 09:25:00 | 1366 | 20.4837 | FALSE | <25mph | TT469 | 2.65 | 2018-06-04T06:14:00Z | 5.99 | 1 | TT469 | 2.65 | 2018-06-04T06:14:00Z | 5.99 | 1 | TT469 | 2.65 | 2018-06-04T06:14:00Z | 5.99 | 2 | TT469 | 2.65 | 2018-06-04T06:14:00Z | 5.99 | 2
PG&E | 2018-06-05 | 10:13 | 40.6183 | -122.3173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JASON COLLINS 530-225-4628 | 101467801 | None | 12000 | Conductor | Overhead | Yes | 43256 | 0.42569 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1631 | 2018 | 6 | 5 | 10 | 13 | 18-0047539 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 277 | 7.1547 | 144_384 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 10:13:00 | 1373 | 12.6046 | FALSE | <25mph | C5599 | 1.27 | 2018-06-05T06:46:00Z | 4 | 8 | RRAC1 | 7.21 | 2018-06-05T06:24:00Z | 12.01 | 9 | C5599 | 1.27 | 2018-06-05T07:36:00Z | 8.01 | 20 | RRAC1 | 7.21 | 2018-06-05T07:24:00Z | 14 | 22
PG&E | 2018-06-05 | 13:45 | 38.5432 | -122.7202 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 102031673 | Unknown | 12000 | Conductor | Overhead | Yes | 43256 | 0.57292 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1633 | 2018 | 6 | 5 | 13 | 45 | 18-0047625 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 40599 | 7.3889 | 125_270 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 13:45:00 | 1375 | 15.9614 | FALSE | <25mph | E1553 | 2.52 | 2018-06-05T06:14:00Z | 12.01 | 24 | E1553 | 2.52 | 2018-06-05T06:14:00Z | 12.01 | 86 | E1553 | 2.52 | 2018-06-05T06:14:00Z | 12.01 | 45 | E1553 | 2.52 | 2018-06-05T06:14:00Z | 12.01 | 165
PG&E | 2018-06-05 | 16:46 | 38.7245 | -120.802 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 103667302 | AT&T | 12000 | Conductor | Overhead | Yes | 43256 | 0.69861 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1634 | 2018 | 6 | 5 | 16 | 46 | 18-0047702 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 40590 | 10.9676 | 208_279 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 16:46:00 | 1376 | 11.728 | FALSE | <25mph | C6129 | 3.23 | 2018-06-05T06:04:00Z | 2.01 | 30 | E3165 | 6.15 | 2018-06-05T07:00:00Z | 5.99 | 50 | C6129 | 3.23 | 2018-06-05T06:04:00Z | 2.01 | 60 | E3165 | 6.15 | 2018-06-05T07:00:00Z | 5.99 | 99
PG&E | 2018-06-08 | 19:03 | 35.154 | -120.594 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101852092 | AT&T | 12000 | Conductor | Overhead | Yes | 43259 | 0.79375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1644 | 2018 | 6 | 8 | 19 | 3 | 18-0049130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2473 | 24.0333 | 218_82 | <25mph | <15mph | HFTD - Distribution | 2018-06-08 19:03:00 | 1386 | 25.9327 | FALSE | 25-40mph | F0194 | 1.62 | 2018-06-08T06:41:00Z | 3 | 24 | E8214 | 6.18 | 2018-06-08T06:27:00Z | 4.99 | 32 | F0194 | 1.62 | 2018-06-08T06:41:00Z | 3 | 45 | E8214 | 6.18 | 2018-06-08T06:27:00Z | 4.99 | 61
PG&E | 2018-06-09 | 0:46 | 35.0745 | -120.5167 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101927520 | Unknown | 12000 | Conductor | Overhead | Yes | 43260 | 0.031944 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1645 | 2018 | 6 | 9 | 0 | 46 | 18-0049171 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 16825 | 5.84 | 221_78 | <25mph | <15mph | HFTD - Distribution | 2018-06-09 00:46:00 | 1387 | 22.9582 | FALSE | <25mph | F0412 | 2.71 | 2018-06-09T06:30:00Z | 3 | 16 | F0412 | 2.71 | 2018-06-09T06:30:00Z | 3 | 36 | F0412 | 2.71 | 2018-06-09T06:30:00Z | 3 | 33 | F0412 | 2.71 | 2018-06-09T06:30:00Z | 3 | 73
PG&E | 2018-06-10 | 17:19 | 38.4157 | -122.9184 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101978419 | AT&T | 12000 | Conductor | Overhead | Yes | 43261 | 0.72153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1647 | 2018 | 6 | 10 | 17 | 19 | 18-0049445 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2386 | 19.6716 | 117_263 | <25mph | <15mph | HFTD - Distribution | 2018-06-10 17:19:00 | 1389 | 23.7271 | FALSE | <25mph | GRWWW | 1.77 | 2018-06-10T06:00:00Z | 14.29 | 43 | DENWW | 6.15 | 2018-06-10T06:00:00Z | 16.4 | 106 | GRWWW | 1.77 | 2018-06-10T06:00:00Z | 14.29 | 87 | DENWW | 6.15 | 2018-06-10T06:00:00Z | 16.4 | 208
PG&E | 2018-06-11 | 17:49 | 34.7329 | -120.0861 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103015183 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43262 | 0.74236 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1649 | 2018 | 6 | 11 | 17 | 49 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 16.7571 | 241_59 | <25mph | <15mph | HFTD - Distribution | 2018-06-11 17:49:00 | 1391 | 18.839 | FALSE | <25mph | UCSE | 3.69 | 2018-06-11T06:50:00Z | 7.81 | 7 | FGMC1 | 4.52 | 2018-06-11T06:35:00Z | 20 | 9 | UCSE | 3.69 | 2018-06-11T07:30:00Z | 8.3 | 13 | FGMC1 | 4.52 | 2018-06-11T06:35:00Z | 20 | 17
PG&E | 2018-06-13 | 11:18 | 35.2927 | -120.429 | Vegetation | Rural | < 3 meters | Customer | N.A. | 101884565 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 0.47083 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1654 | 2018 | 6 | 13 | 11 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.9715 | 225_90 | <25mph | <15mph | HFTD - Distribution | 2018-06-13 11:18:00 | 1396 | 15.2535 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-06-13 | 22:40 | 38.4901 | -122.6661 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SRS181640125 | 101966547 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 0.94444 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1656 | 2018 | 6 | 13 | 22 | 40 | 18-0050782 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 295146 | 2.5247 | 128_267 | <25mph | <15mph | HFTD - Distribution | 2018-06-13 22:40:00 | 1398 | 17.8767 | FALSE | <25mph | E1582 | 2.84 | 2018-06-13T06:43:00Z | 3 | 15 | CRIWW | 6.91 | 2018-06-13T06:00:00Z | 3.8 | 69 | E1582 | 2.84 | 2018-06-13T06:43:00Z | 3 | 30 | CRIWW | 6.91 | 2018-06-13T06:00:00Z | 3.8 | 134
PG&E | 2018-06-14 | 16:12 | 40.4419 | -124.0197 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 101005522 | AT&T | 12000 | Conductor | Overhead | Yes | 43265 | 0.675 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1658 | 2018 | 6 | 14 | 16 | 12 | 18-0051223 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 19601 | 23.9895 | 73_376 | <25mph | <15mph | HFTD - Distribution | 2018-06-14 16:12:00 | 1400 | 23.9895 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-06-15 | 2:56 | 37.4869 | -122.4223 | Vegetation | Rural | < 0.25 Acres | Utility: PG&E | N.A. | Pole 10/5 | None | 60000 | Conductor | Overhead | Yes | 43266 | 0.12222 | Contamination | N.A. | N.A. | N.A. | Unknown |  | no-match | 1659 | 2018 | 6 | 15 | 2 | 56 | INT-11115 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 0 | 6.5721 | 137_211 | <25mph | <15mph | HFTD - Transmission | 2018-06-15 02:56:00 | 1401 | 18.0175 | FALSE | <25mph | C3295 | 3.73 | 2018-06-15T06:23:00Z | 3 | 1 | HSPC1 | 5.28 | 2018-06-15T06:18:00Z | 18.99 | 78 | C3295 | 3.73 | 2018-06-15T07:13:00Z | 8.99 | 4 | HSPC1 | 5.28 | 2018-06-15T07:18:00Z | 21 | 154
PG&E | 2018-06-15 | 9:51 | 37.1986 | -119.4709 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RANCHARIA ENGINE 4255 USFS ENG 52 | 101058060 | Unknown | 12000 | Conductor | Overhead | Yes | 43266 | 0.41042 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1660 | 2018 | 6 | 15 | 9 | 51 | 18-0051354 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 35146 | 7.0865 | 267_195 | <25mph | <15mph | HFTD - Distribution | 2018-06-15 09:51:00 | 1402 | 16.2916 | FALSE | <25mph | NFRC1 | 3.06 | 2018-06-15T06:55:00Z | 8.01 | 1 | NFRC1 | 3.06 | 2018-06-15T06:55:00Z | 8.01 | 1 | NFRC1 | 3.06 | 2018-06-15T06:55:00Z | 8.01 | 2 | NFRC1 | 3.06 | 2018-06-15T06:55:00Z | 8.01 | 2
PG&E | 2018-06-15 | 10:05 | 38.6238 | -121.0221 | Vegetation | Rural | < 3 meters | Customer | N.A. | 101376538 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43266 | 0.42014 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1661 | 2018 | 6 | 15 | 10 | 5 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 10.3423 | 199_273 | <25mph | <15mph | HFTD - Distribution | 2018-06-15 10:05:00 | 1403 | 17.1425 | FALSE | <25mph | E8856 | 3.9 | 2018-06-15T07:00:00Z | 0 | 13 | FSLC1 | 7.47 | 2018-06-15T06:25:00Z | 9.26 | 57 | E8856 | 3.9 | 2018-06-15T08:00:00Z | 0 | 25 | FSLC1 | 7.47 | 2018-06-15T07:25:00Z | 10.63 | 112
PG&E | 2018-06-16 | 19:58 | 37.907 | -121.8063 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100483910 | Unknown | 21000 | Conductor | Overhead | Yes | 43267 | 0.83194 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1670 | 2018 | 6 | 16 | 19 | 58 | 18-0051687 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 3322 | 40.9858 | 164_234 | 40-55mph | 30-45mph | HFTD - Distribution | 2018-06-16 19:58:00 | 1412 | 43.1884 | FALSE | 40-55mph | PG071 | 2.97 | 2018-06-16T06:00:00Z | 33.11 | 14 | PG071 | 2.97 | 2018-06-16T06:00:00Z | 33.11 | 106 | PG071 | 2.97 | 2018-06-16T06:00:00Z | 33.11 | 26 | PG071 | 2.97 | 2018-06-16T06:00:00Z | 33.11 | 219
PG&E | 2018-06-16 | 20:33 | 38.0494 | -122.206 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Contra Costa FD | 101423963 | Unknown | 21000 | Conductor | Overhead | Yes | 43267 | 0.85625 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 1671 | 2018 | 6 | 16 | 20 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 31.0273 | 147_242 | 25-40mph | 30-45mph | HFTD - Distribution | 2018-06-16 20:33:00 | 1413 | 35.6333 | FALSE | 25-40mph | DPXC1 | 2.96 | 2018-06-16T06:42:00Z | 20.98 | 15 | PG064 | 7.4 | 2018-06-16T06:10:00Z | 35.95 | 95 | DPXC1 | 2.96 | 2018-06-16T07:30:00Z | 20.98 | 28 | PG064 | 7.4 | 2018-06-16T06:10:00Z | 35.95 | 190
PG&E | 2018-06-19 | 0:27 | 38.7604 | -120.8224 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101388356 | Unknown | 12000 | Conductor | Overhead | Yes | 43270 | 0.01875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1675 | 2018 | 6 | 19 | 0 | 27 | 18-0052111 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 141652 | 7.2853 | 207_281 | <25mph | <15mph | HFTD - Distribution | 2018-06-19 00:27:00 | 1417 | 13.5304 | FALSE | <25mph | E5691 | 1.82 | 2018-06-19T06:59:00Z | 0 | 12 | TS903 | 6.68 | 2018-06-19T06:37:00Z | 2.01 | 75 | E5691 | 1.82 | 2018-06-19T07:59:00Z | 0 | 24 | E3165 | 5.03 | 2018-06-19T07:41:00Z | 2.01 | 147
PG&E | 2018-06-19 | 10:17 | 38.5918 | -120.7097 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101395943 | AT&T | 21000 | Conductor | Overhead | Yes | 43270 | 0.42847 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1677 | 2018 | 6 | 19 | 10 | 17 | 18-0052222 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 4094 | 8.0346 | 212_272 | <25mph | <15mph | HFTD - Distribution | 2018-06-19 10:17:00 | 1419 | 11.5468 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-06-19 | 14:41 | 37.2158 | -119.6811 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JOE QUINSTORFF 559-683-8008 | 103372829 | Unknown | 21000 | Conductor | Overhead | Yes | 43270 | 0.61181 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1679 | 2018 | 6 | 19 | 14 | 41 | 18-0052327 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 123838 | 9.7956 | 257_196 | <25mph | <15mph | HFTD - Distribution | 2018-06-19 14:41:00 | 1421 | 11.6304 | FALSE | <25mph |  |  |  | 0 | 0 | E5766 | 6.85 | 2018-06-19T06:58:00Z | 0 | 20 |  |  |  | 0 | 0 | E5766 | 6.85 | 2018-06-19T07:53:00Z | 0 | 33
PG&E | 2018-06-20 | 8:30 | 34.7561 | -120.2281 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101858890 | None | 0 – 750 | Conductor | Overhead | Yes | 43271 | 0.35417 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1680 | 2018 | 6 | 20 | 8 | 30 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 2.9211 | 235_60 | <25mph | <15mph | HFTD - Distribution | 2018-06-20 08:30:00 | 1422 | 17.5246 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-06-21 | 18:58 | 35.1224 | -120.3938 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101878933 | AT&T | 12000 | Conductor | Overhead | Yes | 43272 | 0.79028 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1683 | 2018 | 6 | 21 | 18 | 58 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 13.9909 | 227_80 | <25mph | <15mph | HFTD - Distribution | 2018-06-21 18:58:00 | 1425 | 15.3983 | FALSE | <25mph | AU609 | 1.36 | 2018-06-21T06:48:00Z | 0 | 4 | F0412 | 7.22 | 2018-06-21T07:00:00Z | 4 | 11 | AU609 | 1.36 | 2018-06-21T07:48:00Z | 0 | 8 | F0412 | 7.22 | 2018-06-21T08:00:00Z | 4 | 21
PG&E | 2018-06-22 | 17:44 | 37.2485 | -119.5625 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Madera County | 101117749 | None | 0 – 750 | Conductor | Overhead | Yes | 43273 | 0.73889 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1686 | 2018 | 6 | 22 | 17 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 10.123 | 263_198 | <25mph | <15mph | HFTD - Distribution | 2018-06-22 17:44:00 | 1428 | 12.3323 | FALSE | <25mph | NFRC1 | 3.29 | 2018-06-22T06:55:00Z | 8.01 | 1 | NFRC1 | 3.29 | 2018-06-22T06:55:00Z | 8.01 | 42 | NFRC1 | 3.29 | 2018-06-22T07:55:00Z | 8.01 | 2 | NFRC1 | 3.29 | 2018-06-22T07:55:00Z | 8.01 | 84
PG&E | 2018-06-23 | 9:31 | 40.8632 | -122.3962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | RYAN MEANS 530-238-2416 | 101472252 | AT&T | 12000 | Conductor | Overhead | Yes | 43274 | 0.39653 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1688 | 2018 | 6 | 23 | 9 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2018-06-23 09:31:00 | NA | 0 | FALSE | <25mph | CTANT | 1.62 | 2018-06-23T06:15:00Z | 9.93 | 4 | SLFC1 | 4.17 | 2018-06-23T06:19:00Z | 21 | 9 | CTANT | 1.62 | 2018-06-23T06:15:00Z | 9.93 | 7 | SLFC1 | 4.17 | 2018-06-23T06:19:00Z | 21 | 17
PG&E | 2018-06-27 | 18:46 | 40.218 | -123.7989 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TJ alderpoint fire | 100990381 | Unknown | 12000 | Conductor | Overhead | Yes | 43278 | 0.78194 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1700 | 2018 | 6 | 27 | 18 | 46 | 18-0055205 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 21357 | 17.7599 | 81_363 | <25mph | <15mph | HFTD - Distribution | 2018-06-27 18:46:00 | 1441 | 20.5507 | FALSE | <25mph |  |  |  | 0 | 0 | ERCC1 | 5.65 | 2018-06-27T06:28:00Z | 8.99 | 1 |  |  |  | 0 | 0 | ERCC1 | 5.65 | 2018-06-27T06:28:00Z | 8.99 | 2
PG&E | 2018-06-27 | 21:19 | 39.8714 | -123.7119 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 103775148 | Verizon | 12000 | Conductor | Overhead | Yes | 43278 | 0.88819 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1701 | 2018 | 6 | 27 | 21 | 19 | 18-0055211 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 75544 | 26.3038 | 85_344 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-06-27 21:19:00 | 1442 | 27.3779 | FALSE | 25-40mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-06-28 | 12:27 | 38.5982 | -121.0081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | John Reis, 530-622-3858 | 101376954 | Unknown | 21000 | Conductor | Overhead | Yes | 43279 | 0.51875 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1702 | 2018 | 6 | 28 | 12 | 27 | 18-0055479 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 24671 | 12.7651 | 199_272 | <25mph | <15mph | HFTD - Distribution | 2018-06-28 12:27:00 | 1443 | 13.4512 | FALSE | <25mph | E8856 | 2.62 | 2018-06-28T07:00:00Z | 7 | 13 | BENC1 | 4.05 | 2018-06-28T06:59:00Z | 8.01 | 28 | E8856 | 2.62 | 2018-06-28T07:15:00Z | 7 | 25 | BENC1 | 4.05 | 2018-06-28T06:59:00Z | 8.01 | 55
PG&E | 2018-06-28 | 19:41 | 38.5575 | -122.5043 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Brian Coffee | 102267918 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43279 | 0.82014 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1704 | 2018 | 6 | 28 | 19 | 41 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 14.506 | 135_270 | <25mph | <15mph | HFTD - Distribution | 2018-06-28 19:41:00 | 1445 | 15.2819 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-06-30 | 11:14 | 39.3621 | -121.0809 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ENGINEER YUREK | 100091354 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 0.46806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1713 | 2018 | 6 | 30 | 11 | 14 | 18-0055945 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5724 | 3.7745 | 196_314 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 11:14:00 | 1454 | 12.1468 | FALSE | <25mph | E3651 | 2.44 | 2018-06-30T06:30:00Z | 2.01 | 13 | RRRC1 | 4.49 | 2018-06-30T06:13:00Z | 7 | 28 | E3651 | 2.44 | 2018-06-30T07:50:00Z | 3 | 25 | PG030 | 6.5 | 2018-06-30T08:00:00Z | 10.51 | 54
PG&E | 2018-06-30 | 22:18 | 40.6043 | -122.24 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101469808 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43281 | 0.92917 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1716 | 2018 | 6 | 30 | 22 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 10.6263 | 147_383 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 22:18:00 | 1457 | 24.79 | FALSE | <25mph |  |  |  | 0 | 0 | C5599 | 4.85 | 2018-06-30T06:17:00Z | 12.01 | 10 |  |  |  | 0 | 0 | C5599 | 4.85 | 2018-06-30T06:17:00Z | 12.01 | 23
PG&E | 2018-06-30 | 22:36 | 39.1141 | -121.077 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Matt Wallen (530) 277-3312 Incident # NEU015486 | 100105380 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 0.94167 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1717 | 2018 | 6 | 30 | 22 | 36 | 18-0056039 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 8004 | 7.8488 | 196_300 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 22:36:00 | 1458 | 15.8656 | FALSE | <25mph | E1789 | 3.68 | 2018-06-30T06:30:00Z | 4 | 21 | E1789 | 3.68 | 2018-06-30T06:30:00Z | 4 | 64 | E1789 | 3.68 | 2018-06-30T07:48:00Z | 4 | 41 | AT999 | 5.18 | 2018-06-30T07:57:00Z | 8.99 | 121
PG&E | 2018-07-01 | 0:23 | 40.2697 | -124.2386 | Vegetation | Rural | < 3 meters | Fire Agency | fire chief | 100986962 | Unknown | 12000 | Conductor | Overhead | Yes | 43282 | 0.015972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1718 | 2018 | 7 | 1 | 0 | 23 | 18-0056043 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 22872 | 20.9894 | 63_366 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 00:23:00 | 1459 | 27.5371 | FALSE | 25-40mph | PTEC1 | 1.7 | 2018-07-01T06:08:00Z | 44.98 | 1 | PTEC1 | 1.7 | 2018-07-01T06:08:00Z | 44.98 | 1 | PTEC1 | 1.7 | 2018-07-01T06:08:00Z | 44.98 | 2 | PTEC1 | 1.7 | 2018-07-01T06:08:00Z | 44.98 | 2
PG&E | 2018-07-01 | 0:45 | 38.8842 | -120.847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Brian Mackwood (530)708-2711 | 100109003 | None | 21000 | Conductor | Overhead | Yes | 43282 | 0.03125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1719 | 2018 | 7 | 1 | 0 | 45 | 18-0056045 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5760 | 9.2878 | 206_288 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 00:45:00 | 1460 | 12.1055 | FALSE | <25mph | PG033 | 2.7 | 2018-07-01T07:00:00Z | 3.29 | 33 | BDMC1 | 7.75 | 2018-07-01T06:36:00Z | 10 | 41 | PG033 | 2.7 | 2018-07-01T07:00:00Z | 3.29 | 63 | BDMC1 | 7.75 | 2018-07-01T07:36:00Z | 21 | 79
PG&E | 2018-07-01 | 8:13 | 39.4154 | -121.5122 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430344 | AT&T | 12000 | Conductor | Overhead | Yes | 43282 | 0.34236 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1720 | 2018 | 7 | 1 | 8 | 13 | 18-0056061 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 7848 | 6.5616 | 178_317 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 08:13:00 | 1461 | 14.6967 | FALSE | <25mph |  |  |  | 0 | 0 | TT309 | 6.67 | 2018-07-01T06:45:00Z | 5.99 | 2 |  |  |  | 0 | 0 | TT309 | 6.67 | 2018-07-01T06:45:00Z | 5.99 | 4
PG&E | 2018-07-02 | 5:12 | 38.6092 | -122.4595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 707-967-1467 | 102252558 | AT&T | 21000 | Conductor | Overhead | Yes | 43283 | 0.21667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1722 | 2018 | 7 | 2 | 5 | 12 | 18-0056178 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 403 | 6.1424 | 137_273 | <25mph | <15mph | HFTD - Distribution | 2018-07-02 05:12:00 | 1463 | 24.2981 | FALSE | <25mph |  |  |  | 0 | 0 | PG045 | 7.68 | 2018-07-02T06:30:00Z | 5.48 | 11 |  |  |  | 0 | 0 | PG045 | 7.68 | 2018-07-02T07:50:00Z | 10.09 | 21
PG&E | 2018-07-04 | 15:26 | 39.5538 | -123.4255 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102196183 | Verizon | 12000 | Conductor | Overhead | Yes | 43285 | 0.64306 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1726 | 2018 | 7 | 4 | 15 | 26 | 18-0056986 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 32269 | 12.5826 | 96_326 | <25mph | <15mph | HFTD - Distribution | 2018-07-04 15:26:00 | 1466 | 12.5826 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-07-09 | 7:27 | 35.0785 | -120.3948 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101861366 | Unknown | 12000 | Conductor | Overhead | Yes | 43290 | 0.31042 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1735 | 2018 | 7 | 9 | 7 | 27 | 18-0057904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 21045 | 9.782 | 227_78 | <25mph | <15mph | HFTD - Distribution | 2018-07-09 07:27:00 | 1475 | 17.5911 | FALSE | <25mph | AU609 | 1.69 | 2018-07-09T06:48:00Z | 0 | 4 | AU609 | 1.69 | 2018-07-09T06:48:00Z | 0 | 4 | AU609 | 1.69 | 2018-07-09T07:48:00Z | 0 | 8 | F0412 | 5.4 | 2018-07-09T07:55:00Z | 1.01 | 10
PG&E | 2018-07-10 | 6:45 | 37.085 | -122.0744 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 101675262 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43291 | 0.28125 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1737 | 2018 | 7 | 10 | 6 | 45 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 10.4729 | 152_189 | <25mph | <15mph | HFTD - Distribution | 2018-07-10 06:45:00 | 1477 | 23.379 | FALSE | <25mph | E1576 | 2.63 | 2018-07-10T06:58:00Z | 4 | 39 | BNDC1 | 6.27 | 2018-07-10T06:50:00Z | 15.99 | 103 | E1576 | 2.63 | 2018-07-10T07:03:00Z | 4 | 81 | BNDC1 | 6.27 | 2018-07-10T07:50:00Z | 15.99 | 198
PG&E | 2018-07-13 | 10:59 | 39.4836 | -123.7924 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102184869 | AT&T | 12000 | Conductor | Overhead | Yes | 43294 | 0.45764 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1742 | 2018 | 7 | 13 | 10 | 59 | 18-0059522 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 328 | 4.0862 | 81_323 | <25mph | <15mph | HFTD - Distribution | 2018-07-13 10:59:00 | 1482 | 8.6522 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-07-14 | 11:34 | 38.4026 | -122.5489 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103141862 | Verizon | 12000 | Conductor | Overhead | Yes | 43295 | 0.48194 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1745 | 2018 | 7 | 14 | 11 | 34 | 18-0059821 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 6426 | 11.4725 | 133_262 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 11:34:00 | 1485 | 15.7933 | FALSE | <25mph | KENWW | 0.52 | 2018-07-14T06:00:00Z | 9.19 | 2 | BVYWW | 5.16 | 2018-07-14T06:00:00Z | 11.79 | 16 | KENWW | 0.52 | 2018-07-14T06:00:00Z | 9.19 | 3 | BVYWW | 5.16 | 2018-07-14T06:00:00Z | 11.79 | 29
PG&E | 2018-07-14 | 12:40 | 38.5793 | -122.878 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103122744 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 0.52778 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1746 | 2018 | 7 | 14 | 12 | 40 | 18-0059799 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20804 | 12.0574 | 118_272 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 12:40:00 | 1486 | 14.4502 | FALSE | <25mph | R08WW | 2.26 | 2018-07-14T06:00:00Z | 8.59 | 11 | DRYWW | 5.04 | 2018-07-14T06:00:00Z | 10.69 | 57 | R08WW | 2.26 | 2018-07-14T06:00:00Z | 8.59 | 20 | DRYWW | 5.04 | 2018-07-14T06:00:00Z | 10.69 | 103
PG&E | 2018-07-14 | 12:56 | 39.2093 | -121.197 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE DEPT LEFT BEFORE UPTAINING THAT INFO | 100086833 | None | 21000 | Conductor | Overhead | Yes | 43295 | 0.53889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1747 | 2018 | 7 | 14 | 12 | 56 | 18-0059841 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 3720 | 10.2359 | 191_306 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 12:56:00 | 1487 | 12.6903 | FALSE | <25mph |  |  |  | 0 | 0 | RRRC1 | 7.78 | 2018-07-14T06:13:00Z | 4.99 | 35 |  |  |  | 0 | 0 | RRRC1 | 7.78 | 2018-07-14T07:13:00Z | 5.99 | 70
PG&E | 2018-07-14 | 14:44 | 38.9524 | -121.2467 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100035452 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 0.61389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1748 | 2018 | 7 | 14 | 14 | 44 | 18-0059847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2430 | 9.5304 | 189_291 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 14:44:00 | 1488 | 13.6375 | FALSE | <25mph |  |  |  | 0 | 0 | LICC1 | 5.05 | 2018-07-14T06:13:00Z | 4 | 6 |  |  |  | 0 | 0 | E6168 | 5.24 | 2018-07-14T07:13:00Z | 4 | 11
PG&E | 2018-07-14 | 21:38 | 36.3314 | -121.8829 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | ASSISTED JAIMIE | 101672234 | Unknown | 12000 | Conductor | Overhead | Yes | 43295 | 0.90139 | Contact From Object | N.A. | Animal | Pole | Other | bull rubbing pole | Other/Unknown | 1751 | 2018 | 7 | 14 | 21 | 38 | 18-0059900 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 493416 | 26.289 | 160_147 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-07-14 21:38:00 | 1491 | 27.1871 | FALSE | 25-40mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-07-17 | 11:11 | 35.6986 | -120.9777 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | dennis byrnes 8055434244 inc # = 18ca-slu-007640 | 103886652 | Unknown | 21000 | Conductor | Overhead | Yes | 43298 | 0.46597 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1755 | 2018 | 7 | 17 | 11 | 11 | 18-0060637 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 9121 | 4.768 | 201_112 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 11:11:00 | 1495 | 12.6145 | FALSE | <25mph | E9175 | 3.58 | 2018-07-17T06:15:00Z | 4.99 | 12 | D4060 | 6.73 | 2018-07-17T06:25:00Z | 8.01 | 17 | E9175 | 3.58 | 2018-07-17T07:25:00Z | 5.99 | 24 | D4060 | 6.73 | 2018-07-17T07:10:00Z | 8.99 | 34
PG&E | 2018-07-17 | 11:58 | 37.2217 | -121.6778 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Luis Morado state arson fire fighter | 100601345 | Unknown | 12000 | Conductor | Overhead | Yes | 43298 | 0.49861 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1756 | 2018 | 7 | 17 | 11 | 58 | 18-0060617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 5865 | 5.1834 | 170_196 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 11:58:00 | 1496 | 14.408 | FALSE | <25mph |  |  |  | 0 | 0 | C7794 | 7.07 | 2018-07-17T06:00:00Z | 1.01 | 23 |  |  |  | 0 | 0 | C7794 | 7.07 | 2018-07-17T06:00:00Z | 1.01 | 45
PG&E | 2018-07-17 | 16:53 | 38.3955 | -122.9212 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101978449 | AT&T | 12000 | Conductor | Overhead | Yes | 43298 | 0.70347 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1759 | 2018 | 7 | 17 | 16 | 53 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 13.5832 | 116_262 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 16:53:00 | 1499 | 13.5832 | FALSE | <25mph | DUTWW | 3.53 | 2018-07-17T07:00:00Z | 9.19 | 36 | DUTWW | 3.53 | 2018-07-17T07:00:00Z | 9.19 | 80 | DUTWW | 3.53 | 2018-07-17T08:00:00Z | 10.69 | 68 | DUTWW | 3.53 | 2018-07-17T08:00:00Z | 10.69 | 154
PG&E | 2018-07-17 | 19:40 | 40.5927 | -122.4886 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101477082 | AT&T | 12000 | Conductor | Overhead | Yes | 43298 | 0.81944 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1760 | 2018 | 7 | 17 | 19 | 40 | 18-0060840 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 30162 | 14.3022 | 137_382 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 19:40:00 | 1500 | 21.6282 | FALSE | <25mph | MMOC1 | 1.8 | 2018-07-17T07:00:00Z | 10 | 7 | MMOC1 | 1.8 | 2018-07-17T07:00:00Z | 10 | 13 | MMOC1 | 1.8 | 2018-07-17T07:00:00Z | 10 | 12 | MMOC1 | 1.8 | 2018-07-17T07:00:00Z | 10 | 23
PG&E | 2018-07-18 | 1:14 | 38.3671 | -120.5578 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101247987 | Unknown | 12000 | Conductor | Overhead | Yes | 43299 | 0.051389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1761 | 2018 | 7 | 18 | 1 | 14 | 18-0060882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6420 | 6.6576 | 219_259 | <25mph | <15mph | HFTD - Distribution | 2018-07-18 01:14:00 | 1501 | 11.9385 | FALSE | <25mph |  |  |  | 0 | 0 | ESPC1 | 6.8 | 2018-07-18T06:13:00Z | 8.01 | 14 |  |  |  | 0 | 0 | ESPC1 | 6.8 | 2018-07-18T06:13:00Z | 8.01 | 28
PG&E | 2018-07-19 | 0:08 | 36.9372 | -119.4557 | Vegetation | Rural | < 0.25 Acres | Fire Agency | incident # 10559 | 100677019 | AT&T | 12000 | Conductor | Overhead | Yes | 43300 | 0.0055556 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1766 | 2018 | 7 | 19 | 0 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 10.281 | 268_181 | <25mph | <15mph | HFTD - Distribution | 2018-07-19 00:08:00 | 1506 | 18.2382 | FALSE | <25mph | FCHC1 | 3.86 | 2018-07-19T07:00:00Z | 5.99 | 2 | FCHC1 | 3.86 | 2018-07-19T07:00:00Z | 5.99 | 2 | FCHC1 | 3.86 | 2018-07-19T07:00:00Z | 5.99 | 3 | FCHC1 | 3.86 | 2018-07-19T07:00:00Z | 5.99 | 3
PG&E | 2018-07-19 | 5:29 | 40.1918 | -123.5373 | Vegetation | Rural | < 0.25 Acres | Fire Agency | fire captain | 103909820 | Unknown | 12000 | Conductor | Overhead | Yes | 43300 | 0.22847 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1767 | 2018 | 7 | 19 | 5 | 29 | 18-0061308 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 73380 | 5.6109 | 92_361 | <25mph | <15mph | HFTD - Distribution | 2018-07-19 05:29:00 | 1507 | 13.8917 | FALSE | <25mph | ALDC1 | 2.86 | 2018-07-19T06:51:00Z | 4 | 1 | ALDC1 | 2.86 | 2018-07-19T06:51:00Z | 4 | 1 | ALDC1 | 2.86 | 2018-07-19T07:51:00Z | 4 | 2 | ALDC1 | 2.86 | 2018-07-19T07:51:00Z | 4 | 2
PG&E | 2018-07-20 | 6:31 | 37.4318 | -119.9441 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ZACH RUTHERFORD 209-966-3621 | 103909942 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43301 | 0.27153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1771 | 2018 | 7 | 20 | 6 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2004 | 246_208 | <25mph | <15mph | HFTD - Distribution | 2018-07-20 06:31:00 | 1511 | 13.5994 | FALSE | <25mph |  |  |  | 0 | 0 | E9110 | 6.48 | 2018-07-20T06:47:00Z | 5.99 | 9 |  |  |  | 0 | 0 | E9110 | 6.48 | 2018-07-20T07:02:00Z | 5.99 | 18
PG&E | 2018-07-21 | 0:23 | 38.6927 | -120.7921 | Vegetation | Rural | < 3 meters | Fire Agency | CAMINO | 101415904 | AT&T | 12000 | Conductor | Overhead | Yes | 43302 | 0.015972 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1774 | 2018 | 7 | 21 | 0 | 23 | 18-0062206 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 107552 | 9.7365 | 208_277 | <25mph | <15mph | HFTD - Distribution | 2018-07-21 00:23:00 | 1514 | 11.1911 | FALSE | <25mph | C6129 | 3.07 | 2018-07-21T06:24:00Z | 2.01 | 30 | C6129 | 3.07 | 2018-07-21T06:24:00Z | 2.01 | 60 | C6129 | 3.07 | 2018-07-21T06:24:00Z | 2.01 | 60 | E3165 | 7.94 | 2018-07-21T07:58:00Z | 3 | 120
PG&E | 2018-07-21 | 14:51 | 35.6846 | -120.9427 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101943190 | Unknown | 21000 | Conductor | Overhead | Yes | 43302 | 0.61875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1775 | 2018 | 7 | 21 | 14 | 51 | 18-0062364 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 110814 | 14.9597 | 202_111 | <25mph | <15mph | HFTD - Distribution | 2018-07-21 14:51:00 | 1515 | 21.9627 | FALSE | <25mph | TABC1 | 2.21 | 2018-07-21T06:07:00Z | 3 | 1 | E9175 | 5.16 | 2018-07-21T06:50:00Z | 4 | 18 | TABC1 | 2.21 | 2018-07-21T06:07:00Z | 3 | 2 | E9175 | 5.16 | 2018-07-21T06:50:00Z | 4 | 35
PG&E | 2018-07-21 | 16:16 | 40.3439 | -123.7092 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 101009789 | Unknown | 12000 | Conductor | Overhead | Yes | 43302 | 0.67778 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1776 | 2018 | 7 | 21 | 16 | 16 | 18-0062375 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 5184 | 13.8965 | 85_370 | <25mph | <15mph | HFTD - Distribution | 2018-07-21 16:16:00 | 1516 | 13.8965 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-07-23 | 15:11 | 39.4911 | -123.7844 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102184598 | Yes | 12000 | Conductor | Overhead | Yes | 43304 | 0.63264 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1781 | 2018 | 7 | 23 | 15 | 11 | 18-0062842 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 44840 | 8.1345 | 81_323 | <25mph | <15mph | HFTD - Distribution | 2018-07-23 15:11:00 | 1521 | 8.9406 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-07-23 | 17:27 | 39.734 | -121.4965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103843963 | AT&T | 12000 | Conductor | Overhead | Yes | 43304 | 0.72708 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1782 | 2018 | 7 | 23 | 17 | 27 | 18-0062874 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 183629 | 9.1915 | 178_335 | <25mph | <15mph | HFTD - Distribution | 2018-07-23 17:27:00 | 1522 | 13.4352 | FALSE | <25mph | JBGC1 | 0.42 | 2018-07-23T06:13:00Z | 5.99 | 1 | JBGC1 | 0.42 | 2018-07-23T06:13:00Z | 5.99 | 3 | JBGC1 | 0.42 | 2018-07-23T07:13:00Z | 11.01 | 2 | JBGC1 | 0.42 | 2018-07-23T07:13:00Z | 11.01 | 5
PG&E | 2018-07-24 | 13:47 | 39.0606 | -123.4456 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102212216 | Unknown | 12000 | Conductor | Overhead | Yes | 43305 | 0.57431 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1786 | 2018 | 7 | 24 | 13 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 16.5971 | 95_299 | <25mph | <15mph | HFTD - Distribution | 2018-07-24 13:47:00 | 1526 | 19.7448 | FALSE | <25mph | E1763 | 3.79 | 2018-07-24T06:13:00Z | 1.01 | 4 | BNVC1 | 7.27 | 2018-07-24T06:50:00Z | 4 | 8 | E1763 | 3.79 | 2018-07-24T06:13:00Z | 1.01 | 8 | BNVC1 | 7.27 | 2018-07-24T06:50:00Z | 4 | 17
PG&E | 2018-07-25 | 0:42 | 39.7791 | -121.6173 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100327443 | Unknown | 12000 | Conductor | Overhead | Yes | 43306 | 0.029167 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1788 | 2018 | 7 | 25 | 0 | 42 | 18-0063320 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6742 | 1.3279 | 173_337 | <25mph | <15mph | HFTD - Distribution | 2018-07-25 00:42:00 | 1528 | 11.7229 | FALSE | <25mph | PDEC1 | 1.8 | 2018-07-25T07:00:00Z | 1.01 | 2 | JBGC1 | 7.44 | 2018-07-25T06:13:00Z | 10 | 21 | PDEC1 | 1.8 | 2018-07-25T08:00:00Z | 1.01 | 3 | JBGC1 | 7.44 | 2018-07-25T07:13:00Z | 10 | 37
PG&E | 2018-07-27 | 23:12 | 37.18 | -122.029 | Vegetation | Rural | < 3 meters | Fire Agency | Jeremy Wise 408-378-4010 Incident # C182080066 | 100518365 | Unknown | 12000 | Conductor | Overhead | Yes | 43308 | 0.96667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1793 | 2018 | 7 | 27 | 23 | 12 | 18-0064525 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 30475 | 3.2895 | 154_194 | <25mph | <15mph | HFTD - Distribution | 2018-07-27 23:12:00 | 1533 | 9.1823 | FALSE | <25mph | PG050 | 2.33 | 2018-07-27T06:10:00Z | 12.93 | 11 | PG050 | 2.33 | 2018-07-27T06:10:00Z | 12.93 | 125 | PG050 | 2.33 | 2018-07-27T06:10:00Z | 12.93 | 21 | PG050 | 2.33 | 2018-07-27T06:10:00Z | 12.93 | 240
PG&E | 2018-07-28 | 6:51 | 38.7473 | -120.7866 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101418155 | AT&T | 21000 | Conductor | Overhead | Yes | 43309 | 0.28542 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1794 | 2018 | 7 | 28 | 6 | 51 | 18-0064545 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 15429 | 14.6813 | 209_280 | <25mph | <15mph | HFTD - Distribution | 2018-07-28 06:51:00 | 1534 | 14.6813 | FALSE | <25mph | E5691 | 0.5 | 2018-07-28T06:01:00Z | 2.01 | 16 | E3165 | 4.37 | 2018-07-28T06:55:00Z | 4.99 | 54 | E5691 | 0.5 | 2018-07-28T06:01:00Z | 2.01 | 25 | E3165 | 4.37 | 2018-07-28T07:35:00Z | 8.01 | 97
PG&E | 2018-07-29 | 11:39 | 39.0968 | -123.5018 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102177329 | Unknown | 12000 | Conductor | Overhead | Yes | 43310 | 0.48542 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1796 | 2018 | 7 | 29 | 11 | 39 | 18-0064779 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4329 | 14.6452 | 92_301 | <25mph | <15mph | HFTD - Distribution | 2018-07-29 11:39:00 | 1536 | 18.4465 | FALSE | <25mph | E1763 | 2 | 2018-07-29T06:59:00Z | 0 | 2 | E1763 | 2 | 2018-07-29T06:59:00Z | 0 | 2 | E1763 | 2 | 2018-07-29T07:29:00Z | 2.01 | 6 | E1763 | 2 | 2018-07-29T07:29:00Z | 2.01 | 6
PG&E | 2018-07-29 | 17:29 | 38.5777 | -120.8556 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101383255 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43310 | 0.72847 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1797 | 2018 | 7 | 29 | 17 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.882 | 206_271 | <25mph | <15mph | HFTD - Distribution | 2018-07-29 17:29:00 | 1537 | 11.0812 | FALSE | <25mph |  |  |  | 0 | 0 | BENC1 | 4.31 | 2018-07-29T06:59:00Z | 4.99 | 30 |  |  |  | 0 | 0 | BENC1 | 4.31 | 2018-07-29T07:59:00Z | 4.99 | 58
PG&E | 2018-07-30 | 14:36 | 38.1987 | -120.3638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NICK WEBB ( 209) 532-7424 | 103336176 | Unknown | 17000 | Conductor | Overhead | Yes | 43311 | 0.60833 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1800 | 2018 | 7 | 30 | 14 | 36 | 18-0065131 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18530 | 10.5817 | 227_250 | <25mph | <15mph | HFTD - Distribution | 2018-07-30 14:36:00 | 1540 | 14.4256 | FALSE | <25mph | E8204 | 0 | 2018-07-30T06:48:00Z | 0 | 4 | E9838 | 7.59 | 2018-07-30T06:39:00Z | 4.99 | 20 | E8204 | 0 | 2018-07-30T07:48:00Z | 0 | 7 | E9838 | 7.59 | 2018-07-30T06:39:00Z | 4.99 | 37
PG&E | 2018-07-31 | 7:57 | 38.9559 | -122.7274 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102162351 | AT&T | 12000 | Conductor | Overhead | Yes | 43312 | 0.33125 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1803 | 2018 | 7 | 31 | 7 | 57 | 18-0065276 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 89832 | 7.6131 | 125_292 | <25mph | <15mph | HFTD - Distribution | 2018-07-31 07:57:00 | 1543 | 16.0718 | FALSE | <25mph | KELC1 | 3.24 | 2018-07-31T06:57:00Z | 17 | 1 | KELC1 | 3.24 | 2018-07-31T06:57:00Z | 17 | 1 | KELC1 | 3.24 | 2018-07-31T07:57:00Z | 18.99 | 2 | KELC1 | 3.24 | 2018-07-31T07:57:00Z | 18.99 | 2
PG&E | 2018-08-01 | 17:58 | 38.9155 | -122.799 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102156435 | Unknown | 12000 | Conductor | Overhead | Yes | 43313 | 0.74861 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1805 | 2018 | 8 | 1 | 17 | 58 | 18-0065921 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2744 | 14.8702 | 122_290 | <25mph | <15mph | HFTD - Distribution | 2018-08-01 17:58:00 | 1545 | 14.8702 | FALSE | <25mph | E4393 | 3.97 | 2018-08-01T06:15:00Z | 7 | 4 | KELC1 | 4.99 | 2018-08-01T06:57:00Z | 14.99 | 5 | E4393 | 3.97 | 2018-08-01T06:15:00Z | 7 | 8 | KELC1 | 4.99 | 2018-08-01T06:57:00Z | 14.99 | 10
PG&E | 2018-08-03 | 9:45 | 40.4988 | -121.8381 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | ZEIGGLER | 101492431 | Frontier | 12000 | Conductor | Overhead | Yes | 43315 | 0.40625 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1812 | 2018 | 8 | 3 | 9 | 45 | 18-0066484 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 4625 | 8.352 | 164_377 | <25mph | <15mph | HFTD - Distribution | 2018-08-03 09:45:00 | 1552 | 11.95 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-08-04 | 7:22 | 37.9756 | -122.5537 | Building | Urban | Structure Only | Fire Agency | ROSS VALLEY | 102241252 | AT&T | 12000 | Conductor | Overhead | Yes | 43316 | 0.30694 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1817 | 2018 | 8 | 4 | 7 | 22 | 18-0066666 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 6260 | 2.9768 | 132_238 | <25mph | <15mph | HFTD - Distribution | 2018-08-04 07:22:00 | 1557 | 19.5194 | FALSE | <25mph | MDEC1 | 3.77 | 2018-08-04T06:36:00Z | 28.99 | 18 | MDEC1 | 3.77 | 2018-08-04T06:36:00Z | 28.99 | 52 | MDEC1 | 3.77 | 2018-08-04T07:36:00Z | 28.99 | 35 | E9939 | 4.61 | 2018-08-04T07:44:00Z | 30 | 99
PG&E | 2018-08-05 | 13:56 | 37.4005 | -119.7532 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | JIM FORGA 209-966-3621 | 101017235 | Unknown | 12000 | Conductor | Overhead | Yes | 43317 | 0.58056 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1821 | 2018 | 8 | 5 | 13 | 56 | 18-0066905 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 7325 | 10.7759 | 254_206 | <25mph | <15mph | HFTD - Distribution | 2018-08-05 13:56:00 | 1561 | 13.3386 | FALSE | <25mph | MIAC1 | 1.36 | 2018-08-05T06:59:00Z | 10 | 2 | MIAC1 | 1.36 | 2018-08-05T06:59:00Z | 10 | 28 | MIAC1 | 1.36 | 2018-08-05T06:59:00Z | 10 | 4 | MIAC1 | 1.36 | 2018-08-05T06:59:00Z | 10 | 56
PG&E | 2018-08-07 | 9:47 | 38.6556 | -121.0226 | Vegetation | Urban | < 3 meters | Fire Agency | CAL FIRE | 103902317 | AT&T | 21000 | Conductor | Overhead | Yes | 43319 | 0.40764 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1823 | 2018 | 8 | 7 | 9 | 47 | 18-0067412 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 243 | 4.1909 | 198_275 | <25mph | <15mph | HFTD - Distribution | 2018-08-07 09:47:00 | 1563 | 13.5277 | FALSE | <25mph | E4740 | 2.54 | 2018-08-07T07:00:00Z | 1.01 | 20 | BENC1 | 6.56 | 2018-08-07T06:59:00Z | 8.01 | 87 | E4740 | 2.54 | 2018-08-07T08:00:00Z | 3 | 40 | PG073 | 4.79 | 2018-08-07T07:50:00Z | 8.99 | 174
PG&E | 2018-08-07 | 10:19 | 38.1052 | -120.4978 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101282323 | Unknown | 17000 | Lightning Arrestor | Overhead | Yes | 43319 | 0.42986 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1824 | 2018 | 8 | 7 | 10 | 19 | 18-0067659 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 388 | 9.4814 | 221_245 | <25mph | <15mph | HFTD - Distribution | 2018-08-07 10:19:00 | 1564 | 15.9014 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-08-07 | 15:46 | 40.4465 | -122.446 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464611 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43319 | 0.65694 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1826 | 2018 | 8 | 7 | 15 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 7.2812 | 139_374 | <25mph | <15mph | HFTD - Distribution | 2018-08-07 15:46:00 | 1566 | 14.3471 | FALSE | <25mph | E6886 | 2.81 | 2018-08-07T06:31:00Z | 2.01 | 4 | E6886 | 2.81 | 2018-08-07T06:31:00Z | 2.01 | 4 | E6886 | 2.81 | 2018-08-07T07:16:00Z | 2.01 | 8 | E6886 | 2.81 | 2018-08-07T07:16:00Z | 2.01 | 8
PG&E | 2018-08-07 | 17:15 | 37.1181 | -122.1093 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101670606 | AT&T | 12000 | Conductor | Overhead | Yes | 43319 | 0.71875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1827 | 2018 | 8 | 7 | 17 | 15 | 18-0067641 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1988 | 17.3453 | 151_191 | <25mph | <15mph | HFTD - Distribution | 2018-08-07 17:15:00 | 1567 | 17.3453 | FALSE | <25mph | BNDC1 | 3.6 | 2018-08-07T06:50:00Z | 18.01 | 34 | BNDC1 | 3.6 | 2018-08-07T06:50:00Z | 18.01 | 67 | BNDC1 | 3.6 | 2018-08-07T07:50:00Z | 20 | 65 | BNDC1 | 3.6 | 2018-08-07T07:50:00Z | 20 | 124
PG&E | 2018-08-07 | 21:03 | 38.2129 | -120.9184 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102042811 | Unknown | 12000 | Conductor | Overhead | Yes | 43319 | 0.87708 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1828 | 2018 | 8 | 7 | 21 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2018-08-07 21:03:00 | NA | 0 | FALSE | <25mph | CMAC1 | 2.92 | 2018-08-07T06:59:00Z | 3 | 1 | CMAC1 | 2.92 | 2018-08-07T06:59:00Z | 3 | 1 | CMAC1 | 2.92 | 2018-08-07T07:59:00Z | 3 | 2 | CMAC1 | 2.92 | 2018-08-07T07:59:00Z | 3 | 2
PG&E | 2018-08-08 | 10:03 | 40.7933 | -124.0242 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CHIEF | 100983089 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 0.41875 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1829 | 2018 | 8 | 8 | 10 | 3 | 18-0067921 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 27379 | 3.1403 | 73_395 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 10:03:00 | 1568 | 7.3376 | FALSE | <25mph |  |  |  | 0 | 0 | KNNC1 | 7.13 | 2018-08-08T06:55:00Z | 7 | 30 |  |  |  | 0 | 0 | KNNC1 | 7.13 | 2018-08-08T06:55:00Z | 7 | 61
PG&E | 2018-08-08 | 16:02 | 36.4703 | -121.7143 | Vegetation | Rural | < 3 meters | Customer | N.A. | 103910535 | None | 12000 | Conductor | Overhead | Yes | 43320 | 0.66806 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1830 | 2018 | 8 | 8 | 16 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 14.7322 | 168_155 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:02:00 | 1569 | 15.5625 | FALSE | <25mph |  |  |  | 0 | 0 | F1964 | 7.27 | 2018-08-08T07:00:00Z | 2.01 | 5 |  |  |  | 0 | 0 | F1964 | 7.27 | 2018-08-08T08:00:00Z | 2.01 | 8
PG&E | 2018-08-08 | 16:03 | 37.2974 | -122.2651 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 100307515 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 0.66875 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1831 | 2018 | 8 | 8 | 16 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.1654 | 144_201 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:03:00 | 1570 | 9.1654 | FALSE | <25mph | LAHC1 | 0.77 | 2018-08-08T06:07:00Z | 4 | 1 | PG003 | 5.06 | 2018-08-08T06:00:00Z | 12.93 | 57 | LAHC1 | 0.77 | 2018-08-08T06:07:00Z | 4 | 2 | PG003 | 5.06 | 2018-08-08T06:00:00Z | 12.93 | 111
PG&E | 2018-08-10 | 12:54 | 38.799 | -120.73 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101386272 | AT&T | 12000 | Conductor | Overhead | Yes | 43322 | 0.5375 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1832 | 2018 | 8 | 10 | 12 | 54 | 18-0068798 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 26532 | 10.1607 | 211_283 | <25mph | <15mph | HFTD - Distribution | 2018-08-10 12:54:00 | 1571 | 17.3224 | FALSE | <25mph | E3165 | 0.86 | 2018-08-10T06:10:00Z | 4.99 | 8 | PG068 | 4.31 | 2018-08-10T07:00:00Z | 5.03 | 47 | E3165 | 0.86 | 2018-08-10T08:00:00Z | 4.99 | 15 | PG068 | 4.31 | 2018-08-10T07:10:00Z | 6.13 | 91
PG&E | 2018-08-10 | 20:18 | 39.2093 | -121.0615 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100075517 | AT&T | 12000 | Conductor | Overhead | Yes | 43322 | 0.84583 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1835 | 2018 | 8 | 10 | 20 | 18 | 18-0068886 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 581901 | 7.8615 | 197_306 | <25mph | <15mph | HFTD - Distribution | 2018-08-10 20:18:00 | 1574 | 12.349 | FALSE | <25mph | AV369 | 3.86 | 2018-08-10T06:57:00Z | 1.01 | 37 | PG059 | 7.8 | 2018-08-10T06:10:00Z | 7.25 | 76 | AV369 | 3.86 | 2018-08-10T07:57:00Z | 1.01 | 75 | PG059 | 7.8 | 2018-08-10T06:10:00Z | 7.25 | 149
PG&E | 2018-08-12 | 14:46 | 38.6443 | -120.9211 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101410516 | Unknown | 21000 | Conductor | Overhead | Yes | 43324 | 0.61528 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1838 | 2018 | 8 | 12 | 14 | 46 | 18-0069084 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4032 | 11.2318 | 203_274 | <25mph | <15mph | HFTD - Distribution | 2018-08-12 14:46:00 | 1577 | 12.412 | FALSE | <25mph | E8856 | 3.96 | 2018-08-12T06:35:00Z | 8.01 | 27 | PG073 | 7.47 | 2018-08-12T07:00:00Z | 14.92 | 118 | E8856 | 3.96 | 2018-08-12T06:35:00Z | 8.01 | 52 | PG073 | 7.47 | 2018-08-12T07:30:00Z | 19.06 | 228
PG&E | 2018-08-13 | 15:33 | 38.708 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101377799 | Unknown | 21000 | Conductor | Overhead | Yes | 43325 | 0.64792 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1840 | 2018 | 8 | 13 | 15 | 33 | 18-0069470 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1004 | 11.7134 | 201_278 | <25mph | <15mph | HFTD - Distribution | 2018-08-13 15:33:00 | 1579 | 13.7748 | FALSE | <25mph | PG073 | 2.99 | 2018-08-13T06:40:00Z | 13.8 | 60 | PG073 | 2.99 | 2018-08-13T06:40:00Z | 13.8 | 117 | PG073 | 2.99 | 2018-08-13T06:40:00Z | 13.8 | 116 | PG073 | 2.99 | 2018-08-13T06:40:00Z | 13.8 | 226
PG&E | 2018-08-14 | 6:43 | 40.686 | -122.141 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | j.t. zulliger 530-225-2420 | 103379843 | Unknown | 12000 | Conductor | Overhead | Yes | 43326 | 0.27986 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1842 | 2018 | 8 | 14 | 6 | 43 | 18-0069529 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 37986 | 10.4557 | 152_387 | <25mph | <15mph | HFTD - Distribution | 2018-08-14 06:43:00 | 1581 | 11.7634 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-08-14 | 15:18 | 36.9656 | -121.8681 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 103128221 | AT&T | 21000 | Conductor | Overhead | Yes | 43326 | 0.6375 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1843 | 2018 | 8 | 14 | 15 | 18 | 18-0069846 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 15580 | 9.8033 | 161_182 | <25mph | <15mph | HFTD - Distribution | 2018-08-14 15:18:00 | 1582 | 14.8482 | FALSE | <25mph | E8014 | 2.14 | 2018-08-14T06:15:00Z | 8.99 | 34 | E8014 | 2.14 | 2018-08-14T06:15:00Z | 8.99 | 80 | E8014 | 2.14 | 2018-08-14T06:15:00Z | 8.99 | 67 | E8014 | 2.14 | 2018-08-14T06:15:00Z | 8.99 | 158
PG&E | 2018-08-14 | 15:46 | 38.0878 | -122.6002 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103916882 | Verizon | 0 – 750 | Conductor | Overhead | Yes | 43326 | 0.65694 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1844 | 2018 | 8 | 14 | 15 | 46 | 18-0069929 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 546 | 20.6189 | 130_244 | <25mph | <15mph | HFTD - Distribution | 2018-08-14 15:46:00 | 1583 | 26.2074 | FALSE | 25-40mph | E0433 | 1.95 | 2018-08-14T06:35:00Z | 15.99 | 35 | WDAC1 | 7.14 | 2018-08-14T06:51:00Z | 20 | 64 | E0433 | 1.95 | 2018-08-14T06:35:00Z | 15.99 | 70 | WDAC1 | 7.14 | 2018-08-14T06:51:00Z | 20 | 125
PG&E | 2018-08-17 | 9:38 | 40.2997 | -122.3322 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chief | 101509747 | AT&T | 12000 | Conductor | Overhead | Yes | 43329 | 0.40139 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1845 | 2018 | 8 | 17 | 9 | 38 | 18-0071042 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 15510 | 1.1849 | 143_366 | <25mph | <15mph | HFTD - Distribution | 2018-08-17 09:38:00 | 1584 | 12.2164 | FALSE | <25mph | E7114 | 3.57 | 2018-08-17T06:47:00Z | 4.99 | 4 | E7114 | 3.57 | 2018-08-17T06:47:00Z | 4.99 | 4 | E7114 | 3.57 | 2018-08-17T07:47:00Z | 5.99 | 8 | E7114 | 3.57 | 2018-08-17T07:47:00Z | 5.99 | 8
PG&E | 2018-08-20 | 9:34 | 39.8014 | -121.5813 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100400441 | Unknown | 12000 | Conductor | Overhead | Yes | 43332 | 0.39861 | Contact From Object | N.A. | Other | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1849 | 2018 | 8 | 20 | 9 | 34 | 18-0071596 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 394259 | 5.4464 | 175_338 | <25mph | <15mph | HFTD - Distribution | 2018-08-20 09:34:00 | 1588 | 11.8754 | FALSE | <25mph | C4565 | 3.06 | 2018-08-20T06:53:00Z | 3 | 6 | JBGC1 | 6.67 | 2018-08-20T06:13:00Z | 11.01 | 28 | C4565 | 3.06 | 2018-08-20T07:53:00Z | 3 | 12 | JBGC1 | 6.67 | 2018-08-20T07:13:00Z | 11.01 | 54
PG&E | 2018-08-21 | 10:13 | 38.6972 | -120.889 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101385436 | Unknown | 12000 | Conductor | Overhead | Yes | 43333 | 0.42569 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1852 | 2018 | 8 | 21 | 10 | 13 | 18-0072055 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4572 | 5.9109 | 204_277 | <25mph | <15mph | HFTD - Distribution | 2018-08-21 10:13:00 | 1591 | 12.0437 | FALSE | <25mph | PG106 | 1.36 | 2018-08-21T06:40:00Z | 9.22 | 57 | PG073 | 6.99 | 2018-08-21T06:40:00Z | 11.63 | 142 | PG106 | 1.36 | 2018-08-21T06:40:00Z | 9.22 | 111 | PG073 | 6.99 | 2018-08-21T06:40:00Z | 11.63 | 274
PG&E | 2018-08-22 | 17:24 | 37.9519 | -120.3103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101030620 | Unknown | 17000 | Conductor | Overhead | Yes | 43334 | 0.725 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | dampeners | no-match | 1853 | 2018 | 8 | 22 | 17 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 10.7586 | 229_236 | <25mph | <15mph | HFTD - Distribution | 2018-08-22 17:24:00 | 1592 | 13.1476 | FALSE | <25mph | PG029 | 2.2 | 2018-08-22T06:00:00Z | 4.61 | 18 | PG061 | 6.32 | 2018-08-22T06:40:00Z | 5.03 | 39 | PG031 | 2.51 | 2018-08-22T08:00:00Z | 6.58 | 34 | PG031 | 2.51 | 2018-08-22T08:00:00Z | 6.58 | 73
PG&E | 2018-08-22 | 21:56 | 39.0425 | -120.9695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100024728 | Verizon | 12000 | Conductor | Overhead | Yes | 43334 | 0.91389 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1854 | 2018 | 8 | 22 | 21 | 56 | 18-0072654 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29727 | 9.3137 | 201_296 | <25mph | <15mph | HFTD - Distribution | 2018-08-22 21:56:00 | 1593 | 10.5291 | FALSE | <25mph | D9434 | 1.28 | 2018-08-22T07:00:00Z | 0 | 11 | PG032 | 6.31 | 2018-08-22T06:40:00Z | 7 | 44 | D9434 | 1.28 | 2018-08-22T08:00:00Z | 0 | 21 | PG032 | 6.31 | 2018-08-22T07:40:00Z | 7 | 84
PG&E | 2018-08-24 | 1:38 | 39.2029 | -121.2766 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100087099 | AT&T | 21000 | Conductor | Overhead | Yes | 43336 | 0.068056 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1857 | 2018 | 8 | 24 | 1 | 38 | 18-0073021 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 24360 | 13.6343 | 188_305 | <25mph | <15mph | HFTD - Distribution | 2018-08-24 01:38:00 | 1596 | 17.6338 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-08-24 | 5:03 | 39.1184 | -121.0154 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JIM SMITH BATT CHIEF 3 | 100097647 | Unknown | 12000 | Conductor | Overhead | Yes | 43336 | 0.21042 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1858 | 2018 | 8 | 24 | 5 | 3 | 18-0073024 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 4048 | 6.5682 | 199_301 | <25mph | <15mph | HFTD - Distribution | 2018-08-24 05:03:00 | 1597 | 12.3049 | FALSE | <25mph | AT999 | 2.07 | 2018-08-24T07:00:00Z | 0 | 11 | PG059 | 6.98 | 2018-08-24T06:40:00Z | 6.58 | 79 | AT999 | 2.07 | 2018-08-24T07:15:00Z | 2.01 | 21 | PG059 | 6.98 | 2018-08-24T07:10:00Z | 8.12 | 153
PG&E | 2018-08-26 | 15:29 | 39.3599 | -121.1209 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100107472 | Unknown | 12000 | Conductor | Overhead | Yes | 43338 | 0.64514 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1860 | 2018 | 8 | 26 | 15 | 29 | 18-0073601 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 36162 | 13.8191 | 194_314 | <25mph | <15mph | HFTD - Distribution | 2018-08-26 15:29:00 | 1599 | 13.8191 | FALSE | <25mph | RRRC1 | 3.9 | 2018-08-26T06:13:00Z | 4.99 | 1 | RRRC1 | 3.9 | 2018-08-26T06:13:00Z | 4.99 | 27 | RRRC1 | 3.9 | 2018-08-26T07:13:00Z | 7 | 2 | RRRC1 | 3.9 | 2018-08-26T07:13:00Z | 7 | 52
PG&E | 2018-08-28 | 12:50 | 40.2139 | -123.5966 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100994840 | Unknown | 12000 | Conductor | Overhead | Yes | 43340 | 0.53472 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1866 | 2018 | 8 | 28 | 12 | 50 | 18-0074371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 82754 | 9.6027 | 90_363 | <25mph | <15mph | HFTD - Distribution | 2018-08-28 12:50:00 | 1605 | 19.5452 | FALSE | <25mph | ALDC1 | 1.95 | 2018-08-28T06:51:00Z | 3 | 1 | ALDC1 | 1.95 | 2018-08-28T06:51:00Z | 3 | 1 | ALDC1 | 1.95 | 2018-08-28T06:51:00Z | 3 | 2 | ALDC1 | 1.95 | 2018-08-28T06:51:00Z | 3 | 2
PG&E | 2018-08-31 | 13:02 | 40.4775 | -122.4847 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103918932 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 0.54306 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1872 | 2018 | 8 | 31 | 13 | 2 | 18-0075616 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18300 | 0.9461 | 137_376 | <25mph | <15mph | HFTD - Distribution | 2018-08-31 13:02:00 | 1611 | 11.7486 | FALSE | <25mph | PG086 | 3.07 | 2018-08-31T07:00:00Z | 0 | 12 | MMOC1 | 6.41 | 2018-08-31T06:00:00Z | 11.01 | 14 | PG086 | 3.07 | 2018-08-31T08:00:00Z | 1.74 | 22 | MMOC1 | 6.41 | 2018-08-31T06:00:00Z | 11.01 | 25
PG&E | 2018-08-31 | 18:04 | 39.5785 | -123.3842 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102196393 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 0.75278 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1873 | 2018 | 8 | 31 | 18 | 4 | 18-0075741 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18540 | 15.395 | 98_327 | <25mph | <15mph | HFTD - Distribution | 2018-08-31 18:04:00 | 1612 | 16.0884 | FALSE | <25mph |  |  |  | 0 | 0 | RDVC1 | 7.03 | 2018-08-31T06:28:00Z | 7 | 1 |  |  |  | 0 | 0 | RDVC1 | 7.03 | 2018-08-31T07:28:00Z | 7 | 2
PG&E | 2018-08-31 | 18:09 | 37.0548 | -122.0472 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 101803212 | Unknown | 21000 | Conductor | Overhead | Yes | 43343 | 0.75625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1874 | 2018 | 8 | 31 | 18 | 9 | 18-0075730 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 197397 | 21.0516 | 153_187 | <25mph | <15mph | HFTD - Distribution | 2018-08-31 18:09:00 | 1613 | 21.1204 | FALSE | <25mph | E3439 | 3.12 | 2018-08-31T06:39:00Z | 1.01 | 16 | D8979 | 7.19 | 2018-08-31T06:21:00Z | 12.01 | 158 | E3439 | 3.12 | 2018-08-31T07:54:00Z | 1.01 | 33 | D8979 | 7.19 | 2018-08-31T06:21:00Z | 12.01 | 305
PG&E | 2018-09-01 | 14:25 | 36.8088 | -121.5916 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Twr 35/222 | None | 115000 | Conductor | Overhead | Yes | 43344 | 0.60069 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1875 | 2018 | 9 | 1 | 14 | 25 | INT-11331 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 702145 | 13.8683 | 173_173 | <25mph | <15mph | HFTD - Transmission | 2018-09-01 14:25:00 | 1614 | 16.3299 | FALSE | <25mph |  |  |  | 0 | 0 | AP200 | 7.05 | 2018-09-01T06:58:00Z | 0 | 3 |  |  |  | 0 | 0 | AP200 | 7.05 | 2018-09-01T07:53:00Z | 0 | 6
PG&E | 2018-09-02 | 15:36 | 37.4714 | -122.4248 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Arie Delay 659-740-4636 | 103808872 | Unknown | 12000 | Capacitor Bank | Overhead | Yes | 43345 | 0.65 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1876 | 2018 | 9 | 2 | 15 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 11.73 | 137_210 | <25mph | <15mph | HFTD - Distribution | 2018-09-02 15:36:00 | 1615 | 13.6047 | FALSE | <25mph |  |  |  | 0 | 0 | HSPC1 | 6.33 | 2018-09-02T06:18:00Z | 13 | 45 |  |  |  | 0 | 0 | HSPC1 | 6.33 | 2018-09-02T07:18:00Z | 13 | 90
PG&E | 2018-09-03 | 18:29 | 39.4547 | -121.4955 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100395672 | Unknown | 12000 | Conductor | Overhead | Yes | 43346 | 0.77014 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1880 | 2018 | 9 | 3 | 18 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 6.2719 | 178_319 | <25mph | <15mph | HFTD - Distribution | 2018-09-03 18:29:00 | 1619 | 14.7897 | FALSE | <25mph |  |  |  | 0 | 0 | TT309 | 4.73 | 2018-09-03T06:45:00Z | 4 | 2 |  |  |  | 0 | 0 | TT309 | 4.73 | 2018-09-03T06:45:00Z | 4 | 4
PG&E | 2018-09-05 | 16:55 | 37.4655 | -119.9005 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JON BERRY 209-966-4700 | 101087053 | Unknown | 21000 | Conductor | Overhead | Yes | 43348 | 0.70486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1882 | 2018 | 9 | 5 | 16 | 55 | 18-0076909 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 4017 | 13.8551 | 248_210 | <25mph | <15mph | HFTD - Distribution | 2018-09-05 16:55:00 | 1621 | 17.3022 | FALSE | <25mph |  |  |  | 0 | 0 | E9110 | 4.85 | 2018-09-05T06:36:00Z | 8.01 | 6 |  |  |  | 0 | 0 | E9110 | 4.85 | 2018-09-05T06:36:00Z | 8.01 | 12
PG&E | 2018-09-06 | 16:19 | 39.0904 | -120.9464 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 100020676 | Unknown | 12000 | Conductor | Overhead | Yes | 43349 | 0.67986 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1886 | 2018 | 9 | 6 | 16 | 19 | 18-0077280 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 30780 | 10.0605 | 202_299 | <25mph | <15mph | HFTD - Distribution | 2018-09-06 16:19:00 | 1625 | 12.3694 | FALSE | <25mph | D9434 | 3.62 | 2018-09-06T06:00:00Z | 4 | 9 | PG032 | 7.62 | 2018-09-06T06:50:00Z | 7 | 46 | D9434 | 3.62 | 2018-09-06T06:00:00Z | 4 | 17 | PG032 | 7.62 | 2018-09-06T07:10:00Z | 7.25 | 89
PG&E | 2018-09-09 | 4:25 | 38.6534 | -122.8538 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 13/1 | None | 60000 | Conductor | Overhead | Yes | 43352 | 0.18403 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1887 | 2018 | 9 | 9 | 4 | 25 | INT-11353 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 7.8888 | 120_276 | <25mph | <15mph | HFTD - Transmission | 2018-09-09 04:25:00 | 1626 | 22.3261 | FALSE | <25mph | PICWW | 2.16 | 2018-09-09T06:00:00Z | 11.21 | 15 | PG082 | 5.77 | 2018-09-09T06:30:00Z | 19.95 | 38 | PICWW | 2.16 | 2018-09-09T06:00:00Z | 11.21 | 26 | PG082 | 5.77 | 2018-09-09T06:30:00Z | 19.95 | 65
PG&E | 2018-09-10 | 20:37 | 38.0188 | -122.7225 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 102252760 | Unknown | 12000 | Conductor | Overhead | Yes | 43353 | 0.85903 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1889 | 2018 | 9 | 10 | 20 | 37 | 18-0078359 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 219903 | 12.2581 | 125_241 | <25mph | <15mph | HFTD - Distribution | 2018-09-10 20:37:00 | 1628 | 18.8462 | FALSE | <25mph | BBEC1 | 1.27 | 2018-09-10T06:11:00Z | 14.99 | 8 | WDAC1 | 4.66 | 2018-09-10T06:51:00Z | 18.99 | 50 | BBEC1 | 1.27 | 2018-09-10T06:11:00Z | 14.99 | 15 | WDAC1 | 4.66 | 2018-09-10T07:51:00Z | 22.01 | 95
PG&E | 2018-09-11 | 5:23 | 37.376 | -119.6304 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | TROY CHEEK 209-966-3621 | 101023184 | Unknown | 12000 | Conductor | Overhead | Yes | 43354 | 0.22431 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1891 | 2018 | 9 | 11 | 5 | 23 | 18-0078387 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 288 | 4.3046 | 260_205 | <25mph | <15mph | HFTD - Distribution | 2018-09-11 05:23:00 | 1630 | 11.3584 | FALSE | <25mph | BSNC1 | 0.17 | 2018-09-11T06:48:00Z | 8.01 | 23 | MIAC1 | 6.99 | 2018-09-11T06:59:00Z | 8.99 | 67 | BSNC1 | 0.17 | 2018-09-11T07:48:00Z | 10 | 49 | MIAC1 | 6.99 | 2018-09-11T07:59:00Z | 10 | 134
PG&E | 2018-09-14 | 15:08 | 35.328 | -120.6982 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Sean Hernandez Cell # 805 903 3423 | 103400199 | Unknown | 12000 | Conductor | Overhead | Yes | 43357 | 0.63056 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1898 | 2018 | 9 | 14 | 15 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 24.1105 | 213_92 | <25mph | <15mph | HFTD - Distribution | 2018-09-14 15:08:00 | 1637 | 24.1304 | FALSE | <25mph | ARGC1 | 2.05 | 2018-09-14T06:54:00Z | 2.01 | 1 | F2489 | 7.42 | 2018-09-14T06:30:00Z | 8.01 | 17 | ARGC1 | 2.05 | 2018-09-14T07:54:00Z | 3 | 2 | F2489 | 7.42 | 2018-09-14T06:30:00Z | 8.01 | 35
PG&E | 2018-09-16 | 8:26 | 35.3046 | -120.6389 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | Pole 4/23A | None | 70000 | Conductor | Overhead | Yes | 43359 | 0.35139 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1903 | 2018 | 9 | 16 | 8 | 26 | INT-11371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 29925 | 32.6873 | 216_90 | 25-40mph | 30-45mph | HFTD - Transmission | 2018-09-16 08:26:00 | 1642 | 35.3808 | FALSE | 25-40mph | ARGC1 | 2.25 | 2018-09-16T06:54:00Z | 2.01 | 1 | ARGC1 | 2.25 | 2018-09-16T06:54:00Z | 2.01 | 5 | ARGC1 | 2.25 | 2018-09-16T07:54:00Z | 3 | 2 | ARGC1 | 2.25 | 2018-09-16T07:54:00Z | 3 | 10
PG&E | 2018-09-16 | 10:22 | 39.4627 | -123.7837 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 102184303 | AT&T | 12000 | Conductor | Overhead | Yes | 43359 | 0.43194 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1904 | 2018 | 9 | 16 | 10 | 22 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.1285 | 81_321 | <25mph | <15mph | HFTD - Distribution | 2018-09-16 10:22:00 | 1643 | 13.681 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-09-21 | 21:10 | 39.0273 | -122.6627 | Vegetation | Rural | < 3 meters | Customer | N.A. | 102147414 | Unknown | 12000 | Conductor | Overhead | Yes | 43364 | 0.88194 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1908 | 2018 | 9 | 21 | 21 | 10 | 18-0082278 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 281055 | 11.7868 | 128_296 | <25mph | <15mph | HFTD - Distribution | 2018-09-21 21:10:00 | 1647 | 15.5314 | FALSE | <25mph |  |  |  | 0 | 0 | PG097 | 7.92 | 2018-09-21T06:50:00Z | 2.19 | 14 |  |  |  | 0 | 0 | PG115 | 4.77 | 2018-09-21T07:20:00Z | 3.51 | 26
PG&E | 2018-09-21 | 23:02 | 38.6428 | -122.7453 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102218862 | Unknown | 12000 | Conductor | Overhead | Yes | 43364 | 0.95972 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1909 | 2018 | 9 | 21 | 23 | 2 | 18-0082304 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 9470 | 7.2054 | 124_275 | <25mph | <15mph | HFTD - Distribution | 2018-09-21 23:02:00 | 1648 | 14.1592 | FALSE | <25mph | E3235 | 2.39 | 2018-09-21T06:59:00Z | 0 | 12 | PG038 | 6.21 | 2018-09-21T07:00:00Z | 3.51 | 41 | E3235 | 2.39 | 2018-09-21T07:59:00Z | 0 | 23 | PG038 | 6.21 | 2018-09-21T07:40:00Z | 3.51 | 78
PG&E | 2018-09-23 | 15:57 | 37.335 | -121.7679 | Vegetation | Urban | 10 - 99 Acres | Fire Agency | San Jose FD | 100576722 | AT&T | 21000 | Conductor | Overhead | Yes | 43366 | 0.66458 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1912 | 2018 | 9 | 23 | 15 | 57 | 18-0082586 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 231441 | 14.4652 | 166_202 | <25mph | <15mph | HFTD - Distribution | 2018-09-23 15:57:00 | 1651 | 14.4652 | FALSE | <25mph | UCBO | 3.66 | 2018-09-23T06:40:00Z | 2.01 | 25 | MIPC1 | 7.47 | 2018-09-23T06:19:00Z | 8.99 | 85 | UCBO | 3.66 | 2018-09-23T06:40:00Z | 2.01 | 49 | MIPC1 | 7.47 | 2018-09-23T06:19:00Z | 8.99 | 165
PG&E | 2018-09-24 | 0:35 | 39.8152 | -121.6438 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Pole 3/42B | None | 60000 | Conductor | Overhead | Yes | 43367 | 0.024306 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1913 | 2018 | 9 | 24 | 0 | 35 | INT-11388 | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 2407691 | 10.8571 | 172_339 | <25mph | <15mph | HFTD - Transmission | 2018-09-24 00:35:00 | 1652 | 11.6135 | FALSE | <25mph | C8878 | 3.93 | 2018-09-24T06:58:00Z | 3 | 25 | CSTC1 | 7.71 | 2018-09-24T06:51:00Z | 5.99 | 40 | C8878 | 3.93 | 2018-09-24T07:43:00Z | 4 | 47 | CSTC1 | 7.71 | 2018-09-24T07:51:00Z | 8.01 | 75
PG&E | 2018-09-27 | 3:40 | 37.5473 | -120.3255 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Twr 12/2 | None | 70000 | Conductor | Overhead | Yes | 43370 | 0.15278 | Contact From Object | N.A. | Other | Electric Facility | Unknown | guano | no-match | 1916 | 2018 | 9 | 27 | 3 | 40 | INT-11393 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 0 | 2.5171 | 229_214 | <25mph | <15mph | HFTD - Transmission | 2018-09-27 03:40:00 | 1655 | 12.4207 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-09-27 | 12:43 | 38.5148 | -122.4463 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Twr 000/010 | None | 60000 | Conductor | Overhead | Yes | 43370 | 0.52986 | Contact From Object | N.A. | Other | Electric Facility | Human Error | helicopter | no-match | 1917 | 2018 | 9 | 27 | 12 | 43 | INT-11394 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1488992 | 4.4433 | 137_268 | <25mph | <15mph | HFTD - Transmission | 2018-09-27 12:43:00 | 1656 | 10.4879 | FALSE | <25mph |  |  |  | 0 | 0 | PG018 | 4.41 | 2018-09-27T06:10:00Z | 3.51 | 21 |  |  |  | 0 | 0 | PG018 | 4.41 | 2018-09-27T08:00:00Z | 3.51 | 39
PG&E | 2018-09-29 | 16:16 | 41.0219 | -123.655 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Hoopa Fire Dept | 100962165 | Unknown | 12000 | Conductor | Overhead | Yes | 43372 | 0.67778 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1923 | 2018 | 9 | 29 | 16 | 16 | 18-0084877 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 16028 | 7.8421 | 89_407 | <25mph | <15mph | HFTD - Distribution | 2018-09-29 16:16:00 | 1662 | 11.5265 | FALSE | <25mph |  |  |  | 0 | 0 | BHTC1 | 7.5 | 2018-09-29T06:46:00Z | 13 | 6 |  |  |  | 0 | 0 | BHTC1 | 7.5 | 2018-09-29T07:46:00Z | 21 | 9
PG&E | 2018-10-07 | 1:44 | 37.178 | -122.0267 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Mike Mathiesen 408-472-1613 Incident # SCU7096 | 100518363 | Unknown | 12000 | Conductor | Overhead | Yes | 43380 | 0.072222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1929 | 2018 | 10 | 7 | 1 | 44 | 18-0087807 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 224444 | 25.0906 | 154_194 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-07 01:44:00 | 1668 | 25.864 | FALSE | 25-40mph | PG050 | 2.46 | 2018-10-07T06:30:00Z | 14.25 | 11 | PG057 | 6.61 | 2018-10-07T06:20:00Z | 21.92 | 140 | PG050 | 2.46 | 2018-10-07T07:50:00Z | 16.67 | 21 | PG057 | 6.61 | 2018-10-07T07:40:00Z | 23.67 | 274
PG&E | 2018-10-08 | 11:03 | 38.2621 | -122.7881 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101987186 | AT&T | 12000 | Conductor | Overhead | No | N.A. | N.A. | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1933 | 2018 | 10 | 8 | 11 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 15.6859 | 122_254 | <25mph | <15mph | HFTD - Distribution | 2018-10-08 11:03:00 | 1672 | 17.3485 | FALSE | <25mph |  |  |  | 0 | 0 | F2270 | 5.08 | 2018-10-08T06:04:00Z | 10 | 16 |  |  |  | 0 | 0 | F2270 | 5.08 | 2018-10-08T06:04:00Z | 10 | 32
PG&E | 2018-10-14 | 11:40 | 40.3598 | -122.4388 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TOM STROING 530-200-5113 | 101506416 | AT&T | 12000 | Conductor | Overhead | Yes | 43387 | 0.48611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1938 | 2018 | 10 | 14 | 11 | 40 | 18-0090193 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 945 | 30.6414 | 139_370 | 25-40mph | 30-45mph | HFTD - Distribution | 2018-10-14 11:40:00 | 1677 | 30.6414 | FALSE | 25-40mph |  |  |  | 0 | 0 | E7114 | 4.61 | 2018-10-14T06:00:00Z | 10 | 5 |  |  |  | 0 | 0 | E7114 | 4.61 | 2018-10-14T07:45:00Z | 10 | 8
PG&E | 2018-10-14 | 19:39 | 38.446 | -120.5147 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | IC- Dillon Gissell- 209-295-7735 | 103384485 | Unknown | 12000 | Conductor | Overhead | Yes | 43387 | 0.81875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1939 | 2018 | 10 | 14 | 19 | 39 | 18-0090288 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3497327 | 25.4932 | 220_264 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-14 19:39:00 | 1678 | 30.9108 | FALSE | 25-40mph | C9148 | 3.52 | 2018-10-14T06:34:00Z | 22.01 | 18 | C9148 | 3.52 | 2018-10-14T06:34:00Z | 22.01 | 37 | C9148 | 3.52 | 2018-10-14T06:34:00Z | 22.01 | 34 | C9148 | 3.52 | 2018-10-14T06:34:00Z | 22.01 | 69
PG&E | 2018-10-14 | 20:08 | 38.8935 | -120.8497 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103674516 | Unknown | 21000 | Conductor | Overhead | Yes | 43387 | 0.83889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1940 | 2018 | 10 | 14 | 20 | 8 | 18-0090299 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 48095 | 8.663 | 206_288 | <25mph | <15mph | HFTD - Distribution | 2018-10-14 20:08:00 | 1679 | 24.0259 | FALSE | <25mph | PG033 | 2.11 | 2018-10-14T07:00:00Z | 6.13 | 27 | BDMC1 | 7.81 | 2018-10-14T06:36:00Z | 17 | 35 | PG033 | 2.11 | 2018-10-14T07:00:00Z | 6.13 | 51 | BDMC1 | 7.81 | 2018-10-14T06:36:00Z | 17 | 66
PG&E | 2018-10-15 | 3:23 | 38.2897 | -120.5803 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103378003 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43388 | 0.14097 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1941 | 2018 | 10 | 15 | 3 | 23 | 18-0090342 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1464 | 26.0611 | 218_255 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-15 03:23:00 | 1680 | 26.2858 | FALSE | 25-40mph | AT317 | 3.74 | 2018-10-15T06:50:00Z | 23 | 13 | ESPC1 | 4.93 | 2018-10-15T06:13:00Z | 44.98 | 26 | AT317 | 3.74 | 2018-10-15T06:50:00Z | 23 | 25 | ESPC1 | 4.93 | 2018-10-15T07:13:00Z | 47 | 50
PG&E | 2018-10-16 | 10:44 | 40.5097 | -124.1624 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101004106 | Unknown | 12000 | Conductor | Overhead | Yes | 43389 | 0.44722 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1942 | 2018 | 10 | 16 | 10 | 44 | 18-0090952 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 2081 | 4.5851 | 67_380 | <25mph | <15mph | HFTD - Distribution | 2018-10-16 10:44:00 | 1681 | 13.3626 | FALSE | <25mph |  |  |  | 0 | 0 | C5061 | 4.32 | 2018-10-16T07:00:00Z | 0 | 7 |  |  |  | 0 | 0 | C5061 | 4.32 | 2018-10-16T07:59:00Z | 0 | 14
PG&E | 2018-10-16 | 16:30 | 38.7754 | -122.8976 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MARK GRADEK (707) 889-4303 | 101962692 | AT&T | 12000 | Conductor | Overhead | Yes | 43389 | 0.6875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1943 | 2018 | 10 | 16 | 16 | 30 | 18-0091127 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 744 | 10.3513 | 118_282 | <25mph | <15mph | HFTD - Distribution | 2018-10-16 16:30:00 | 1682 | 19.9126 | FALSE | <25mph | PG090 | 1.05 | 2018-10-16T06:20:00Z | 4.38 | 7 | PG125 | 5.67 | 2018-10-16T07:00:00Z | 14.25 | 26 | PG090 | 1.05 | 2018-10-16T07:20:00Z | 10.29 | 13 | HWKC1 | 4.29 | 2018-10-16T07:56:00Z | 18.99 | 49
PG&E | 2018-10-20 | 14:31 | 40.5218 | -124.1137 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Str. 003/000 | None | 60000 | Conductor | Overhead | Yes | 43393 | 0.60486 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1947 | 2018 | 10 | 20 | 14 | 31 | INT-11477 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 410982 | 9.6901 | 69_380 | <25mph | <15mph | HFTD - Transmission | 2018-10-20 14:31:00 | 1686 | 10.3412 | FALSE | <25mph | AT493 | 3.34 | 2018-10-20T06:58:00Z | 4.99 | 22 | AT493 | 3.34 | 2018-10-20T06:58:00Z | 4.99 | 22 | AT493 | 3.34 | 2018-10-20T07:18:00Z | 4.99 | 43 | AT493 | 3.34 | 2018-10-20T07:18:00Z | 4.99 | 43
PG&E | 2018-10-21 | 0:32 | 35.5035 | -120.6025 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101886776 | Unknown | 21000 | Conductor | Overhead | Yes | 43394 | 0.022222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1948 | 2018 | 10 | 21 | 0 | 32 | 18-0092526 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 302559 | 9.0366 | 217_101 | <25mph | <15mph | HFTD - Distribution | 2018-10-21 00:32:00 | 1687 | 16.4549 | FALSE | <25mph |  |  |  | 0 | 0 | TT469 | 4.38 | 2018-10-21T06:14:00Z | 4 | 28 |  |  |  | 0 | 0 | TT469 | 4.38 | 2018-10-21T07:14:00Z | 4 | 55
PG&E | 2018-10-24 | 7:08 | 37.9475 | -120.2671 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SCOTT PITTMAN 209-768-8182 TCU INCIDENT# 012528 | 101047865 | Unknown | 17000 | Conductor | Overhead | Yes | 43397 | 0.29722 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1949 | 2018 | 10 | 24 | 7 | 8 | 18-0093599 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 13433 | 8.6394 | 231_236 | <25mph | <15mph | HFTD - Distribution | 2018-10-24 07:08:00 | 1688 | 12.0171 | FALSE | <25mph | PG031 | 1.92 | 2018-10-24T07:00:00Z | 6.35 | 19 | PG166 | 7.04 | 2018-10-24T06:50:00Z | 11.83 | 54 | PG031 | 1.92 | 2018-10-24T07:40:00Z | 7.9 | 35 | PG166 | 7.04 | 2018-10-24T06:50:00Z | 11.83 | 100
PG&E | 2018-10-24 | 14:18 | 36.7265 | -119.1086 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CHRIS CHRISTOPHERSON (559)493-4320 I.C #18CAFKUO15649 | 100691946 | None | 12000 | Conductor | Overhead | Yes | 43397 | 0.59583 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1950 | 2018 | 10 | 24 | 14 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 7.8375 | 283_170 | <25mph | <15mph | HFTD - Distribution | 2018-10-24 14:18:00 | 1689 | 7.8887 | FALSE | <25mph |  |  |  | 0 | 0 | PHRC1 | 5.37 | 2018-10-24T06:58:00Z | 8.99 | 17 |  |  |  | 0 | 0 | PHRC1 | 5.37 | 2018-10-24T07:58:00Z | 10 | 34
PG&E | 2018-10-25 | 18:47 | 35.5566 | -118.8168 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | GREG BLACK (661)391-7000 | 100203660 | None | 0 – 750 | Conductor | Overhead | Yes | 43398 | 0.78264 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1951 | 2018 | 10 | 25 | 18 | 47 | 18-0094369 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 1309 | 7.552 | 298_105 | <25mph | <15mph | HFTD - Distribution | 2018-10-25 18:47:00 | 1690 | 11.6197 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-10-26 | 20:55 | 40.1528 | -122.3634 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT. ROB WAELTY 530-527-6113 | 101553579 | Unknown | 12000 | Conductor | Overhead | Yes | 43399 | 0.87153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1953 | 2018 | 10 | 26 | 20 | 55 | 18-0094702 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4812 | 9.9443 | 142_358 | <25mph | <15mph | HFTD - Distribution | 2018-10-26 20:55:00 | 1692 | 10.2925 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-10-28 | 8:50 | 36.3792 | -121.8454 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TONY (831) 625-6415 | 101672342 | Unknown | 12000 | Conductor | Overhead | Yes | 43401 | 0.36806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1954 | 2018 | 10 | 28 | 8 | 50 | 18-0094889 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 3046 | 22.934 | 162_150 | <25mph | <15mph | HFTD - Distribution | 2018-10-28 08:50:00 | 1693 | 23.289 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-11-01 | 20:45 | 38.372 | -123.0507 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103852431 | AT&T | 12000 | Conductor | Overhead | Yes | 43405 | 0.86458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1958 | 2018 | 11 | 1 | 20 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.9426 | 111_260 | <25mph | <15mph | HFTD - Distribution | 2018-11-01 20:45:00 | 1697 | 13.8199 | FALSE | <25mph | BBYC1 | 3.77 | 2018-11-01T07:00:00Z | 0.51 | 2 | BDZC1 | 4.05 | 2018-11-01T06:10:00Z | 6.51 | 20 | BBYC1 | 3.77 | 2018-11-01T08:00:00Z | 0.85 | 3 | BDZC1 | 4.05 | 2018-11-01T08:00:00Z | 7.02 | 38
PG&E | 2018-11-07 | 15:49 | 37.0003 | -121.9802 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 101684527 | Unknown | 21000 | Capacitor Bank | Overhead | Yes | 43411 | 0.65903 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1959 | 2018 | 11 | 7 | 15 | 49 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 5.4365 | 156_184 | <25mph | <15mph | HFTD - Distribution | 2018-11-07 15:49:00 | 1698 | 11.342 | FALSE | <25mph | C8539 | 3.2 | 2018-11-07T07:57:00Z | 5.99 | 56 | E7291 | 5.58 | 2018-11-07T07:17:00Z | 8.99 | 130 | C9585 | 2.14 | 2018-11-07T08:12:00Z | 11.01 | 109 | C9585 | 2.14 | 2018-11-07T08:12:00Z | 11.01 | 251
PG&E | 2018-11-09 | 4:49 | 39.8234 | -121.8382 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100402367 | AT&T | 12000 | Conductor | Overhead | Yes | 43413 | 0.20069 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1963 | 2018 | 11 | 9 | 4 | 49 | 18-0098482 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 11900 | 0.23999 | 164_340 | <25mph | <15mph | HFTD - Distribution | 2018-11-09 04:49:00 | 1703 | 7.1467 | FALSE | <25mph | D8132 | 3.69 | 2018-11-09T07:15:00Z | 2.01 | 5 | CSTC1 | 4.96 | 2018-11-09T07:51:00Z | 8.01 | 13 | D8132 | 3.69 | 2018-11-09T08:45:00Z | 3 | 8 | CSTC1 | 4.96 | 2018-11-09T07:51:00Z | 8.01 | 23
PG&E | 2018-11-09 | 8:59 | 37.2809 | -122.1214 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100546562 | AT&T | 12000 | Conductor | Overhead | Yes | 43413 | 0.37431 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1964 | 2018 | 11 | 9 | 8 | 59 | 18-0098521 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 77077 | 5.2345 | 150_200 | <25mph | <15mph | HFTD - Distribution | 2018-11-09 08:59:00 | 1704 | 17.3931 | FALSE | <25mph | E0516 | 1.72 | 2018-11-09T08:00:00Z | 17 | 39 | PG152 | 4.64 | 2018-11-09T07:20:00Z | 31.14 | 172 | E0516 | 1.72 | 2018-11-09T09:00:00Z | 21 | 75 | PG152 | 4.64 | 2018-11-09T07:20:00Z | 31.14 | 331
PG&E | 2018-11-10 | 13:31 | 37.0467 | -121.9853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101671641 | Unknown | 21000 | Conductor | Overhead | Yes | 43414 | 0.56319 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1966 | 2018 | 11 | 10 | 13 | 31 | 18-0098856 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 1482 | 7.3629 | 156_187 | <25mph | <15mph | HFTD - Distribution | 2018-11-10 13:31:00 | 1706 | 13.8913 | FALSE | <25mph | PG062 | 2.37 | 2018-11-10T08:00:00Z | 9.86 | 45 | PG004 | 7.89 | 2018-11-10T07:10:00Z | 11.83 | 186 | PG062 | 2.37 | 2018-11-10T08:20:00Z | 10.96 | 84 | PG004 | 7.89 | 2018-11-10T07:10:00Z | 11.83 | 356
PG&E | 2018-11-11 | 4:18 | 38.4341 | -122.5522 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102032588 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43415 | 0.17917 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1967 | 2018 | 11 | 11 | 4 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.8216 | 132_263 | <25mph | <15mph | HFTD - Distribution | 2018-11-11 04:18:00 | 1707 | 11.1813 | FALSE | <25mph |  |  |  | 0 | 0 | PG091 | 4.41 | 2018-11-11T07:10:00Z | 23.24 | 26 |  |  |  | 0 | 0 | PG091 | 4.41 | 2018-11-11T07:10:00Z | 23.24 | 50
PG&E | 2018-11-13 | 15:41 | 37.0644 | -121.9578 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101680441 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43417 | 0.65347 | Other | N.A. | N.A. | N.A. | Human Error | Grow house | Other/Unknown | 1973 | 2018 | 11 | 13 | 15 | 41 | 18-0099492 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 21484 | 1.9347 | 157_188 | <25mph | <15mph | HFTD - Distribution | 2018-11-13 15:41:00 | 1713 | 13.1257 | FALSE | <25mph | PG062 | 0.72 | 2018-11-13T08:00:00Z | 5.91 | 41 | PG057 | 4.36 | 2018-11-13T07:20:00Z | 9.86 | 181 | PG062 | 0.72 | 2018-11-13T08:10:00Z | 6.35 | 79 | PG057 | 4.36 | 2018-11-13T07:20:00Z | 9.86 | 351
PG&E | 2018-11-15 | 6:09 | 38.3599 | -122.3682 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102241814 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43419 | 0.25625 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1974 | 2018 | 11 | 15 | 6 | 9 | 18-0099862 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 441 | 10.2454 | 140_259 | <25mph | <15mph | HFTD - Distribution | 2018-11-15 06:09:00 | 1714 | 12.9788 | FALSE | <25mph | PG021 | 1.9 | 2018-11-15T07:20:00Z | 2.42 | 7 | PG021 | 1.9 | 2018-11-15T07:20:00Z | 2.42 | 21 | PG021 | 1.9 | 2018-11-15T08:20:00Z | 2.64 | 13 | PG021 | 1.9 | 2018-11-15T08:20:00Z | 2.64 | 39
PG&E | 2018-11-15 | 6:34 | 38.6082 | -120.9532 | Vegetation | Rural | < 0.25 Acres | Self Extinguished | N.A. | 101414740 | Unknown | 12000 | Conductor | Overhead | Yes | 43419 | 0.27361 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1975 | 2018 | 11 | 15 | 6 | 34 | 18-0099901 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 5325 | 11.5356 | 201_273 | <25mph | <15mph | HFTD - Distribution | 2018-11-15 06:34:00 | 1715 | 14.51 | FALSE | <25mph | BENC1 | 1.6 | 2018-11-15T07:59:00Z | 7 | 21 | BENC1 | 1.6 | 2018-11-15T07:59:00Z | 7 | 108 | BENC1 | 1.6 | 2018-11-15T08:59:00Z | 7 | 40 | E4740 | 7.49 | 2018-11-15T08:58:00Z | 8.99 | 206
PG&E | 2018-11-16 | 17:02 | 38.7574 | -120.9012 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101409894 | AT&T | 21000 | Conductor | Overhead | Yes | 43420 | 0.70972 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1976 | 2018 | 11 | 16 | 17 | 2 | 18-0100490 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 119860 | 5.5125 | 204_281 | <25mph | <15mph | HFTD - Distribution | 2018-11-16 17:02:00 | 1716 | 12.5682 | FALSE | <25mph | PG106 | 3.02 | 2018-11-16T07:40:00Z | 5.03 | 33 | PG068 | 7.29 | 2018-11-16T08:00:00Z | 6.8 | 136 | PG106 | 3.02 | 2018-11-16T09:00:00Z | 5.26 | 63 | PG068 | 7.29 | 2018-11-16T08:10:00Z | 8.55 | 264
PG&E | 2018-11-17 | 17:20 | 38.7082 | -120.6927 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101421319 | Unknown | 12000 | Conductor | Overhead | Yes | 43421 | 0.72222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1977 | 2018 | 11 | 17 | 17 | 20 | 18-0100697 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 35749 | 6.6792 | 213_278 | <25mph | <15mph | HFTD - Distribution | 2018-11-17 17:20:00 | 1717 | 12.841 | FALSE | <25mph | PG077 | 1.14 | 2018-11-17T07:50:00Z | 1.32 | 14 | PG104 | 6.43 | 2018-11-17T08:00:00Z | 13.8 | 72 | PG077 | 1.14 | 2018-11-17T07:50:00Z | 1.32 | 25 | PG104 | 6.43 | 2018-11-17T08:10:00Z | 14.03 | 137
PG&E | 2018-11-21 | 2:16 | 40.4383 | -124.3847 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101005309 | Frontier | 12000 | Conductor | Overhead | Yes | 43425 | 0.094444 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | Other/Unknown | 1982 | 2018 | 11 | 21 | 2 | 16 | 18-0101683 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 4834 | 28.3314 | 57_376 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-11-21 02:16:00 | 1722 | 31.7518 | FALSE | 25-40mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2018-12-12 | 12:09 | 38.727 | -120.7947 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 101404403 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43446 | 0.50625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1984 | 2018 | 12 | 12 | 12 | 9 | No ILIS or TOTL available | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.1462 | 208_279 | <25mph | <15mph | HFTD - Distribution | 2018-12-12 12:09:00 | 1724 | 13.5134 | FALSE | <25mph | PG068 | 1.89 | 2018-12-12T08:00:00Z | 4.16 | 37 | PG027 | 6.17 | 2018-12-12T08:00:00Z | 7 | 76 | PG068 | 1.89 | 2018-12-12T08:00:00Z | 4.16 | 73 | PG027 | 6.17 | 2018-12-12T08:50:00Z | 8.32 | 148
PG&E | 2018-12-14 | 10:32 | 40.4379 | -123.7834 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101009136 | Unknown | 12000 | Conductor | Overhead | Yes | 43448 | 0.43889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1985 | 2018 | 12 | 14 | 10 | 32 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 36.1442 | 82_375 | 25-40mph | 30-45mph | HFTD - Distribution | 2018-12-14 10:32:00 | 1725 | 36.1442 | FALSE | 25-40mph |  |  |  | 0 | 0 | PG204 | 5.47 | 2018-12-14T07:50:00Z | 2.64 | 7 |  |  |  | 0 | 0 | PG204 | 5.47 | 2018-12-14T08:40:00Z | 3.51 | 13
1. Butte | 2015-09-09 | 14:26 | 38.3297 | -120.7042 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1987 | 2015 | 9 | 9 | 14 | 26 |  | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 1353755 | 12.0917 | 212_257 | <25mph | <15mph | HFTD - Distribution | 2015-09-09 14:26:00 | 332 | 14.8248 | FALSE | <25mph |  |  |  | 0 | 0 | MTZC1 | 5.02 | 2015-09-09T06:56:00Z | 7 | 1 |  |  |  | 0 | 0 | MTZC1 | 5.02 | 2015-09-09T07:56:00Z | 8.99 | 2
2. Cascade (Neu Wind Complex) | 2017-10-08 | 23:45 | 39.322 | -121.4021 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1988 | 2017 | 10 | 8 | 23 | 45 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Equip Failure | Conductor | 0 | 17.3686 | 182_312 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 23:45:00 | 1213 | 29.7104 | FALSE | 25-40mph |  |  |  | 0 | 0 | BNGC1 | 4.15 | 2017-10-08T06:51:00Z | 3 | 1 |  |  |  | 0 | 0 | BNGC1 | 4.15 | 2017-10-08T07:51:00Z | 3 | 2
3. Redwood Valley (Mendocino Lake Complex) | 2017-10-08 | 23:36 | 39.2487 | -123.1663 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1989 | 2017 | 10 | 8 | 23 | 36 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 24.7673 | 107_309 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 23:36:00 | 1212 | 30.3049 | FALSE | 25-40mph |  |  |  | 0 | 0 | E7513 | 5.24 | 2017-10-08T06:28:00Z | 3 | 25 |  |  |  | 0 | 0 | E7513 | 5.24 | 2017-10-08T06:28:00Z | 3 | 49
4. Nuns (Central LNU Complex) | 2017-10-08 | 22:00 | 38.4041 | -122.5209 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1990 | 2017 | 10 | 8 | 22 | 0 |  | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 45.6439 | 134_262 | 40-55mph | >=45mph | HFTD - Distribution | 2017-10-08 22:00:00 | 1207 | 46.2981 | FALSE | 40-55mph | KENWW | 1.15 | 2017-10-08T07:00:00Z | 4.61 | 6 | F11WW | 4.55 | 2017-10-08T07:00:00Z | 14.2 | 16 | KENWW | 1.15 | 2017-10-08T07:00:00Z | 4.61 | 11 | F11WW | 4.55 | 2017-10-08T07:00:00Z | 14.2 | 29
5. Atlas (Southern LNU Complex) | 2017-10-08 | 21:52 | 38.3921 | -122.2437 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1991 | 2017 | 10 | 8 | 21 | 52 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 37.6357 | 146_261 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-08 21:52:00 | 1206 | 41.3099 | FALSE | 40-55mph | F0187 | 3.03 | 2017-10-08T07:00:00Z | 2.01 | 5 | ATLC1 | 5.83 | 2017-10-08T06:29:00Z | 10 | 6 | F0187 | 3.03 | 2017-10-08T07:00:00Z | 2.01 | 8 | ATLC1 | 5.83 | 2017-10-08T06:29:00Z | 10 | 15
7. Camp Fire | 2018-11-08 | 6:33 | 39.8134 | -121.4347 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 60000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1993 | 2018 | 11 | 8 | 6 | 33 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Conductor | 826291590 | 33.1236 | 181_339 | 25-40mph | 30-45mph | HFTD - Transmission | 2018-11-08 06:33:00 | 1699 | 39.0185 | FALSE | 25-40mph |  |  |  | 0 | 0 | JBGC1 | 6.08 | 2018-11-08T07:13:00Z | 44 | 1 |  |  |  | 0 | 0 | JBGC1 | 6.08 | 2018-11-08T08:13:00Z | 44.98 | 2
PG&E | 2019-01-16 | 0:17 | 38.0621 | -120.1964 | Vegetation | Conifer Forest | Structure Only | Cal Fire |  | 163661701 |  | 17000 | Conductor | Overhead | Yes | 43481 | 0.011806 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-01 | 2019 | 1 | 16 | 0 | 17 | 19-0010443 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1041827 | 14.8061 | 234_243 | <25mph | <15mph | HFTD - Distribution | 2019-01-16 00:17:00 | 1728 | 28.2081 | FALSE | 25-40mph | MOUC1 | 2.77 | 2019-01-16T07:02:00Z | 38.01 | 1 | MOUC1 | 2.77 | 2019-01-16T07:02:00Z | 38.01 | 22 | MOUC1 | 2.77 | 2019-01-16T07:02:00Z | 38.01 | 2 | MOUC1 | 2.77 | 2019-01-16T07:02:00Z | 38.01 | 41
PG&E | 2019-03-13 | 16:08 | 39.8831 | -122.5498 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 6Fn0313191607 |  | 12000 | Conductor | Overhead | Yes | 43537 | 0.67222 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-194 | 2019 | 3 | 13 | 16 | 8 | 19-0033617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 21012 | 20.7105 | 134_343 | <25mph | <15mph | HFTD - Distribution | 2019-03-13 16:08:00 | 1734 | 26.4067 | FALSE | 25-40mph | TCKC1 | 3.76 | 2019-03-13T06:28:00Z | 13 | 1 | EPKC1 | 5.75 | 2019-03-13T06:03:00Z | 28.01 | 9 | TCKC1 | 3.76 | 2019-03-13T07:28:00Z | 15.99 | 2 | EPKC1 | 5.75 | 2019-03-13T06:03:00Z | 28.01 | 17
PG&E | 2019-03-19 | 12:52 | 37.9956 | -120.3244 | Tree - cutting, 3rd party | Hardwood Forest | 1 meter - < 3 meters | Self Extinguished |  | 101045032 |  | 17000 | Conductor | Overhead | Yes | 43543 | 0.53611 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-187 | 2019 | 3 | 19 | 12 | 52 | 19-0035101 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 70602 | 12.9023 | 229_239 | <25mph | <15mph | HFTD - Distribution | 2019-03-19 12:52:00 | 1736 | 14.3226 | FALSE | <25mph | PG061 | 3.8 | 2019-03-19T07:00:00Z | 8.99 | 21 | PG166 | 7.85 | 2019-03-19T07:00:00Z | 18.86 | 68 | PG061 | 3.8 | 2019-03-19T08:00:00Z | 9.22 | 39 | PG166 | 7.85 | 2019-03-19T07:50:00Z | 20.4 | 127
PG&E | 2019-04-09 | 14:07 | 34.6311 | -119.9813 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Fire Dept | Santa Barbra County FD | 101863014 |  | 12000 | Conductor | Overhead | Yes | 43564 | 0.58819 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-263 | 2019 | 4 | 9 | 14 | 7 | 19-0040969 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 70756 | 38.5369 | 246_53 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-09 14:07:00 | 1737 | 43.1384 | FALSE | 40-55mph |  |  |  | 0 | 0 | SXWC1 | 5.08 | 2019-04-09T06:09:00Z | 7 | 13 |  |  |  | 0 | 0 | UCSE | 5.53 | 2019-04-09T07:40:00Z | 7.2 | 23
PG&E | 2019-04-09 | 15:27 | 37.7341 | -120.0776 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 101076921 |  | 21000 | Pole | Overhead | Yes | 43564 | 0.64375 | Vegetation |  | Veg. contact | Pole |  |  | Branch (Not overhanging, > 12ft) | 2019-313 | 2019 | 4 | 9 | 15 | 27 | 19-0041008 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 179862 | 22.8983 | 240_225 | <25mph | <15mph | HFTD - Distribution | 2019-04-09 15:27:00 | 1738 | 29.8749 | FALSE | 25-40mph | PG112 | 3.29 | 2019-04-09T06:20:00Z | 10.51 | 14 | PG155 | 7.32 | 2019-04-09T06:50:00Z | 12.71 | 29 | PG112 | 3.29 | 2019-04-09T07:50:00Z | 13.8 | 26 | PG155 | 7.32 | 2019-04-09T07:50:00Z | 19.51 | 54
PG&E | 2019-04-20 | 6:57 | 37.8686 | -121.6843 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | East County FD | Unknown |  | 17000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-321 | 2019 | 4 | 20 | 6 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 39.0116 | 170_232 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-20 06:57:00 | 1744 | 39.0116 | FALSE | 25-40mph | D3588 | 2.98 | 2019-04-20T07:00:00Z | 10 | 6 | PG066 | 6.23 | 2019-04-20T06:30:00Z | 37.04 | 109 | D3588 | 2.98 | 2019-04-20T07:51:00Z | 18.01 | 11 | KC83 | 4.32 | 2019-04-20T07:35:00Z | 43.73 | 207
PG&E | 2019-04-28 | 12:36 | 39.6756 | -121.5677 |  | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 100404366 |  | 12000 | Conductor | Overhead | Yes | 43583 | 0.525 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-166 | 2019 | 4 | 28 | 12 | 36 | 19-0046853 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 79810 | 6.7497 | 175_331 | <25mph | <15mph | HFTD - Distribution | 2019-04-28 12:36:00 | 1752 | 11.2512 | FALSE | <25mph | PG295 | 0.21 | 2019-04-28T06:50:00Z | 9.22 | 7 | PG295 | 0.21 | 2019-04-28T06:50:00Z | 9.22 | 25 | PG295 | 0.21 | 2019-04-28T06:50:00Z | 9.22 | 13 | JBGC1 | 5.9 | 2019-04-28T07:13:00Z | 11.01 | 46
PG&E | 2019-05-08 | 10:23 | 39.3851 | -122.557 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | Colusa FD | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-312 | 2019 | 5 | 8 | 10 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 11.1721 | 133_316 | <25mph | <15mph | HFTD - Distribution | 2019-05-08 10:23:00 | 1764 | 11.4886 | FALSE | <25mph | SYWC1 | 1.49 | 2019-05-08T06:26:00Z | 4 | 1 | PG294 | 6.56 | 2019-05-08T06:00:00Z | 10.74 | 16 | SYWC1 | 1.49 | 2019-05-08T07:26:00Z | 4.99 | 2 | PG294 | 6.56 | 2019-05-08T06:00:00Z | 10.74 | 30
PG&E | 2019-05-10 | 14:52 | 40.704 | -122.8314 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Fire Dept | Lewiston FD | Keswick-Trinity 60Kv Line |  | 60000 | Conductor | Overhead | Yes | 43595 | 0.61944 | Vegetation |  | Contact from Object - Other | Electric Facility |  |  | no-match | 2019-301 | 2019 | 5 | 10 | 14 | 52 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.0535 | 123_389 | <25mph | <15mph | HFTD - Transmission | 2019-05-10 14:52:00 | 1766 | 13.0849 | FALSE | <25mph |  |  |  | 0 | 0 | TCAC1 | 5.87 | 2019-05-10T06:28:00Z | 14.99 | 5 |  |  |  | 0 | 0 | TCAC1 | 5.87 | 2019-05-10T06:28:00Z | 14.99 | 8
PG&E | 2019-05-15 | 21:31 | 38.5731 | -122.9603 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Unknown |  | 103931177 |  | 12000 | Conductor | Overhead | Yes | 43600 | 0.89653 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-316 | 2019 | 5 | 15 | 21 | 31 | 19-0052480 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 27780 | 16.5892 | 115_271 | <25mph | <15mph | HFTD - Distribution | 2019-05-15 21:31:00 | 1774 | 23.8094 | FALSE | <25mph | D9841 | 3.34 | 2019-05-15T07:00:00Z | 1.01 | 5 | AR798 | 4.72 | 2019-05-15T06:56:00Z | 10 | 43 | D9841 | 3.34 | 2019-05-15T07:00:00Z | 1.01 | 8 | AR798 | 4.72 | 2019-05-15T06:56:00Z | 10 | 84
PG&E | 2019-05-17 | 15:12 | 38.4797 | -123.1486 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 42811111 |  | 12000 | Conductor | Overhead | Yes | 43602 | 0.63333 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-200 | 2019 | 5 | 17 | 15 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 19.5511 | 107_266 | <25mph | <15mph | HFTD - Distribution | 2019-05-17 15:12:00 | 1775 | 20.334 | FALSE | <25mph | E8483 | 3.61 | 2019-05-17T06:30:00Z | 8.99 | 5 | E8483 | 3.61 | 2019-05-17T06:30:00Z | 8.99 | 17 | E8483 | 3.61 | 2019-05-17T06:30:00Z | 8.99 | 9 | E8483 | 3.61 | 2019-05-17T06:30:00Z | 8.99 | 29
PG&E | 2019-05-17 | 18:54 | 38.0476 | -122.2064 | Bird Found | Urban | 3 meters - 0.25 Acres | Fire Dept | Crockett FD | 2Jt0517191854 |  | 21000 | Pole | Overhead | Yes | 43602 | 0.7875 | Contact - Animal - Bird |  | Animal contact | Pole | Animal Contact |  | Other/Unknown | 2019-02 | 2019 | 5 | 17 | 18 | 54 | 19-0053464 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 20.6557 | 147_242 | <25mph | <15mph | HFTD - Distribution | 2019-05-17 18:54:00 | 1776 | 21.5879 | FALSE | <25mph | DPXC1 | 2.96 | 2019-05-17T06:24:00Z | 21.99 | 17 | UPBC1 | 4.72 | 2019-05-17T06:42:00Z | 32.97 | 102 | DPXC1 | 2.96 | 2019-05-17T06:24:00Z | 21.99 | 32 | UPBC1 | 4.72 | 2019-05-17T06:42:00Z | 32.97 | 192
PG&E | 2019-05-24 | 15:03 | 35.1696 | -120.5103 |  | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 40589503 |  | 500000 | Pole | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-100 | 2019 | 5 | 24 | 15 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 14.866 | 222_83 | <25mph | <15mph | HFTD - Transmission | 2019-05-24 15:03:00 | 1780 | 15.7146 | FALSE | <25mph | C9687 | 3.56 | 2019-05-24T06:55:00Z | 0 | 12 | PG168 | 5.97 | 2019-05-24T07:00:00Z | 4.83 | 46 | C9687 | 3.56 | 2019-05-24T07:55:00Z | 0 | 24 | PG168 | 5.97 | 2019-05-24T07:00:00Z | 4.83 | 90
PG&E | 2019-05-29 | 16:54 | 37.0371 | -119.5209 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 100680674 |  | 12000 | Pole | Overhead | Yes | 43614 | 0.70417 | Vegetation |  | Veg. contact | Pole |  |  | Dead | 2019-202 | 2019 | 5 | 29 | 16 | 54 | 19-0059237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 6780 | 6.6167 | 265_186 | <25mph | <15mph | HFTD - Distribution | 2019-05-29 16:54:00 | 1787 | 9.3593 | FALSE | <25mph | PG219 | 2.84 | 2019-05-29T06:40:00Z | 3.06 | 8 | PG202 | 6.2 | 2019-05-29T06:30:00Z | 7.25 | 57 | PG219 | 2.84 | 2019-05-29T08:00:00Z | 4.16 | 15 | PG202 | 6.2 | 2019-05-29T06:30:00Z | 7.25 | 97
PG&E | 2019-05-29 | 20:25 | 39.0194 | -121.0608 |  | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match |  | 2019 | 5 | 29 | 20 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 14.177 | 197_295 | <25mph | <15mph | HFTD - Distribution | 2019-05-29 20:25:00 | 1789 | 14.177 | FALSE | <25mph | PG349 | 3.78 | 2019-05-29T06:50:00Z | 4.83 | 23 | PG367 | 7.83 | 2019-05-29T06:20:00Z | 7 | 59 | PG349 | 3.78 | 2019-05-29T07:50:00Z | 5.91 | 42 | PG332 | 6.22 | 2019-05-29T07:40:00Z | 8.77 | 111
PG&E | 2019-05-30 | 8:18 | 35.7005 | -120.8104 | Vehicle | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 101871463 |  | 12000 | Pole | Overhead | Yes | 43615 | 0.34583 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-274 | 2019 | 5 | 30 | 8 | 18 | 19-0059906 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 171603 | 10.8019 | 208_112 | <25mph | <15mph | HFTD - Distribution | 2019-05-30 08:18:00 | 1791 | 17.2262 | FALSE | <25mph |  |  |  | 0 | 0 | D4060 | 4.58 | 2019-05-30T06:02:00Z | 8.01 | 12 |  |  |  | 0 | 0 | D4060 | 4.58 | 2019-05-30T06:02:00Z | 8.01 | 23
PG&E | 2019-05-31 | 15:25 | 40.4431 | -121.8211 |  | Hardwood Woodland | 1 meter - < 3 meters | Self Extinguished |  | 101556319 |  | 12000 | Conductor | Overhead | Yes | 43616 | 0.64236 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-88 | 2019 | 5 | 31 | 15 | 25 | 19-0060901 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 55546 | 8.5736 | 165_374 | <25mph | <15mph | HFTD - Distribution | 2019-05-31 15:25:00 | 1795 | 18.5418 | FALSE | <25mph | PG313 | 2.94 | 2019-05-31T06:50:00Z | 16.22 | 15 | PG193 | 6.12 | 2019-05-31T06:40:00Z | 18.41 | 22 | PG130 | 1.76 | 2019-05-31T07:50:00Z | 17.54 | 33 | PG193 | 6.12 | 2019-05-31T08:00:00Z | 22.57 | 52
PG&E | 2019-06-03 | 14:31 | 40.6822 | -122.2806 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 101466598 |  | 12000 | Transformer | Overhead | Yes | 43619 | 0.60486 | Equipment - Overloaded | Transformer |  |  |  |  | no-match | 2019-161 | 2019 | 6 | 3 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 6.522 | 146_387 | <25mph | <15mph | HFTD - Distribution | 2019-06-03 14:31:00 | 1798 | 12.4331 | FALSE | <25mph |  |  |  | 0 | 0 | PG307 | 4.7 | 2019-06-03T06:50:00Z | 2.42 | 19 |  |  |  | 0 | 0 | PG307 | 4.7 | 2019-06-03T08:00:00Z | 3.94 | 38
PG&E | 2019-06-03 | 14:47 | 40.4419 | -122.3036 |  | Herbaceous | 1 meter - < 3 meters | Fire Dept | Anderson FD | 101495889 |  | 12000 | Insulator | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-456 | 2019 | 6 | 3 | 14 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 9.9807 | 145_374 | <25mph | <15mph | HFTD - Distribution | 2019-06-03 14:47:00 | 1799 | 16.209 | FALSE | <25mph | AP525 | 3.17 | 2019-06-03T06:55:00Z | 0 | 6 | PG174 | 6.35 | 2019-06-03T06:00:00Z | 10.29 | 17 | AP525 | 3.17 | 2019-06-03T07:55:00Z | 0 | 12 | PG174 | 6.35 | 2019-06-03T06:00:00Z | 10.29 | 33
PG&E | 2019-06-06 | 9:01 | 35.6384 | -118.9687 | Bird Found | Herbaceous | 0.25 - 10 Acres | Fire Dept | Kern County FD | 100216096 |  | 21000 | Conductor | Overhead | No |  |  | Contact - Animal - Other |  | Animal contact |  | Animal Contact |  | no-match | 2019-228 | 2019 | 6 | 6 | 9 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 4.6796 | 291_110 | <25mph | <15mph | HFTD - Distribution | 2019-06-06 09:01:00 | 1803 | 21.162 | FALSE | <25mph | PG159 | 2.52 | 2019-06-06T06:50:00Z | 9.86 | 14 | PG159 | 2.52 | 2019-06-06T06:50:00Z | 9.86 | 28 | PG159 | 2.52 | 2019-06-06T06:50:00Z | 9.86 | 26 | PG159 | 2.52 | 2019-06-06T06:50:00Z | 9.86 | 52
PG&E | 2019-06-06 | 20:30 | 38.4969 | -122.6435 |  | Barren/Other | < 1 meter | Self Extinguished |  | Unknown |  | 230000 | Circuit Breaker | Overhead | Yes | 43622 | 0.85417 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | no-match | 2019-102 | 2019 | 6 | 6 | 20 | 30 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 16.883 | 129_267 | <25mph | <15mph | HFTD - Transmission | 2019-06-06 20:30:00 | 1804 | 23.129 | FALSE | <25mph | RSAC1 | 3.91 | 2019-06-06T06:29:00Z | 8.01 | 17 | PG162 | 5.7 | 2019-06-06T06:00:00Z | 23.02 | 91 | RSAC1 | 3.91 | 2019-06-06T07:29:00Z | 11.01 | 34 | PG162 | 5.7 | 2019-06-06T06:00:00Z | 23.02 | 172
PG&E | 2019-06-07 | 9:58 | 38.7285 | -123.3528 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 042861101 |  | 21000 | Conductor | Overhead | Yes | 43623 | 0.41528 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-358 | 2019 | 6 | 7 | 9 | 58 | 19-0064216 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 5301 | 16.456 | 98_280 | <25mph | <15mph | HFTD - Distribution | 2019-06-07 09:58:00 | 1805 | 19.4921 | FALSE | <25mph | OAAC1 | 2.48 | 2019-06-07T06:33:00Z | 35.99 | 1 | OAAC1 | 2.48 | 2019-06-07T06:33:00Z | 35.99 | 13 | OAAC1 | 2.48 | 2019-06-07T06:33:00Z | 35.99 | 2 | OAAC1 | 2.48 | 2019-06-07T06:33:00Z | 35.99 | 25
PG&E | 2019-06-08 | 18:51 | 38.6105 | -122.9732 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 42751113 |  | 12000 | Conductor | Overhead | Yes | 43624 | 0.78542 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-355 | 2019 | 6 | 8 | 18 | 51 | 19-0064689 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 44664 | 14.8219 | 114_273 | <25mph | <15mph | HFTD - Distribution | 2019-06-08 18:51:00 | 1812 | 19.8533 | FALSE | <25mph |  |  |  | 0 | 0 | PG243 | 5.7 | 2019-06-08T06:20:00Z | 12.48 | 51 |  |  |  | 0 | 0 | PG243 | 5.7 | 2019-06-08T07:10:00Z | 14.47 | 100
PG&E | 2019-06-10 | 13:29 | 38.8137 | -120.9433 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Other | Customer | 153652109 |  | 21000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-243 | 2019 | 6 | 10 | 13 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.2437 | 202_284 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 13:29:00 | 1823 | 9.9566 | FALSE | <25mph | PLTC1 | 3.76 | 2019-06-10T06:56:00Z | 4 | 15 | PG073 | 7.24 | 2019-06-10T07:00:00Z | 11.18 | 62 | PLTC1 | 3.76 | 2019-06-10T07:56:00Z | 4 | 28 | PG073 | 7.24 | 2019-06-10T07:10:00Z | 14.25 | 117
PG&E | 2019-06-10 | 16:18 | 38.1107 | -122.9025 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 42291101 |  | 12000 | Conductor | Overhead | Yes | 43626 | 0.67917 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-401 | 2019 | 6 | 10 | 16 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.6937 | 117_246 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 16:18:00 | 1826 | 12.047 | FALSE | <25mph | PG046 | 2.87 | 2019-06-10T06:40:00Z | 12.93 | 21 | PG046 | 2.87 | 2019-06-10T06:40:00Z | 12.93 | 21 | PG046 | 2.87 | 2019-06-10T06:40:00Z | 12.93 | 39 | PG046 | 2.87 | 2019-06-10T06:40:00Z | 12.93 | 39
PG&E | 2019-06-10 | 16:34 | 38.821 | -120.846 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Garden Valley FD | 153082106 |  | 21000 | Conductor | Overhead | Yes | 43626 | 0.69028 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-372 | 2019 | 6 | 10 | 16 | 34 | 19-0065481 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14169 | 8.5329 | 206_284 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 16:34:00 | 1827 | 15.7607 | FALSE | <25mph | PG180 | 3.67 | 2019-06-10T07:00:00Z | 6.35 | 14 | PG104 | 6.61 | 2019-06-10T07:00:00Z | 14.47 | 81 | PG180 | 3.67 | 2019-06-10T08:00:00Z | 6.58 | 26 | PG104 | 6.61 | 2019-06-10T07:00:00Z | 14.47 | 154
PG&E | 2019-06-13 | 0:30 | 36.5759 | -121.7284 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire |  | 182222104 |  | 21000 | Conductor | Overhead | Yes | 43629 | 0.020833 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-341 | 2019 | 6 | 13 | 0 | 30 | 19-0067072 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 148986 | 9.1422 | 167_161 | <25mph | <15mph | HFTD - Distribution | 2019-06-13 00:30:00 | 1838 | 14.9804 | FALSE | <25mph | PG268 | 1.87 | 2019-06-13T06:50:00Z | 4.61 | 11 | PG318 | 7.33 | 2019-06-13T07:00:00Z | 12.28 | 29 | PG268 | 1.87 | 2019-06-13T07:30:00Z | 6.8 | 21 | PG318 | 7.33 | 2019-06-13T08:00:00Z | 15.99 | 55
PG&E | 2019-06-14 | 4:38 | 37.5525 | -120.3254 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 011/008 |  | 70000 | Insulator | Overhead | No |  |  | Equipment - PG&E | Insulator |  |  |  |  | no-match | 2019-79 | 2019 | 6 | 14 | 4 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | N.A. | 8.8948 | 229_214 | <25mph | <15mph | HFTD - Transmission | 2019-06-14 04:38:00 | 1839 | 16.3246 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2019-06-15 | 14:08 | 38.8802 | -122.6125 | Tree - cutting, 3rd party | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 43361103 |  | 12000 | Pole | Overhead | Yes | 43631 | 0.58889 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | Other/Unknown | 2019-19 | 2019 | 6 | 15 | 14 | 8 | 19-0068074 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 259562 | 11.2331 | 130_288 | <25mph | <15mph | HFTD - Distribution | 2019-06-15 14:08:00 | 1841 | 15.703 | FALSE | <25mph | PG110 | 3.62 | 2019-06-15T06:00:00Z | 7 | 14 | KELC1 | 5.5 | 2019-06-15T06:57:00Z | 14.99 | 58 | PG110 | 3.62 | 2019-06-15T06:00:00Z | 7 | 26 | KELC1 | 5.5 | 2019-06-15T07:57:00Z | 14.99 | 106
PG&E | 2019-06-17 | 10:25 | 38.511 | -122.2134 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 43051101 |  | 12000 | Conductor | Overhead | Yes | 43633 | 0.43403 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-84 | 2019 | 6 | 17 | 10 | 25 | 19-0068579 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 306900 | 10.2943 | 147_267 | <25mph | <15mph | HFTD - Distribution | 2019-06-17 10:25:00 | 1843 | 15.8677 | FALSE | <25mph | PG048 | 0.14 | 2019-06-17T06:30:00Z | 11.63 | 8 | PG048 | 0.14 | 2019-06-17T06:30:00Z | 11.63 | 50 | PG048 | 0.14 | 2019-06-17T06:30:00Z | 11.63 | 15 | PG048 | 0.14 | 2019-06-17T06:30:00Z | 11.63 | 93
PG&E | 2019-06-18 | 19:49 | 35.8876 | -120.9217 | Bird Found | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Pole | Overhead | Yes | 43634 | 0.82569 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | no-match | 2019-55 | 2019 | 6 | 18 | 19 | 49 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 15.5935 | 203_122 | <25mph | <15mph | HFTD - Distribution | 2019-06-18 19:49:00 | 1852 | 21.7258 | FALSE | <25mph |  |  |  | 0 | 0 | PG360 | 6.27 | 2019-06-18T06:10:00Z | 16.89 | 15 |  |  |  | 0 | 0 | RBYC1 | 6.84 | 2019-06-18T07:12:00Z | 17 | 28
PG&E | 2019-06-19 | 11:44 | 39.8612 | -121.6907 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100400933 |  | 12000 | Conductor | Overhead | Yes | 43635 | 0.48889 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-224 | 2019 | 6 | 19 | 11 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.9144 | 170_342 | <25mph | <15mph | HFTD - Distribution | 2019-06-19 11:44:00 | 1855 | 12.1329 | FALSE | <25mph | PG337 | 3.36 | 2019-06-19T06:10:00Z | 5.48 | 26 | PG339 | 7.65 | 2019-06-19T06:40:00Z | 10.29 | 73 | PG337 | 3.36 | 2019-06-19T07:20:00Z | 7.25 | 50 | CSTC1 | 4.21 | 2019-06-19T07:51:00Z | 11.01 | 132
PG&E | 2019-06-26 | 13:14 | 40.0185 | -122.4107 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | Circuit Id 103331101 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43642 | 0.55139 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-331 | 2019 | 6 | 26 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2684 | 140_351 | <25mph | <15mph | HFTD - Distribution | 2019-06-26 13:14:00 | 1870 | 19.4401 | FALSE | <25mph |  |  |  | 0 | 0 | PG276 | 6.5 | 2019-06-26T07:00:00Z | 13.6 | 14 |  |  |  | 0 | 0 | PG276 | 6.5 | 2019-06-26T07:00:00Z | 13.6 | 26
PG&E | 2019-06-27 | 2:23 | 36.8198 | -119.3334 | Bird Found | Hardwood Woodland | 0.25 - 10 Acres | Self Extinguished |  | Kings River-Sanger-Reedley 115Kv At 16/089 |  | 115000 | Insulator | Overhead | Yes | 43643 | 0.099306 | Equipment - PG&E | Insulator |  |  |  |  | no-match | 2019-104 | 2019 | 6 | 27 | 2 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | N.A. | 13.572 | 273_175 | <25mph | <15mph | HFTD - Transmission | 2019-06-27 02:23:00 | 1872 | 13.572 | FALSE | <25mph | PG408 | 3.33 | 2019-06-27T06:40:00Z | 4.83 | 7 | PG233 | 6.47 | 2019-06-27T06:20:00Z | 7.67 | 21 | PG408 | 3.33 | 2019-06-27T06:40:00Z | 4.83 | 13 | PG233 | 6.47 | 2019-06-27T06:20:00Z | 7.67 | 40
PG&E | 2019-07-01 | 2:15 | 38.2955 | -120.8335 |  | Shrub | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-252 | 2019 | 7 | 1 | 2 | 15 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.9479 | 207_255 | <25mph | <15mph | HFTD - Distribution | 2019-07-01 02:15:00 | 1878 | 14.184 | FALSE | <25mph |  |  |  | 0 | 0 | TS389 | 4.67 | 2019-07-01T06:53:00Z | 14 | 32 |  |  |  | 0 | 0 | TS389 | 4.67 | 2019-07-01T06:53:00Z | 14 | 60
PG&E | 2019-07-06 | 14:22 | 34.6388 | -119.9695 |  | Herbaceous | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | 182721104 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43652 | 0.59861 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-153 | 2019 | 7 | 6 | 14 | 22 | 19-0074960 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 14213 | 21.2189 | 246_54 | <25mph | <15mph | HFTD - Distribution | 2019-07-06 14:22:00 | 1888 | 23.8361 | FALSE | <25mph |  |  |  | 0 | 0 | FGMC1 | 6.93 | 2019-07-06T06:35:00Z | 8.99 | 22 |  |  |  | 0 | 0 | FGMC1 | 6.93 | 2019-07-06T07:35:00Z | 8.99 | 42
PG&E | 2019-07-11 | 15:27 | 39.5657 | -120.6614 | Vegetation | Conifer Forest | 0.25 - 10 Acres | Unknown |  | 100102596 |  | 12000 | Pole | Overhead | Yes | 43657 | 0.64375 | Vegetation |  | Veg. contact | Pole |  |  | no-match | 2019-03 | 2019 | 7 | 11 | 15 | 27 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 13.7516 | 214_325 | <25mph | <15mph | HFTD - Distribution | 2019-07-11 15:27:00 | 1894 | 13.818 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2019-07-13 | 13:13 | 34.7273 | -120.4357 |  | Shrub | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | Y44 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43659 | 0.55069 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-154 | 2019 | 7 | 13 | 13 | 13 | 19-0077070 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 18256 | 12.2026 | 225_58 | <25mph | <15mph | HFTD - Distribution | 2019-07-13 13:13:00 | 1900 | 12.8932 | FALSE | <25mph | VDBC1 | 3.58 | 2019-07-13T06:22:00Z | 4.99 | 5 | VDBC1 | 3.58 | 2019-07-13T06:22:00Z | 4.99 | 24 | VDBC1 | 3.58 | 2019-07-13T07:22:00Z | 4.99 | 10 | VDBC1 | 3.58 | 2019-07-13T07:22:00Z | 4.99 | 47
PG&E | 2019-07-15 | 7:51 | 38.3266 | -122.568 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 42721104 |  | 12000 | Conductor | Overhead | Yes | 43661 | 0.32708 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-343 | 2019 | 7 | 15 | 7 | 51 | 19-0077351 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2348 | 31.0114 | 132_257 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-07-15 07:51:00 | 1903 | 35.3209 | FALSE | 25-40mph | PG177 | 1.33 | 2019-07-15T07:00:00Z | 23.02 | 11 | PG177 | 1.33 | 2019-07-15T07:00:00Z | 23.02 | 46 | PG177 | 1.33 | 2019-07-15T08:00:00Z | 23.24 | 21 | PG177 | 1.33 | 2019-07-15T08:00:00Z | 23.24 | 90
PG&E | 2019-07-16 | 17:31 | 40.1691 | -122.3053 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103541103 |  | 12000 | Conductor | Overhead | Yes | 43662 | 0.72986 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-375 | 2019 | 7 | 16 | 17 | 31 | 19-0078094 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 45533 | 5.1951 | 144_359 | <25mph | <15mph | HFTD - Distribution | 2019-07-16 17:31:00 | 1907 | 20.1358 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2019-07-17 | 7:49 | 34.5066 | -120.2247 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Santa Barbara County FD | 4Bx0717190747 |  | 12000 | Other | Overhead | Yes | 43663 | 0.32569 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-425 | 2019 | 7 | 17 | 7 | 49 | 19-0078239 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 19608 | 17.3045 | 235_46 | <25mph | <15mph | HFTD - Distribution | 2019-07-17 07:49:00 | 1908 | 28.4942 | FALSE | 25-40mph | GVTC1 | 1.4 | 2019-07-17T06:09:00Z | 40 | 8 | GVTC1 | 1.4 | 2019-07-17T06:09:00Z | 40 | 8 | GVTC1 | 1.4 | 2019-07-17T07:09:00Z | 40 | 15 | GVTC1 | 1.4 | 2019-07-17T07:09:00Z | 40 | 15
PG&E | 2019-07-18 | 19:57 | 37.081 | -119.4865 |  | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | No |  |  | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-09 | 2019 | 7 | 18 | 19 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.8761 | 266_189 | <25mph | <15mph | HFTD - Distribution | 2019-07-18 19:57:00 | 1914 | 14.7588 | FALSE | <25mph | PG389 | 1.62 | 2019-07-18T06:00:00Z | 8.77 | 39 | SE370 | 7.06 | 2019-07-18T06:10:00Z | 11.41 | 104 | PG389 | 1.62 | 2019-07-18T06:00:00Z | 8.77 | 74 | SE370 | 7.06 | 2019-07-18T06:10:00Z | 11.41 | 195
PG&E | 2019-07-18 | 10:27 | 38.3033 | -120.6718 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | B561 |  | 12000 | Other | Overhead | Yes | 43664 | 0.43542 | Equipment - PG&E | Other |  |  |  |  | Other/Unknown | 2019-68 | 2019 | 7 | 18 | 10 | 27 | 19-0078904 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45558 | 8.6789 | 214_256 | <25mph | <15mph | HFTD - Distribution | 2019-07-18 10:27:00 | 1910 | 16.0413 | FALSE | <25mph | PG372 | 0.86 | 2019-07-18T07:00:00Z | 4.83 | 14 | TS389 | 7.11 | 2019-07-18T06:53:00Z | 7 | 59 | PG372 | 0.86 | 2019-07-18T07:50:00Z | 7.67 | 26 | PG372 | 0.86 | 2019-07-18T07:50:00Z | 7.67 | 110
PG&E | 2019-07-19 | 11:59 | 37.9162 | -120.349 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 163351703 |  | 17000 | Conductor | Overhead | Yes | 43665 | 0.49931 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-376 | 2019 | 7 | 19 | 11 | 59 | 19-0079030 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24042 | 10.7946 | 228_234 | <25mph | <15mph | HFTD - Distribution | 2019-07-19 11:59:00 | 1915 | 10.8841 | FALSE | <25mph | PG166 | 2.3 | 2019-07-19T06:00:00Z | 10.96 | 32 | PG166 | 2.3 | 2019-07-19T06:00:00Z | 10.96 | 51 | PG166 | 2.3 | 2019-07-19T06:00:00Z | 10.96 | 60 | PG166 | 2.3 | 2019-07-19T06:00:00Z | 10.96 | 95
PG&E | 2019-07-21 | 12:46 | 37.0517 | -122.1522 | Vegetation | Urban | 1 meter - < 3 meters | Cal Fire |  | 82931101 |  | 12000 | Conductor | Overhead | Yes | 43667 | 0.53194 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-377 | 2019 | 7 | 21 | 12 | 46 | 19-0079583 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 89102 | 9.1847 | 149_187 | <25mph | <15mph | HFTD - Distribution | 2019-07-21 12:46:00 | 1918 | 10.1366 | FALSE | <25mph | PG047 | 1.66 | 2019-07-21T06:50:00Z | 2.19 | 7 | PG262 | 7.56 | 2019-07-21T06:50:00Z | 5.91 | 107 | PG047 | 1.66 | 2019-07-21T07:40:00Z | 2.86 | 13 | PG262 | 7.56 | 2019-07-21T06:50:00Z | 5.91 | 201
PG&E | 2019-07-21 | 10:14 | 38.9716 | -120.9991 |  | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire | Placer Hill FD | 152241102 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43667 | 0.42639 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-127 | 2019 | 7 | 21 | 10 | 14 | 19-0079578 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 32850 | 6.8026 | 199_293 | <25mph | <15mph | HFTD - Distribution | 2019-07-21 10:14:00 | 1916 | 10.8012 | FALSE | <25mph | C0713 | 3.87 | 2019-07-21T07:00:00Z | 0 | 16 | PG349 | 6.34 | 2019-07-21T06:40:00Z | 3.94 | 45 | C0713 | 3.87 | 2019-07-21T07:59:00Z | 0 | 31 | PG349 | 6.34 | 2019-07-21T08:00:00Z | 5.03 | 90
PG&E | 2019-07-22 | 8:11 | 38.7687 | -120.9633 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | El Dorado County FD | 6Ht0722190809 |  | 21000 | Other | Overhead | Yes | 43668 | 0.34097 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-49 | 2019 | 7 | 22 | 8 | 11 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.6529 | 201_281 | <25mph | <15mph | HFTD - Distribution | 2019-07-22 08:11:00 | 1920 | 11.9774 | FALSE | <25mph | PG027 | 3.71 | 2019-07-22T06:20:00Z | 5.48 | 14 | PG111 | 5.58 | 2019-07-22T06:00:00Z | 5.48 | 121 | PG027 | 3.71 | 2019-07-22T07:30:00Z | 8.32 | 26 | PG027 | 3.71 | 2019-07-22T07:30:00Z | 8.32 | 231
PG&E | 2019-07-22 | 21:39 | 38.8618 | -121.1044 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 152561103 |  | 12000 | Conductor | Overhead | Yes | 43668 | 0.90208 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-336 | 2019 | 7 | 22 | 21 | 39 | 19-0080025 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 9842 | 9.5984 | 195_286 | <25mph | <15mph | HFTD - Distribution | 2019-07-22 21:39:00 | 1921 | 13.5446 | FALSE | <25mph | D8862 | 2.4 | 2019-07-22T06:15:00Z | 4 | 5 | F5165 | 7.23 | 2019-07-22T06:55:00Z | 4 | 29 | D8862 | 2.4 | 2019-07-22T07:15:00Z | 4 | 8 | F5165 | 7.23 | 2019-07-22T07:40:00Z | 4 | 53
PG&E | 2019-07-23 | 16:31 | 37.2447 | -121.9999 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Santa Clara County FD | 83371104 |  | 12000 | Conductor | Overhead | Yes | 43669 | 0.68819 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-378 | 2019 | 7 | 23 | 16 | 31 | 19-0080428 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 19250 | 12.7214 | 156_198 | <25mph | <15mph | HFTD - Distribution | 2019-07-23 16:31:00 | 1922 | 12.7214 | FALSE | <25mph | PG154 | 2.55 | 2019-07-23T06:50:00Z | 10.96 | 81 | PG154 | 2.55 | 2019-07-23T06:50:00Z | 10.96 | 224 | PG154 | 2.55 | 2019-07-23T06:50:00Z | 10.96 | 156 | PG154 | 2.55 | 2019-07-23T06:50:00Z | 10.96 | 439
PG&E | 2019-07-23 | 16:55 | 37.2128 | -119.505 | Gun Shot | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | 252521103 |  | 12000 | Conductor | Overhead | Yes | 43669 | 0.70486 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-434 | 2019 | 7 | 23 | 16 | 55 | 19-0080383 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 513358 | 13.6168 | 265_196 | <25mph | <15mph | HFTD - Distribution | 2019-07-23 16:55:00 | 1923 | 13.6168 | FALSE | <25mph | PG467 | 3.77 | 2019-07-23T06:40:00Z | 15.99 | 9 | PG467 | 3.77 | 2019-07-23T06:40:00Z | 15.99 | 30 | PG467 | 3.77 | 2019-07-23T07:20:00Z | 15.99 | 16 | PG467 | 3.77 | 2019-07-23T07:20:00Z | 15.99 | 55
PG&E | 2019-07-25 | 0:15 | 39.0662 | -120.9754 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Placer Hills FD | 152491101 |  | 12000 | Conductor | Overhead | Yes | 43671 | 0.010417 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-379 | 2019 | 7 | 25 | 0 | 15 | 19-0080924 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7845 | 8.7511 | 200_298 | <25mph | <15mph | HFTD - Distribution | 2019-07-25 00:15:00 | 1927 | 11.2312 | FALSE | <25mph | PG377 | 2.2 | 2019-07-25T07:00:00Z | 4.16 | 31 | PG032 | 7.47 | 2019-07-25T06:30:00Z | 5.91 | 54 | PG377 | 2.2 | 2019-07-25T07:10:00Z | 5.7 | 61 | PG032 | 7.47 | 2019-07-25T07:10:00Z | 8.55 | 108
PG&E | 2019-07-25 | 7:39 | 39.1735 | -123.5763 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Oj 2 P/Ss Of Cgc# 215532055340 |  | 12000 | Other | Overhead | Yes | 43671 | 0.31875 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-380 | 2019 | 7 | 25 | 7 | 39 | 19-0080947 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 790 | 2.0398 | 89_305 | <25mph | <15mph | HFTD - Distribution | 2019-07-25 07:39:00 | 1928 | 13.3511 | FALSE | <25mph |  |  |  | 0 | 0 | PG485 | 4.89 | 2019-07-25T06:30:00Z | 3.74 | 18 |  |  |  | 0 | 0 | PG485 | 4.89 | 2019-07-25T06:30:00Z | 3.74 | 35
PG&E | 2019-07-26 | 12:03 | 38.8003 | -120.8258 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire |  | 153082106 |  | 21000 | Conductor | Overhead | Yes | 43672 | 0.50208 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-381 | 2019 | 7 | 26 | 12 | 3 | 19-0081559 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 16465 | 9.8294 | 207_283 | <25mph | <15mph | HFTD - Distribution | 2019-07-26 12:03:00 | 1931 | 11.2958 | FALSE | <25mph | E5691 | 3.74 | 2019-07-26T06:58:00Z | 0 | 12 | PG068 | 5.03 | 2019-07-26T06:30:00Z | 5.48 | 111 | E5691 | 3.74 | 2019-07-26T07:58:00Z | 0 | 24 | PG180 | 4.28 | 2019-07-26T07:10:00Z | 5.48 | 215
PG&E | 2019-07-27 | 8:22 | 40.3789 | -122.1873 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Self Extinguished |  | 103461102 |  | 12000 | Conductor | Overhead | Yes | 43673 | 0.34861 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-382 | 2019 | 7 | 27 | 8 | 22 | 19-0081756 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 456 | 4.4493 | 149_370 | <25mph | <15mph | HFTD - Distribution | 2019-07-27 08:22:00 | 1935 | 12.5056 | FALSE | <25mph | PG335 | 2.07 | 2019-07-27T06:00:00Z | 9.64 | 7 | PG320 | 4.66 | 2019-07-27T06:50:00Z | 11.41 | 21 | PG335 | 2.07 | 2019-07-27T06:00:00Z | 9.64 | 13 | PG320 | 4.66 | 2019-07-27T06:50:00Z | 11.41 | 39
PG&E | 2019-07-27 | 16:17 | 37.7266 | -120.3246 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire |  | 252811102 |  | 12000 | Conductor | Overhead | Yes | 43673 | 0.67847 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-383 | 2019 | 7 | 27 | 16 | 17 | 19-0081851 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 2694 | 12.1046 | 229_224 | <25mph | <15mph | HFTD - Distribution | 2019-07-27 16:17:00 | 1937 | 12.3506 | FALSE | <25mph | PG186 | 3.42 | 2019-07-27T06:40:00Z | 8.12 | 14 | PG186 | 3.42 | 2019-07-27T06:40:00Z | 8.12 | 33 | PG186 | 3.42 | 2019-07-27T06:40:00Z | 8.12 | 26 | PG186 | 3.42 | 2019-07-27T06:40:00Z | 8.12 | 61
PG&E | 2019-07-27 | 4:51 | 37.9486 | -120.4656 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 163781705 |  | 17000 | Conductor | Overhead | Yes | 43673 | 0.20208 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-385 | 2019 | 7 | 27 | 4 | 51 | 19-0081744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 1364 | 13.5826 | 223_236 | <25mph | <15mph | HFTD - Distribution | 2019-07-27 04:51:00 | 1934 | 16.9934 | FALSE | <25mph | PG167 | 3.88 | 2019-07-27T06:40:00Z | 5.26 | 14 | PG166 | 6.57 | 2019-07-27T07:00:00Z | 12.06 | 35 | PG167 | 3.88 | 2019-07-27T06:40:00Z | 5.26 | 26 | PG166 | 6.57 | 2019-07-27T07:00:00Z | 12.06 | 65
PG&E | 2019-07-30 | 15:15 | 39.1207 | -121.072 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 152691104 |  | 12000 | Conductor | Overhead | Yes | 43676 | 0.63542 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-386 | 2019 | 7 | 30 | 15 | 15 | 19-0082713 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 31302 | 12.2921 | 196_301 | <25mph | <15mph | HFTD - Distribution | 2019-07-30 15:15:00 | 1942 | 13.0851 | FALSE | <25mph | E1789 | 3.69 | 2019-07-30T06:24:00Z | 8.01 | 11 | PG429 | 7.54 | 2019-07-30T06:20:00Z | 8.32 | 88 | E1789 | 3.69 | 2019-07-30T06:24:00Z | 8.01 | 21 | PG367 | 7.57 | 2019-07-30T07:40:00Z | 16.44 | 171
PG&E | 2019-08-01 | 13:28 | 38.5721 | -120.6803 | Equipment Failure/Involved, Overhead | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 153662102 |  | 21000 | Conductor | Overhead | Yes | 43678 | 0.56111 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-170 | 2019 | 8 | 1 | 13 | 28 | 19-0083500 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1374 | 13.6823 | 213_271 | <25mph | <15mph | HFTD - Distribution | 2019-08-01 13:28:00 | 1945 | 13.6823 | FALSE | <25mph |  |  |  | 0 | 0 | PG433 | 7.73 | 2019-08-01T07:00:00Z | 11.83 | 31 |  |  |  | 0 | 0 | PG433 | 7.73 | 2019-08-01T07:20:00Z | 15.77 | 59
PG&E | 2019-08-05 | 22:38 | 37.1869 | -119.7902 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Unknown |  | 322066125092 |  | 21000 | Transformer | Overhead | Yes | 43682 | 0.94306 | Equipment - Overloaded | Transformer |  |  |  |  | Other/Unknown | 2019-134 | 2019 | 8 | 5 | 22 | 38 | 19-0084586 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 996 | 7.0886 | 253_195 | <25mph | <15mph | HFTD - Distribution | 2019-08-05 22:38:00 | 1952 | 12.3468 | FALSE | <25mph | PG434 | 0.93 | 2019-08-05T06:50:00Z | 6.13 | 19 | PG425 | 4.53 | 2019-08-05T06:30:00Z | 7.9 | 47 | PG434 | 0.93 | 2019-08-05T07:40:00Z | 6.35 | 37 | PG460 | 7.2 | 2019-08-05T07:30:00Z | 11.63 | 89
PG&E | 2019-08-06 | 12:12 | 39.0506 | -121.0614 | Vegetation | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 100107532 |  | 12000 | Insulator | Overhead | Yes | 43683 | 0.50833 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-391 | 2019 | 8 | 6 | 12 | 12 | 19-0084799 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 60943 | 9.0082 | 197_297 | <25mph | <15mph | HFTD - Distribution | 2019-08-06 12:12:00 | 1954 | 11.6739 | FALSE | <25mph | C5488 | 2.4 | 2019-08-06T06:23:00Z | 4.99 | 25 | E1789 | 7.54 | 2019-08-06T06:54:00Z | 7 | 69 | C5488 | 2.4 | 2019-08-06T06:23:00Z | 4.99 | 50 | E1789 | 7.54 | 2019-08-06T06:54:00Z | 7 | 132
PG&E | 2019-08-11 | 1:19 | 39.1152 | -121.001 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100097796 |  | 12000 | Other | Overhead | Yes | 43688 | 0.054861 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-387 | 2019 | 8 | 11 | 1 | 19 | 19-0086613 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6200 | 9.9563 | 199_300 | <25mph | <15mph | HFTD - Distribution | 2019-08-11 01:19:00 | 1965 | 18.5914 | FALSE | <25mph | PG377 | 1.68 | 2019-08-11T07:00:00Z | 1.52 | 13 | AV504 | 7.68 | 2019-08-11T06:55:00Z | 7 | 79 | PG377 | 1.68 | 2019-08-11T08:00:00Z | 2.86 | 25 | AV504 | 7.68 | 2019-08-11T07:05:00Z | 8.01 | 151
PG&E | 2019-08-12 | 20:06 | 39.0952 | -123.4937 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 102177212 |  | 12000 | Conductor | Overhead | Yes | 43689 | 0.8375 | Vegetation |  | Veg. contact |  |  |  | Fell into (No defect) | 2019-400 | 2019 | 8 | 12 | 20 | 6 | 19-0087090 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2508 | 13.5331 | 93_301 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 20:06:00 | 1970 | 19.4805 | FALSE | <25mph | PG256 | 1.12 | 2019-08-12T06:10:00Z | 1.74 | 10 | PG248 | 4.67 | 2019-08-12T06:10:00Z | 4.16 | 17 | PG256 | 1.12 | 2019-08-12T06:10:00Z | 1.74 | 20 | PG248 | 4.67 | 2019-08-12T07:40:00Z | 4.38 | 33
PG&E | 2019-08-12 | 17:42 | 38.6618 | -120.7451 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 101415488, 101404439 |  | 12000 | Pole | Overhead | Yes | 43689 | 0.7375 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (slight defect) | 2019-241 | 2019 | 8 | 12 | 17 | 42 | 19-0087080 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 54604 | 8.3029 | 210_275 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 17:42:00 | 1968 | 11.2889 | FALSE | <25mph | PG354 | 3.38 | 2019-08-12T07:00:00Z | 7.67 | 16 | PG354 | 3.38 | 2019-08-12T07:00:00Z | 7.67 | 57 | PG354 | 3.38 | 2019-08-12T07:40:00Z | 11.41 | 28 | PG354 | 3.38 | 2019-08-12T07:40:00Z | 11.41 | 106
PG&E | 2019-08-13 | 10:30 | 36.6102 | -121.4452 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 40761041 |  | 115000 | Other | Overhead | Yes | 43690 | 0.4375 | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-164 | 2019 | 8 | 13 | 10 | 30 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 6.9179 | 180_162 | <25mph | <15mph | HFTD - Transmission | 2019-08-13 10:30:00 | 1973 | 18.8698 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2019-08-14 | 10:16 | 35.379 | -120.4232 | Vegetation | Hardwood Woodland | < 1 meter | Cal Fire |  | 512769069280 |  | 21000 | Conductor | Overhead | Yes | 43691 | 0.42778 | Vegetation | [5 empty] | no-match |  | 2019 | 8 | 14 | 10 | 16 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.0314 | 226_94 | <25mph | <15mph | HFTD - Distribution | 2019-08-14 10:16:00 | 1976 | 14.3934 | FALSE | <25mph | PG235 | 1.2 | 2019-08-14T06:30:00Z | 5.48 | 28 | PG190 | 6.24 | 2019-08-14T06:00:00Z | 12.06 | 56 | PG235 | 1.2 | 2019-08-14T06:30:00Z | 5.48 | 52 | PG190 | 6.24 | 2019-08-14T06:00:00Z | 12.06 | 104
PG&E | 2019-08-16 | 8:19 | 40.1235 | -123.8758 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Self Extinguished |  | 192221102-2101118022{5563} |  | 12000 | Conductor | Overhead | Yes | 43693 | 0.34653 | Vegetation | [5 empty] | Other/Unknown |  | 2019 | 8 | 16 | 8 | 19 | 19-0088744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 2979 | 5.7689 | 78_358 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 08:19:00 | 1983 | 18.468 | FALSE | <25mph | ERCC1 | 2.93 | 2019-08-16T06:28:00Z | 12.01 | 1 | ERCC1 | 2.93 | 2019-08-16T06:28:00Z | 12.01 | 33 | ERCC1 | 2.93 | 2019-08-16T06:28:00Z | 12.01 | 2 | ERCC1 | 2.93 | 2019-08-16T06:28:00Z | 12.01 | 62
PG&E | 2019-08-16 | 10:31 | 39.3714 | -121.3221 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103191101 |  | 12000 | Conductor | Overhead | Yes | 43693 | 0.43819 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-397 | 2019 | 8 | 16 | 10 | 31 | 19-0088805 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4580 | 6.4736 | 186_315 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 10:31:00 | 1984 | 15.7456 | FALSE | <25mph | PG298 | 3.48 | 2019-08-16T06:50:00Z | 6.8 | 8 | PG381 | 4.94 | 2019-08-16T07:00:00Z | 14.25 | 43 | PG298 | 3.48 | 2019-08-16T08:00:00Z | 7.25 | 15 | PG381 | 4.94 | 2019-08-16T07:00:00Z | 14.25 | 80
PG&E | 2019-08-19 | 17:27 | 40.9399 | -123.6322 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | California Department of Forestry | 192171101 |  | 12000 | Conductor | Overhead | Yes | 43696 | 0.72708 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-340 | 2019 | 8 | 19 | 17 | 27 | 19-0089645 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 410686 | 10.6326 | 90_403 | <25mph | <15mph | HFTD - Distribution | 2019-08-19 17:27:00 | 1989 | 14.2926 | FALSE | <25mph | D8984 | 1.44 | 2019-08-19T06:03:00Z | 8.99 | 6 | HOAC1 | 7.73 | 2019-08-19T06:40:00Z | 11.01 | 7 | D8984 | 1.44 | 2019-08-19T06:03:00Z | 8.99 | 11 | HOAC1 | 7.73 | 2019-08-19T06:40:00Z | 11.01 | 13
PG&E | 2019-08-20 | 9:03 | 41.1088 | -121.5034 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-297 | 2019 | 8 | 20 | 9 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 2.4258 | 178_411 | <25mph | <15mph | HFTD - Distribution | 2019-08-20 09:03:00 | 1990 | 15.6046 | FALSE | <25mph | PG384 | 3.7 | 2019-08-20T06:40:00Z | 2.64 | 7 | PG499 | 7.38 | 2019-08-20T06:00:00Z | 9.42 | 14 | PG384 | 3.7 | 2019-08-20T07:20:00Z | 3.06 | 13 | PG499 | 7.38 | 2019-08-20T06:00:00Z | 9.42 | 26
PG&E | 2019-08-22 | 22:23 | 39.139 | -121.0194 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 152481106 |  | 12000 | Conductor | Overhead | Yes | 43699 | 0.93264 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-346 | 2019 | 8 | 22 | 22 | 23 | 19-0091224 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38628 | 9.4944 | 199_302 | <25mph | <15mph | HFTD - Distribution | 2019-08-22 22:23:00 | 1993 | 12.3163 | FALSE | <25mph | PG377 | 3.46 | 2019-08-22T07:00:00Z | 5.48 | 11 | E1789 | 6.14 | 2019-08-22T07:00:00Z | 5.99 | 93 | PG377 | 3.46 | 2019-08-22T07:00:00Z | 5.48 | 21 | E1789 | 6.14 | 2019-08-22T08:00:00Z | 5.99 | 184
PG&E | 2019-08-24 | 19:02 | 39.0497 | -121.0614 | Vehicle | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 103956556 |  | 12000 | Pole | Overhead | Yes | 43701 | 0.79306 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-114 | 2019 | 8 | 24 | 19 | 2 | 19-0091826 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 144608 | 8.3287 | 197_297 | <25mph | <15mph | HFTD - Distribution | 2019-08-24 19:02:00 | 1998 | 11.3213 | FALSE | <25mph | C0713 | 2.52 | 2019-08-24T06:39:00Z | 1.01 | 26 | E1789 | 7.6 | 2019-08-24T06:48:00Z | 8.01 | 75 | C0713 | 2.52 | 2019-08-24T06:39:00Z | 1.01 | 51 | PG332 | 5.71 | 2019-08-24T07:20:00Z | 8.77 | 141
PG&E | 2019-08-25 | 13:13 | 41.0935 | -123.6942 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Unknown | 115334464574 |  | 12000 | Transformer | Overhead | Yes | 43702 | 0.55069 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-351 | 2019 | 8 | 25 | 13 | 13 | 19-0091921 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 20311 | 7.6384 | 87_411 | <25mph | <15mph | HFTD - Distribution | 2019-08-25 13:13:00 | 2001 | 10.5423 | FALSE | <25mph | BIIC1 | 3.05 | 2019-08-25T06:40:00Z | 5.99 | 9 | BIIC1 | 3.05 | 2019-08-25T06:40:00Z | 5.99 | 9 | BIIC1 | 3.05 | 2019-08-25T06:40:00Z | 5.99 | 17 | BIIC1 | 3.05 | 2019-08-25T06:40:00Z | 5.99 | 17
PG&E | 2019-08-31 | 10:20 | 40.661 | -122.356 | Vehicle | Barren/Other | 3 meters - 0.25 Acres | Fire Dept | Shasta Lake FD | 103571671 | Yes | 12000 | Fuse | Overbuild | Yes | 43708 | 0.43056 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-421 | 2019 | 8 | 31 | 10 | 20 | 19-0094332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3050 | 3.1396 | 143_386 | <25mph | <15mph | HFTD - Distribution | 2019-08-31 10:20:00 | 2007 | 12.9011 | FALSE | <25mph | F5970 | 1.07 | 2019-08-31T06:00:00Z | 3 | 23 | PG519 | 6.72 | 2019-08-31T06:30:00Z | 5.55 | 62 | F5970 | 1.07 | 2019-08-31T07:16:00Z | 4 | 45 | PG519 | 6.72 | 2019-08-31T08:00:00Z | 11.99 | 118
PG&E | 2019-09-01 | 16:50 | 35.908 | -121.011 |  | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 103477437 |  | 12000 | Pole | Overhead | Yes | 43709 | 0.70139 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-17 | 2019 | 9 | 1 | 16 | 50 | 19-0094475 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45432 | 5.8888 | 199_124 | <25mph | <15mph | HFTD - Distribution | 2019-09-01 16:50:00 | 2009 | 25.5842 | FALSE | 25-40mph |  |  |  | 0 | 0 | PG140 | 7.9 | 2019-09-01T06:20:00Z | 3.74 | 21 |  |  |  | 0 | 0 | PG171 | 7.31 | 2019-09-01T08:00:00Z | 4.83 | 39
PG&E | 2019-09-05 | 23:02 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire | California Department of Forestry | 101670112 |  | 12000 | Fuse | Overhead | Yes | 43713 | 0.95972 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-388 | 2019 | 9 | 5 | 23 | 2 | 19-0095858 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 17920 | 6.8605 | 147_193 | <25mph | <15mph | HFTD - Distribution | 2019-09-05 23:02:00 | 2016 | 8.0768 | FALSE | <25mph | BNDC1 | 2.84 | 2019-09-05T06:50:00Z | 3 | 15 | BNDC1 | 2.84 | 2019-09-05T06:50:00Z | 3 | 66 | BNDC1 | 2.84 | 2019-09-05T07:50:00Z | 3 | 28 | C1844 | 4.46 | 2019-09-05T07:29:00Z | 3 | 128
PG&E | 2019-09-10 | 7:13 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 82841102 |  | 12000 | Conductor | Overhead | Yes | 43718 | 0.30069 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-369 | 2019 | 9 | 10 | 7 | 13 | 19-0097264 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 23500 | 14.6244 | 147_193 | <25mph | <15mph | HFTD - Distribution | 2019-09-10 07:13:00 | 2029 | 17.7422 | FALSE | <25mph | PG472 | 2.91 | 2019-09-10T07:00:00Z | 23.44 | 15 | PG472 | 2.91 | 2019-09-10T07:00:00Z | 23.44 | 65 | PG472 | 2.91 | 2019-09-10T07:00:00Z | 23.44 | 28 | PG472 | 2.91 | 2019-09-10T07:00:00Z | 23.44 | 125
PG&E | 2019-09-11 | 21:03 | 38.3132 | -120.9809 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 163341103 |  | 12000 | Conductor | Overhead | Yes | 43719 | 0.87708 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-370 | 2019 | 9 | 11 | 21 | 3 | 19-0098003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25994 | 11.7888 | 200_256 | <25mph | <15mph | HFTD - Distribution | 2019-09-11 21:03:00 | 2035 | 13.1911 | FALSE | <25mph | PG401 | 2.35 | 2019-09-11T06:00:00Z | 3.06 | 7 | CFAC1 | 5.36 | 2019-09-11T06:05:00Z | 7 | 25 | PG401 | 2.35 | 2019-09-11T06:00:00Z | 3.06 | 13 | CFAC1 | 5.36 | 2019-09-11T06:05:00Z | 7 | 51
PG&E | 2019-09-11 | 18:56 | 37.9937 | -122.137 | Bird Found | Hardwood Woodland | Other | Unknown |  | Unknown |  | 115000 | Other | Overhead | Yes | 43719 | 0.78889 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-42 | 2019 | 9 | 11 | 18 | 56 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | N.A. | 16.9097 | 150_239 | <25mph | <15mph | HFTD - Transmission | 2019-09-11 18:56:00 | 2034 | 19.7995 | FALSE | <25mph | PG064 | 2.53 | 2019-09-11T06:00:00Z | 16.15 | 54 | PG064 | 2.53 | 2019-09-11T06:00:00Z | 16.15 | 209 | PG064 | 2.53 | 2019-09-11T06:00:00Z | 16.15 | 103 | PG064 | 2.53 | 2019-09-11T06:00:00Z | 16.15 | 396
PG&E | 2019-09-12 | 14:25 | 37.3144 | -122.1865 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 024131103 |  | 12000 | Conductor | Overhead | Yes | 43720 | 0.60069 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-217 | 2019 | 9 | 12 | 14 | 25 | 19-0098386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 89097 | 5.2412 | 147_201 | <25mph | <15mph | HFTD - Distribution | 2019-09-12 14:25:00 | 2036 | 15.0249 | FALSE | <25mph | PG152 | 1.17 | 2019-09-12T06:00:00Z | 9.28 | 49 | PG150 | 4.6 | 2019-09-12T06:40:00Z | 10.16 | 161 | PG152 | 1.17 | 2019-09-12T06:00:00Z | 9.28 | 100 | PG150 | 4.6 | 2019-09-12T06:40:00Z | 10.16 | 318
PG&E | 2019-09-13 | 6:30 | 37.3348 | -121.7716 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 83392110 |  | 21000 | Splice/Clamp/Connector | Overhead | Yes | 43721 | 0.27083 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-444 | 2019 | 9 | 13 | 6 | 30 | 19-0098560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 35534 | 3.3882 | 166_202 | <25mph | <15mph | HFTD - Distribution | 2019-09-13 06:30:00 | 2037 | 14.1926 | FALSE | <25mph | PG477 | 2.08 | 2019-09-13T06:30:00Z | 9.35 | 54 | PG477 | 2.08 | 2019-09-13T06:30:00Z | 9.35 | 122 | PG477 | 2.08 | 2019-09-13T06:30:00Z | 9.35 | 101 | PG477 | 2.08 | 2019-09-13T06:30:00Z | 9.35 | 231
PG&E | 2019-09-13 | 8:53 | 39.0754 | -121.1717 | Bird Found | Herbaceous | 0.25 - 10 Acres | Fire Dept | Consolidated FD | Etr0913190810 |  | 12000 | Other | Overhead | Yes | 43721 | 0.37014 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-46 | 2019 | 9 | 13 | 8 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 10.4382 | 192_298 | <25mph | <15mph | HFTD - Distribution | 2019-09-13 08:53:00 | 2038 | 13.5808 | FALSE | <25mph | PG367 | 1.38 | 2019-09-13T06:00:00Z | 8.68 | 10 | PG367 | 1.38 | 2019-09-13T06:00:00Z | 8.68 | 45 | PG367 | 1.38 | 2019-09-13T06:00:00Z | 8.68 | 22 | PG367 | 1.38 | 2019-09-13T06:00:00Z | 8.68 | 89
PG&E | 2019-09-15 | 12:38 | 38.1194 | -120.8013 | Vehicle | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103959405 |  | 12000 | Pole | Overhead | Yes | 43723 | 0.52639 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-118 | 2019 | 9 | 15 | 12 | 38 | 19-0099234 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 5378 | 7.5852 | 208_246 | <25mph | <15mph | HFTD - Distribution | 2019-09-15 12:38:00 | 2043 | 14.1961 | FALSE | <25mph | F0465 | 3.04 | 2019-09-15T06:31:00Z | 2.01 | 12 | PG375 | 4.65 | 2019-09-15T06:40:00Z | 5.19 | 26 | F0465 | 3.04 | 2019-09-15T07:36:00Z | 3 | 24 | PG375 | 4.65 | 2019-09-15T08:00:00Z | 7.61 | 50
PG&E | 2019-09-16 | 14:39 | 37.3762 | -119.8729 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 254452102 |  | 21000 | Conductor | Overhead | Yes | 43724 | 0.61042 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-417 | 2019 | 9 | 16 | 14 | 39 | 19-0099772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 121254 | 13.3091 | 249_205 | <25mph | <15mph | HFTD - Distribution | 2019-09-16 14:39:00 | 2045 | 14.9838 | FALSE | <25mph | PG571 | 0.83 | 2019-09-16T06:10:00Z | 7.74 | 14 | MIAC1 | 7.6 | 2019-09-16T06:59:00Z | 8.01 | 55 | PG571 | 0.83 | 2019-09-16T06:10:00Z | 7.74 | 26 | MIAC1 | 7.6 | 2019-09-16T06:59:00Z | 8.01 | 103
PG&E | 2019-09-22 | 11:56 | 37.5168 | -119.9159 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103967994 |  | 21000 | Pole | Overhead | Yes | 43730 | 0.49722 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-452 | 2019 | 9 | 22 | 11 | 56 | 19-0102232 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 133232 | 11.5782 | 247_213 | <25mph | <15mph | HFTD - Distribution | 2019-09-22 11:56:00 | 2051 | 13.905 | FALSE | <25mph | PG189 | 1.46 | 2019-09-22T06:10:00Z | 6.22 | 15 | PG575 | 7.53 | 2019-09-22T06:00:00Z | 6.35 | 68 | PG189 | 1.46 | 2019-09-22T06:10:00Z | 6.22 | 28 | PG575 | 7.53 | 2019-09-22T06:00:00Z | 6.35 | 127
PG&E | 2019-09-26 | 14:12 | 36.9517 | -121.8278 | Vegetation | Shrub | 1 meter - < 3 meters | Cal Fire |  | 2287 |  | 21000 | Conductor | Overhead | Yes | 43734 | 0.59167 | Vegetation |  | Veg. contact |  |  |  | Branch (OverHanging) | 2019-352 | 2019 | 9 | 26 | 14 | 12 | 19-0104163 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 2856 | 23.4173 | 163_181 | <25mph | <15mph | HFTD - Distribution | 2019-09-26 14:12:00 | 2060 | 23.8621 | FALSE | <25mph | E7291 | 3.61 | 2019-09-26T07:00:00Z | 8.01 | 35 | E7291 | 3.61 | 2019-09-26T07:00:00Z | 8.01 | 99 | E7291 | 3.61 | 2019-09-26T07:00:00Z | 8.01 | 66 | E7291 | 3.61 | 2019-09-26T07:00:00Z | 8.01 | 188
PG&E | 2019-09-27 | 10:30 | 36.5336 | -121.1464 | Vegetation | Barren/Other | 0.25 - 10 Acres | Cal Fire |  | 182492105 |  | 21000 | Conductor | Overhead | Yes | 43735 | 0.4375 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-359 | 2019 | 9 | 27 | 10 | 30 | 19-0104536 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20631 | 5.3593 | 193_158 | <25mph | <15mph | HFTD - Distribution | 2019-09-27 10:30:00 | 2062 | 16.3021 | FALSE | <25mph | PG406 | 3.05 | 2019-09-27T06:00:00Z | 11.41 | 14 | PG406 | 3.05 | 2019-09-27T06:00:00Z | 11.41 | 22 | PG406 | 3.05 | 2019-09-27T06:00:00Z | 11.41 | 26 | PG406 | 3.05 | 2019-09-27T06:00:00Z | 11.41 | 41
PG&E | 2019-09-28 | 13:16 | 37.2553 | -119.5057 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 252531103 |  | 12000 | Conductor | Overhead | Yes | 43736 | 0.55278 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-36 | 2019 | 9 | 28 | 13 | 16 | 19-0104972 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 1296 | 12.1111 | 265_198 | <25mph | <15mph | HFTD - Distribution | 2019-09-28 13:16:00 | 2064 | 13.545 | FALSE | <25mph | PG573 | 3.43 | 2019-09-28T07:00:00Z | 8.61 | 8 | PG573 | 3.43 | 2019-09-28T07:00:00Z | 8.61 | 68 | PG573 | 3.43 | 2019-09-28T07:00:00Z | 8.61 | 16 | PG573 | 3.43 | 2019-09-28T07:00:00Z | 8.61 | 140
PG&E | 2019-09-30 | 14:29 | 34.6139 | -120.1799 | Contact with High Voltage, 3rd party | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 183041102 |  | 12000 | Conductor | Overhead | Yes | 43738 | 0.60347 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-13 | 2019 | 9 | 30 | 14 | 29 | 19-0105582 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 4080 | 26.8876 | 237_52 | 25-40mph | 15-30mph | HFTD - Distribution | 2019-09-30 14:29:00 | 2072 | 27.9753 | FALSE | 25-40mph | C9206 | 2.6 | 2019-09-30T06:56:00Z | 0 | 12 | TT480 | 6.42 | 2019-09-30T06:20:00Z | 12.01 | 16 | C9206 | 2.6 | 2019-09-30T07:56:00Z | 0 | 24 | TT480 | 6.42 | 2019-09-30T06:20:00Z | 12.01 | 32
PG&E | 2019-10-04 | 19:07 | 40.4964 | -122.0448 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | Yes | 43742 | 0.79653 | Equipment - Overloaded | Other |  |  |  |  | no-match | 2019-257 | 2019 | 10 | 4 | 19 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 6.2955 | 155_377 | <25mph | <15mph | HFTD - Distribution | 2019-10-04 19:07:00 | 2076 | 10.3362 | FALSE | <25mph | PG107 | 2.58 | 2019-10-04T06:10:00Z | 4.54 | 7 | PG322 | 7.46 | 2019-10-04T06:50:00Z | 6.44 | 42 | PG107 | 2.58 | 2019-10-04T06:10:00Z | 4.54 | 13 | PG322 | 7.46 | 2019-10-04T06:50:00Z | 6.44 | 78
PG&E | 2019-10-08 | 17:59 | 35.2979 | -120.4868 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 182541103 |  | 12000 | Conductor | Overhead | Yes | 43746 | 0.74931 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-207 | 2019 | 10 | 8 | 17 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.8254 | 223_90 | <25mph | <15mph | HFTD - Distribution | 2019-10-08 17:59:00 | 2082 | 10.8694 | FALSE | <25mph | PG240 | 3.72 | 2019-10-08T06:40:00Z | 1.61 | 7 | PG235 | 6.78 | 2019-10-08T06:00:00Z | 9.64 | 35 | PG240 | 3.72 | 2019-10-08T07:20:00Z | 2.77 | 13 | PG235 | 6.78 | 2019-10-08T06:00:00Z | 9.64 | 65
PG&E | 2019-10-15 | 0:41 | 37.3237 | -119.6173 |  | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | Circuit 254432102 |  | 21000 | Insulator | Overhead | Yes | 43753 | 0.028472 | Equipment - PG&E | Insulator |  |  |  |  | Other/Unknown | 2019-168 | 2019 | 10 | 15 | 0 | 41 | 19-0111571 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 741 | 8.1986 | 260_202 | <25mph | <15mph | HFTD - Distribution | 2019-10-15 00:41:00 | 2092 | 11.0003 | FALSE | <25mph | BSNC1 | 3.84 | 2019-10-15T06:48:00Z | 8.99 | 54 | BSNC1 | 3.84 | 2019-10-15T06:48:00Z | 8.99 | 80 | BSNC1 | 3.84 | 2019-10-15T06:48:00Z | 8.99 | 106 | BSNC1 | 3.84 | 2019-10-15T06:48:00Z | 8.99 | 156
PG&E | 2019-10-17 | 19:44 | 37.6494 | -120.357 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 5Tr1017191903 |  | 12000 | Conductor | Overhead | Yes | 43755 | 0.82222 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-423 | 2019 | 10 | 17 | 19 | 44 | 19-0113175 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 10105 | 17.2183 | 228_220 | <25mph | <15mph | HFTD - Distribution | 2019-10-17 19:44:00 | 2093 | 19.6404 | FALSE | <25mph | PG459 | 0.92 | 2019-10-17T06:20:00Z | 15.93 | 7 | PG186 | 7.71 | 2019-10-17T06:20:00Z | 16.28 | 21 | PG459 | 0.92 | 2019-10-17T07:40:00Z | 23.17 | 13 | PG186 | 7.71 | 2019-10-17T07:50:00Z | 25.05 | 39
PG&E | 2019-10-20 | 17:09 | 37.1585 | -122.1339 |  | Conifer Forest | 1 meter - < 3 meters | Employee |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match |  | 2019 | 10 | 20 | 17 | 9 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 13.248 | 150_193 | <25mph | <15mph | HFTD - Distribution | 2019-10-20 17:09:00 | 2098 | 15.6656 | FALSE | <25mph | PG472 | 2.84 | 2019-10-20T06:30:00Z | 12.28 | 41 | AV151 | 4.67 | 2019-10-20T06:05:00Z | 14 | 104 | PG472 | 2.84 | 2019-10-20T06:30:00Z | 12.28 | 79 | AV151 | 4.67 | 2019-10-20T06:05:00Z | 14 | 201
PG&E | 2019-10-23 | 21:27 | 38.7959 | -122.7673 |  | Herbaceous | 100+ Acres | Cal Fire |  | 001/006 |  | 230000 | Jumper | Overhead | Yes | 43761 | 0.88819 | Under Investigation | Jumper |  |  |  | This ignition relates to the Kincade Fire, which is reported in compliance with D.19-05-037. The origin and cause of the Kincade Fire is under investigation by CAL FIRE and PG&E. At this time, PG&E has not formed a conclusion about the origin or cause of the Kincade Fire. | no-match |  | 2019 | 10 | 23 | 21 | 27 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 35.6848 | 123_284 | 25-40mph | 30-45mph | HFTD - Transmission | 2019-10-23 21:27:00 | 2102 | 39.9048 | FALSE | 25-40mph | PG305 | 2.22 | 2019-10-23T06:40:00Z | 21.18 | 21 | PG303 | 4.59 | 2019-10-23T06:40:00Z | 30.53 | 71 | PG305 | 2.22 | 2019-10-23T06:40:00Z | 21.18 | 39 | PG303 | 4.59 | 2019-10-23T06:40:00Z | 30.53 | 132
PG&E | 2019-10-28 | 17:48 | 37.0309 | -121.7788 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 101682849 |  | 21000 | Conductor | Overhead | Yes | 43766 | 0.74167 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-389 | 2019 | 10 | 28 | 17 | 48 | 19-0118112 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 16698 | 8.4978 | 165_186 | <25mph | <15mph | HFTD - Distribution | 2019-10-28 17:48:00 | 2135 | 19.9036 | FALSE | <25mph | PG370 | 3.22 | 2019-10-28T06:00:00Z | 42.17 | 22 | PG370 | 3.22 | 2019-10-28T06:00:00Z | 42.17 | 43 | PG370 | 3.22 | 2019-10-28T06:00:00Z | 42.17 | 41 | PG370 | 3.22 | 2019-10-28T06:00:00Z | 42.17 | 80
PG&E | 2019-10-28 | 18:46 | 38.5646 | -122.4642 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 43432104 |  | 21000 | Conductor | Overhead | Yes | 43766 | 0.78194 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-357 | 2019 | 10 | 28 | 18 | 46 | 19-0118147 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 496944 | 12.9758 | 136_271 | <25mph | <15mph | HFTD - Distribution | 2019-10-28 18:46:00 | 2136 | 31.1526 | FALSE | 25-40mph | PG199 | 2.69 | 2019-10-28T07:00:00Z | 32.21 | 23 | PG162 | 6.69 | 2019-10-28T06:30:00Z | 35.08 | 79 | PG199 | 2.69 | 2019-10-28T07:00:00Z | 32.21 | 44 | PG162 | 6.69 | 2019-10-28T06:30:00Z | 35.08 | 148
PG&E | 2019-10-28 | 13:00 | 39.3208 | -121.1273 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 100099164 |  | 12000 | Transformer | Overbuild | Yes | 43766 | 0.54167 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-398 | 2019 | 10 | 28 | 13 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.567 | 194_312 | <25mph | <15mph | HFTD - Distribution | 2019-10-28 13:00:00 | 2133 | 16.9711 | FALSE | <25mph | RRRC1 | 1.31 | 2019-10-28T06:13:00Z | 7 | 8 | PG348 | 4.93 | 2019-10-28T07:00:00Z | 15.28 | 62 | RRRC1 | 1.31 | 2019-10-28T06:13:00Z | 7 | 15 | PG424 | 7.74 | 2019-10-28T07:20:00Z | 23.6 | 112
PG&E | 2019-10-29 | 3:29 | 37.0374 | -121.5207 | Animal Found | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 1471 |  | 21000 | Fuse | Overhead | Yes | 43767 | 0.14514 | Contact - Animal - Other |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-283 | 2019 | 10 | 29 | 3 | 29 | 19-0118370 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 3294 | 2.601 | 177_186 | <25mph | <15mph | HFTD - Distribution | 2019-10-29 03:29:00 | 2137 | 15.317 | FALSE | <25mph | PG509 | 2.27 | 2019-10-29T06:00:00Z | 7.09 | 31 | PG509 | 2.27 | 2019-10-29T06:00:00Z | 7.09 | 46 | PG509 | 2.27 | 2019-10-29T06:00:00Z | 7.09 | 61 | PG509 | 2.27 | 2019-10-29T06:00:00Z | 7.09 | 88
PG&E | 2019-10-30 | 13:32 | 38.4792 | -122.0302 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 063681102 |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact |  |  |  | no-match | 2019-338 | 2019 | 10 | 30 | 13 | 32 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.8557 | 155_266 | <25mph | <15mph | HFTD - Distribution | 2019-10-30 13:32:00 | 2143 | 17.0659 | FALSE | <25mph | PG431 | 3.57 | 2019-10-30T06:20:00Z | 30.4 | 7 | PG583 | 4.98 | 2019-10-30T06:00:00Z | 32.82 | 14 | PG431 | 3.57 | 2019-10-30T06:20:00Z | 30.4 | 13 | PG583 | 4.98 | 2019-10-30T06:00:00Z | 32.82 | 26
PG&E | 2019-10-31 | 21:21 | 39.661 | -120.6264 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Fire Dept | Sierra County FD | 152101101 |  | 12000 | Conductor | Overhead | Yes | 43769 | 0.88958 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-390 | 2019 | 10 | 31 | 21 | 21 | 19-0115942 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 7121279 | 13.8814 | 215_331 | <25mph | <15mph | HFTD - Distribution | 2019-10-31 21:21:00 | 2148 | 14.2162 | FALSE | <25mph |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 2019-10-31 | 17:23 | 38.0458 | -122.1905 |  | Herbaceous | 1 meter - < 3 meters | Fire Dept | Crockett FD | 13432207 |  | 21000 | Conductor | Overhead | Yes | 43769 | 0.72431 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-05 | 2019 | 10 | 31 | 17 | 23 | 19-0119756 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 138161 | 2.9536 | 148_242 | <25mph | <15mph | HFTD - Distribution | 2019-10-31 17:23:00 | 2147 | 12.6781 | FALSE | <25mph | DPXC1 | 3.83 | 2019-10-31T06:30:00Z | 10 | 40 | DPXC1 | 3.83 | 2019-10-31T06:30:00Z | 10 | 108 | DPXC1 | 3.83 | 2019-10-31T06:30:00Z | 10 | 74 | DPXC1 | 3.83 | 2019-10-31T06:30:00Z | 10 | 206
PG&E | 2019-10-31 | 16:09 | 38.3845 | -122.1893 | Vegetation | Agriculture | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact |  |  |  | no-match | 2019-396 | 2019 | 10 | 31 | 16 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 5.3253 | 148_260 | <25mph | <15mph | HFTD - Distribution | 2019-10-31 16:09:00 | 2146 | 18.7786 | FALSE | <25mph | F0187 | 2.71 | 2019-10-31T06:15:00Z | 8.99 | 10 | PG185 | 4.03 | 2019-10-31T06:50:00Z | 17.83 | 66 | F0187 | 2.71 | 2019-10-31T06:15:00Z | 8.99 | 21 | PG185 | 4.03 | 2019-10-31T07:10:00Z | 18.99 | 126
PG&E | 2019-11-03 | 18:26 | 36.2323 | -121.7622 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 182941102 |  | 12000 | Conductor | Overhead | Yes | 43772 | 0.76806 | Vegetation |  | Veg. contact |  |  |  | Fell into (Moderate-Severe defect) | 2019-371 | 2019 | 11 | 3 | 18 | 26 | 19-0120570 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 59211 | 9.4075 | 166_142 | <25mph | <15mph | HFTD - Distribution | 2019-11-03 18:26:00 | 2152 | 16.3887 | FALSE | <25mph | PG362 | 1.69 | 2019-11-03T06:30:00Z | 20.18 | 13 | PG362 | 1.69 | 2019-11-03T06:30:00Z | 20.18 | 13 | PG362 | 1.69 | 2019-11-03T07:50:00Z | 20.18 | 23 | PG362 | 1.69 | 2019-11-03T07:50:00Z | 20.18 | 23
PG&E | 2019-11-04 | 23:32 | 34.6619 | -120.0852 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 8145 |  | 12000 | Conductor | Overhead | Yes | 43773 | 0.98056 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-125 | 2019 | 11 | 4 | 23 | 32 | 19-0121150 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 20066 | 2.0041 | 241_55 | <25mph | <15mph | HFTD - Distribution | 2019-11-04 23:32:00 | 2155 | 13.4228 | FALSE | <25mph | SXWC1 | 2.51 | 2019-11-04T07:09:00Z | 4.99 | 15 | TT594 | 4.6 | 2019-11-04T07:46:00Z | 5.99 | 40 | SXWC1 | 2.51 | 2019-11-04T08:09:00Z | 4.99 | 28 | TT480 | 7.81 | 2019-11-04T08:20:00Z | 8.99 | 77
PG&E | 2019-11-10 | 9:47 | 35.0787 | -120.4974 |  | Herbaceous | 1 meter - < 3 meters | Cal Fire |  | 4Bx1110190931 |  | 12000 | Conductor | Overhead | Yes | 43779 | 0.40764 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-431 | 2019 | 11 | 10 | 9 | 47 | 19-0123396 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 19943 | 5.9544 | 222_78 | <25mph | <15mph | HFTD - Distribution | 2019-11-10 09:47:00 | 2161 | 16.9334 | FALSE | <25mph | PG168 | 0.77 | 2019-11-10T07:00:00Z | 8.05 | 14 | PG168 | 0.77 | 2019-11-10T07:00:00Z | 8.05 | 63 | PG168 | 0.77 | 2019-11-10T09:00:00Z | 11.34 | 26 | PG168 | 0.77 | 2019-11-10T09:00:00Z | 11.34 | 126
PG&E | 2019-11-11 | 6:52 | 36.6822 | -119.1806 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 4Tj1111191656 |  | 12000 | Other | Overhead | Yes | 43780 | 0.28611 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-453 | 2019 | 11 | 11 | 6 | 52 | 19-0123468 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 109129 | 2.952 | 280_167 | <25mph | <15mph | HFTD - Distribution | 2019-11-11 06:52:00 | 2162 | 12.1773 | FALSE | <25mph | PG258 | 2.49 | 2019-11-11T07:50:00Z | 7 | 21 | PG374 | 4.84 | 2019-11-11T07:20:00Z | 7.61 | 62 | PG258 | 2.49 | 2019-11-11T07:50:00Z | 7 | 39 | PG374 | 4.84 | 2019-11-11T08:20:00Z | 7.81 | 116
PG&E | 2019-11-11 | 9:46 | 37.8782 | -120.4596 | Vehicle | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 101020184 |  | 17000 | Other | Overhead | Yes | 43780 | 0.40694 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-82 | 2019 | 11 | 11 | 9 | 46 | 19-0123520 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 38170 | 5.2001 | 223_232 | <25mph | <15mph | HFTD - Distribution | 2019-11-11 09:46:00 | 2163 | 14.6078 | FALSE | <25mph | GNSC1 | 3.86 | 2019-11-11T07:03:00Z | 4.99 | 1 | PG166 | 4.81 | 2019-11-11T07:30:00Z | 6.71 | 15 | GNSC1 | 3.86 | 2019-11-11T08:03:00Z | 5.99 | 2 | PG166 | 4.81 | 2019-11-11T09:00:00Z | 9.06 | 28
PG&E | 2019-11-21 | 16:26 | 40.3231 | -123.9202 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 192311141 |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-416 | 2019 | 11 | 21 | 16 | 26 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 5.8466 | 77_369 | <25mph | <15mph | HFTD - Distribution | 2019-11-21 16:26:00 | 2173 | 12.9212 | FALSE | <25mph |  |  |  | 0 | 0 | PG274 | 5.92 | 2019-11-21T07:30:00Z | 2.26 | 7 |  |  |  | 0 | 0 | PG274 | 5.92 | 2019-11-21T08:40:00Z | 2.55 | 13
PG&E | 2019-11-22 | 4:43 | 39.6736 | -121.3855 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 103751102 |  | 12000 | Conductor | Overhead | Yes | 43791 | 0.19653 | Vegetation |  | Veg. contact |  |  |  | Fell into (slight defect) | 2019-428 | 2019 | 11 | 22 | 4 | 43 | 19-0127475 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3712 | 7.9177 | 183_331 | <25mph | <15mph | HFTD - Distribution | 2019-11-22 04:43:00 | 2174 | 11.8215 | FALSE | <25mph | PG099 | 3.33 | 2019-11-22T08:00:00Z | 0 | 7 | JBGC1 | 6.99 | 2019-11-22T07:13:00Z | 13 | 36 | PG099 | 3.33 | 2019-11-22T09:00:00Z | 0 | 13 | JBGC1 | 6.99 | 2019-11-22T08:13:00Z | 13 | 67
PG&E | 2019-11-26 | 14:18 | 35.4427 | -120.7567 |  | Urban | 0.25 - 10 Acres | Cal Fire |  | 511791771829 |  | 12000 | Other | Overhead | Yes | 43795 | 0.59583 | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-211 | 2019 | 11 | 26 | 14 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 2.9904 | 211_98 | <25mph | <15mph | HFTD - Distribution | 2019-11-26 14:18:00 | 2177 | 25.9333 | FALSE | 25-40mph | PG141 | 2.39 | 2019-11-26T07:00:00Z | 31.5 | 14 | PG141 | 2.39 | 2019-11-26T07:00:00Z | 31.5 | 72 | PG141 | 2.39 | 2019-11-26T07:00:00Z | 31.5 | 26 | PG141 | 2.39 | 2019-11-26T07:00:00Z | 31.5 | 138
PG&E | 2019-11-27 | 15:39 | 40.6579 | -122.4211 |  | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 103521102-2101107406{2413} |  | 12000 | Fuse | Overhead | Yes | 43796 | 0.65208 | Other Fire: Non-PG&E related | [5 empty] | Other/Unknown |  | 2019 | 11 | 27 | 15 | 39 | 19-0130770 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip failure | Fuse | 8302 | 6.9489 | 140_386 | <25mph | <15mph | HFTD - Distribution | 2019-11-27 15:39:00 | 2179 | 14.036 | FALSE | <25mph | F5970 | 3 | 2019-11-27T07:47:00Z | 17 | 11 | PG265 | 7.46 | 2019-11-27T08:00:00Z | 38.07 | 75 | F5970 | 3 | 2019-11-27T09:00:00Z | 17 | 22 | PG265 | 7.46 | 2019-11-27T08:00:00Z | 38.07 | 142
PG&E | 2019-11-27 | 6:37 | 37.2717 | -122.3078 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 24101103 |  | 12000 | Conductor | Overhead | Yes | 43796 | 0.27569 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-362 | 2019 | 11 | 27 | 6 | 37 | 19-0130047 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 16680 | 9.7328 | 142_199 | <25mph | <15mph | HFTD - Distribution | 2019-11-27 06:37:00 | 2178 | 32.4983 | FALSE | 25-40mph | LAHC1 | 3.7 | 2019-11-27T07:07:00Z | 11.01 | 1 | PG150 | 6.93 | 2019-11-27T07:40:00Z | 32.37 | 33 | LAHC1 | 3.7 | 2019-11-27T08:07:00Z | 14.99 | 2 | PG150 | 6.93 | 2019-11-27T08:10:00Z | 32.73 | 61
PG&E | 2019-11-29 | 20:18 | 39.8503 | -121.6312 |  | Shrub | 1 meter - < 3 meters | Unknown |  | 40700248, 42578814, 42578813 |  | 60000 | Pole | Overhead | Yes | 43798 | 0.84583 | Equipment - PG&E | Pole |  |  |  |  | no-match | 2019-10 | 2019 | 11 | 29 | 20 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Pole | N.A. | 13.1829 | 173_341 | <25mph | <15mph | HFTD - Transmission | 2019-11-29 20:18:00 | 2180 | 13.969 | FALSE | <25mph | PG333 | 3.51 | 2019-11-29T07:00:00Z | 10.38 | 54 | PG333 | 3.51 | 2019-11-29T07:00:00Z | 10.38 | 99 | PG333 | 3.51 | 2019-11-29T07:00:00Z | 10.38 | 102 | PG333 | 3.51 | 2019-11-29T07:00:00Z | 10.38 | 185
PG&E | 2019-12-18 | 5:25 | 38.2817 | -120.517 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 101273893 |  | 12000 | Pole | Overhead | Yes | 43817 | 0.22569 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (No defect) | 2019-361 | 2019 | 12 | 18 | 5 | 25 | 19-0137065 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3185 | 6.993 | 220_255 | <25mph | <15mph | HFTD - Distribution | 2019-12-18 05:25:00 | 2183 | 18.6148 | FALSE | <25mph | ESPC1 | 1.49 | 2019-12-18T07:13:00Z | 15.99 | 25 | ESPC1 | 1.49 | 2019-12-18T07:13:00Z | 15.99 | 51 | ESPC1 | 1.49 | 2019-12-18T08:13:00Z | 15.99 | 48 | ESPC1 | 1.49 | 2019-12-18T08:13:00Z | 15.99 | 95
Note on AP4: Based on the max wind gust speed in the hour of ignition. used wind gust speed factor of 1.6.
Note on AW4: Based on the max wind gust speed +/- 12 hours of ignition. Used wind gust speed factor of 1.6.
Note on AY4: based on mph_day_max
Note on AM675: Chong, Yanping: was under investigation, Kincade

## Ign HFTD+W Clean
CPUC Reportable Ignitions from 2015-2019 + 7 fires ¦ HFTD + Wind Station Analysis
Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations | [7 empty] | Used in the pivot | [7 empty] | Used in Pivot | Used for Tranche | Used in the Risk Input Sheet | Used in Pivot | Used in the Risk Input Sheet | Used in the Risk Input | Used in EO-WF-14 | [7 empty] | 1
Utility Name | Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | Notes (Optional): | Veg Subdriver | 0_Ignition ID | 0_Year | 0_Month | 0_Day | 0_Hour | 0_Minute | 0_Outage ID | 0_HFTD Zone | 0_HFTD | 0_RFW Applicable | 0_Transmission/Distribution | 0_Tranche | 0_Fire Greater than 300 Acres | 0_Driver | 0_Subdriver | 0_Customer Minutes Interrupted | 1_wg_mph | 1_we_sn | 1_Wind Categorization | 1_Wind Category | 1_Tranche | 2_dt_local | 2_wg_row | 2_wg_mph_day_max | 1_same date and time as other ignition | 2_Wind Category | 4m/1h stid | 4m/1h time | 4m/1h dist | 4m/1h gust mph | 4m/1h count | 4m/1h Category | 8m/1h stid | 8m/1h time | 8m/1h dist | 8m/1h gust mph | 8m/1h count | 8m/1h Category | 4m/2h stid | 4m/2h time | 4m/2h dist | 4m/2h gust mph | 4m/2h count | 4m/2h Category | 8m/2h stid | 8m/2h time | 8m/2h dist | 8m/2h gust mph | 8m/2h count | 8m/2h Category
PG&E | 2015-01-16 07:07 | 42020.2965 | 38.7753 | -122.7004 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 102167494 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0257 | 2015 | 1 | 16 | 7 | 7 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 19.4177 | 126_282 | <25mph | <15mph | HFTD - Distribution | 2015-01-16 07:07:00 | 4 | 24.2776 | FALSE | <25mph |  |  |  | 0 | 0 | No data | HWKC1 | 7.87 | 2015-01-16T14:56:00Z | 11.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | HWKC1 | 7.87 | 2015-01-16T14:56:00Z | 11.01 | 2 | < 25mph
PG&E | 2015-01-26 03:51 | 42030.1604 | 37.0539 | -122.1587 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42030.1604 | 2015-01-26 03:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0258 | 2015 | 1 | 26 | 3 | 51 | 15-0007000 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7602 | 14.3078 | 149_187 | <25mph | <15mph | HFTD - Distribution | 2015-01-26 03:51:00 | 5 | 14.9656 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BNDC1 | 5.38 | 2015-01-26T11:50:00Z | 10 | 52 | < 25mph |  |  |  | 0 | 0 | No data | BNDC1 | 5.38 | 2015-01-26T11:50:00Z | 10 | 97 | < 25mph
PG&E | 2015-02-06 06:01 | 42041.2507 | 38.6059 | -121.0221 | Vegetation | Rural | < 3 meters | Fire Agency |  | 6661 Ryan Ranch Road, El Dorado Hills |  | 21000 | Conductor | Overhead | Yes | 42041.2507 | 2015-02-06 06:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0259 | 2015 | 2 | 6 | 6 | 1 | 15-0009876 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 51996 | 16.7927 | 199_272 | <25mph | <15mph | HFTD - Distribution | 2015-02-06 06:01:00 | 6 | 30.3484 | FALSE | 25-40mph | D4314 | 3.45 | 2015-02-06T13:58:00Z | 46.95 | 12 | 40-55mph | BENC1 | 4.89 | 2015-02-06T13:59:00Z | 59.01 | 40 | 55mph+ | D4314 | 3.45 | 2015-02-06T13:58:00Z | 46.95 | 24 | 40-55mph | BENC1 | 4.89 | 2015-02-06T13:59:00Z | 59.01 | 79 | 55mph+
PG&E | 2015-02-07 18:38 | 42042.7764 | 40.4674 | -123.6545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | mile marker 36.61, hwy 36, bridgeville |  | 12000 | Conductor | Overhead | Yes | 42042.7764 | 2015-02-07 18:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0262 | 2015 | 2 | 7 | 18 | 38 | 15-0011390 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 7691 | 20.9308 | 88_377 | <25mph | <15mph | HFTD - Distribution | 2015-02-07 18:38:00 | 9 | 24.639 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MDDC1 | 6.88 | 2015-02-08T01:53:00Z | 24 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MDDC1 | 6.88 | 2015-02-08T01:53:00Z | 24 | 2 | < 25mph
PG&E | 2015-02-23 02:05 | 42058.0868 | 39.3027 | -121.0175 | Vegetation | Rural | < 3 meters | Fire Agency | NEVADA CITY FIRE | 100086316 |  | 12000 | Conductor | Overhead | Yes | 42058.0868 | 2015-02-23 02:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0267 | 2015 | 2 | 23 | 2 | 5 | 15-0014910 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 93279 | 24.5459 | 199_311 | <25mph | <15mph | HFTD - Distribution | 2015-02-23 02:05:00 | 14 | 25.6662 | FALSE | 25-40mph | E3651 | 2.92 | 2015-02-23T09:05:00Z | 14.99 | 13 | < 25mph | KGOO | 5.49 | 2015-02-23T09:40:00Z | 31.07 | 67 | 25-40mph | E3651 | 2.92 | 2015-02-23T10:50:00Z | 16.98 | 25 | < 25mph | KGOO | 5.49 | 2015-02-23T09:40:00Z | 31.07 | 131 | 25-40mph
PG&E | 2015-02-23 13:25 | 42058.559 | 38.5046 | -122.7408 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RINCON VALLEY | BEHIND 4870 CARRIAGE LN SANTA ROSA |  | 12000 | Conductor | Overhead | Yes | 42058.559 | 2015-02-23 13:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0268 | 2015 | 2 | 23 | 13 | 25 | 15-0015168 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 85762 | 20.3218 | 124_267 | <25mph | <15mph | HFTD - Distribution | 2015-02-23 13:25:00 | 15 | 32.6885 | FALSE | 25-40mph | RSAC1 | 2.39 | 2015-02-23T20:29:00Z | 34 | 11 | 25-40mph | RSAC1 | 2.39 | 2015-02-23T20:29:00Z | 34 | 73 | 25-40mph | RSAC1 | 2.39 | 2015-02-23T20:29:00Z | 34 | 22 | 25-40mph | RSAC1 | 2.39 | 2015-02-23T20:29:00Z | 34 | 145 | 25-40mph
PG&E | 2015-03-04 18:44 | 42067.7806 | 38.9995 | -122.7545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kelseyville FD | 102156367 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42067.7806 | 2015-03-04 18:44 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0271 | 2015 | 3 | 4 | 18 | 44 | 15-0017374 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29532 | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2015-03-04 18:44:00 | NA | 0 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.58 | 2015-03-05T01:57:00Z | 11.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.58 | 2015-03-05T01:57:00Z | 11.01 | 2 | < 25mph
PG&E | 2015-03-07 13:35 | 42070.566 | 38.7091 | -122.6484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 14417 western mine rd, Middletown |  | 12000 | Conductor | Overhead | Yes | 42070.566 | 2015-03-07 13:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0272 | 2015 | 3 | 7 | 13 | 35 | 15-0018003 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2263 | 3.8777 | 128_279 | <25mph | <15mph | HFTD - Distribution | 2015-03-07 13:35:00 | 18 | 14.4715 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2050 | 7.98 | 2015-03-07T21:33:00Z | 7 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E2050 | 7.98 | 2015-03-07T21:48:00Z | 8.99 | 8 | < 25mph
PG&E | 2015-03-14 02:30 | 42077.1042 | 38.9038 | -122.7579 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 9210 Wildcat Road, Kelseyville |  | 12000 | Conductor | Overhead | Yes | 42077.1042 | 2015-03-14 02:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0274 | 2015 | 3 | 14 | 2 | 30 | 15-0019556 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2280 | 8.9688 | 124_289 | <25mph | <15mph | HFTD - Distribution | 2015-03-14 02:30:00 | 20 | 8.9688 | FALSE | <25mph | KELC1 | 2.83 | 2015-03-14T08:57:00Z | 0 | 1 | < 25mph | E4393 | 6.32 | 2015-03-14T08:57:00Z | 4.99 | 5 | < 25mph | KELC1 | 2.83 | 2015-03-14T09:57:00Z | 0 | 2 | < 25mph | E4393 | 6.32 | 2015-03-14T08:57:00Z | 4.99 | 10 | < 25mph
PG&E | 2015-03-15 22:47 | 42078.9493 | 38.3346 | -120.5325 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 103106530 |  | 12000 | Conductor | Overhead | Yes | 42078.9493 | 2015-03-15 22:47 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0279 | 2015 | 3 | 15 | 22 | 47 | 15-0019709 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 14520 | 7.4897 | 220_257 | <25mph | <15mph | HFTD - Distribution | 2015-03-15 22:47:00 | 25 | 18.5478 | FALSE | <25mph | D9396 | 3.65 | 2015-03-16T05:46:00Z | 2.01 | 11 | < 25mph | MTZC1 | 7.54 | 2015-03-16T04:56:00Z | 7 | 25 | < 25mph | D9396 | 3.65 | 2015-03-16T06:44:00Z | 2.01 | 20 | < 25mph | MTZC1 | 7.54 | 2015-03-16T04:56:00Z | 7 | 47 | < 25mph
PG&E | 2015-04-02 09:44 | 42096.4056 | 39.6772 | -121.492 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100338726 |  | 12000 | Conductor | Overhead | Yes | 42096.4056 | 2015-04-02 09:44 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0284 | 2015 | 4 | 2 | 9 | 44 | 15-0023747 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 100204 | 15.7458 | 178_332 | <25mph | <15mph | HFTD - Distribution | 2015-04-02 09:44:00 | 30 | 15.7458 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JBGC1 | 4.06 | 2015-04-02T16:13:00Z | 37 | 12 | 25-40mph |  |  |  | 0 | 0 | No data | JBGC1 | 4.06 | 2015-04-02T16:13:00Z | 37 | 21 | 25-40mph
PG&E | 2015-04-04 16:49 | 42098.7007 | 38.8824 | -122.5914 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 20748 Jerusalem Grade Road, Middletown |  | 12000 | Other | Overhead | Yes | 42098.7007 | 2015-04-04 16:49 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0285 | 2015 | 4 | 4 | 16 | 49 | 15-0024208 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 20448 | 16.9925 | 131_288 | <25mph | <15mph | HFTD - Distribution | 2015-04-04 16:49:00 | 31 | 19.3597 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.51 | 2015-04-04T22:57:00Z | 22.01 | 13 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.51 | 2015-04-04T23:57:00Z | 25.99 | 26 | 25-40mph
PG&E | 2015-04-11 17:16 | 42105.7194 | 40.5462 | -122.2343 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101491414 |  | 12000 | Conductor | Overhead | Yes | 42105.7194 | 2015-04-11 17:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0286 | 2015 | 4 | 11 | 17 | 16 | 15-0026023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 11914 | 19.429 | 148_380 | <25mph | <15mph | HFTD - Distribution | 2015-04-11 17:16:00 | 32 | 19.429 | FALSE | <25mph | RRAC1 | 3.7 | 2015-04-11T23:24:00Z | 12.01 | 1 | < 25mph | C5599 | 6.52 | 2015-04-12T00:04:00Z | 14 | 9 | < 25mph | RRAC1 | 3.7 | 2015-04-11T23:24:00Z | 12.01 | 2 | < 25mph | C5599 | 6.52 | 2015-04-12T01:04:00Z | 20.98 | 18 | < 25mph
PG&E | 2015-04-27 12:54 | 42121.5375 | 35.4871 | -120.6756 | Vegetation | Rural | < 3 meters | Unknown |  | 103310601 |  | 21000 | Conductor | Overhead | Yes | 42121.5375 | 2015-04-27 12:54 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0301 | 2015 | 4 | 27 | 12 | 54 | 15-0029875 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 5836 | 7.5834 | 214_100 | <25mph | <15mph | HFTD - Distribution | 2015-04-27 12:54:00 | 47 | 19.0974 | FALSE | <25mph | E1179 | 1.84 | 2015-04-27T19:26:00Z | 8.99 | 8 | < 25mph | E2260 | 4.42 | 2015-04-27T19:11:00Z | 10.98 | 14 | < 25mph | E1179 | 1.84 | 2015-04-27T19:26:00Z | 8.99 | 16 | < 25mph | E2260 | 4.42 | 2015-04-27T20:32:00Z | 14 | 29 | < 25mph
PG&E | 2015-04-30 00:26 | 42124.0181 | 37.2401 | -122.2472 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 1145 VERDE R |  | 12000 | Conductor | Overhead | Yes | 42124.0181 | 2015-04-30 00:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0304 | 2015 | 4 | 30 | 0 | 26 | 15-0030607 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1256 | 5.7566 | 145_197 | <25mph | <15mph | HFTD - Distribution | 2015-04-30 00:26:00 | 50 | 15.5915 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.52 | 2015-04-30T07:07:00Z | 4.99 | 9 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.52 | 2015-04-30T08:07:00Z | 5.99 | 17 | < 25mph
PG&E | 2015-05-02 16:51 | 42126.7021 | 37.3284 | -119.643 | Vegetation | Rural | < 0.25 Acres | Fire Agency | MADERA COUNTY | 103768995 |  | 12000 | Conductor | Overhead | Yes | 42126.7021 | 2015-05-02 16:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0305 | 2015 | 5 | 2 | 16 | 51 | 15-0031285 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 79805 | 9.7158 | 259_202 | <25mph | <15mph | HFTD - Distribution | 2015-05-02 16:51:00 | 51 | 12.4769 | FALSE | <25mph | AT301 | 1.62 | 2015-05-02T23:51:00Z | 18.99 | 34 | < 25mph | AT301 | 1.62 | 2015-05-02T23:51:00Z | 18.99 | 60 | < 25mph | AT301 | 1.62 | 2015-05-02T23:56:00Z | 18.99 | 65 | < 25mph | AT301 | 1.62 | 2015-05-02T23:56:00Z | 18.99 | 119 | < 25mph
PG&E | 2015-05-06 17:17 | 42130.7201 | 37.4273 | -119.8803 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | BOOSTER 8179 INDIAN PEEK N/O MIWUK | None | 21000 | Other | Overhead | Yes | 42130.7201 | 2015-05-06 17:17 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0307 | 2015 | 5 | 6 | 17 | 17 | 15-0032311 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 81600 | 12.4413 | 249_208 | <25mph | <15mph | HFTD - Distribution | 2015-05-06 17:17:00 | 53 | 13.2212 | FALSE | <25mph | C1522 | 2.85 | 2015-05-06T23:47:00Z | 13 | 6 | < 25mph | MIAC1 | 7.42 | 2015-05-06T23:59:00Z | 20 | 9 | < 25mph | C1522 | 2.85 | 2015-05-06T23:47:00Z | 13 | 11 | < 25mph | MIAC1 | 7.42 | 2015-05-06T23:59:00Z | 20 | 17 | < 25mph
PG&E | 2015-05-09 13:10 | 42133.5486 | 39.2343 | -121.2468 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100000103 | None | 21000 | Conductor | Overhead | Yes | 42133.5486 | 2015-05-09 13:10 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0311 | 2015 | 5 | 9 | 13 | 10 | 15-0033085 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 382926 | 12.172 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 13:10:00 | 57 | 17.071 | FALSE | <25mph | E2572 | 3.27 | 2015-05-09T19:28:00Z | 7 | 12 | < 25mph | E2572 | 3.27 | 2015-05-09T19:28:00Z | 7 | 12 | < 25mph | E2572 | 3.27 | 2015-05-09T19:28:00Z | 7 | 12 | < 25mph | E2572 | 3.27 | 2015-05-09T19:28:00Z | 7 | 12 | < 25mph
PG&E | 2015-05-09 21:37 | 42133.9007 | 39.2848 | -121.0219 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100004095 | Pacific Bell | 12000 | Fuse | Overhead | Yes | 42133.9007 | 2015-05-09 21:37 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0312 | 2015 | 5 | 9 | 21 | 37 | 15-0033109 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 11 | 9.2188 | 198_310 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 21:37:00 | 58 | 15.4234 | FALSE | <25mph | E5439 | 3.42 | 2015-05-10T04:00:00Z | 4 | 28 | < 25mph | RRRC1 | 5.26 | 2015-05-10T04:13:00Z | 5.99 | 66 | < 25mph | E5439 | 3.42 | 2015-05-10T04:00:00Z | 4 | 56 | < 25mph | RRRC1 | 5.26 | 2015-05-10T05:13:00Z | 5.99 | 130 | < 25mph
PG&E | 2015-05-21 09:23 | 42145.391 | 38.5996 | -122.9935 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 4 SPANS LOAD SIDE 2993 |  | 12000 | Conductor | Overhead | Yes | 42145.391 | 2015-05-21 09:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0324 | 2015 | 5 | 21 | 9 | 23 | 15-0035686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2850 | 1.6525 | 114_273 | <25mph | <15mph | HFTD - Distribution | 2015-05-21 09:23:00 | 70 | 15.124 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D3481 | 5.82 | 2015-05-21T16:22:00Z | 4 | 31 | < 25mph |  |  |  | 0 | 0 | No data | D3481 | 5.82 | 2015-05-21T17:17:00Z | 7 | 63 | < 25mph
PG&E | 2015-05-27 21:44 | 42151.9056 | 39.169 | -120.9612 | Vegetation | Rural | < 0.25 Acres | Fire Agency | PEARDALE F.D. | 100077687 |  | 12000 | Conductor | Overhead | Yes | 42151.9056 | 2015-05-27 21:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0329 | 2015 | 5 | 27 | 21 | 44 | 15-0036850 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10828 | 3.691 | 201_303 | <25mph | <15mph | HFTD - Distribution | 2015-05-27 21:44:00 | 75 | 11.9096 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5439 | 7.11 | 2015-05-28T04:20:00Z | 2.01 | 62 | < 25mph |  |  |  | 0 | 0 | No data | SETC1 | 4.24 | 2015-05-28T05:28:00Z | 5.99 | 119 | < 25mph
PG&E | 2015-06-03 09:33 | 42158.3979 | 39.6896 | -121.6216 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42158.3979 | 2015-06-03 09:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0341 | 2015 | 6 | 3 | 9 | 33 | 15-0038091 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 28146 | 6.3564 | 173_332 | <25mph | <15mph | HFTD - Distribution | 2015-06-03 09:33:00 | 87 | 12.6567 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JBGC1 | 7.74 | 2015-06-03T16:13:00Z | 8.99 | 12 | < 25mph |  |  |  | 0 | 0 | No data | CICC1 | 6.93 | 2015-06-03T16:54:00Z | 10 | 25 | < 25mph
PG&E | 2015-06-04 13:17 | 42159.5535 | 39.2694 | -123.7841 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42159.5535 | 2015-06-04 13:17 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0344 | 2015 | 6 | 4 | 13 | 17 | 15-0038501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20525 | 22.1312 | 81_311 | <25mph | <15mph | HFTD - Distribution | 2015-06-04 13:17:00 | 90 | 22.6218 | FALSE | <25mph | KLLR | 1.7 | 2015-06-04T19:55:00Z | 16.11 | 7 | < 25mph | KLLR | 1.7 | 2015-06-04T19:55:00Z | 16.11 | 9 | < 25mph | KLLR | 1.7 | 2015-06-04T20:55:00Z | 17.25 | 14 | < 25mph | KLLR | 1.7 | 2015-06-04T20:55:00Z | 17.25 | 18 | < 25mph
PG&E | 2015-06-04 20:00 | 42159.8333 | 38.6916 | -120.8606 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101412760 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42159.8333 | 2015-06-04 20:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0347 | 2015 | 6 | 4 | 20 | 0 | 15-0038597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 9640 | 2.0731 | 205_277 | <25mph | <15mph | HFTD - Distribution | 2015-06-04 20:00:00 | 93 | 11.0268 | FALSE | <25mph | E6490 | 1.72 | 2015-06-05T02:01:00Z | 7 | 25 | < 25mph | D4464 | 6.46 | 2015-06-05T02:16:00Z | 8.01 | 60 | < 25mph | E6490 | 1.72 | 2015-06-05T02:01:00Z | 7 | 49 | < 25mph | D4464 | 6.46 | 2015-06-05T02:16:00Z | 8.01 | 119 | < 25mph
PG&E | 2015-06-05 01:25 | 42160.059 | 38.3461 | -122.3998 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | 4870 REDWOOD |  | 21000 | Conductor | Overhead | Yes | 42160.059 | 2015-06-05 01:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0348 | 2015 | 6 | 5 | 1 | 25 | 15-0038607 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 53842 | 2.8209 | 139_258 | <25mph | <15mph | HFTD - Distribution | 2015-06-05 01:25:00 | 94 | 16.3328 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6860 | 6.98 | 2015-06-05T08:07:00Z | 1.01 | 23 | < 25mph |  |  |  | 0 | 0 | No data | E6860 | 6.98 | 2015-06-05T09:22:00Z | 1.01 | 45 | < 25mph
PG&E | 2015-06-06 15:38 | 42161.6514 | 39.0409 | -123.4019 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 11480 ANDERSON VALLEY WAY @ BRIDGE |  | 12000 | Conductor | Overhead | Yes | 42161.6514 | 2015-06-06 15:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0355 | 2015 | 6 | 6 | 15 | 38 | 15-0039056 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 1748 | 19.2204 | 97_298 | <25mph | <15mph | HFTD - Distribution | 2015-06-06 15:38:00 | 101 | 19.2204 | FALSE | <25mph | E4777 | 3.27 | 2015-06-06T22:26:00Z | 14 | 2 | < 25mph | BNVC1 | 4.68 | 2015-06-06T21:50:00Z | 17 | 7 | < 25mph | E4777 | 3.27 | 2015-06-06T22:40:00Z | 14 | 3 | < 25mph | BNVC1 | 4.68 | 2015-06-06T22:50:00Z | 21 | 13 | < 25mph
PG&E | 2015-06-08 14:18 | 42163.5958 | 38.1796 | -120.959 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 102048579 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42163.5958 | 2015-06-08 14:18 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0360 | 2015 | 6 | 8 | 14 | 18 | 15-0039368 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 65168 | 7.0021 | 201_249 | <25mph | <15mph | HFTD - Distribution | 2015-06-08 14:18:00 | 106 | 9.7763 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CMAC1 | 5.88 | 2015-06-08T20:59:00Z | 12.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CMAC1 | 5.88 | 2015-06-08T21:59:00Z | 12.01 | 2 | < 25mph
PG&E | 2015-06-09 15:24 | 42164.6417 | 38.3651 | -122.2541 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | load side 2987 | Yes | 21000 | Conductor | Overhead | Yes | 42164.6417 | 2015-06-09 15:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0368 | 2015 | 6 | 9 | 15 | 24 | 15-0039825 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 651298 | 15.2247 | 145_259 | <25mph | <15mph | HFTD - Distribution | 2015-06-09 15:24:00 | 114 | 15.4726 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ATLC1 | 7.61 | 2015-06-09T21:29:00Z | 48 | 21 | 40-55mph |  |  |  | 0 | 0 | No data | ATLC1 | 7.61 | 2015-06-09T22:29:00Z | 53.02 | 41 | 40-55mph
PG&E | 2015-06-09 16:20 | 42164.6806 | 38.3822 | -122.4316 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102269716 | Pacific Bell | 21000 | Unknown | Overhead | Yes | 42164.6806 | 2015-06-09 16:20 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0369 | 2015 | 6 | 9 | 16 | 20 | 15-0039860 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 4184 | 20.783 | 138_260 | <25mph | <15mph | HFTD - Distribution | 2015-06-09 16:20:00 | 115 | 24.1918 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7241 | 7.11 | 2015-06-09T22:38:00Z | 17.98 | 18 | < 25mph |  |  |  | 0 | 0 | No data | E7241 | 7.11 | 2015-06-09T22:38:00Z | 17.98 | 38 | < 25mph
PG&E | 2015-06-12 13:07 | 42167.5465 | 40.4077 | -122.4104 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS STREET FROM 4139 OLD HAPPY VALLEY RD |  | 12000 | Lightning Arrestor | Overhead | No |  |  | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | no-match | 0378 | 2015 | 6 | 12 | 13 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Lightning Arrestor | N.A. | 9.7698 | 140_372 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 13:07:00 | 124 | 24.3549 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 7.46 | 2015-06-12T19:27:00Z | 14.99 | 8 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 7.46 | 2015-06-12T20:15:00Z | 20 | 16 | < 25mph
PG&E | 2015-06-12 23:32 | 42167.9806 | 39.2308 | -121.1559 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 10903 PROSPECTOR RD ROUGH AND READY | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42167.9806 | 2015-06-12 23:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0380 | 2015 | 6 | 12 | 23 | 32 | 15-0040789 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 20 | 12.2901 | 193_307 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 23:32:00 | 126 | 14.4252 | FALSE | <25mph | E2572 | 1.63 | 2015-06-13T06:29:00Z | 5.99 | 18 | < 25mph | E5439 | 5.49 | 2015-06-13T06:25:00Z | 8.99 | 65 | < 25mph | E2572 | 1.63 | 2015-06-13T06:34:00Z | 5.99 | 35 | < 25mph | RRRC1 | 5.44 | 2015-06-13T07:13:00Z | 12.01 | 129 | < 25mph
PG&E | 2015-06-15 15:35 | 42170.6493 | 37.1852 | -121.7595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Jose city | 100618215 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42170.6493 | 2015-06-15 15:35 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0384 | 2015 | 6 | 15 | 15 | 35 | 15-0041178 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 345 | 20.7397 | 166_194 | <25mph | <15mph | HFTD - Distribution | 2015-06-15 15:35:00 | 130 | 21.599 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C9520 | 5.63 | 2015-06-15T21:46:00Z | 11.99 | 42 | < 25mph |  |  |  | 0 | 0 | No data | C2789 | 6.18 | 2015-06-15T23:35:00Z | 14 | 84 | < 25mph
PG&E | 2015-06-21 13:31 | 42176.5632 | 37.375 | -119.6116 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103204866 |  | 0 – 750 | Conductor | Overhead | No |  |  | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0399 | 2015 | 6 | 21 | 13 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 11.8124 | 260_205 | <25mph | <15mph | HFTD - Distribution | 2015-06-21 13:31:00 | 145 | 12.2407 | FALSE | <25mph | D7171 | 3.95 | 2015-06-21T19:55:00Z | 16.98 | 25 | < 25mph | MIAC1 | 7.96 | 2015-06-21T19:59:00Z | 22.01 | 69 | < 25mph | AT301 | 3.85 | 2015-06-21T21:27:00Z | 18.99 | 49 | < 25mph | MIAC1 | 7.96 | 2015-06-21T19:59:00Z | 22.01 | 133 | < 25mph
PG&E | 2015-06-22 11:58 | 42177.4986 | 39.1737 | -121.0667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | SENTINAL WY |  | 12000 | Conductor | Overhead | Yes | 42177.4986 | 2015-06-22 11:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0400 | 2015 | 6 | 22 | 11 | 58 | 15-0042502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 148438 | 10.8591 | 197_304 | <25mph | <15mph | HFTD - Distribution | 2015-06-22 11:58:00 | 146 | 12.4713 | FALSE | <25mph | AS856 | 3.16 | 2015-06-22T18:58:00Z | 10 | 25 | < 25mph | E5439 | 4.77 | 2015-06-22T18:56:00Z | 10.98 | 85 | < 25mph | AS856 | 3.16 | 2015-06-22T19:58:00Z | 11.99 | 49 | < 25mph | AS856 | 3.16 | 2015-06-22T19:58:00Z | 11.99 | 170 | < 25mph
PG&E | 2015-06-27 12:48 | 42182.5333 | 37.9474 | -120.4274 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101034512 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.5333 | 2015-06-27 12:48 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0414 | 2015 | 6 | 27 | 12 | 48 | 15-0043755 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 150075 | 11.0891 | 224_236 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 12:48:00 | 159 | 19.6587 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data | KO22 | 5.72 | 2015-06-27T19:55:00Z | 16.11 | 1 | < 25mph
PG&E | 2015-06-27 21:15 | 42182.8854 | 39.2699 | -121.0403 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 16151 INDAIN FLAT RD |  | 12000 | Conductor | Overhead | Yes | 42182.8854 | 2015-06-27 21:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0416 | 2015 | 6 | 27 | 21 | 15 | 15-0043789 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4210 | 5.8168 | 198_309 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 21:15:00 | 161 | 11.6482 | FALSE | <25mph | E5439 | 2.06 | 2015-06-28T04:15:00Z | 2.01 | 40 | < 25mph | RRRC1 | 4.73 | 2015-06-28T04:13:00Z | 7 | 49 | < 25mph | E5439 | 2.06 | 2015-06-28T05:15:00Z | 4 | 72 | < 25mph | RRRC1 | 4.73 | 2015-06-28T04:13:00Z | 7 | 88 | < 25mph
PG&E | 2015-06-27 22:28 | 42182.9361 | 38.1194 | -120.6218 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 101281699 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.9361 | 2015-06-27 22:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0417 | 2015 | 6 | 27 | 22 | 28 | 15-0043798 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 517 | 14.2862 | 216_246 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 22:28:00 | 162 | 15.5829 | FALSE | <25mph | C9085 | 3.92 | 2015-06-28T05:15:00Z | 1.01 | 2 | < 25mph | C9085 | 3.92 | 2015-06-28T05:15:00Z | 1.01 | 2 | < 25mph | C9085 | 3.92 | 2015-06-28T06:05:00Z | 1.01 | 5 | < 25mph | C9085 | 3.92 | 2015-06-28T06:05:00Z | 1.01 | 5 | < 25mph
PG&E | 2015-06-28 02:50 | 42183.1181 | 35.491 | -120.731 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 13505 Santa Lucia Rd. Atascadero |  | 12000 | Conductor | Overhead | Yes | 42183.1181 | 2015-06-28 02:50 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0418 | 2015 | 6 | 28 | 2 | 50 | 15-0043807 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 12323 | 9.9634 | 212_101 | <25mph | <15mph | HFTD - Distribution | 2015-06-28 02:50:00 | 163 | 24.8049 | FALSE | <25mph | E6394 | 1.17 | 2015-06-28T09:37:00Z | 0 | 4 | < 25mph | E2260 | 6.83 | 2015-06-28T09:01:00Z | 3 | 6 | < 25mph | E6394 | 1.17 | 2015-06-28T10:22:00Z | 3 | 8 | < 25mph | E6394 | 1.17 | 2015-06-28T10:22:00Z | 3 | 15 | < 25mph
PG&E | 2015-06-28 21:07 | 42183.8799 | 39.7405 | -121.4974 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | DEADWOOD RD, JARBO GAP |  | 12000 | Conductor | Overhead | Yes | 42183.8799 | 2015-06-28 21:07 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0424 | 2015 | 6 | 28 | 21 | 7 | 15-0043869 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 45683 | 12.2547 | 178_335 | <25mph | <15mph | HFTD - Distribution | 2015-06-28 21:07:00 | 169 | 17.5682 | FALSE | <25mph | JBGC1 | 0.55 | 2015-06-29T03:13:00Z | 4.99 | 1 | < 25mph | JBGC1 | 0.55 | 2015-06-29T03:13:00Z | 4.99 | 2 | < 25mph | JBGC1 | 0.55 | 2015-06-29T04:13:00Z | 5.99 | 2 | < 25mph | JBGC1 | 0.55 | 2015-06-29T04:13:00Z | 5.99 | 7 | < 25mph
PG&E | 2015-06-30 18:18 | 42185.7625 | 36.2199 | -121.7534 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | loadside of 88973 | unknown | 12000 | Conductor | Overhead | Yes | 42185.7625 | 2015-06-30 18:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0432 | 2015 | 6 | 30 | 18 | 18 | 15-0044405 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 158 | 5.7006 | 166_141 | <25mph | <15mph | HFTD - Distribution | 2015-06-30 18:18:00 | 177 | 8.2628 | FALSE | <25mph | PPSC1 | 2.3 | 2015-07-01T01:04:00Z | 8.99 | 1 | < 25mph | PPSC1 | 2.3 | 2015-07-01T01:04:00Z | 8.99 | 3 | < 25mph | PPSC1 | 2.3 | 2015-07-01T01:04:00Z | 8.99 | 2 | < 25mph | PPSC1 | 2.3 | 2015-07-01T01:04:00Z | 8.99 | 8 | < 25mph
PG&E | 2015-07-01 09:17 | 42186.3868 | 38.5715 | -122.5443 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42186.3868 | 2015-07-01 09:17 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0433 | 2015 | 7 | 1 | 9 | 17 | 15-0044529 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 85168 | 0.56943 | 133_271 | <25mph | <15mph | HFTD - Distribution | 2015-07-01 09:17:00 | 178 | 20.9979 | FALSE | <25mph | E2050 | 3.6 | 2015-07-01T16:14:00Z | 3 | 4 | < 25mph | E2050 | 3.6 | 2015-07-01T16:14:00Z | 3 | 21 | < 25mph | E2050 | 3.6 | 2015-07-01T17:15:00Z | 4.99 | 8 | < 25mph | E2050 | 3.6 | 2015-07-01T17:15:00Z | 4.99 | 33 | < 25mph
PG&E | 2015-07-01 12:57 | 42186.5396 | 39.4146 | -121.379 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42186.5396 | 2015-07-01 12:57 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0434 | 2015 | 7 | 1 | 12 | 57 | 15-0044609 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 12.6482 | 183_317 | <25mph | <15mph | HFTD - Distribution | 2015-07-01 12:57:00 | 179 | 18.7031 | FALSE | <25mph | BNGC1 | 2.37 | 2015-07-01T19:51:00Z | 15.99 | 1 | < 25mph | BNGC1 | 2.37 | 2015-07-01T19:51:00Z | 15.99 | 1 | < 25mph | BNGC1 | 2.37 | 2015-07-01T20:51:00Z | 17 | 2 | < 25mph | BNGC1 | 2.37 | 2015-07-01T20:51:00Z | 17 | 2 | < 25mph
PG&E | 2015-07-03 03:23 | 42188.141 | 35.6785 | -120.9567 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 1 soan 1 conducter 1 span loade side transformer formtr 1008493290 |  | 21000 | Conductor | Overhead | Yes | 42188.141 | 2015-07-03 03:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0438 | 2015 | 7 | 3 | 3 | 23 | 15-0045239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 978 | 7.7054 | 202_111 | <25mph | <15mph | HFTD - Distribution | 2015-07-03 03:23:00 | 183 | 16.8894 | FALSE | <25mph | TABC1 | 2.38 | 2015-07-03T10:07:00Z | 1.01 | 1 | < 25mph | D4060 | 6.58 | 2015-07-03T10:19:00Z | 2.01 | 5 | < 25mph | TABC1 | 2.38 | 2015-07-03T11:07:00Z | 3 | 2 | < 25mph | TABC1 | 2.38 | 2015-07-03T11:07:00Z | 3 | 10 | < 25mph
PG&E | 2015-07-04 01:14 | 42189.0514 | 38.9566 | -121.0434 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100037226 |  | 12000 | Other | Overhead | Yes | 42189.0514 | 2015-07-04 01:14 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0441 | 2015 | 7 | 4 | 1 | 14 | 15-0045440 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 53865 | 7.3476 | 198_292 | <25mph | <15mph | HFTD - Distribution | 2015-07-04 01:14:00 | 186 | 12.3228 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8862 | 5.23 | 2015-07-04T07:21:00Z | 5.99 | 25 | < 25mph |  |  |  | 0 | 0 | No data | D8862 | 5.23 | 2015-07-04T07:21:00Z | 5.99 | 49 | < 25mph
PG&E | 2015-07-05 09:42 | 42190.4042 | 35.5323 | -120.7371 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 0 – 750 | Conductor | Overhead | No |  |  | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0444 | 2015 | 7 | 5 | 9 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 11.0729 | 211_103 | <25mph | <15mph | HFTD - Distribution | 2015-07-05 09:42:00 | 189 | 25.4306 | FALSE | 25-40mph | E6394 | 1.7 | 2015-07-05T16:08:00Z | 12.01 | 4 | < 25mph | E6394 | 1.7 | 2015-07-05T16:08:00Z | 12.01 | 4 | < 25mph | E6394 | 1.7 | 2015-07-05T16:54:00Z | 13 | 8 | < 25mph | E6394 | 1.7 | 2015-07-05T16:54:00Z | 13 | 8 | < 25mph
PG&E | 2015-07-05 21:21 | 42190.8896 | 38.6524 | -120.6278 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | one span east of c/o 1055 |  | 21000 | Conductor | Overhead | Yes | 42190.8896 | 2015-07-05 21:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0445 | 2015 | 7 | 5 | 21 | 21 | 15-0045605 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 22374 | 5.6191 | 215_275 | <25mph | <15mph | HFTD - Distribution | 2015-07-05 21:21:00 | 190 | 12.9317 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GZFC1 | 5.69 | 2015-07-06T04:17:00Z | 3 | 1 | < 25mph |  |  |  | 0 | 0 | No data | GZFC1 | 5.69 | 2015-07-06T04:17:00Z | 3 | 2 | < 25mph
PG&E | 2015-07-07 10:42 | 42192.4458 | 39.1138 | -121.0655 | Vegetation | Rural | < 0.25 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42192.4458 | 2015-07-07 10:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0448 | 2015 | 7 | 7 | 10 | 42 | 15-0045985 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 46738 | 10.1548 | 197_300 | <25mph | <15mph | HFTD - Distribution | 2015-07-07 10:42:00 | 193 | 12.5396 | FALSE | <25mph | C5488 | 3.42 | 2015-07-07T17:40:00Z | 4.99 | 4 | < 25mph | E1789 | 4.22 | 2015-07-07T17:18:00Z | 7 | 55 | < 25mph | C5488 | 3.42 | 2015-07-07T18:20:00Z | 7 | 9 | < 25mph | E1789 | 4.22 | 2015-07-07T18:42:00Z | 8.01 | 115 | < 25mph
PG&E | 2015-07-07 15:27 | 42192.6438 | 35.155 | -120.5442 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 303corraltos cyn rd | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42192.6438 | 2015-07-07 15:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0449 | 2015 | 7 | 7 | 15 | 27 | 15-0046127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 98566 | 24.1391 | 220_82 | <25mph | <15mph | HFTD - Distribution | 2015-07-07 15:27:00 | 194 | 24.1391 | FALSE | <25mph | C9814 | 3.58 | 2015-07-07T22:23:00Z | 10 | 6 | < 25mph | KSBP | 7.64 | 2015-07-07T21:56:00Z | 34.52 | 7 | 25-40mph | C9814 | 3.58 | 2015-07-07T23:03:00Z | 10 | 12 | < 25mph | KSBP | 7.64 | 2015-07-07T21:56:00Z | 34.52 | 14 | 25-40mph
PG&E | 2015-07-12 17:04 | 42197.7111 | 37.4713 | -122.4256 | Vegetation | Rural | < 0.25 Acres | Fire Agency | COUNTY FIRE | 1 s w c509 |  | 12000 | Conductor | Overhead | Yes | 42197.7111 | 2015-07-12 17:04 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown | Jumper | Other/Unknown | 0456 | 2015 | 7 | 12 | 17 | 4 | 15-0047023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 117853 | 14.8289 | 137_210 | <25mph | <15mph | HFTD - Distribution | 2015-07-12 17:04:00 | 201 | 14.9925 | FALSE | <25mph | D9259 | 3.49 | 2015-07-12T23:43:00Z | 5.99 | 4 | < 25mph | PUGC1 | 7 | 2015-07-12T23:18:00Z | 25.99 | 48 | 25-40mph | D9259 | 3.49 | 2015-07-13T00:28:00Z | 5.99 | 8 | < 25mph | PUGC1 | 7 | 2015-07-12T23:18:00Z | 25.99 | 99 | 25-40mph
PG&E | 2015-07-15 09:00 | 42200.375 | 36.997 | -121.7381 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101795728 |  | 21000 | Conductor | Overhead | Yes | 42200.375 | 2015-07-15 09:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0463 | 2015 | 7 | 15 | 9 | 0 | 15-0047650 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3800 | 8.5113 | 167_184 | <25mph | <15mph | HFTD - Distribution | 2015-07-15 09:00:00 | 208 | 13.379 | FALSE | <25mph | CTOC1 | 3.71 | 2015-07-15T15:27:00Z | 3 | 1 | < 25mph | E4962 | 6.01 | 2015-07-15T15:52:00Z | 4.99 | 32 | < 25mph | CTOC1 | 3.71 | 2015-07-15T15:27:00Z | 3 | 2 | < 25mph | C4503 | 7.38 | 2015-07-15T16:55:00Z | 7 | 65 | < 25mph
PG&E | 2015-07-16 19:11 | 42201.7993 | 37.1989 | -119.7712 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 20334 ROAD 400 |  | 12000 | Conductor | Overhead | Yes | 42201.7993 | 2015-07-16 19:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0465 | 2015 | 7 | 16 | 19 | 11 | 15-0048064 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 8.6422 | 254_195 | <25mph | <15mph | HFTD - Distribution | 2015-07-16 19:11:00 | 210 | 13.1745 | FALSE | <25mph | D7022 | 1.32 | 2015-07-17T01:21:00Z | 11.01 | 20 | < 25mph | D7022 | 1.32 | 2015-07-17T01:21:00Z | 11.01 | 20 | < 25mph | D7022 | 1.32 | 2015-07-17T01:21:00Z | 11.01 | 38 | < 25mph | D7022 | 1.32 | 2015-07-17T01:21:00Z | 11.01 | 38 | < 25mph
PG&E | 2015-07-18 17:00 | 42203.7083 | 38.8383 | -123.6297 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | off HWY 1 PA |  | 12000 | Conductor | Overhead | Yes | 42203.7083 | 2015-07-18 17:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0470 | 2015 | 7 | 18 | 17 | 0 | 15-0048394 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 51806 | 18.0824 | 86_287 | <25mph | <15mph | HFTD - Distribution | 2015-07-18 17:00:00 | 215 | 27.3037 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | ANVC1 | 6.68 | 2015-07-18T23:36:00Z | 14.99 | 10 | < 25mph |  |  |  | 0 | 0 | No data | ANVC1 | 6.68 | 2015-07-18T23:36:00Z | 14.99 | 20 | < 25mph
PG&E | 2015-07-22 14:21 | 42207.5979 | 38.7935 | -120.714 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | s\ 3204 stope dr |  | 12000 | Conductor | Overhead | Yes | 42207.5979 | 2015-07-22 14:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0478 | 2015 | 7 | 22 | 14 | 21 | 15-0049908 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 149206 | 14.9339 | 212_283 | <25mph | <15mph | HFTD - Distribution | 2015-07-22 14:21:00 | 223 | 15.8107 | FALSE | <25mph | E3165 | 1.79 | 2015-07-22T20:38:00Z | 10 | 5 | < 25mph | BDMC1 | 7.66 | 2015-07-22T20:36:00Z | 17 | 24 | < 25mph | E3165 | 1.79 | 2015-07-22T21:39:00Z | 14 | 11 | < 25mph | BDMC1 | 7.66 | 2015-07-22T20:36:00Z | 17 | 51 | < 25mph
PG&E | 2015-07-24 14:30 | 42209.6042 | 36.6913 | -119.0312 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46970 DUNLAP RD | YES | 0 – 750 | Transformer | Overhead | Yes | 42209.6042 | 2015-07-24 14:30 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0482 | 2015 | 7 | 24 | 14 | 30 | 15-0050401 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 281 | 12.3885 | 287_168 | <25mph | <15mph | HFTD - Distribution | 2015-07-24 14:30:00 | 227 | 13.0893 | FALSE | <25mph | PHRC1 | 0.81 | 2015-07-24T20:58:00Z | 14.99 | 1 | < 25mph | PHRC1 | 0.81 | 2015-07-24T20:58:00Z | 14.99 | 11 | < 25mph | PHRC1 | 0.81 | 2015-07-24T21:58:00Z | 15.99 | 2 | < 25mph | PHRC1 | 0.81 | 2015-07-24T21:58:00Z | 15.99 | 24 | < 25mph
PG&E | 2015-07-26 12:25 | 42211.5174 | 39.1586 | -121.0634 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 15499 ALLISON RANCH RD |  | 12000 | Conductor | Overhead | Yes | 42211.5174 | 2015-07-26 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0485 | 2015 | 7 | 26 | 12 | 25 | 15-0050558 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2224 | 13.0644 | 197_303 | <25mph | <15mph | HFTD - Distribution | 2015-07-26 12:25:00 | 230 | 13.6917 | FALSE | <25mph | E1789 | 3.9 | 2015-07-26T19:24:00Z | 12.01 | 10 | < 25mph | E1789 | 3.9 | 2015-07-26T19:24:00Z | 12.01 | 68 | < 25mph | E1789 | 3.9 | 2015-07-26T19:54:00Z | 12.01 | 20 | < 25mph | E6355 | 6.63 | 2015-07-26T20:21:00Z | 12.01 | 133 | < 25mph
PG&E | 2015-07-30 17:56 | 42215.7472 | 37.9021 | -120.4739 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101019808 |  | 17000 | Conductor | Overhead | Yes | 42215.7472 | 2015-07-30 17:56 | Contact From Object | N.A. | Other | Electric Facility | Unknown | osprey nest | Other/Unknown | 0499 | 2015 | 7 | 30 | 17 | 56 | 15-0051764 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 615 | 11.6086 | 222_234 | <25mph | <15mph | HFTD - Distribution | 2015-07-30 17:56:00 | 244 | 16.9062 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.96 | 2015-07-31T00:03:00Z | 18.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.96 | 2015-07-31T00:03:00Z | 18.99 | 2 | < 25mph
PG&E | 2015-07-30 19:11 | 42215.7993 | 37.8102 | -120.1287 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE |  |  | 17000 | Conductor | Overhead | Yes | 42215.7993 | 2015-07-30 19:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0500 | 2015 | 7 | 30 | 19 | 11 | 15-0051772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26776 | 10.007 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2015-07-30 19:11:00 | 245 | 11.7658 | FALSE | <25mph | SEWC1 | 1.66 | 2015-07-31T01:16:00Z | 14.99 | 5 | < 25mph | SEWC1 | 1.66 | 2015-07-31T01:16:00Z | 14.99 | 7 | < 25mph | SEWC1 | 1.66 | 2015-07-31T01:16:00Z | 14.99 | 10 | < 25mph | SEWC1 | 1.66 | 2015-07-31T01:16:00Z | 14.99 | 14 | < 25mph
PG&E | 2015-07-31 22:45 | 42216.9479 | 38.3805 | -120.5628 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS FROM 1958 QUAIL LN WEST POINT | None | 12000 | Conductor | Overhead | Yes | 42216.9479 | 2015-07-31 22:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0503 | 2015 | 7 | 31 | 22 | 45 | 15-0052033 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 33559 | 6.4734 | 218_260 | <25mph | <15mph | HFTD - Distribution | 2015-07-31 22:45:00 | 248 | 15.0324 | FALSE | <25mph | AT450 | 2.7 | 2015-08-01T05:19:00Z | 3 | 3 | < 25mph | C9148 | 7.8 | 2015-08-01T04:48:00Z | 7 | 20 | < 25mph | AT450 | 2.7 | 2015-08-01T06:45:00Z | 4 | 5 | < 25mph | C9148 | 7.8 | 2015-08-01T04:48:00Z | 7 | 38 | < 25mph
PG&E | 2015-08-03 00:07 | 42219.0049 | 40.5056 | -122.347 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | COTTONWOOD FIRE DEPT | 101503428 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42219.0049 | 2015-08-03 00:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0509 | 2015 | 8 | 3 | 0 | 7 | 15-0052184 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 10427 | 9.7241 | 143_378 | <25mph | <15mph | HFTD - Distribution | 2015-08-03 00:07:00 | 254 | 13.2206 | FALSE | <25mph | RRAC1 | 2.97 | 2015-08-03T06:24:00Z | 8.01 | 7 | < 25mph | RRAC1 | 2.97 | 2015-08-03T06:24:00Z | 8.01 | 15 | < 25mph | RRAC1 | 2.97 | 2015-08-03T06:24:00Z | 8.01 | 14 | < 25mph | RRAC1 | 2.97 | 2015-08-03T06:24:00Z | 8.01 | 30 | < 25mph
PG&E | 2015-08-03 17:53 | 42219.7451 | 39.3361 | -121.1894 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Pole 000/008 |  | 60000 | Conductor | Overhead | Yes | 42219.7451 | 2015-08-03 17:53 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0510 | 2015 | 8 | 3 | 17 | 53 | TM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 11.0618 | 191_313 | <25mph | <15mph | HFTD - Transmission | 2015-08-03 17:53:00 | 255 | 11.5241 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RRRC1 | 4.47 | 2015-08-04T00:13:00Z | 14 | 30 | < 25mph |  |  |  | 0 | 0 | No data | RRRC1 | 4.47 | 2015-08-04T01:13:00Z | 14.99 | 60 | < 25mph
PG&E | 2015-08-04 16:05 | 42220.6701 | 40.0822 | -121.1538 | Vegetation | Rural | < 0.25 Acres | Fire Agency | USFS | 100441220 | None | 0 – 750 | Fuse | Overhead | Yes | 42220.6701 | 2015-08-04 16:05 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0511 | 2015 | 8 | 4 | 16 | 5 | 15-0052743 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 4591 | 11.3093 | 193_354 | <25mph | <15mph | HFTD - Distribution | 2015-08-04 16:05:00 | 256 | 18.1222 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TR180 | 5.53 | 2015-08-04T22:59:00Z | 14 | 1 | < 25mph |  |  |  | 0 | 0 | No data | TR180 | 5.53 | 2015-08-04T22:59:00Z | 14 | 2 | < 25mph
PG&E | 2015-08-07 06:32 | 42223.2722 | 37.84 | -122.1823 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100498058 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42223.2722 | 2015-08-07 06:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0517 | 2015 | 8 | 7 | 6 | 32 | 15-0053493 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.7497 | 148_230 | <25mph | <15mph | HFTD - Distribution | 2015-08-07 06:32:00 | 261 | 20.6611 | FALSE | <25mph | ONOC1 | 2.72 | 2015-08-07T12:33:00Z | 14 | 60 | < 25mph | LTRC1 | 6.31 | 2015-08-07T13:28:00Z | 24.99 | 155 | < 25mph | ONOC1 | 2.72 | 2015-08-07T12:33:00Z | 14 | 120 | < 25mph | LTRC1 | 6.31 | 2015-08-07T13:28:00Z | 24.99 | 305 | < 25mph
PG&E | 2015-08-08 07:42 | 42224.3208 | 39.2007 | -121.2137 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100076217 | Pacific Bell | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0519 | 2015 | 8 | 8 | 7 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 14.1661 | 190_305 | <25mph | <15mph | HFTD - Distribution | 2015-08-08 07:42:00 | 263 | 14.9803 | FALSE | <25mph | E2572 | 2.41 | 2015-08-08T13:53:00Z | 1.01 | 13 | < 25mph | E1789 | 5.79 | 2015-08-08T14:12:00Z | 4.99 | 42 | < 25mph | E2572 | 2.41 | 2015-08-08T15:38:00Z | 1.01 | 20 | < 25mph | E1789 | 5.79 | 2015-08-08T15:42:00Z | 4.99 | 77 | < 25mph
PG&E | 2015-08-12 17:38 | 42228.7347 | 40.2153 | -123.8681 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 1 SP LD SD METER 1007960761 |  | 12000 | Conductor | Overhead | Yes | 42228.7347 | 2015-08-12 17:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0525 | 2015 | 8 | 12 | 17 | 38 | 15-0054643 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 14640 | 10.9518 | 79_363 | <25mph | <15mph | HFTD - Distribution | 2015-08-12 17:38:00 | 269 | 13.2342 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ERCC1 | 5.81 | 2015-08-13T00:28:00Z | 15.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | ERCC1 | 5.81 | 2015-08-13T00:28:00Z | 15.99 | 2 | < 25mph
PG&E | 2015-08-13 03:46 | 42229.1569 | 37.2072 | -119.7343 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 44365 SAVAGE RD COARSEGOLD |  | 21000 | Conductor | Overhead | Yes | 42229.1569 | 2015-08-13 03:46 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0526 | 2015 | 8 | 13 | 3 | 46 | 15-0054655 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 7600 | 7.8941 | 255_196 | <25mph | <15mph | HFTD - Distribution | 2015-08-13 03:46:00 | 270 | 10.403 | FALSE | <25mph | D7022 | 2.54 | 2015-08-13T10:41:00Z | 0 | 6 | < 25mph | E5766 | 4.34 | 2015-08-13T10:42:00Z | 0 | 18 | < 25mph | D7022 | 2.54 | 2015-08-13T11:41:00Z | 0 | 12 | < 25mph | E5766 | 4.34 | 2015-08-13T11:42:00Z | 0 | 36 | < 25mph
PG&E | 2015-08-14 15:09 | 42230.6312 | 40.9829 | -121.7802 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101514540 |  | 21000 | Conductor | Overhead | Yes | 42230.6312 | 2015-08-14 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0530 | 2015 | 8 | 14 | 15 | 9 | 15-0055136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3072 | 14.8278 | 167_404 | <25mph | <15mph | HFTD - Distribution | 2015-08-14 15:09:00 | 274 | 16.5644 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AS418 | 7.42 | 2015-08-14T21:31:00Z | 17 | 6 | < 25mph |  |  |  | 0 | 0 | No data | AS418 | 7.42 | 2015-08-14T23:01:00Z | 17 | 12 | < 25mph
PG&E | 2015-08-14 17:44 | 42230.7389 | 37.8894 | -120.4933 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | ENTRANCE TO 14650 HWY 108, JAMESTOWN |  | 17000 | Conductor | Overhead | Yes | 42230.7389 | 2015-08-14 17:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0531 | 2015 | 8 | 14 | 17 | 44 | 15-0055160 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 1726 | 11.4655 | 222_233 | <25mph | <15mph | HFTD - Distribution | 2015-08-14 17:44:00 | 275 | 13.236 | FALSE | <25mph | GNSC1 | 3.85 | 2015-08-15T00:03:00Z | 17 | 1 | < 25mph | GNSC1 | 3.85 | 2015-08-15T00:03:00Z | 17 | 8 | < 25mph | GNSC1 | 3.85 | 2015-08-15T00:03:00Z | 17 | 2 | < 25mph | GNSC1 | 3.85 | 2015-08-15T00:03:00Z | 17 | 15 | < 25mph
PG&E | 2015-08-16 07:35 | 42232.316 | 35.4572 | -120.6567 | Vegetation | Rural | < 3 meters | Utility: PG&E |  | 8932 SAN GABRIEL RD. SW C/O OF LOT, Atascadero | None | 0 – 750 | Conductor | Overhead | Yes | 42232.316 | 2015-08-16 07:35 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0534 | 2015 | 8 | 16 | 7 | 35 | 15-0055284 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.0129 | 215_99 | <25mph | <15mph | HFTD - Distribution | 2015-08-16 07:35:00 | 278 | 16.9932 | FALSE | <25mph | E1179 | 1.71 | 2015-08-16T14:13:00Z | 2.01 | 4 | < 25mph | E1179 | 1.71 | 2015-08-16T14:13:00Z | 2.01 | 9 | < 25mph | E2260 | 2.13 | 2015-08-16T15:10:00Z | 2.01 | 11 | < 25mph | E2260 | 2.13 | 2015-08-16T15:10:00Z | 2.01 | 19 | < 25mph
PG&E | 2015-08-17 08:37 | 42233.359 | 37.0757 | -122.023 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101800237 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0537 | 2015 | 8 | 17 | 8 | 37 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 1.4249 | 154_188 | <25mph | <15mph | HFTD - Distribution | 2015-08-17 08:37:00 | 281 | 11.7495 | FALSE | <25mph | E5965 | 3.61 | 2015-08-17T15:35:00Z | 4 | 32 | < 25mph | AR172 | 6.98 | 2015-08-17T15:30:00Z | 4.99 | 145 | < 25mph | E5965 | 3.61 | 2015-08-17T16:35:00Z | 7 | 63 | < 25mph | E5965 | 3.61 | 2015-08-17T16:35:00Z | 7 | 286 | < 25mph
PG&E | 2015-08-17 20:57 | 42233.8729 | 36.6867 | -119.0612 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46371 ORCHARD DRIVE |  | 12000 | Conductor | Overhead | Yes | 42233.8729 | 2015-08-17 20:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0540 | 2015 | 8 | 17 | 20 | 57 | 15-0055696 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 34398 | 8.6424 | 285_168 | <25mph | <15mph | HFTD - Distribution | 2015-08-17 20:57:00 | 284 | 13.6283 | FALSE | <25mph | PHRC1 | 2.47 | 2015-08-18T02:58:00Z | 5.99 | 1 | < 25mph | PHRC1 | 2.47 | 2015-08-18T02:58:00Z | 5.99 | 2 | < 25mph | PHRC1 | 2.47 | 2015-08-18T03:58:00Z | 8.99 | 2 | < 25mph | PHRC1 | 2.47 | 2015-08-18T03:58:00Z | 8.99 | 14 | < 25mph
PG&E | 2015-08-19 06:20 | 42235.2639 | 39.2831 | -123.2931 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | MTR#50001225 | None | 12000 | Conductor | Overhead | Yes | 42235.2639 | 2015-08-19 06:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0545 | 2015 | 8 | 19 | 6 | 20 | 15-0055982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5403 | 1.4303 | 102_311 | <25mph | <15mph | HFTD - Distribution | 2015-08-19 06:20:00 | 289 | 19.8186 | FALSE | <25mph | AU552 | 3.69 | 2015-08-19T12:42:00Z | 5.99 | 12 | < 25mph | AU552 | 3.69 | 2015-08-19T12:42:00Z | 5.99 | 40 | < 25mph | AU552 | 3.69 | 2015-08-19T12:42:00Z | 5.99 | 24 | < 25mph | AU552 | 3.69 | 2015-08-19T12:42:00Z | 5.99 | 78 | < 25mph
PG&E | 2015-08-22 20:38 | 42238.8597 | 38.7748 | -120.8564 | Vegetation | Rural | < 3 meters | Self Extinguished |  | at base of co pole 21721 - 720 Woodridge Rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42238.8597 | 2015-08-22 20:38 | Contact From Object | N.A. | Vegetation | Communication Facility | Unknown | tree hit phone lines | Fell into (Moderate-Severe defect) | 0549 | 2015 | 8 | 22 | 20 | 38 | 15-0056766 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26513 | 9.2929 | 206_282 | <25mph | <15mph | HFTD - Distribution | 2015-08-22 20:38:00 | 293 | 10.7008 | FALSE | <25mph | E5691 | 3.87 | 2015-08-23T03:21:00Z | 4 | 12 | < 25mph | E5691 | 3.87 | 2015-08-23T03:21:00Z | 4 | 45 | < 25mph | E5691 | 3.87 | 2015-08-23T03:21:00Z | 4 | 24 | < 25mph | E5691 | 3.87 | 2015-08-23T03:21:00Z | 4 | 89 | < 25mph
PG&E | 2015-08-24 22:48 | 42240.95 | 37.896 | -122.6011 | Vegetation | Rural | < 3 meters | Fire Agency | marin county fire | 200' east of pan toll rd 50' north of panoramic hwy |  | 12000 | Unknown | Overhead | Yes | 42240.95 | 2015-08-24 22:48 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0552 | 2015 | 8 | 24 | 22 | 48 | 15-0057082 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 1128 | 8.5935 | 130_234 | <25mph | <15mph | HFTD - Distribution | 2015-08-24 22:48:00 | 296 | 14.2171 | FALSE | <25mph | MDEC1 | 2.32 | 2015-08-25T05:36:00Z | 13 | 5 | < 25mph | MDEC1 | 2.32 | 2015-08-25T05:36:00Z | 13 | 9 | < 25mph | MDEC1 | 2.32 | 2015-08-25T06:36:00Z | 14.99 | 10 | < 25mph | MDEC1 | 2.32 | 2015-08-25T06:36:00Z | 14.99 | 18 | < 25mph
PG&E | 2015-08-28 11:48 | 42244.4917 | 38.8513 | -121.1469 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100055373 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0562 | 2015 | 8 | 28 | 11 | 48 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 8.8306 | 193_286 | <25mph | <15mph | HFTD - Distribution | 2015-08-28 11:48:00 | 306 | 13.8724 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.53 | 2015-08-28T17:56:00Z | 10 | 16 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.53 | 2015-08-28T18:56:00Z | 13 | 30 | < 25mph
PG&E | 2015-08-28 12:02 | 42244.5014 | 37.9047 | -122.2058 | Vegetation | Rural | < 0.25 Acres | Fire Agency | EB MUD | 103623279 |  | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0563 | 2015 | 8 | 28 | 12 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 10.0355 | 147_234 | <25mph | <15mph | HFTD - Distribution | 2015-08-28 12:02:00 | 307 | 16.9223 | FALSE | <25mph | E5555 | 3.43 | 2015-08-28T18:54:00Z | 10 | 32 | < 25mph | E5555 | 3.43 | 2015-08-28T18:54:00Z | 10 | 123 | < 25mph | LBNL1 | 3.01 | 2015-08-28T19:45:00Z | 11.61 | 66 | < 25mph | E6179 | 6.07 | 2015-08-28T19:49:00Z | 13 | 251 | < 25mph
PG&E | 2015-08-29 03:30 | 42245.1458 | 38.6302 | -122.8327 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Dirt road across from 3204 Rio Lindo Rd, Healdsburg |  | 12000 | Conductor | Overhead | Yes | 42245.1458 | 2015-08-29 03:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0566 | 2015 | 8 | 29 | 3 | 30 | 15-0058127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4780 | 9.2134 | 120_274 | <25mph | <15mph | HFTD - Distribution | 2015-08-29 03:30:00 | 310 | 15.1029 | FALSE | <25mph | D2144 | 1.2 | 2015-08-29T10:00:00Z | 3 | 9 | < 25mph | HWKC1 | 7.25 | 2015-08-29T09:56:00Z | 4.99 | 27 | < 25mph | D2144 | 1.2 | 2015-08-29T10:00:00Z | 3 | 15 | < 25mph | HWKC1 | 7.25 | 2015-08-29T10:56:00Z | 12.01 | 52 | < 25mph
PG&E | 2015-08-30 17:05 | 42246.7118 | 38.4039 | -120.5559 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | centennial mine rd |  | 12000 | Conductor | Overhead | Yes | 42246.7118 | 2015-08-30 17:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0567 | 2015 | 8 | 30 | 17 | 5 | 15-0058273 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 40298 | 10.8566 | 219_261 | <25mph | <15mph | HFTD - Distribution | 2015-08-30 17:05:00 | 311 | 12.2451 | FALSE | <25mph | AT450 | 1.93 | 2015-08-30T23:45:00Z | 12.01 | 13 | < 25mph | C9148 | 6.15 | 2015-08-30T23:49:00Z | 14.99 | 27 | < 25mph | AT450 | 1.93 | 2015-08-30T23:45:00Z | 12.01 | 25 | < 25mph | C9148 | 6.15 | 2015-08-30T23:49:00Z | 14.99 | 53 | < 25mph
PG&E | 2015-08-31 14:28 | 42247.6028 | 36.5325 | -121.1462 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 29401 Hwy 25 |  | 21000 | Conductor | Overhead | Yes | 42247.6028 | 2015-08-31 14:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0568 | 2015 | 8 | 31 | 14 | 28 | 15-0058455 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25668 | 4.8975 | 193_158 | <25mph | <15mph | HFTD - Distribution | 2015-08-31 14:28:00 | 312 | 19.6836 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.27 | 2015-08-31T20:37:00Z | 13 | 1 | < 25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.27 | 2015-08-31T20:37:00Z | 13 | 2 | < 25mph
PG&E | 2015-09-04 07:49 | 42251.3257 | 40.2318 | -122.3643 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | E/O FRONTIER RD & N/O WAGON WAY |  | 12000 | Conductor | Overhead | Yes | 42251.3257 | 2015-09-04 07:49 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0577 | 2015 | 9 | 4 | 7 | 49 | 15-0059323 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 9563 | 2.343 | 142_362 | <25mph | <15mph | HFTD - Distribution | 2015-09-04 07:49:00 | 321 | 17.9748 | FALSE | <25mph | D6527 | 1.77 | 2015-09-04T13:53:00Z | 4.99 | 1 | < 25mph | E7114 | 5.07 | 2015-09-04T14:49:00Z | 24 | 4 | < 25mph | D6527 | 1.77 | 2015-09-04T13:53:00Z | 4.99 | 1 | < 25mph | E7114 | 5.07 | 2015-09-04T15:21:00Z | 30 | 7 | 25-40mph
PG&E | 2015-09-06 19:27 | 42253.8104 | 34.6195 | -120.2534 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Santa Barbara County Fire | meter# 1008400678 | Verizon | 12000 | Conductor | Overhead | Yes | 42253.8104 | 2015-09-06 19:27 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0582 | 2015 | 9 | 6 | 19 | 27 | 15-0059612 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 863 | 14.7315 | 234_53 | <25mph | <15mph | HFTD - Distribution | 2015-09-06 19:27:00 | 326 | 17.7534 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C9206 | 6.79 | 2015-09-07T02:01:00Z | 4.99 | 8 | < 25mph |  |  |  | 0 | 0 | No data | C9206 | 6.79 | 2015-09-07T02:01:00Z | 4.99 | 15 | < 25mph
PG&E | 2015-09-09 10:47 | 42256.4493 | 37.1041 | -121.8853 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100520291 |  | 12000 | Conductor | Overhead | Yes | 42256.4493 | 2015-09-09 10:47 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0587 | 2015 | 9 | 9 | 10 | 47 | 15-0060074 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 142401 | 4.2376 | 161_190 | <25mph | <15mph | HFTD - Distribution | 2015-09-09 10:47:00 | 331 | 18.9097 | FALSE | <25mph | E6085 | 0.69 | 2015-09-09T17:16:00Z | 8.01 | 10 | < 25mph | E6085 | 0.69 | 2015-09-09T17:16:00Z | 8.01 | 101 | < 25mph | E6085 | 0.69 | 2015-09-09T18:31:00Z | 10 | 20 | < 25mph | C2789 | 6.89 | 2015-09-09T18:40:00Z | 11.01 | 197 | < 25mph
PG&E | 2015-09-10 05:42 | 42257.2375 | 37.4609 | -121.8434 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100619766 | None | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0588 | 2015 | 9 | 10 | 5 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 1.7354 | 163_209 | <25mph | <15mph | HFTD - Distribution | 2015-09-10 05:42:00 | 333 | 13.8129 | FALSE | <25mph | E3968 | 2.89 | 2015-09-10T12:37:00Z | 2.01 | 12 | < 25mph | RSPC1 | 6.56 | 2015-09-10T12:28:00Z | 7 | 16 | < 25mph | E3968 | 2.89 | 2015-09-10T12:37:00Z | 2.01 | 25 | < 25mph | RSPC1 | 6.56 | 2015-09-10T13:28:00Z | 7 | 33 | < 25mph
PG&E | 2015-09-10 16:24 | 42257.6833 | 38.5049 | -122.3535 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103159970 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42257.6833 | 2015-09-10 16:24 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0589 | 2015 | 9 | 10 | 16 | 24 | 15-0060610 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 130124 | 14.3548 | 141_267 | <25mph | <15mph | HFTD - Distribution | 2015-09-10 16:24:00 | 334 | 16.5969 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.22 | 2015-09-10T22:29:00Z | 28.99 | 1 | 25-40mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.22 | 2015-09-10T22:29:00Z | 28.99 | 2 | 25-40mph
PG&E | 2015-09-10 18:39 | 42257.7771 | 40.7569 | -123.7958 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 096/004 |  | 115000 | Conductor | Overhead | Yes | 42257.7771 | 2015-09-10 18:39 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0590 | 2015 | 9 | 10 | 18 | 39 | RM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 2.2423 | 82_393 | <25mph | <15mph | HFTD - Transmission | 2015-09-10 18:39:00 | 335 | 12.4043 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.39 | 2015-09-11T00:55:00Z | 8.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.39 | 2015-09-11T00:55:00Z | 8.99 | 2 | < 25mph
PG&E | 2015-09-11 08:15 | 42258.3438 | 38.1094 | -122.87 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102293992 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42258.3438 | 2015-09-11 08:15 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0592 | 2015 | 9 | 11 | 8 | 15 | 15-0060698 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 32419 | 6.2068 | 118_246 | <25mph | <15mph | HFTD - Distribution | 2015-09-11 08:15:00 | 337 | 16.9176 | FALSE | <25mph | PREC1 | 3.64 | 2015-09-11T15:05:00Z | 8.99 | 1 | < 25mph | PTRCA | 4.48 | 2015-09-11T15:10:00Z | 12.91 | 7 | < 25mph | PREC1 | 3.64 | 2015-09-11T16:05:00Z | 10 | 2 | < 25mph | PTRCA | 4.48 | 2015-09-11T16:10:00Z | 13.4 | 14 | < 25mph
PG&E | 2015-09-12 09:51 | 42259.4104 | 39.1164 | -121.0693 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | TOP OF AVALON PLACE, GRASS VALLEY TOWER NUMBER 19/152 40689729 |  | 115000 | Conductor | Overhead | Yes | 42259.4104 | 2015-09-12 09:51 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0594 | 2015 | 9 | 12 | 9 | 51 | VD-2015-079 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.5014 | 196_301 | <25mph | <15mph | HFTD - Transmission | 2015-09-12 09:51:00 | 339 | 14.0472 | FALSE | <25mph | E1789 | 3.95 | 2015-09-12T16:48:00Z | 7 | 8 | < 25mph | E1789 | 3.95 | 2015-09-12T16:48:00Z | 7 | 41 | < 25mph | E1789 | 3.95 | 2015-09-12T16:48:00Z | 7 | 16 | < 25mph | E1789 | 3.95 | 2015-09-12T16:48:00Z | 7 | 83 | < 25mph
PG&E | 2015-09-18 17:05 | 42265.7118 | 37.8992 | -120.4551 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101019893 |  | 17000 | Conductor | Overhead | Yes | 42265.7118 | 2015-09-18 17:05 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0602 | 2015 | 9 | 18 | 17 | 5 | 15-0062207 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 35222 | 9.055 | 223_234 | <25mph | <15mph | HFTD - Distribution | 2015-09-18 17:05:00 | 347 | 11.0018 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.2 | 2015-09-19T00:03:00Z | 14.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.2 | 2015-09-19T00:03:00Z | 14.99 | 2 | < 25mph
PG&E | 2015-09-19 09:51 | 42266.4104 | 38.4755 | -122.9069 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FORESTVILLE | 103334444 |  | 12000 | Conductor | Overhead | Yes | 42266.4104 | 2015-09-19 09:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0603 | 2015 | 9 | 19 | 9 | 51 | 15-0062267 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 488 | 1.1332 | 117_266 | <25mph | <15mph | HFTD - Distribution | 2015-09-19 09:51:00 | 348 | 13.7107 | FALSE | <25mph | D4623 | 2.94 | 2015-09-19T16:36:00Z | 1.01 | 7 | < 25mph | E5234 | 7.03 | 2015-09-19T16:28:00Z | 5.99 | 81 | < 25mph | D4623 | 2.94 | 2015-09-19T17:51:00Z | 3 | 13 | < 25mph | E5234 | 7.03 | 2015-09-19T16:28:00Z | 5.99 | 171 | < 25mph
PG&E | 2015-09-20 18:53 | 42267.7868 | 39.8638 | -121.6599 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42267.7868 | 2015-09-20 18:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0604 | 2015 | 9 | 20 | 18 | 53 | 15-0062407 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 3479 | 4.6718 | 171_342 | <25mph | <15mph | HFTD - Distribution | 2015-09-20 18:53:00 | 349 | 13.083 | FALSE | <25mph | C8878 | 0.76 | 2015-09-21T01:53:00Z | 4 | 16 | < 25mph | CSTC1 | 5.81 | 2015-09-21T01:51:00Z | 10 | 19 | < 25mph | C8878 | 0.76 | 2015-09-21T02:33:00Z | 4 | 33 | < 25mph | CSTC1 | 5.81 | 2015-09-21T01:51:00Z | 10 | 38 | < 25mph
PG&E | 2015-09-24 04:30 | 42271.1875 | 38.6769 | -123.314 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Str. 041/007 |  | 60000 | Conductor | Overhead | Yes | 42271.1875 | 2015-09-24 04:30 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0613 | 2015 | 9 | 24 | 4 | 30 | FU-2015-057 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 22680 | 6.5939 | 100_277 | <25mph | <15mph | HFTD - Transmission | 2015-09-24 04:30:00 | 358 | 13.8122 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D2695 | 7.76 | 2015-09-24T11:12:00Z | 8.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | D2695 | 7.76 | 2015-09-24T11:12:00Z | 8.99 | 8 | < 25mph
PG&E | 2015-09-24 13:56 | 42271.5806 | 39.3508 | -121.2454 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 9692 Rices-Texas Hill rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42271.5806 | 2015-09-24 13:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0614 | 2015 | 9 | 24 | 13 | 56 | 15-0063159 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 51917 | 10.3419 | 189_313 | <25mph | <15mph | HFTD - Distribution | 2015-09-24 13:56:00 | 359 | 13.3743 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RRRC1 | 7.59 | 2015-09-24T20:13:00Z | 10 | 2 | < 25mph |  |  |  | 0 | 0 | No data | BNGC1 | 7.8 | 2015-09-24T21:51:00Z | 12.01 | 4 | < 25mph
PG&E | 2015-09-25 17:28 | 42272.7278 | 38.7169 | -120.7693 | Vegetation | Rural | < 0.25 Acres | Fire Agency | el dorado F D | 101405928 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42272.7278 | 2015-09-25 17:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0616 | 2015 | 9 | 25 | 17 | 28 | 15-0063666 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 111180 | 8.3925 | 209_279 | <25mph | <15mph | HFTD - Distribution | 2015-09-25 17:28:00 | 361 | 11.4196 | FALSE | <25mph | E5691 | 2.8 | 2015-09-25T23:45:00Z | 7 | 16 | < 25mph | C6129 | 4.54 | 2015-09-25T23:39:00Z | 12.01 | 40 | < 25mph | E5691 | 2.8 | 2015-09-25T23:45:00Z | 7 | 28 | < 25mph | C6129 | 4.54 | 2015-09-25T23:39:00Z | 12.01 | 76 | < 25mph
PG&E | 2015-09-28 09:42 | 42275.4042 | 37.9623 | -122.1765 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100458692 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42275.4042 | 2015-09-28 09:42 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0619 | 2015 | 9 | 28 | 9 | 42 | 15-0066062 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 2125 | 9.6053 | 148_237 | <25mph | <15mph | HFTD - Distribution | 2015-09-28 09:42:00 | 364 | 19.5931 | FALSE | <25mph | PLEC1 | 3.75 | 2015-09-28T16:28:00Z | 14.99 | 6 | < 25mph | UPBC1 | 6.07 | 2015-09-28T15:42:00Z | 20.98 | 147 | < 25mph | PLEC1 | 3.75 | 2015-09-28T16:28:00Z | 14.99 | 7 | < 25mph | MZXC1 | 5.72 | 2015-09-28T17:18:00Z | 20.98 | 286 | < 25mph
PG&E | 2015-10-03 21:11 | 42280.8826 | 39.7358 | -121.6855 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | honey run rd at cutouts 16015 |  | 12000 | Conductor | Overhead | Yes | 42280.8826 | 2015-10-03 21:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0632 | 2015 | 10 | 3 | 21 | 11 | 15-0067708 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 10499 | 20.0626 | 170_335 | <25mph | <15mph | HFTD - Distribution | 2015-10-03 21:11:00 | 377 | 26.1472 | FALSE | 25-40mph | PDEC1 | 3.46 | 2015-10-04T04:00:00Z | 14 | 1 | < 25mph | E4833 | 6.49 | 2015-10-04T03:45:00Z | 18.99 | 7 | < 25mph | PDEC1 | 3.46 | 2015-10-04T05:00:00Z | 15.99 | 2 | < 25mph | E4833 | 6.49 | 2015-10-04T03:45:00Z | 18.99 | 15 | < 25mph
PG&E | 2015-10-07 15:04 | 42284.6277 | 35.3079 | -120.8328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101924901 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42284.6277 | 2015-10-07 15:04 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0640 | 2015 | 10 | 7 | 15 | 3 | 15-0068730 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 77896 | 15.4357 | 207_90 | <25mph | <15mph | HFTD - Distribution | 2015-10-07 15:03:00 | 384 | 16.4418 | FALSE | <25mph | E1668 | 0.48 | 2015-10-07T22:00:00Z | 15.99 | 5 | < 25mph | E1668 | 0.48 | 2015-10-07T22:00:00Z | 15.99 | 7 | < 25mph | E6113 | 0.7 | 2015-10-07T22:46:00Z | 18.01 | 11 | < 25mph | E6113 | 0.7 | 2015-10-07T22:46:00Z | 18.01 | 14 | < 25mph
PG&E | 2015-10-09 06:32 | 42286.2722 | 38.364 | -122.9173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 320 Freestone St, Frestone | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0642 | 2015 | 10 | 9 | 6 | 32 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 2.6818 | 117_260 | <25mph | <15mph | HFTD - Distribution | 2015-10-09 06:32:00 | 386 | 15.5803 | FALSE | <25mph | D2849 | 3.33 | 2015-10-09T13:22:00Z | 3 | 22 | < 25mph | D2849 | 3.33 | 2015-10-09T13:22:00Z | 3 | 49 | < 25mph | D2849 | 3.33 | 2015-10-09T13:22:00Z | 3 | 44 | < 25mph | D2849 | 3.33 | 2015-10-09T13:22:00Z | 3 | 99 | < 25mph
PG&E | 2015-10-16 09:43 | 42293.4049 | 39.187 | -123.2015 | Vegetation | Rural | < 3 meters | Unknown |  | 102196855 |  | 12000 | Conductor | Overhead | Yes | 42293.4049 | 2015-10-16 09:43 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0653 | 2015 | 10 | 16 | 9 | 43 | 15-0070948 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 65228 | 2.2696 | 105_305 | <25mph | <15mph | HFTD - Distribution | 2015-10-16 09:43:00 | 397 | 16.8813 | FALSE | <25mph | E7513 | 1.34 | 2015-10-16T16:08:00Z | 3 | 13 | < 25mph | E7513 | 1.34 | 2015-10-16T16:08:00Z | 3 | 25 | < 25mph | E7513 | 1.34 | 2015-10-16T17:38:00Z | 4 | 25 | < 25mph | E7513 | 1.34 | 2015-10-16T17:38:00Z | 4 | 49 | < 25mph
PG&E | 2015-10-25 05:50 | 42302.2431 | 37.7843 | -121.7683 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | cutouts 9504 |  | 21000 | Conductor | Overhead | Yes | 42302.2431 | 2015-10-25 05:50 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0657 | 2015 | 10 | 25 | 5 | 50 | 15-0073203 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 10710 | 23.3456 | 166_227 | <25mph | <15mph | HFTD - Distribution | 2015-10-25 05:50:00 | 401 | 23.3456 | FALSE | <25mph | VAQC1 | 1.86 | 2015-10-25T12:45:00Z | 15.99 | 2 | < 25mph | VAQC1 | 1.86 | 2015-10-25T12:45:00Z | 15.99 | 2 | < 25mph | VAQC1 | 1.86 | 2015-10-25T13:45:00Z | 18.99 | 4 | < 25mph | VAQC1 | 1.86 | 2015-10-25T13:45:00Z | 18.99 | 4 | < 25mph
PG&E | 2015-10-30 17:13 | 42307.7174 | 38.3166 | -120.7226 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 7600 HWY 49, Jackson | None | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0662 | 2015 | 10 | 30 | 17 | 13 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 8.0122 | 211_256 | <25mph | <15mph | HFTD - Distribution | 2015-10-30 17:13:00 | 406 | 12.822 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.34 | 2015-10-30T23:56:00Z | 11.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.34 | 2015-10-30T23:56:00Z | 11.01 | 2 | < 25mph
PG&E | 2015-10-31 07:45 | 42308.3229 | 38.1157 | -120.8931 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal FIRE | 103763040 |  | 12000 | Conductor | Overhead | Yes | 42308.3229 | 2015-10-31 07:45 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0663 | 2015 | 10 | 31 | 7 | 45 | 15-0074424 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 314565 | 11.8471 | 204_245 | <25mph | <15mph | HFTD - Distribution | 2015-10-31 07:45:00 | 407 | 12.187 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CMAC1 | 7.6 | 2015-10-31T13:59:00Z | 12.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CMAC1 | 7.6 | 2015-10-31T14:59:00Z | 13 | 2 | < 25mph
PG&E | 2015-11-09 05:55 | 42317.2465 | 34.9984 | -120.3634 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42317.2465 | 2015-11-09 05:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0673 | 2015 | 11 | 9 | 5 | 55 | 15-0076534 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 205393 | 8.4294 | 228_73 | <25mph | <15mph | HFTD - Distribution | 2015-11-09 05:55:00 | 417 | 17.7768 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AU609 | 7.47 | 2015-11-09T13:07:00Z | 2.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | AU609 | 7.47 | 2015-11-09T13:07:00Z | 2.01 | 7 | < 25mph
PG&E | 2015-11-15 16:30 | 42323.6875 | 37.0007 | -121.885 | Vegetation | Rural | < 3 meters | Customer |  | 101691004 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42323.6875 | 2015-11-15 16:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0676 | 2015 | 11 | 15 | 16 | 30 | 15-0077978 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 25920 | 24.6094 | 161_184 | <25mph | <15mph | HFTD - Distribution | 2015-11-15 16:30:00 | 420 | 25.3186 | FALSE | 25-40mph | E7291 | 2.82 | 2015-11-16T00:21:00Z | 32.01 | 33 | 25-40mph | E7291 | 2.82 | 2015-11-16T00:21:00Z | 32.01 | 123 | 25-40mph | E7291 | 2.82 | 2015-11-16T00:21:00Z | 32.01 | 62 | 25-40mph | E7291 | 2.82 | 2015-11-16T00:21:00Z | 32.01 | 232 | 25-40mph
PG&E | 2015-11-21 10:36 | 42329.4417 | 38.0679 | -120.1872 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101045952 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42329.4417 | 2015-11-21 10:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0677 | 2015 | 11 | 21 | 10 | 36 | 15-0079868 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18350 | 7.816 | 235_243 | <25mph | <15mph | HFTD - Distribution | 2015-11-21 10:36:00 | 421 | 16.6927 | FALSE | <25mph | MOUC1 | 3.29 | 2015-11-21T18:02:00Z | 17 | 1 | < 25mph | MOUC1 | 3.29 | 2015-11-21T18:02:00Z | 17 | 1 | < 25mph | MOUC1 | 3.29 | 2015-11-21T19:02:00Z | 18.01 | 2 | < 25mph | MOUC1 | 3.29 | 2015-11-21T19:02:00Z | 18.01 | 2 | < 25mph
PG&E | 2015-12-01 12:03 | 42339.5021 | 35.6744 | -120.9932 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal FIRE | 101860660 |  | 21000 | Conductor | Overhead | Yes | 42339.5021 | 2015-12-01 12:03 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0680 | 2015 | 12 | 1 | 12 | 3 | 15-0081983 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 42427 | 6.9865 | 200_111 | <25mph | <15mph | HFTD - Distribution | 2015-12-01 12:03:00 | 424 | 12.3916 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TABC1 | 4.07 | 2015-12-01T19:07:00Z | 8.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | TABC1 | 4.07 | 2015-12-01T19:07:00Z | 8.99 | 2 | < 25mph
PG&E | 2015-12-03 12:10 | 42341.5069 | 40.0277 | -120.9652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | usfs | spanish creek campground |  | 12000 | Conductor | Overhead | Yes | 42341.5069 | 2015-12-03 12:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0683 | 2015 | 12 | 3 | 12 | 10 | 15-0082505 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 196854 | 26.293 | 201_351 | 25-40mph | 15-30mph | HFTD - Distribution | 2015-12-03 12:10:00 | 427 | 26.9543 | FALSE | 25-40mph | CHAC1 | 3.2 | 2015-12-03T19:47:00Z | 47 | 2 | 40-55mph | CHAC1 | 3.2 | 2015-12-03T19:47:00Z | 47 | 3 | 40-55mph | CHAC1 | 3.2 | 2015-12-03T20:47:00Z | 59.01 | 4 | 55mph+ | CHAC1 | 3.2 | 2015-12-03T20:47:00Z | 59.01 | 6 | 55mph+
PG&E | 2015-12-08 12:41 | 42346.5285 | 38.2489 | -120.5228 | Other | Rural | Structure Only | Unknown |  | 7026 Railroad Flat Road, Mountain Ranch |  | 12000 | Conductor | Overhead | Yes | 42346.5285 | 2015-12-08 12:41 | Contact From Object | N.A. | Other | Electric Facility | Human Error | AT&T work error | Other/Unknown | 0684 | 2015 | 12 | 8 | 12 | 41 | 15-0083435 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1120 | 3.9918 | 220_253 | <25mph | <15mph | HFTD - Distribution | 2015-12-08 12:41:00 | 428 | 10.4116 | FALSE | <25mph | ESPC1 | 3.04 | 2015-12-08T20:13:00Z | 5.99 | 6 | < 25mph | ESPC1 | 3.04 | 2015-12-08T20:13:00Z | 5.99 | 6 | < 25mph | ESPC1 | 3.04 | 2015-12-08T21:13:00Z | 10 | 13 | < 25mph | ESPC1 | 3.04 | 2015-12-08T21:13:00Z | 10 | 13 | < 25mph
PG&E | 2015-12-31 19:12 | 42369.8 | 37.1568 | -121.9868 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LOS GATOS MONTE SERENO SARATOGA | 100518215 | Verizon | 21000 | Conductor | Overhead | Yes | 42369.8 | 2015-12-31 19:12 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0689 | 2015 | 12 | 31 | 19 | 12 | 15-0087962 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7979 | 7.4149 | 156_193 | <25mph | <15mph | HFTD - Distribution | 2015-12-31 19:12:00 | 433 | 10.9251 | FALSE | <25mph | D8979 | 2.76 | 2016-01-01T02:57:00Z | 10 | 23 | < 25mph | E6085 | 6.01 | 2016-01-01T02:32:00Z | 10 | 176 | < 25mph | D8979 | 2.76 | 2016-01-01T04:08:00Z | 12.01 | 45 | < 25mph | D8979 | 2.76 | 2016-01-01T04:08:00Z | 12.01 | 346 | < 25mph
PG&E | 2016-01-21 21:32 | 42390.8972 | 40.553 | -124.1116 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100994021 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42390.8972 | 2016-01-21 21:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0690 | 2016 | 1 | 21 | 21 | 32 | 16-0007239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 6468 | 26.2481 | 69_382 | 25-40mph | 15-30mph | HFTD - Distribution | 2016-01-21 21:32:00 | 434 | 29.6828 | FALSE | 25-40mph | KFOT | 1.14 | 2016-01-22T05:15:00Z | 36.82 | 28 | 25-40mph | KFOT | 1.14 | 2016-01-22T05:15:00Z | 36.82 | 28 | 25-40mph | KFOT | 1.14 | 2016-01-22T05:35:00Z | 48.34 | 55 | 40-55mph | KFOT | 1.14 | 2016-01-22T05:35:00Z | 48.34 | 55 | 40-55mph
PG&E | 2016-02-08 03:55 | 42408.1632 | 39.7852 | -121.5056 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100337507 |  | 12000 | Conductor | Overhead | Yes | 42408.1632 | 2016-02-08 03:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0694 | 2016 | 2 | 8 | 3 | 55 | 16-0011201 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 87046 | 36.3276 | 178_337 | 25-40mph | 30-45mph | HFTD - Distribution | 2016-02-08 03:55:00 | 438 | 40.0336 | FALSE | 40-55mph | JBGC1 | 3.52 | 2016-02-08T11:13:00Z | 45.99 | 1 | 40-55mph | JBGC1 | 3.52 | 2016-02-08T11:13:00Z | 45.99 | 23 | 40-55mph | JBGC1 | 3.52 | 2016-02-08T12:13:00Z | 57 | 2 | 55mph+ | JBGC1 | 3.52 | 2016-02-08T12:13:00Z | 57 | 46 | 55mph+
PG&E | 2016-04-08 13:14 | 42468.5514 | 39.0429 | -121.1002 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100086751 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42468.5514 | 2016-04-08 13:14 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0705 | 2016 | 4 | 8 | 13 | 14 | 16-0027237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 11817 | 10.7666 | 195_296 | <25mph | <15mph | HFTD - Distribution | 2016-04-08 13:14:00 | 449 | 10.7666 | FALSE | <25mph | C0713 | 3.59 | 2016-04-08T19:24:00Z | 8.01 | 17 | < 25mph | E1789 | 7.22 | 2016-04-08T20:00:00Z | 8.99 | 40 | < 25mph | C0713 | 3.59 | 2016-04-08T20:34:00Z | 10 | 33 | < 25mph | C0713 | 3.59 | 2016-04-08T20:34:00Z | 10 | 80 | < 25mph
PG&E | 2016-04-13 19:28 | 42473.8111 | 40.4954 | -124.1219 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103659313 |  | 12000 | Conductor | Overhead | Yes | 42473.8111 | 2016-04-13 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0706 | 2016 | 4 | 13 | 19 | 28 | 16-0028421 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 688 | 19.0823 | 68_379 | <25mph | <15mph | HFTD - Distribution | 2016-04-13 19:28:00 | 450 | 22.9769 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KFOT | 4.03 | 2016-04-14T01:55:00Z | 32.21 | 30 | 25-40mph |  |  |  | 0 | 0 | No data | KFOT | 4.03 | 2016-04-14T01:55:00Z | 32.21 | 58 | 25-40mph
PG&E | 2016-04-21 09:25 | 42481.3924 | 39.293 | -123.769 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 103312287 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0711 | 2016 | 4 | 21 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 8.8774 | 81_312 | <25mph | <15mph | HFTD - Distribution | 2016-04-21 09:25:00 | 455 | 20.2474 | FALSE | <25mph | E6025 | 0.21 | 2016-04-21T16:15:00Z | 3 | 4 | < 25mph | E6025 | 0.21 | 2016-04-21T16:15:00Z | 3 | 4 | < 25mph | E6025 | 0.21 | 2016-04-21T17:15:00Z | 4.99 | 8 | < 25mph | E6025 | 0.21 | 2016-04-21T17:15:00Z | 4.99 | 8 | < 25mph
PG&E | 2016-04-30 | 17:59 | 38.3142 | -120.9015 | Vegetation | RURAL | < 3 meters | Fire Agency | Kern County FD |  |  | 12000 | Conductor | Overhead | Yes | 42490 | 0.74931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0719 | 2016 | 4 | 30 | 17 | 59 | 16-0032910 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 722 | 19.7396 | 204_256 | <25mph | <15mph | HFTD - Distribution | 2016-04-30 17:59:00 | 465 | 19.7396 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CMAC1 | 6.54 | 2016-04-30T06:59:00Z | 23 | 3 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 4.81 | 2016-04-30T07:05:00Z | 28.99 | 6 | 25-40mph
PG&E | 2016-05-12 20:15 | 42502.8438 | 35.1922 | -120.4563 | Vegetation | RURAL | < 3 meters | Self Extinguished | N.A. | 101857280 |  | 12000 | Conductor | Overhead | Yes | 42502.8438 | 2016-05-12 20:15 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0727 | 2016 | 5 | 12 | 20 | 15 | 16-0035728 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 54088 | 8.5669 | 224_84 | <25mph | <15mph | HFTD - Distribution | 2016-05-12 20:15:00 | 471 | 14.182 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AU609 | 7.02 | 2016-05-13T02:21:00Z | 10 | 11 | < 25mph |  |  |  | 0 | 0 | No data | AU609 | 7.02 | 2016-05-13T02:21:00Z | 10 | 25 | < 25mph
PG&E | 2016-05-15 15:54 | 42505.6625 | 36.7948 | -119.3966 | Vegetation | RURAL | 100 - 299 Acres | Fire Agency | Cal Fire | 100729685 | None | 12000 | Conductor | Overhead | Yes | 42505.6625 | 2016-05-15 15:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0730 | 2016 | 5 | 15 | 15 | 54 | 16-0036136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 180310 | 10.5903 | 270_173 | <25mph | <15mph | HFTD - Distribution | 2016-05-15 15:54:00 | 474 | 14.7659 | FALSE | <25mph |  |  |  | 0 | 0 | No data | FCHC1 | 7.54 | 2016-05-15T22:00:00Z | 12.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | FCHC1 | 7.54 | 2016-05-15T23:00:00Z | 15.99 | 2 | < 25mph
PG&E | 2016-05-18 | 18:24 | 39.7381 | -123.1587 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42508 | 0.76667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0735 | 2016 | 5 | 18 | 18 | 24 | 16-0036911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1482 | 13.4862 | 108_336 | <25mph | <15mph | HFTD - Distribution | 2016-05-18 18:24:00 | 480 | 21.4181 | FALSE | <25mph | C3111 | 2.79 | 2016-05-18T06:56:00Z | 0 | 2 | < 25mph | EELC1 | 7.26 | 2016-05-18T06:45:00Z | 13 | 3 | < 25mph | C3111 | 2.79 | 2016-05-18T07:57:00Z | 0 | 6 | < 25mph | EELC1 | 7.26 | 2016-05-18T06:45:00Z | 13 | 8 | < 25mph
PG&E | 2016-05-19 01:42 | 42509.0708 | 34.6645 | -120.4 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Santa Barbara County FD | 101916587 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42509.0708 | 2016-05-19 01:42 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | no-match | 0738 | 2016 | 5 | 19 | 1 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 6.9523 | 227_55 | <25mph | <15mph | HFTD - Distribution | 2016-05-19 01:42:00 | 482 | 22.8605 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D4531 | 5.16 | 2016-05-19T08:04:00Z | 4 | 3 | < 25mph |  |  |  | 0 | 0 | No data | D4531 | 5.16 | 2016-05-19T09:19:00Z | 4 | 7 | < 25mph
PG&E | 2016-05-20 15:01 | 15:01 | 39.0559 | -123.4581 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102198323 |  | 12000 | Conductor | Overhead | Yes | 42510.6257 | 0.62569 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0741 | 2016 | 5 | 20 | 15 | 1 | 16-0037479 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2720 | 20.9117 | 94_299 | <25mph | <15mph | HFTD - Distribution | 2016-05-20 15:01:00 | 484 | 20.9117 | FALSE | <25mph | E1763 | 3.93 | 2016-05-20T21:19:00Z | 11.01 | 4 | < 25mph | BNVC1 | 7.56 | 2016-05-20T21:50:00Z | 25.99 | 6 | 25-40mph | E1763 | 3.93 | 2016-05-20T22:18:00Z | 12.01 | 8 | < 25mph | BNVC1 | 7.56 | 2016-05-20T22:50:00Z | 27 | 15 | 25-40mph
PG&E | 2016-05-29 14:19 | 42519.5965 | 40.5795 | -122.4694 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103156596 | Yes | 12000 | Conductor | Overhead | Yes | 42519.5965 | 2016-05-29 14:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0751 | 2016 | 5 | 29 | 14 | 19 | 16-0039619 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3860 | 1.6611 | 138_382 | <25mph | <15mph | HFTD - Distribution | 2016-05-29 14:19:00 | 494 | 20.6013 | FALSE | <25mph | MMOC1 | 1.91 | 2016-05-29T21:00:00Z | 8.01 | 5 | < 25mph | E6886 | 6.63 | 2016-05-29T20:41:00Z | 8.01 | 13 | < 25mph | MMOC1 | 1.91 | 2016-05-29T22:00:00Z | 8.01 | 10 | < 25mph | C5599 | 7.38 | 2016-05-29T21:31:00Z | 8.99 | 26 | < 25mph
PG&E | 2016-05-31 04:02 | 42521.1681 | 35.7984 | -120.9743 | Vegetation | RURAL | < 0.25 Acres | Utility: PG&E | N.A. | 101863413 |  | 12000 | Conductor | Overhead | Yes | 42521.1681 | 2016-05-31 04:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0754 | 2016 | 5 | 31 | 4 | 2 | 16-0039748 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 51888 | 1.5922 | 201_118 | <25mph | <15mph | HFTD - Distribution | 2016-05-31 04:02:00 | 497 | 16.9662 | FALSE | <25mph | E9175 | 3.45 | 2016-05-31T10:42:00Z | 1.01 | 13 | < 25mph | E9175 | 3.45 | 2016-05-31T10:42:00Z | 1.01 | 17 | < 25mph | E9175 | 3.45 | 2016-05-31T11:22:00Z | 1.01 | 25 | < 25mph | E9175 | 3.45 | 2016-05-31T11:22:00Z | 1.01 | 33 | < 25mph
PG&E | 2016-06-03 | 42524.5111 | 38.6435 | -120.6959 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | cal-fire and usfs | 103119737 |  | 21000 | Conductor | Overhead | Yes | 42524 | 2016-06-03 12:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0764 | 2016 | 6 | 3 | 12 | 16 | 16-0040808 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 101354 | 7.6436 | 213_274 | <25mph | <15mph | HFTD - Distribution | 2016-06-03 12:16:00 | 507 | 11.74 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6490 | 7.82 | 2016-06-03T06:56:00Z | 0 | 16 | < 25mph |  |  |  | 0 | 0 | No data | E6490 | 7.82 | 2016-06-03T07:56:00Z | 2.01 | 32 | < 25mph
PG&E | 2016-06-04 | 22:15 | 38.5117 | -122.9373 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42525 | 0.92708 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0768 | 2016 | 6 | 4 | 22 | 15 | 16-0041119 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7220 | 6.1483 | 116_268 | <25mph | <15mph | HFTD - Distribution | 2016-06-04 22:15:00 | 514 | 16.4728 | FALSE | <25mph | D9841 | 2.58 | 2016-06-04T06:52:00Z | 0 | 11 | < 25mph | E9070 | 7.35 | 2016-06-04T06:25:00Z | 5.99 | 75 | < 25mph | D9841 | 2.58 | 2016-06-04T07:52:00Z | 0 | 21 | < 25mph | E9070 | 7.35 | 2016-06-04T07:25:00Z | 5.99 | 142 | < 25mph
PG&E | 2016-06-06 | 42527.825 | 38.9129 | -121.1192 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire/placer fire | 100050264 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42527 | 2016-06-06 19:48 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0775 | 2016 | 6 | 6 | 19 | 48 | 16-0041497 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 2039 | 14.8039 | 194_289 | <25mph | <15mph | HFTD - Distribution | 2016-06-06 19:48:00 | 518 | 15.3816 | FALSE | <25mph | D8862 | 3.32 | 2016-06-06T06:49:00Z | 4 | 4 | < 25mph | D8862 | 3.32 | 2016-06-06T06:49:00Z | 4 | 4 | < 25mph | D8862 | 3.32 | 2016-06-06T07:04:00Z | 5.99 | 8 | < 25mph | D8862 | 3.32 | 2016-06-06T07:04:00Z | 5.99 | 8 | < 25mph
PG&E | 2016-06-10 15:51 | 42531.6604 | 39.9934 | -123.7883 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100992291 |  | 12000 | Conductor | Overhead | Yes | 42531.6604 | 2016-06-10 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0788 | 2016 | 6 | 10 | 15 | 51 | 16-0042501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | N.A. | 22.4156 | 82_351 | <25mph | <15mph | HFTD - Distribution | 2016-06-10 15:51:00 | 531 | 22.7996 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AV037 | 5.5 | 2016-06-10T22:23:00Z | 8.99 | 3 | < 25mph |  |  |  | 0 | 0 | No data | AV037 | 5.5 | 2016-06-10T23:13:00Z | 11.01 | 7 | < 25mph
PG&E | 2016-06-11 | 42532.8229 | 39.3265 | -121.3921 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101292512 |  | 0 – 750 | Transformer | Overhead | Yes | 42532 | 2016-06-11 19:45 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0790 | 2016 | 6 | 11 | 19 | 45 | 16-0042611 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 642 | 8.1809 | 183_312 | <25mph | <15mph | HFTD - Distribution | 2016-06-11 19:45:00 | 533 | 16.0839 | FALSE | <25mph | BNGC1 | 3.76 | 2016-06-11T06:51:00Z | 1.01 | 1 | < 25mph | BNGC1 | 3.76 | 2016-06-11T06:51:00Z | 1.01 | 1 | < 25mph | BNGC1 | 3.76 | 2016-06-11T07:51:00Z | 4 | 2 | < 25mph | BNGC1 | 3.76 | 2016-06-11T07:51:00Z | 4 | 2 | < 25mph
PG&E | 2016-06-12 | 42533.5514 | 37.5096 | -120.0462 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101083986 |  | 0 – 750 | Conductor | Overhead | Yes | 42533 | 2016-06-12 13:14 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0795 | 2016 | 6 | 12 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.8806 | 241_212 | <25mph | <15mph | HFTD - Distribution | 2016-06-12 13:14:00 | 539 | 13.4596 | FALSE | <25mph | MPOC1 | 3.28 | 2016-06-12T06:07:00Z | 11.01 | 1 | < 25mph | MPOC1 | 3.28 | 2016-06-12T06:07:00Z | 11.01 | 1 | < 25mph | MPOC1 | 3.28 | 2016-06-12T06:07:00Z | 11.01 | 2 | < 25mph | MPOC1 | 3.28 | 2016-06-12T06:07:00Z | 11.01 | 2 | < 25mph
PG&E | 2016-06-12 01:45 | 1:45 | 37.4643 | -122.3459 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Unknown | 100265854 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42533.0729 | 0.072917 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0796 | 2016 | 6 | 12 | 1 | 45 | 16-0042637 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 19836 | 11.0705 | 141_210 | <25mph | <15mph | HFTD - Distribution | 2016-06-12 01:45:00 | 534 | 17.9563 | FALSE | <25mph | PUGC1 | 2.7 | 2016-06-12T08:18:00Z | 8.01 | 8 | < 25mph | AU981 | 5.46 | 2016-06-12T08:44:00Z | 20 | 85 | < 25mph | PUGC1 | 2.7 | 2016-06-12T08:18:00Z | 8.01 | 17 | < 25mph | E2649 | 7.02 | 2016-06-12T09:44:00Z | 24 | 171 | < 25mph
PG&E | 2016-06-15 | 42536.5479 | 38.4433 | -120.7568 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103169620 |  | 12000 | Conductor | Overhead | Yes | 42536 | 2016-06-15 13:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0801 | 2016 | 6 | 15 | 13 | 9 | 16-0043476 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 23963 | 15.7348 | 210_263 | <25mph | <15mph | HFTD - Distribution | 2016-06-15 13:09:00 | 543 | 16.8625 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.74 | 2016-06-15T06:56:00Z | 4.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.74 | 2016-06-15T07:56:00Z | 5.99 | 2 | < 25mph
PG&E | 2016-06-19 | 42540.5049 | 39.3811 | -123.7737 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102187888 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 12:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0807 | 2016 | 6 | 19 | 12 | 7 | 16-0044317 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6100 | 11.4602 | 81_317 | <25mph | <15mph | HFTD - Distribution | 2016-06-19 12:07:00 | 550 | 15.3844 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6025 | 6.3 | 2016-06-19T06:30:00Z | 3 | 5 | < 25mph |  |  |  | 0 | 0 | No data | E6025 | 6.3 | 2016-06-19T06:30:00Z | 3 | 9 | < 25mph
PG&E | 2016-06-19 | 42540.7215 | 38.4508 | -122.3546 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire--napa fire | 102256859 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 17:19 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0808 | 2016 | 6 | 19 | 17 | 19 | 16-0044337 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 672 | 13.296 | 141_264 | <25mph | <15mph | HFTD - Distribution | 2016-06-19 17:19:00 | 552 | 13.7776 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.13 | 2016-06-19T06:29:00Z | 11.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.13 | 2016-06-19T06:29:00Z | 11.01 | 2 | < 25mph
PG&E | 2016-06-20 | 42541.6979 | 41.0697 | -123.6789 | Vegetation | RURAL | < 3 meters | Fire Agency | Hoopa FD | 101011420 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42541 | 2016-06-20 16:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0811 | 2016 | 6 | 20 | 16 | 45 | 16-0044577 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7361 | 15.1157 | 88_410 | <25mph | <15mph | HFTD - Distribution | 2016-06-20 16:45:00 | 554 | 15.1157 | FALSE | <25mph | HOAC1 | 1.56 | 2016-06-20T06:40:00Z | 3 | 1 | < 25mph | HOAC1 | 1.56 | 2016-06-20T06:40:00Z | 3 | 1 | < 25mph | HOAC1 | 1.56 | 2016-06-20T06:40:00Z | 3 | 2 | < 25mph | HOAC1 | 1.56 | 2016-06-20T06:40:00Z | 3 | 2 | < 25mph
PG&E | 2016-06-21 | 20:49 | 35.5352 | -120.8457 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101900832 |  | 12000 | Conductor | Overhead | Yes | 42542 | 0.86736 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0812 | 2016 | 6 | 21 | 20 | 49 | 16-0044904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7806 | 8.2716 | 207_103 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 20:49:00 | 558 | 17.6234 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6394 | 6.56 | 2016-06-21T06:59:00Z | 1.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6394 | 6.56 | 2016-06-21T07:59:00Z | 1.01 | 8 | < 25mph
PG&E | 2016-06-21 | 42542.4229 | 39.0294 | -121.2927 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100024816 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | no-match | 0813 | 2016 | 6 | 21 | 10 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 5.0939 | 187_296 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 10:09:00 | 555 | 12.3682 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5440 | 6.7 | 2016-06-21T06:47:00Z | 7 | 28 | < 25mph |  |  |  | 0 | 0 | No data | E5440 | 6.7 | 2016-06-21T06:47:00Z | 7 | 56 | < 25mph
PG&E | 2016-06-21 | 42542.7035 | 38.4233 | -122.5448 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | KENWOOD FIRE XST | 102036904 | Yes | 0 – 750 | Conductor | Overhead | Yes | 42542 | 2016-06-21 16:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0814 | 2016 | 6 | 21 | 16 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 14.0146 | 133_263 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 16:53:00 | 556 | 14.0381 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1582 | 5.25 | 2016-06-21T06:33:00Z | 4 | 14 | < 25mph |  |  |  | 0 | 0 | No data | E1582 | 5.25 | 2016-06-21T06:33:00Z | 4 | 28 | < 25mph
PG&E | 2016-06-24 | 42545.6097 | 40.22 | -122.283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101526647 | PACIFIC BELL | 0 – 750 | Unknown | Overhead | Yes | 42545 | 2016-06-24 14:38 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0821 | 2016 | 6 | 24 | 14 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 11.9685 | 145_362 | <25mph | <15mph | HFTD - Distribution | 2016-06-24 14:38:00 | 564 | 17.4582 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KRBL | 5.07 | 2016-06-24T06:54:00Z | 23.02 | 1 | < 25mph |  |  |  | 0 | 0 | No data | KRBL | 5.07 | 2016-06-24T06:54:00Z | 23.02 | 1 | < 25mph
PG&E | 2016-06-26 | 42547.6931 | 39.5042 | -121.4475 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100375810 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42547 | 2016-06-26 16:38 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0823 | 2016 | 6 | 26 | 16 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 9.04 | 180_322 | <25mph | <15mph | HFTD - Distribution | 2016-06-26 16:38:00 | 567 | 14.524 | FALSE | <25mph | TT309 | 3.14 | 2016-06-26T06:45:00Z | 8.01 | 1 | < 25mph | TT309 | 3.14 | 2016-06-26T06:45:00Z | 8.01 | 1 | < 25mph | TT309 | 3.14 | 2016-06-26T06:45:00Z | 8.01 | 2 | < 25mph | TT309 | 3.14 | 2016-06-26T06:45:00Z | 8.01 | 2 | < 25mph
PG&E | 2016-06-26 11:06 | 42547.4625 | 40.4832 | -122.0466 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101483777 | FRONTIER | 12000 | Conductor | Overhead | Yes | 42547.4625 | 2016-06-26 11:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0826 | 2016 | 6 | 26 | 11 | 6 | 16-0045846 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 15520 | 6.1274 | 155_376 | <25mph | <15mph | HFTD - Distribution | 2016-06-26 11:06:00 | 566 | 14.8861 | FALSE | <25mph | AR225 | 3.09 | 2016-06-26T17:25:00Z | 8.01 | 10 | < 25mph | AR225 | 3.09 | 2016-06-26T17:25:00Z | 8.01 | 10 | < 25mph | AR225 | 3.09 | 2016-06-26T18:45:00Z | 8.01 | 22 | < 25mph | AR225 | 3.09 | 2016-06-26T18:45:00Z | 8.01 | 22 | < 25mph
PG&E | 2016-06-30 | 0:03 | 39.8157 | -121.5994 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42551 | 0.0020833 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0832 | 2016 | 6 | 30 | 0 | 3 | 16-0046763 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 299100 | 7.8781 | 174_339 | <25mph | <15mph | HFTD - Distribution | 2016-06-30 00:03:00 | 575 | 11.8323 | FALSE | <25mph | C4565 | 1.82 | 2016-06-30T06:40:00Z | 3 | 2 | < 25mph | C4565 | 1.82 | 2016-06-30T06:40:00Z | 3 | 15 | < 25mph | C4565 | 1.82 | 2016-06-30T07:30:00Z | 3 | 5 | < 25mph | C4565 | 1.82 | 2016-06-30T07:30:00Z | 3 | 31 | < 25mph
PG&E | 2016-07-03 15:00 | 42554.625 | 38.0348 | -120.3809 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101050507 |  | 17000 | Conductor | Overhead | Yes | 42554.625 | 2016-07-03 15:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0837 | 2016 | 7 | 3 | 15 | 0 | 16-0047689 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38812 | 10.6263 | 226_241 | <25mph | <15mph | HFTD - Distribution | 2016-07-03 15:00:00 | 580 | 12.5395 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MOUC1 | 7.53 | 2016-07-03T21:02:00Z | 14.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MOUC1 | 7.53 | 2016-07-03T22:02:00Z | 17 | 2 | < 25mph
PG&E | 2016-07-08 10:49 | 42559.4507 | 38.3373 | -122.1211 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 102291118 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42559.4507 | 2016-07-08 10:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0842 | 2016 | 7 | 8 | 10 | 49 | 16-0048647 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 19469 | 8.3702 | 151_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-08 10:49:00 | 585 | 20.6133 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6079 | 6.28 | 2016-07-08T17:23:00Z | 14.99 | 12 | < 25mph |  |  |  | 0 | 0 | No data | E6079 | 6.28 | 2016-07-08T17:23:00Z | 14.99 | 23 | < 25mph
PG&E | 2016-07-15 05:19 | 42566.2215 | 35.1839 | -120.5018 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101846594 |  | 12000 | Conductor | Overhead | Yes | 42566.2215 | 2016-07-15 05:19 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0851 | 2016 | 7 | 15 | 5 | 19 | 16-0050086 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 62404 | 2.6454 | 222_84 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 05:19:00 | 594 | 14.1102 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D6295 | 5.2 | 2016-07-15T12:11:00Z | 0 | 8 | < 25mph |  |  |  | 0 | 0 | No data | D6295 | 5.2 | 2016-07-15T13:01:00Z | 0 | 15 | < 25mph
PG&E | 2016-07-15 14:09 | 42566.5896 | 38.6965 | -120.8598 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412774 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.5896 | 2016-07-15 14:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0852 | 2016 | 7 | 15 | 14 | 9 | 16-0050274 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 11253 | 10.7453 | 205_277 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 14:09:00 | 595 | 14.2057 | FALSE | <25mph | C6129 | 0.59 | 2016-07-15T20:39:00Z | 12.01 | 31 | < 25mph | C6129 | 0.59 | 2016-07-15T20:39:00Z | 12.01 | 65 | < 25mph | C6129 | 0.59 | 2016-07-15T20:39:00Z | 12.01 | 61 | < 25mph | C6129 | 0.59 | 2016-07-15T20:39:00Z | 12.01 | 130 | < 25mph
PG&E | 2016-07-15 14:26 | 42566.6014 | 38.1366 | -122.7092 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | NOVATO FIRE AND OTHERS | 102013570 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.6014 | 2016-07-15 14:26 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0853 | 2016 | 7 | 15 | 14 | 26 | 16-0050269 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 758 | 13.1533 | 125_247 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 14:26:00 | 596 | 15.659 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BBEC1 | 7.51 | 2016-07-15T21:11:00Z | 13 | 25 | < 25mph |  |  |  | 0 | 0 | No data | BBEC1 | 7.51 | 2016-07-15T21:11:00Z | 13 | 50 | < 25mph
PG&E | 2016-07-16 00:58 | 42567.0403 | 36.4379 | -121.9198 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101669758 |  | 12000 | Other | Overhead | Yes | 42567.0403 | 2016-07-16 00:58 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0855 | 2016 | 7 | 16 | 0 | 58 | 16-0050335 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 8976 | 11.1025 | 159_153 | <25mph | <15mph | HFTD - Distribution | 2016-07-16 00:58:00 | 598 | 18.5622 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6019 | 7.86 | 2016-07-16T07:42:00Z | 4.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6019 | 7.86 | 2016-07-16T08:27:00Z | 4.99 | 8 | < 25mph
PG&E | 2016-07-16 08:19 | 42567.3465 | 37.4828 | -119.87 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101079104 | None | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0856 | 2016 | 7 | 16 | 8 | 19 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 2.1905 | 249_211 | <25mph | <15mph | HFTD - Distribution | 2016-07-16 08:19:00 | 599 | 13.487 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MPOC1 | 6.57 | 2016-07-16T15:07:00Z | 8.01 | 10 | < 25mph |  |  |  | 0 | 0 | No data | MPOC1 | 6.57 | 2016-07-16T15:07:00Z | 8.01 | 19 | < 25mph
PG&E | 2016-07-20 19:15 | 42571.8021 | 37.7712 | -121.8104 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100898986 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42571.8021 | 2016-07-20 19:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0865 | 2016 | 7 | 20 | 19 | 15 | 16-0051308 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3013 | 17.1873 | 164_226 | <25mph | <15mph | HFTD - Distribution | 2016-07-20 19:15:00 | 608 | 18.9944 | FALSE | <25mph | LVMC1 | 3.62 | 2016-07-21T02:02:00Z | 18.01 | 1 | < 25mph | VAQC1 | 4.3 | 2016-07-21T01:45:00Z | 20 | 57 | < 25mph | LVMC1 | 3.62 | 2016-07-21T03:02:00Z | 18.99 | 2 | < 25mph | VAQC1 | 4.3 | 2016-07-21T02:45:00Z | 24 | 115 | < 25mph
PG&E | 2016-07-21 21:45 | 42572.9062 | 40.8566 | -122.3387 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101455670 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0870 | 2016 | 7 | 21 | 21 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.7351 | 143_397 | <25mph | <15mph | HFTD - Distribution | 2016-07-21 21:45:00 | 613 | 15.1303 | FALSE | <25mph |  |  |  | 0 | 0 | No data | SLFC1 | 6.48 | 2016-07-22T04:19:00Z | 15.99 | 5 | < 25mph |  |  |  | 0 | 0 | No data | SLFC1 | 6.48 | 2016-07-22T04:19:00Z | 15.99 | 10 | < 25mph
PG&E | 2016-07-24 16:24 | 42575.6833 | 38.0105 | -122.1941 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | CCD | 103049639 |  | 115000 | Conductor | Overhead | Yes | 42575.6833 | 2016-07-24 16:24 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0876 | 2016 | 7 | 24 | 16 | 24 | PS-2016-013 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 0 | 18.9534 | 148_240 | <25mph | <15mph | HFTD - Transmission | 2016-07-24 16:24:00 | 619 | 23.7155 | FALSE | <25mph | E6179 | 3.92 | 2016-07-24T23:20:00Z | 12.01 | 12 | < 25mph | DPXC1 | 4.78 | 2016-07-24T22:48:00Z | 22.12 | 80 | < 25mph | E6179 | 3.92 | 2016-07-25T00:20:00Z | 14.99 | 24 | < 25mph | DPXC1 | 4.78 | 2016-07-24T22:48:00Z | 22.12 | 156 | < 25mph
PG&E | 2016-07-25 15:32 | 42576.6472 | 38.3522 | -120.7107 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42576.6472 | 2016-07-25 15:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0878 | 2016 | 7 | 25 | 15 | 32 | 16-0052398 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 19951 | 10.4912 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-25 15:32:00 | 621 | 14.4675 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2016-07-25T21:56:00Z | 8.99 | 2 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2016-07-25T22:56:00Z | 11.01 | 4 | < 25mph
PG&E | 2016-07-27 11:53 | 42578.4951 | 37.8649 | -120.5134 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101041792 |  | 17000 | Conductor | Overhead | Yes | 42578.4951 | 2016-07-27 11:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0880 | 2016 | 7 | 27 | 11 | 53 | 16-0052942 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 14734 | 9.7065 | 221_232 | <25mph | <15mph | HFTD - Distribution | 2016-07-27 11:53:00 | 622 | 14.5426 | FALSE | <25mph | GNSC1 | 2.2 | 2016-07-27T18:03:00Z | 10 | 1 | < 25mph | GNSC1 | 2.2 | 2016-07-27T18:03:00Z | 10 | 8 | < 25mph | GNSC1 | 2.2 | 2016-07-27T19:03:00Z | 10 | 2 | < 25mph | GNSC1 | 2.2 | 2016-07-27T19:03:00Z | 10 | 16 | < 25mph
PG&E | 2016-07-27 17:05 | 42578.7118 | 38.5392 | -122.7656 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102029945 |  | 60000 | Conductor | Overhead | Yes | 42578.7118 | 2016-07-27 17:05 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0882 | 2016 | 7 | 27 | 17 | 5 | FU-2016-047 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 18.1446 | 123_269 | <25mph | <15mph | HFTD - Transmission | 2016-07-27 17:05:00 | 625 | 18.1446 | FALSE | <25mph | E6724 | 1.55 | 2016-07-27T23:20:00Z | 14 | 19 | < 25mph | E6724 | 1.55 | 2016-07-27T23:20:00Z | 14 | 89 | < 25mph | E6724 | 1.55 | 2016-07-28T00:30:00Z | 14 | 37 | < 25mph | E6724 | 1.55 | 2016-07-28T00:30:00Z | 14 | 166 | < 25mph
PG&E | 2016-07-28 08:12 | 42579.3417 | 37.8207 | -120.1388 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101037043 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0884 | 2016 | 7 | 28 | 8 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 1.7128 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 08:12:00 | 627 | 11.4062 | FALSE | <25mph | SEWC1 | 2.5 | 2016-07-28T14:16:00Z | 10 | 5 | < 25mph | SEWC1 | 2.5 | 2016-07-28T14:16:00Z | 10 | 5 | < 25mph | SEWC1 | 2.5 | 2016-07-28T14:16:00Z | 10 | 10 | < 25mph | SEWC1 | 2.5 | 2016-07-28T14:16:00Z | 10 | 10 | < 25mph
PG&E | 2016-07-28 12:58 | 42579.5403 | 37.2371 | -119.8157 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103323932 |  | 21000 | Conductor | Overhead | Yes | 42579.5403 | 2016-07-28 12:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0885 | 2016 | 7 | 28 | 12 | 58 | 16-0053313 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 15215 | 9.4729 | 252_197 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 12:58:00 | 628 | 14.0324 | FALSE | <25mph | E5766 | 0.77 | 2016-07-28T19:25:00Z | 8.01 | 12 | < 25mph | E5766 | 0.77 | 2016-07-28T19:25:00Z | 8.01 | 12 | < 25mph | E5766 | 0.77 | 2016-07-28T19:25:00Z | 8.01 | 12 | < 25mph | E5766 | 0.77 | 2016-07-28T19:25:00Z | 8.01 | 12 | < 25mph
PG&E | 2016-07-28 13:19 | 42579.5549 | 39.7127 | -123.4973 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102195566 |  | 12000 | Conductor | Overhead | Yes | 42579.5549 | 2016-07-28 13:19 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0886 | 2016 | 7 | 28 | 13 | 19 | 16-0053369 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 4447 | 11.1949 | 93_335 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 13:19:00 | 629 | 12.238 | FALSE | <25mph | LAYC1 | 0.97 | 2016-07-28T19:29:00Z | 7 | 1 | < 25mph | LAYC1 | 0.97 | 2016-07-28T19:29:00Z | 7 | 1 | < 25mph | LAYC1 | 0.97 | 2016-07-28T20:29:00Z | 10 | 2 | < 25mph | LAYC1 | 0.97 | 2016-07-28T20:29:00Z | 10 | 2 | < 25mph
PG&E | 2016-07-28 14:24 | 42579.6 | 37.8232 | -120.1356 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101037045 |  | 17000 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Guy/Span Wire | N.A. | N.A. | Unknown |  | no-match | 0888 | 2016 | 7 | 28 | 14 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Guy/Span Wire | N.A. | 10.9021 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 14:24:00 | 631 | 11.4062 | FALSE | <25mph | SEWC1 | 2.46 | 2016-07-28T21:16:00Z | 14.99 | 5 | < 25mph | SEWC1 | 2.46 | 2016-07-28T21:16:00Z | 14.99 | 5 | < 25mph | SEWC1 | 2.46 | 2016-07-28T22:16:00Z | 15.99 | 9 | < 25mph | SEWC1 | 2.46 | 2016-07-28T22:16:00Z | 15.99 | 9 | < 25mph
PG&E | 2016-07-29 | 18:16 | 38.5769 | -122.6187 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Selma Fire Department |  |  | 12000 | Conductor | Overhead | Yes | 42580 | 0.76111 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0890 | 2016 | 7 | 29 | 18 | 16 | 16-0053726 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 177834 | 13.7145 | 130_271 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 18:16:00 | 635 | 15.1116 | FALSE | <25mph | E2050 | 1.89 | 2016-07-29T06:56:00Z | 0 | 15 | < 25mph | E2362 | 7.38 | 2016-07-29T06:20:00Z | 4 | 26 | < 25mph | E2050 | 1.89 | 2016-07-29T07:56:00Z | 0 | 30 | < 25mph | E2362 | 7.38 | 2016-07-29T06:20:00Z | 4 | 50 | < 25mph
PG&E | 2016-07-29 01:31 | 42580.0632 | 41.0396 | -123.674 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Hoopa FD | 100962351 |  | 12000 | Conductor | Overhead | Yes | 42580.0632 | 2016-07-29 01:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0891 | 2016 | 7 | 29 | 1 | 31 | 16-0053478 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1418 | 4.1421 | 88_408 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 01:31:00 | 633 | 13.6696 | FALSE | <25mph | HOAC1 | 0.58 | 2016-07-29T07:40:00Z | 3 | 1 | < 25mph | HOAC1 | 0.58 | 2016-07-29T07:40:00Z | 3 | 1 | < 25mph | HOAC1 | 0.58 | 2016-07-29T08:40:00Z | 4 | 2 | < 25mph | HOAC1 | 0.58 | 2016-07-29T08:40:00Z | 4 | 2 | < 25mph
PG&E | 2016-07-31 12:11 | 42582.5076 | 38.7827 | -120.9168 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101417359 |  | 21000 | Conductor | Overhead | Yes | 42582.5076 | 2016-07-31 12:11 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0895 | 2016 | 7 | 31 | 12 | 11 | 16-0053949 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 10.9662 | 203_282 | <25mph | <15mph | HFTD - Distribution | 2016-07-31 12:11:00 | 638 | 14.1387 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 6.02 | 2016-07-31T18:56:00Z | 12.01 | 43 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 6.02 | 2016-07-31T18:56:00Z | 12.01 | 81 | < 25mph
PG&E | 2016-08-01 | 42583.5347 | 38.9044 | -121.1274 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100078299 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42583 | 2016-08-01 12:50 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0896 | 2016 | 8 | 1 | 12 | 50 | 16-0054142 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 855 | 9.1677 | 194_289 | <25mph | <15mph | HFTD - Distribution | 2016-08-01 12:50:00 | 639 | 14.2258 | FALSE | <25mph | D8862 | 3.4 | 2016-08-01T06:23:00Z | 4 | 4 | < 25mph | LICC1 | 7.66 | 2016-08-01T06:13:00Z | 8.99 | 5 | < 25mph | D8862 | 3.4 | 2016-08-01T06:23:00Z | 4 | 8 | < 25mph | LICC1 | 7.66 | 2016-08-01T07:13:00Z | 11.01 | 10 | < 25mph
PG&E | 2016-08-01 | 42583.7701 | 38.6956 | -120.9283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412720 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0898 | 2016 | 8 | 1 | 18 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2359 | 203_277 | <25mph | <15mph | HFTD - Distribution | 2016-08-01 18:29:00 | 641 | 12.0255 | FALSE | <25mph | D4464 | 2.83 | 2016-08-01T06:05:00Z | 4 | 17 | < 25mph | D4464 | 2.83 | 2016-08-01T06:05:00Z | 4 | 73 | < 25mph | D4464 | 2.83 | 2016-08-01T06:05:00Z | 4 | 31 | < 25mph | BENC1 | 7.25 | 2016-08-01T07:59:00Z | 4.99 | 136 | < 25mph
PG&E | 2016-08-02 | 42584.6771 | 37.0312 | -119.4395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Fresno County FD | 100675986 |  | 12000 | Conductor | Overhead | Yes | 42584 | 2016-08-02 16:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0900 | 2016 | 8 | 2 | 16 | 15 | 16-0054552 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 265566 | 14.0604 | 268_186 | <25mph | <15mph | HFTD - Distribution | 2016-08-02 16:15:00 | 643 | 14.6638 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTQC1 | 4.04 | 2016-08-02T06:52:00Z | 4 | 5 | < 25mph |  |  |  | 0 | 0 | No data | MTQC1 | 4.04 | 2016-08-02T07:52:00Z | 4 | 11 | < 25mph
PG&E | 2016-08-03 | 42585.1931 | 38.8474 | -120.812 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire garden valley fire | 103809676 |  | 21000 | Conductor | Overhead | Yes | 42585 | 2016-08-03 04:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0901 | 2016 | 8 | 3 | 4 | 38 | 16-0054597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2751 | 9.4989 | 208_286 | <25mph | <15mph | HFTD - Distribution | 2016-08-03 04:38:00 | 644 | 11.5219 | FALSE | <25mph | D5266 | 2.62 | 2016-08-03T06:44:00Z | 3 | 13 | < 25mph | BDMC1 | 6.95 | 2016-08-03T06:36:00Z | 5.99 | 31 | < 25mph | D5266 | 2.62 | 2016-08-03T07:54:00Z | 3 | 22 | < 25mph | BDMC1 | 6.95 | 2016-08-03T07:36:00Z | 7 | 63 | < 25mph
PG&E | 2016-08-03 | 42585.5285 | 39.3269 | -120.6033 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100001032 |  | 12000 | Conductor | Overhead | Yes | 42585 | 2016-08-03 12:41 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0902 | 2016 | 8 | 3 | 12 | 41 | 16-0054769 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 20554 | 9.0542 | 216_312 | <25mph | <15mph | HFTD - Distribution | 2016-08-03 12:41:00 | 645 | 12.3394 | FALSE | <25mph | CISCO | 2.6 | 2016-08-03T06:00:00Z | 7.9 | 12 | < 25mph | CISCO | 2.6 | 2016-08-03T06:00:00Z | 7.9 | 16 | < 25mph | CISCO | 2.6 | 2016-08-03T07:30:00Z | 10.11 | 22 | < 25mph | CISCO | 2.6 | 2016-08-03T07:30:00Z | 10.11 | 30 | < 25mph
PG&E | 2016-08-05 | 42587.5292 | 38.4048 | -120.5292 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101244628 |  | 12000 | Conductor | Overhead | Yes | 42587 | 2016-08-05 12:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0906 | 2016 | 8 | 5 | 12 | 42 | 16-0055368 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 363 | 12.0247 | 220_261 | <25mph | <15mph | HFTD - Distribution | 2016-08-05 12:42:00 | 649 | 12.7612 | FALSE | <25mph | AT450 | 0.53 | 2016-08-05T07:00:00Z | 0 | 13 | < 25mph | MTZC1 | 6.75 | 2016-08-05T06:56:00Z | 8.99 | 24 | < 25mph | AT450 | 0.53 | 2016-08-05T08:00:00Z | 0 | 25 | < 25mph | MTZC1 | 6.75 | 2016-08-05T07:56:00Z | 8.99 | 47 | < 25mph
PG&E | 2016-08-05 | 42587.6153 | 40.4797 | -123.7803 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103572261 |  | 12000 | Conductor | Overhead | Yes | 42587 | 2016-08-05 14:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0907 | 2016 | 8 | 5 | 14 | 46 | 16-0055425 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 7019 | 13.7408 | 83_377 | <25mph | <15mph | HFTD - Distribution | 2016-08-05 14:46:00 | 650 | 14.7579 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E8593 | 4.09 | 2016-08-05T07:00:00Z | 5.99 | 13 | < 25mph |  |  |  | 0 | 0 | No data | E8593 | 4.09 | 2016-08-05T07:30:00Z | 7 | 25 | < 25mph
PG&E | 2016-08-07 | 42589.5972 | 37.2316 | -122.1552 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire/woodside fire | 103413747 |  | 12000 | Conductor | Overhead | Yes | 42589 | 2016-08-07 14:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0910 | 2016 | 8 | 7 | 14 | 20 | 16-0055597 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29869 | 12.3369 | 149_197 | <25mph | <15mph | HFTD - Distribution | 2016-08-07 14:20:00 | 653 | 12.9748 | FALSE | <25mph | E6800 | 0.63 | 2016-08-07T06:51:00Z | 4 | 4 | < 25mph | BNDC1 | 7.02 | 2016-08-07T06:50:00Z | 14.99 | 59 | < 25mph | E6800 | 0.63 | 2016-08-07T07:36:00Z | 4 | 8 | < 25mph | BNDC1 | 7.02 | 2016-08-07T07:50:00Z | 14.99 | 116 | < 25mph
PG&E | 2016-08-08 | 42590.6556 | 37.1382 | -121.9672 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100519919 |  | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0912 | 2016 | 8 | 8 | 15 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 8.8992 | 157_192 | <25mph | <15mph | HFTD - Distribution | 2016-08-08 15:44:00 | 655 | 10.1741 | FALSE | <25mph | D9791 | 1.67 | 2016-08-08T07:00:00Z | 0 | 27 | < 25mph | E6085 | 4.45 | 2016-08-08T06:06:00Z | 5.99 | 135 | < 25mph | D8979 | 1.09 | 2016-08-08T07:42:00Z | 1.01 | 55 | < 25mph | E6085 | 4.45 | 2016-08-08T06:06:00Z | 5.99 | 267 | < 25mph
PG&E | 2016-08-09 | 42591.8063 | 38.9187 | -120.9525 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | El Dorado County FD | 100038028 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0915 | 2016 | 8 | 9 | 19 | 21 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.2678 | 201_290 | <25mph | <15mph | HFTD - Distribution | 2016-08-09 19:21:00 | 658 | 10.7446 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8862 | 6.76 | 2016-08-09T06:14:00Z | 4.99 | 17 | < 25mph |  |  |  | 0 | 0 | No data | D8862 | 6.76 | 2016-08-09T06:14:00Z | 4.99 | 34 | < 25mph
PG&E | 2016-08-10 | 42592.3583 | 37.0575 | -121.9556 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 101680487 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0917 | 2016 | 8 | 10 | 8 | 36 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 6.3982 | 157_187 | <25mph | <15mph | HFTD - Distribution | 2016-08-10 08:36:00 | 659 | 9.833 | FALSE | <25mph | AR172 | 3.97 | 2016-08-10T07:00:00Z | 4.99 | 43 | < 25mph | C8539 | 7.1 | 2016-08-10T06:56:00Z | 4.99 | 172 | < 25mph | AR172 | 3.97 | 2016-08-10T07:15:00Z | 4.99 | 84 | < 25mph | E5038 | 6.34 | 2016-08-10T07:31:00Z | 4.99 | 340 | < 25mph
PG&E | 2016-08-12 | 42594.4222 | 38.8751 | -122.4223 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 102168360 |  | 12000 | Conductor | Overhead | Yes | 42594 | 2016-08-12 10:08 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0922 | 2016 | 8 | 12 | 10 | 8 | 16-0056982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 1368 | 5.1025 | 138_288 | <25mph | <15mph | HFTD - Distribution | 2016-08-12 10:08:00 | 665 | 17.0718 | FALSE | <25mph | KNXC1 | 0.95 | 2016-08-12T06:09:00Z | 3 | 1 | < 25mph | KNXC1 | 0.95 | 2016-08-12T06:09:00Z | 3 | 9 | < 25mph | KNXC1 | 0.95 | 2016-08-12T07:09:00Z | 4 | 2 | < 25mph | KNXC1 | 0.95 | 2016-08-12T07:09:00Z | 4 | 18 | < 25mph
PG&E | 2016-08-13 | 14:31 | 37.4642 | -119.8589 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire |  |  | 21000 | Conductor | Overhead | Yes | 42595 | 0.60486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0923 | 2016 | 8 | 13 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.5527 | 249_210 | <25mph | <15mph | HFTD - Distribution | 2016-08-13 14:31:00 | 667 | 11.4441 | FALSE | <25mph | E9110 | 3.11 | 2016-08-13T06:44:00Z | 5.99 | 3 | < 25mph | E9110 | 3.11 | 2016-08-13T06:44:00Z | 5.99 | 7 | < 25mph | E9110 | 3.11 | 2016-08-13T07:59:00Z | 5.99 | 7 | < 25mph | E9110 | 3.11 | 2016-08-13T07:59:00Z | 5.99 | 15 | < 25mph
PG&E | 2016-08-13 | 42595.5833 | 39.2009 | -121.213 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100011376 | PACIFIC BELL | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0924 | 2016 | 8 | 13 | 14 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 9.674 | 190_305 | <25mph | <15mph | HFTD - Distribution | 2016-08-13 14:00:00 | 666 | 11.9455 | FALSE | <25mph | E2572 | 2.38 | 2016-08-13T06:48:00Z | 1.01 | 11 | < 25mph | E1789 | 5.78 | 2016-08-13T07:00:00Z | 4.99 | 36 | < 25mph | E2572 | 2.38 | 2016-08-13T06:48:00Z | 1.01 | 21 | < 25mph | E1789 | 5.78 | 2016-08-13T07:18:00Z | 7 | 70 | < 25mph
PG&E | 2016-08-15 | 42597.6549 | 37.8784 | -120.4488 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101020079 |  | 17000 | Conductor | Overhead | Yes | 42597 | 2016-08-15 15:43 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0928 | 2016 | 8 | 15 | 15 | 43 | 16-0057465 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 122905 | 10.0906 | 223_232 | <25mph | <15mph | HFTD - Distribution | 2016-08-15 15:43:00 | 671 | 12.9875 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.26 | 2016-08-15T06:03:00Z | 11.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.26 | 2016-08-15T06:03:00Z | 11.01 | 2 | < 25mph
PG&E | 2016-08-17 | 42599.516 | 41.2495 | -123.7671 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103315791 |  | 12000 | Conductor | Overhead | Yes | 42599 | 2016-08-17 12:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0932 | 2016 | 8 | 17 | 12 | 23 | 16-0058002 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 16544 | 13.4388 | 84_420 | <25mph | <15mph | HFTD - Distribution | 2016-08-17 12:23:00 | 675 | 14.3475 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TS777 | 6.47 | 2016-08-17T06:04:00Z | 3 | 2 | < 25mph |  |  |  | 0 | 0 | No data | NTCC1 | 5.46 | 2016-08-17T07:45:00Z | 4 | 4 | < 25mph
PG&E | 2016-08-17 | 42599.7757 | 37.3078 | -119.6511 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101020932 |  | 21000 | Conductor | Overhead | Yes | 42599 | 2016-08-17 18:37 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0934 | 2016 | 8 | 17 | 18 | 37 | 16-0058019 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 59379 | 5.4346 | 259_201 | <25mph | <15mph | HFTD - Distribution | 2016-08-17 18:37:00 | 677 | 11.1875 | FALSE | <25mph | D7171 | 3.9 | 2016-08-17T06:09:00Z | 5.99 | 26 | < 25mph | BSNC1 | 5.02 | 2016-08-17T06:48:00Z | 8.01 | 57 | < 25mph | D7171 | 3.9 | 2016-08-17T06:09:00Z | 5.99 | 54 | < 25mph | BSNC1 | 5.02 | 2016-08-17T07:48:00Z | 8.01 | 114 | < 25mph
PG&E | 2016-08-19 | 42601.6826 | 39.2235 | -123.755 | Vegetation | RURAL | < 3 meters | Fire Agency | Albion-Little River FD | 102206661 |  | 12000 | Conductor | Overhead | Yes | 42601 | 2016-08-19 16:23 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0938 | 2016 | 8 | 19 | 16 | 23 | 16-0058677 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 95106 | 9.7374 | 82_308 | <25mph | <15mph | HFTD - Distribution | 2016-08-19 16:23:00 | 681 | 11.9986 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6025 | 4.66 | 2016-08-19T07:00:00Z | 0 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6025 | 4.66 | 2016-08-19T08:00:00Z | 1.01 | 7 | < 25mph
PG&E | 2016-08-21 | 42603.5431 | 38.4445 | -122.2496 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102291451 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42603 | 2016-08-21 13:02 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0940 | 2016 | 8 | 21 | 13 | 2 | 16-0058847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 12780 | 10.3444 | 145_264 | <25mph | <15mph | HFTD - Distribution | 2016-08-21 13:02:00 | 683 | 21.5044 | FALSE | <25mph | ATLC1 | 2.26 | 2016-08-21T06:29:00Z | 2.01 | 1 | < 25mph | ATLC1 | 2.26 | 2016-08-21T06:29:00Z | 2.01 | 1 | < 25mph | ATLC1 | 2.26 | 2016-08-21T07:29:00Z | 4 | 2 | < 25mph | ATLC1 | 2.26 | 2016-08-21T07:29:00Z | 4 | 3 | < 25mph
PG&E | 2016-08-22 | 42604.6736 | 37.9666 | -120.2395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Toulumne City FD | 101043683 |  | 17000 | Conductor | Overhead | Yes | 42604 | 2016-08-22 16:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0941 | 2016 | 8 | 22 | 16 | 10 | 16-0059149 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 78534 | 13.4322 | 233_237 | <25mph | <15mph | HFTD - Distribution | 2016-08-22 16:10:00 | 684 | 13.7297 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.67 | 2016-08-22T06:02:00Z | 13 | 5 | < 25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.67 | 2016-08-22T07:02:00Z | 14 | 10 | < 25mph
PG&E | 2016-08-25 | 42607.5028 | 36.9726 | -119.3816 | Vegetation | RURAL | < 3 meters | Utility: PG&E | N.A. | 100651318 | PONDEROSA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0945 | 2016 | 8 | 25 | 12 | 4 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.3948 | 271_183 | <25mph | <15mph | HFTD - Distribution | 2016-08-25 12:04:00 | 689 | 15.1668 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTQC1 | 5.65 | 2016-08-25T06:52:00Z | 4.99 | 6 | < 25mph |  |  |  | 0 | 0 | No data | TRMC1 | 5.94 | 2016-08-25T07:52:00Z | 4.99 | 13 | < 25mph
PG&E | 2016-08-30 | 42612.6674 | 36.5941 | -121.9212 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Unknown | 101734977 |  | 21000 | Conductor | Overhead | Yes | 42612 | 2016-08-30 16:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0951 | 2016 | 8 | 30 | 16 | 1 | 16-0061130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 199327 | 14.6893 | 159_162 | <25mph | <15mph | HFTD - Distribution | 2016-08-30 16:01:00 | 694 | 14.6893 | FALSE | <25mph | E8505 | 2.6 | 2016-08-30T06:15:00Z | 20 | 48 | < 25mph | E8505 | 2.6 | 2016-08-30T06:15:00Z | 20 | 52 | < 25mph | E8505 | 2.6 | 2016-08-30T06:15:00Z | 20 | 91 | < 25mph | E8505 | 2.6 | 2016-08-30T06:15:00Z | 20 | 99 | < 25mph
PG&E | 2016-08-31 | 42613.6194 | 35.1918 | -120.4697 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101942860 |  | 12000 | Conductor | Overhead | Yes | 42613 | 2016-08-31 14:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0955 | 2016 | 8 | 31 | 14 | 52 | 16-0061423 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 156294 | 16.7717 | 224_84 | <25mph | <15mph | HFTD - Distribution | 2016-08-31 14:52:00 | 697 | 16.7717 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C9687 | 6.31 | 2016-08-31T06:30:00Z | 4.99 | 13 | < 25mph |  |  |  | 0 | 0 | No data | C9687 | 6.31 | 2016-08-31T06:30:00Z | 4.99 | 23 | < 25mph
PG&E | 2016-09-12 | 4:24 | 36.3999 | -121.902 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire Hwy 1 Carmel Hill | 101669614 |  | 12000 | Conductor | Overhead | Yes | 42625 | 0.18333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0973 | 2016 | 9 | 12 | 4 | 24 | 16-0063826 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 130604 | 5.4712 | 159_151 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 04:24:00 | 715 | 8.1881 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TR419 | 7.81 | 2016-09-12T06:15:00Z | 14 | 1 | < 25mph |  |  |  | 0 | 0 | No data | TR419 | 7.81 | 2016-09-12T07:15:00Z | 15.99 | 2 | < 25mph
PG&E | 2016-09-12 | 12:38 | 38.7832 | -120.6006 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101421708 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42625 | 0.52639 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0974 | 2016 | 9 | 12 | 12 | 38 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 15.5165 | 217_282 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 12:38:00 | 716 | 15.5342 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E3165 | 7.91 | 2016-09-12T06:37:00Z | 4 | 6 | < 25mph |  |  |  | 0 | 0 | No data | E3165 | 7.91 | 2016-09-12T06:37:00Z | 4 | 12 | < 25mph
PG&E | 2016-09-15 | 15:56 | 37.1102 | -121.9509 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100520198 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42628 | 0.66389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0982 | 2016 | 9 | 15 | 15 | 56 | 16-0065001 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 28900 | 4.729 | 158_190 | <25mph | <15mph | HFTD - Distribution | 2016-09-15 15:56:00 | 724 | 12.2674 | FALSE | <25mph | D8979 | 1.17 | 2016-09-15T06:16:00Z | 7 | 56 | < 25mph | D8979 | 1.17 | 2016-09-15T06:16:00Z | 7 | 108 | < 25mph | D8979 | 1.17 | 2016-09-15T07:18:00Z | 8.01 | 107 | < 25mph | E9039 | 4.03 | 2016-09-15T07:56:00Z | 8.99 | 204 | < 25mph
PG&E | 2016-09-16 20:56 | 42629.8722 | 39.8387 | -121.7023 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 100441760 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42629.8722 | 2016-09-16 20:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0983 | 2016 | 9 | 16 | 20 | 56 | 16-0065273 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 314427 | 11.5178 | 170_340 | <25mph | <15mph | HFTD - Distribution | 2016-09-16 20:56:00 | 725 | 12.6422 | FALSE | <25mph | C8878 | 3.59 | 2016-09-17T03:53:00Z | 0 | 12 | < 25mph | CSTC1 | 4.21 | 2016-09-17T03:51:00Z | 7 | 14 | < 25mph | C8878 | 3.59 | 2016-09-17T03:53:00Z | 0 | 12 | < 25mph | CSTC1 | 4.21 | 2016-09-17T04:51:00Z | 7 | 16 | < 25mph
PG&E | 2016-09-18 | 14:33 | 37.1619 | -122.1347 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire & Boulder Creek Fire Dept. | 103410909 | Yes | 12000 | Conductor | Overhead | Yes | 42631 | 0.60625 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0986 | 2016 | 9 | 18 | 14 | 33 | 16-0065437 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 54983 | 5.897 | 150_193 | <25mph | <15mph | HFTD - Distribution | 2016-09-18 14:33:00 | 728 | 11.3228 | FALSE | <25mph | BNDC1 | 2.99 | 2016-09-18T06:50:00Z | 7 | 23 | < 25mph | BNDC1 | 2.99 | 2016-09-18T06:50:00Z | 7 | 49 | < 25mph | BNDC1 | 2.99 | 2016-09-18T06:50:00Z | 7 | 43 | < 25mph | BNDC1 | 2.99 | 2016-09-18T06:50:00Z | 7 | 94 | < 25mph
PG&E | 2016-09-20 | 8:25 | 40.0044 | -123.7871 | Vegetation | RURAL | < 3 meters | Self Extinguished | N.A. | 100992643 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42633 | 0.35069 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0990 | 2016 | 9 | 20 | 8 | 25 | 16-0065910 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 798 | 11.2567 | 82_351 | <25mph | <15mph | HFTD - Distribution | 2016-09-20 08:25:00 | 732 | 20.9022 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AV037 | 4.73 | 2016-09-20T06:23:00Z | 4 | 3 | < 25mph |  |  |  | 0 | 0 | No data | AV037 | 4.73 | 2016-09-20T07:03:00Z | 4 | 7 | < 25mph
PG&E | 2016-09-21 | 10:01 | 39.1173 | -121.071 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100014315 | PACIFIC BELL | 115000 | Conductor | Overhead | Yes | 42634 | 0.41736 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0991 | 2016 | 9 | 21 | 10 | 1 | INT-08560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 18.3543 | 196_301 | <25mph | <15mph | HFTD - Transmission | 2016-09-21 10:01:00 | 734 | 24.3978 | FALSE | <25mph | E1789 | 3.84 | 2016-09-21T06:54:00Z | 13 | 29 | < 25mph | E1789 | 3.84 | 2016-09-21T06:54:00Z | 13 | 87 | < 25mph | E1789 | 3.84 | 2016-09-21T06:54:00Z | 13 | 57 | < 25mph | E1789 | 3.84 | 2016-09-21T06:54:00Z | 13 | 165 | < 25mph
PG&E | 2016-09-22 | 13:53 | 40.224 | -122.3417 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101539450 | None | 12000 | Conductor | Overhead | Yes | 42635 | 0.57847 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0996 | 2016 | 9 | 22 | 13 | 53 | 16-0066692 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 14706 | 14.6017 | 143_362 | <25mph | <15mph | HFTD - Distribution | 2016-09-22 13:53:00 | 739 | 20.1469 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 6.08 | 2016-09-22T06:24:00Z | 14 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 6.08 | 2016-09-22T07:54:00Z | 18.01 | 8 | < 25mph
PG&E | 2016-09-23 05:23 | 15:23 | 39.3784 | -121.0922 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100091491 | None | 12000 | Conductor | Overhead | Yes | 42636.2243 | 0.64097 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0999 | 2016 | 9 | 23 | 15 | 23 | 16-0067089 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 80185 | 10.9717 | 195_315 | <25mph | <15mph | HFTD - Distribution | 2016-09-23 15:23:00 | 741 | 11.3047 | FALSE | <25mph | E3651 | 3.67 | 2016-09-23T12:20:00Z | 0 | 12 | < 25mph | RRRC1 | 5.34 | 2016-09-23T12:13:00Z | 8.01 | 13 | < 25mph | E3651 | 3.67 | 2016-09-23T13:20:00Z | 0 | 24 | < 25mph | RRRC1 | 5.34 | 2016-09-23T12:13:00Z | 8.01 | 26 | < 25mph
PG&E | 2016-09-25 | 19:19 | 37.0993 | -122.1155 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire ben lomond fire | 101670837 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42638 | 0.80486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1003 | 2016 | 9 | 25 | 19 | 19 | 16-0067346 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1497 | 2.1111 | 150_190 | <25mph | <15mph | HFTD - Distribution | 2016-09-25 19:19:00 | 746 | 9.8702 | FALSE | <25mph | BNDC1 | 3.83 | 2016-09-25T06:50:00Z | 8.99 | 28 | < 25mph | BNDC1 | 3.83 | 2016-09-25T06:50:00Z | 8.99 | 47 | < 25mph | BNDC1 | 3.83 | 2016-09-25T07:50:00Z | 10 | 55 | < 25mph | BNDC1 | 3.83 | 2016-09-25T07:50:00Z | 10 | 96 | < 25mph
PG&E | 2016-09-25 10:35 | 42638.441 | 38.8019 | -122.8176 | Vegetation | RURAL | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103613996 |  | 115000 | Other | Overhead | Yes | 2016-09-25 10:35 | 2016-09-25 10:35 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1004 | 2016 | 9 | 25 | 10 | 35 | INT-08572 | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Equip Failure - Other | 0 | 28.1055 | 121_284 | 25-40mph | 15-30mph | HFTD - Transmission | 2016-09-25 10:35:00 | 743 | 28.9174 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | HWKC1 | 4.73 | 2016-09-25T16:56:00Z | 35.99 | 2 | 25-40mph |  |  |  | 0 | 0 | No data | HWKC1 | 4.73 | 2016-09-25T17:56:00Z | 35.99 | 4 | 25-40mph
PG&E | 2016-09-26 | 10:40 | 38.0157 | -122.6889 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | marin county fire | 102252082 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42639 | 0.44444 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1005 | 2016 | 9 | 26 | 10 | 40 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 4.5159 | 126_240 | <25mph | <15mph | HFTD - Distribution | 2016-09-26 10:40:00 | 747 | 11.2091 | FALSE | <25mph | WDAC1 | 2.97 | 2016-09-26T06:51:00Z | 12.01 | 2 | < 25mph | WDAC1 | 2.97 | 2016-09-26T06:51:00Z | 12.01 | 27 | < 25mph | WDAC1 | 2.97 | 2016-09-26T06:51:00Z | 12.01 | 4 | < 25mph | WDAC1 | 2.97 | 2016-09-26T06:51:00Z | 12.01 | 56 | < 25mph
PG&E | 2016-09-28 | 14:00 | 35.2145 | -118.5625 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire |  |  | 0 – 750 | Conductor | Overhead | Yes | 42641 | 0.58333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1008 | 2016 | 9 | 28 | 14 | 0 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.8467 | 310_87 | <25mph | <15mph | HFTD - Distribution | 2016-09-28 14:00:00 | 750 | 26.957 | FALSE | 25-40mph | HFLC1 | 3.31 | 2016-09-28T06:13:00Z | 15.99 | 7 | < 25mph | HFLC1 | 3.31 | 2016-09-28T06:13:00Z | 15.99 | 28 | < 25mph | HFLC1 | 3.31 | 2016-09-28T06:13:00Z | 15.99 | 15 | < 25mph | HFLC1 | 3.31 | 2016-09-28T06:13:00Z | 15.99 | 58 | < 25mph
PG&E | 2016-10-02 16:41 | 16:41 | 39.8888 | -121.6648 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103358082 |  | 12000 | Other | Overhead | Yes | 42645.6954 | 0.69514 | Other | N.A. | N.A. | N.A. | Weather | lightning strike | Other/Unknown | 1013 | 2016 | 10 | 2 | 16 | 41 | 16-0069050 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 339550 | 8.5152 | 171_343 | <25mph | <15mph | HFTD - Distribution | 2016-10-02 16:41:00 | 755 | 17.2989 | FALSE | <25mph | C8878 | 1.4 | 2016-10-02T23:28:00Z | 1.01 | 12 | < 25mph | CSTC1 | 5.65 | 2016-10-02T22:51:00Z | 18.01 | 19 | < 25mph | C8878 | 1.4 | 2016-10-03T00:38:00Z | 14 | 24 | < 25mph | CSTC1 | 5.65 | 2016-10-02T23:51:00Z | 28.01 | 42 | 25-40mph
PG&E | 2016-10-08 15:05 | 15:04 | 38.6686 | -120.9091 | Vegetation | RURAL | < 0.25 Acres | Customer | N.A. | 101380856 |  | 0 – 750 | Capacitor Bank | Overhead | Yes | 42651.6284 | 0.62778 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1021 | 2016 | 10 | 8 | 15 | 4 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 10.4532 | 203_276 | <25mph | <15mph | HFTD - Distribution | 2016-10-08 15:04:00 | 762 | 14.8776 | FALSE | <25mph | C6129 | 3.74 | 2016-10-08T21:09:00Z | 12.01 | 18 | < 25mph | C6129 | 3.74 | 2016-10-08T21:09:00Z | 12.01 | 64 | < 25mph | C6129 | 3.74 | 2016-10-08T21:09:00Z | 12.01 | 36 | < 25mph | C6129 | 3.74 | 2016-10-08T21:09:00Z | 12.01 | 126 | < 25mph
PG&E | 2016-10-09 18:52 | 18:52 | 38.656 | -120.9725 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101376768 |  | 12000 | Conductor | Overhead | Yes | 42652.7862 | 0.78611 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1024 | 2016 | 10 | 9 | 18 | 52 | 16-0070676 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 98361 | 11.3582 | 201_275 | <25mph | <15mph | HFTD - Distribution | 2016-10-09 18:52:00 | 765 | 14.948 | FALSE | <25mph | D7401 | 2.79 | 2016-10-10T01:03:00Z | 1.01 | 8 | < 25mph | BENC1 | 4.97 | 2016-10-10T00:59:00Z | 8.01 | 63 | < 25mph | D7401 | 2.79 | 2016-10-10T02:03:00Z | 1.01 | 16 | < 25mph | BENC1 | 4.97 | 2016-10-10T00:59:00Z | 8.01 | 126 | < 25mph
PG&E | 2016-10-11 23:17 | 23:16 | 39.0201 | -120.8294 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire.foresthill fire | 100025501 |  | 60000 | Conductor | Overhead | Yes | 42654.9701 | 0.96944 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error |  | no-match | 1028 | 2016 | 10 | 11 | 23 | 16 | INT-08640 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 0 | 7.6312 | 207_295 | <25mph | <15mph | HFTD - Transmission | 2016-10-11 23:16:00 | 769 | 11.1078 | FALSE | <25mph | AU268 | 0.89 | 2016-10-12T06:04:00Z | 2.01 | 6 | < 25mph | FSHC1 | 7.19 | 2016-10-12T05:33:00Z | 3 | 7 | < 25mph | AU268 | 0.89 | 2016-10-12T06:49:00Z | 2.01 | 9 | < 25mph | FSHC1 | 7.19 | 2016-10-12T06:33:00Z | 3 | 11 | < 25mph
PG&E | 2016-10-13 23:23 | 23:14 | 40.4901 | -122.3729 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | SHASTA COUNTY FIRE | 101502366 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42656.9745 | 0.96806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1029 | 2016 | 10 | 13 | 23 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 30.3025 | 142_377 | 25-40mph | 30-45mph | HFTD - Distribution | 2016-10-13 23:14:00 | 770 | 30.3025 | FALSE | 25-40mph | E6886 | 3.41 | 2016-10-14T05:33:00Z | 41 | 4 | 40-55mph | KRDD | 4.3 | 2016-10-14T05:55:00Z | 50.64 | 17 | 40-55mph | E6886 | 3.41 | 2016-10-14T06:48:00Z | 47 | 8 | 40-55mph | KRDD | 4.3 | 2016-10-14T06:53:00Z | 56.39 | 39 | 55mph+
PG&E | 2016-10-14 04:33 | 4:32 | 40.5228 | -121.6813 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101513661 |  | 12000 | Conductor | Overhead | Yes | 42657.1893 | 0.18889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1032 | 2016 | 10 | 14 | 4 | 32 | 16-0071897 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 38950 | 28.7152 | 171_378 | 25-40mph | 15-30mph | HFTD - Distribution | 2016-10-14 04:32:00 | 773 | 31.1927 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | VIOC1 | 5.45 | 2016-10-14T10:52:00Z | 31 | 1 | 25-40mph |  |  |  | 0 | 0 | No data | VIOC1 | 5.45 | 2016-10-14T10:52:00Z | 31 | 2 | 25-40mph
PG&E | 2016-10-14 19:45 | 19:44 | 39.6245 | -121.5382 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100435570 |  | 0 – 750 | Conductor | Overhead | Yes | 42657.8228 | 0.82222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1036 | 2016 | 10 | 14 | 19 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.5623 | 177_329 | <25mph | <15mph | HFTD - Distribution | 2016-10-14 19:44:00 | 777 | 22.2526 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CICC1 | 5.69 | 2016-10-15T01:54:00Z | 18.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CICC1 | 5.69 | 2016-10-15T01:54:00Z | 18.99 | 2 | < 25mph
PG&E | 2016-10-19 10:42 | 10:42 | 38.5098 | -122.45 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | st helena | 102242552 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42662.4459 | 0.44583 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1040 | 2016 | 10 | 19 | 10 | 42 | 16-0073955 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 693 | 4.5329 | 137_268 | <25mph | <15mph | HFTD - Distribution | 2016-10-19 10:42:00 | 781 | 13.4953 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AT925 | 4.5 | 2016-10-19T17:15:00Z | 8.01 | 12 | < 25mph |  |  |  | 0 | 0 | No data | AT925 | 4.5 | 2016-10-19T18:40:00Z | 10 | 24 | < 25mph
PG&E | 2016-10-23 18:44 | 18:10 | 38.021 | -120.5991 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101272943 |  | 115000 | Conductor | Overhead | Yes | 42666.7804 | 0.75694 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1043 | 2016 | 10 | 23 | 18 | 10 | INT-08709 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 0 | 9.2045 | 217_240 | <25mph | <15mph | HFTD - Transmission | 2016-10-23 18:10:00 | 784 | 15.0974 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2861 | 6.79 | 2016-10-24T01:26:00Z | 3 | 10 | < 25mph |  |  |  | 0 | 0 | No data | E2861 | 6.79 | 2016-10-24T02:29:00Z | 3 | 20 | < 25mph
PG&E | 2016-11-09 | 9:06 | 37.4532 | -119.6413 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | US FOREST SERVICE | 101017062 |  | 12000 | Conductor | Overhead | Yes | 42683 | 0.37917 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1046 | 2016 | 11 | 9 | 9 | 6 | 16-0078863 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1586 | 6.3162 | 259_209 | <25mph | <15mph | HFTD - Distribution | 2016-11-09 09:06:00 | 787 | 14.6769 | FALSE | <25mph | TR172 | 1.09 | 2016-11-09T07:45:00Z | 8.99 | 5 | < 25mph | TR172 | 1.09 | 2016-11-09T07:45:00Z | 8.99 | 25 | < 25mph | TR172 | 1.09 | 2016-11-09T08:45:00Z | 12.01 | 8 | < 25mph | TR172 | 1.09 | 2016-11-09T08:45:00Z | 12.01 | 47 | < 25mph
PG&E | 2016-11-15 | 17:27 | 39.7275 | -121.6557 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100327525 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42689 | 0.72708 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 1049 | 2016 | 11 | 15 | 17 | 27 | 16-0080083 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 69231 | 9.6883 | 172_334 | <25mph | <15mph | HFTD - Distribution | 2016-11-15 17:27:00 | 790 | 16.6369 | FALSE | <25mph | PDEC1 | 2.44 | 2016-11-15T08:00:00Z | 2.01 | 2 | < 25mph | PDEC1 | 2.44 | 2016-11-15T08:00:00Z | 2.01 | 2 | < 25mph | PDEC1 | 2.44 | 2016-11-15T09:00:00Z | 2.01 | 3 | < 25mph | PDEC1 | 2.44 | 2016-11-15T09:00:00Z | 2.01 | 3 | < 25mph
PG&E | 2017-04-04 13:36 | 13:29 | 35.6885 | -120.7653 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101945026 | None | 12000 | Conductor | Overhead | Yes | 42829.567 | 0.56181 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1064 | 2017 | 4 | 4 | 13 | 29 | 17-0036460 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 167151 | 3.61 | 210_111 | <25mph | <15mph | HFTD - Distribution | 2017-04-04 13:29:00 | 804 | 8.6409 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D4060 | 7.1 | 2017-04-04T20:22:00Z | 5.99 | 3 | < 25mph |  |  |  | 0 | 0 | No data | D4060 | 7.1 | 2017-04-04T20:22:00Z | 5.99 | 3 | < 25mph
PG&E | 2017-04-25 12:39 | 12:38 | 38.6583 | -120.9762 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101376746 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 42850.5271 | 0.52639 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1072 | 2017 | 4 | 25 | 12 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 9.948 | 200_275 | <25mph | <15mph | HFTD - Distribution | 2017-04-25 12:38:00 | 812 | 10.5664 | FALSE | <25mph | D7401 | 2.53 | 2017-04-25T18:45:00Z | 10 | 3 | < 25mph | C6129 | 7.33 | 2017-04-25T19:24:00Z | 20 | 56 | < 25mph | D7401 | 2.53 | 2017-04-25T18:45:00Z | 10 | 5 | < 25mph | C6129 | 7.33 | 2017-04-25T19:24:00Z | 20 | 102 | < 25mph
PG&E | 2017-04-28 16:21 | 15:49 | 38.7679 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chris paper fire investigator, 530/677-1868. incident #caaeuo11821 | 101409833 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42853.6815 | 0.65903 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1077 | 2017 | 4 | 28 | 15 | 49 | 17-0043771 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 82614 | 19.7837 | 201_281 | <25mph | <15mph | HFTD - Distribution | 2017-04-28 15:49:00 | 817 | 25.4223 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | D7401 | 6.46 | 2017-04-28T22:51:00Z | 25.99 | 53 | 25-40mph |  |  |  | 0 | 0 | No data | D7401 | 6.46 | 2017-04-28T22:51:00Z | 25.99 | 104 | 25-40mph
PG&E | 2017-04-29 15:29 | 15:07 | 37.0349 | -119.5242 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100678661 | Unknown | 12000 | Conductor | Overhead | Yes | 42854.6453 | 0.62986 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1078 | 2017 | 4 | 29 | 15 | 7 | 17-0043911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 7.6275 | 265_186 | <25mph | <15mph | HFTD - Distribution | 2017-04-29 15:07:00 | 818 | 19.1329 | FALSE | <25mph | PRHC1 | 2.76 | 2017-04-29T22:27:00Z | 10 | 1 | < 25mph | PRHC1 | 2.76 | 2017-04-29T22:27:00Z | 10 | 1 | < 25mph | PRHC1 | 2.76 | 2017-04-29T23:27:00Z | 13 | 2 | < 25mph | PRHC1 | 2.76 | 2017-04-29T23:27:00Z | 13 | 2 | < 25mph
PG&E | 2017-05-05 15:52 | 15:52 | 40.3776 | -123.0019 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101501566 | None | 12000 | Conductor | Overhead | Yes | 42860.6614 | 15:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1084 | 2017 | 5 | 5 | 15 | 52 | 17-0045707 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 56893 | 24.5621 | 115_371 | <25mph | <15mph | HFTD - Distribution | 2017-05-05 15:52:00 | 824 | 35.0644 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | YOBC1 | 4.35 | 2017-05-05T22:35:00Z | 5.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | YOBC1 | 4.35 | 2017-05-05T23:35:00Z | 7 | 2 | < 25mph
PG&E | 2017-05-06 11:23 | 11:18 | 40.7951 | -124.029 | Vegetation | Rural | < 3 Meters | Fire Agency | chief rick harden 7074423352 | 103661154 | Unknown | 12000 | Conductor | Overhead | Yes | 42861.4744 | 0.47083 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1086 | 2017 | 5 | 6 | 11 | 18 | 17-0045785 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 113630 | 26.2788 | 73_395 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-05-06 11:18:00 | 826 | 28.8261 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | D8223 | 6.16 | 2017-05-06T17:35:00Z | 27 | 35 | 25-40mph |  |  |  | 0 | 0 | No data | D8223 | 6.16 | 2017-05-06T19:10:00Z | 30 | 76 | 25-40mph
PG&E | 2017-05-09 18:41 | 18:26 | 40.8689 | -123.5156 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | todd wright fire chief. 5307392493 | 103796045 | Unknown | 12000 | Conductor | Overhead | Yes | 42864.7782 | 0.76806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1092 | 2017 | 5 | 9 | 18 | 26 | 17-0046642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 108117 | 15.9566 | 94_399 | <25mph | <15mph | HFTD - Distribution | 2017-05-09 18:26:00 | 832 | 17.9691 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LYEC1 | 5.31 | 2017-05-10T00:46:00Z | 10 | 1 | < 25mph |  |  |  | 0 | 0 | No data | LYEC1 | 5.31 | 2017-05-10T00:46:00Z | 10 | 2 | < 25mph
PG&E | 2017-05-14 | 11:59 | 38.0798 | -122.8665 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102247059 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42869 | 0.49931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1095 | 2017 | 5 | 14 | 11 | 59 | 17-0047802 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 377483 | 24.3878 | 118_244 | <25mph | <15mph | HFTD - Distribution | 2017-05-14 11:59:00 | 835 | 24.3878 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PTRCA | 4.65 | 2017-05-14T06:30:00Z | 27.2 | 12 | 25-40mph |  |  |  | 0 | 0 | No data | PTRCA | 4.65 | 2017-05-14T06:30:00Z | 27.2 | 18 | 25-40mph
PG&E | 2017-05-15 | 3:05 | 35.6261 | -120.8962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101873299 | Unknown | 21000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1097 | 2017 | 5 | 15 | 3 | 5 | 17-0047837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 337188 | 4.016 | 204_108 | <25mph | <15mph | HFTD - Distribution | 2017-05-15 03:05:00 | 837 | 18.5139 | FALSE | <25mph | TABC1 | 2.62 | 2017-05-15T06:07:00Z | 3 | 1 | < 25mph | TABC1 | 2.62 | 2017-05-15T06:07:00Z | 3 | 1 | < 25mph | TABC1 | 2.62 | 2017-05-15T07:07:00Z | 3 | 2 | < 25mph | TABC1 | 2.62 | 2017-05-15T07:07:00Z | 3 | 2 | < 25mph
PG&E | 2017-05-15 16:14 | 16:00 | 37.1766 | -119.8189 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SHAUN FAIRBANKS 559-683-4823 | 101108423 | SIERRA | 21000 | Conductor | Overhead | Yes | 42870.6767 | 0.66667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1099 | 2017 | 5 | 15 | 16 | 0 | 17-0048096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20007 | 15.7465 | 251_194 | <25mph | <15mph | HFTD - Distribution | 2017-05-15 16:00:00 | 839 | 20.7849 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5766 | 4.44 | 2017-05-15T22:22:00Z | 5.99 | 11 | < 25mph |  |  |  | 0 | 0 | No data | E5766 | 4.44 | 2017-05-15T22:22:00Z | 5.99 | 23 | < 25mph
PG&E | 2017-05-24 16:25 | 16:24 | 38.834 | -121.1197 | Vegetation | Rural | < 3 Meters | Fire Agency | Fire Capt | 103838109 | None | 12000 | Conductor | Overhead | Yes | 42879.6837 | 16:24 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | no-match | 1111 | 2017 | 5 | 24 | 16 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 20.975 | 194_285 | <25mph | <15mph | HFTD - Distribution | 2017-05-24 16:24:00 | 851 | 20.975 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 5.95 | 2017-05-24T22:56:00Z | 15.99 | 21 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 5.95 | 2017-05-24T23:56:00Z | 15.99 | 40 | < 25mph
PG&E | 2017-05-25 15:05 | 15:05 | 36.5217 | -121.8473 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Buddy Bloxham 831-236-5659 | 101778611 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42880.6288 | 0.62847 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1113 | 2017 | 5 | 25 | 15 | 5 | 17-0050761 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 13965 | 25.8899 | 162_158 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-05-25 15:05:00 | 853 | 26.2648 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E8505 | 7.82 | 2017-05-25T21:07:00Z | 31 | 34 | 25-40mph |  |  |  | 0 | 0 | No data | KMRY | 4.75 | 2017-05-25T22:54:00Z | 32.21 | 77 | 25-40mph
PG&E | 2017-05-25 17:36 | 16:55 | 38.3986 | -122.9876 | Vegetation | Rural | < 3 Meters | Utility: PG&E | N.A. | 101974034 | Unknown | 12000 | Conductor | Overhead | Yes | 42880.7334 | 0.70486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1114 | 2017 | 5 | 25 | 16 | 55 | 17-0050815 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 2644 | 12.6436 | 114_262 | <25mph | <15mph | HFTD - Distribution | 2017-05-25 16:55:00 | 854 | 13.2306 | FALSE | <25mph | D2849 | 1.17 | 2017-05-26T00:17:00Z | 10 | 12 | < 25mph | DUTWW | 7.06 | 2017-05-26T00:00:00Z | 17.81 | 55 | < 25mph | D2849 | 1.17 | 2017-05-26T00:17:00Z | 10 | 23 | < 25mph | DUTWW | 7.06 | 2017-05-26T01:00:00Z | 17.81 | 109 | < 25mph
PG&E | 2017-06-03 13:35 | 13:26 | 38.9017 | -121.2056 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100043664 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42889.5662 | 0.55972 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1122 | 2017 | 6 | 3 | 13 | 26 | 17-0052543 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29512 | 13.2044 | 191_289 | <25mph | <15mph | HFTD - Distribution | 2017-06-03 13:26:00 | 862 | 14.9142 | FALSE | <25mph | LICC1 | 3.58 | 2017-06-03T20:13:00Z | 8.99 | 1 | < 25mph | LICC1 | 3.58 | 2017-06-03T20:13:00Z | 8.99 | 19 | < 25mph | LICC1 | 3.58 | 2017-06-03T20:13:00Z | 8.99 | 2 | < 25mph | AR944 | 7.74 | 2017-06-03T20:45:00Z | 8.99 | 36 | < 25mph
PG&E | 2017-06-08 15:19 | 15:08 | 34.6058 | -120.0214 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SHAWN STEINER | 101947678 | Unknown | 12000 | Conductor | Overhead | Yes | 42894.6382 | 0.63056 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1136 | 2017 | 6 | 8 | 15 | 8 | 17-0053783 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 41311 | 18.6266 | 244_52 | <25mph | <15mph | HFTD - Distribution | 2017-06-08 15:08:00 | 875 | 20.2983 | FALSE | <25mph | KIZA | 3.08 | 2017-06-08T21:55:00Z | 19.57 | 2 | < 25mph | SXWC1 | 5.38 | 2017-06-08T22:09:00Z | 23 | 18 | < 25mph | KIZA | 3.08 | 2017-06-08T23:15:00Z | 20.71 | 5 | < 25mph | SXWC1 | 5.38 | 2017-06-08T23:09:00Z | 24 | 39 | < 25mph
PG&E | 2017-06-10 07:38 | 07:37 | 35.4359 | -120.4957 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101890429 | Unknown | 21000 | Conductor | Overhead | Yes | 42896.3177 | 07:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1140 | 2017 | 6 | 10 | 7 | 37 | 17-0054182 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 34397 | 9.2577 | 222_98 | <25mph | <15mph | HFTD - Distribution | 2017-06-10 07:37:00 | 879 | 18.05 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2260 | 7.67 | 2017-06-10T14:14:00Z | 4 | 5 | < 25mph |  |  |  | 0 | 0 | No data | E2260 | 7.67 | 2017-06-10T15:26:00Z | 12.01 | 10 | < 25mph
PG&E | 2017-06-13 | 14:30 | 37.8526 | -122.1853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Tower 005/035c | Unknown | 115000 | Conductor | Overhead | Yes | 42899 | 0.60417 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1143 | 2017 | 6 | 13 | 14 | 30 | INT-09744 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | Balloons | 0 | 10.6352 | 148_231 | <25mph | <15mph | HFTD - Transmission | 2017-06-13 14:30:00 | 882 | 14.5193 | FALSE | <25mph | LBNL1 | 3.84 | 2017-06-13T07:00:00Z | 14.05 | 45 | < 25mph | LBNL1 | 3.84 | 2017-06-13T07:00:00Z | 14.05 | 123 | < 25mph | LBNL1 | 3.84 | 2017-06-13T07:00:00Z | 14.05 | 93 | < 25mph | LTRC1 | 6.59 | 2017-06-13T07:28:00Z | 17 | 258 | < 25mph
PG&E | 2017-06-15 04:31 | 2:58 | 40.299 | -122.4318 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101511631 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42901.1885 | 0.12361 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | Other/Unknown | 1145 | 2017 | 6 | 15 | 2 | 58 | 17-0055359 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1762 | 9.755 | 139_366 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 02:58:00 | 884 | 19.4408 | FALSE | <25mph | E7114 | 1.68 | 2017-06-15T10:47:00Z | 3 | 4 | < 25mph | E7114 | 1.68 | 2017-06-15T10:47:00Z | 3 | 4 | < 25mph | E7114 | 1.68 | 2017-06-15T10:47:00Z | 3 | 7 | < 25mph | E7114 | 1.68 | 2017-06-15T10:47:00Z | 3 | 7 | < 25mph
PG&E | 2017-06-15 08:08 | 7:39 | 39.2276 | -121.2348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE CHIEF | 103676075 | Unknown | 21000 | Conductor | Overhead | Yes | 42901.3391 | 0.31875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1147 | 2017 | 6 | 15 | 7 | 39 | 17-0055387 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 740 | 10.5195 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 07:39:00 | 886 | 12.4202 | FALSE | <25mph | E2572 | 2.6 | 2017-06-15T15:03:00Z | 1.01 | 11 | < 25mph | E1789 | 7.9 | 2017-06-15T15:06:00Z | 4 | 25 | < 25mph | E2572 | 2.6 | 2017-06-15T16:03:00Z | 2.01 | 21 | < 25mph | E1789 | 7.9 | 2017-06-15T16:00:00Z | 5.99 | 48 | < 25mph
PG&E | 2017-06-15 15:04 | 15:01 | 39.3913 | -123.3054 | Vegetation | Rural | < 0.25 Acres | Fire Agency | STEPHEN | 103838176 | YES | 12000 | Conductor | Overhead | Yes | 42901.6279 | 0.62569 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1148 | 2017 | 6 | 15 | 15 | 1 | 17-0055557 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 180469 | 19.6681 | 101_317 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 15:01:00 | 887 | 19.7788 | FALSE | <25mph | E4027 | 2.73 | 2017-06-15T21:48:00Z | 17 | 22 | < 25mph | AU552 | 4.26 | 2017-06-15T22:04:00Z | 20 | 36 | < 25mph | E4027 | 2.73 | 2017-06-15T23:03:00Z | 17 | 39 | < 25mph | AU552 | 4.26 | 2017-06-15T23:01:00Z | 20 | 65 | < 25mph
PG&E | 2017-06-16 19:15 | 19:14 | 38.3443 | -122.7812 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101970801 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42902.8019 | 19:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1155 | 2017 | 6 | 16 | 19 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 20.0158 | 122_259 | <25mph | <15mph | HFTD - Distribution | 2017-06-16 19:14:00 | 894 | 22.0101 | FALSE | <25mph | AR323 | 3.41 | 2017-06-17T01:49:00Z | 15.99 | 12 | < 25mph | BTOWW | 5.5 | 2017-06-17T01:45:00Z | 22.1 | 44 | < 25mph | AR323 | 3.41 | 2017-06-17T01:49:00Z | 15.99 | 24 | < 25mph | BTOWW | 5.5 | 2017-06-17T01:45:00Z | 22.1 | 92 | < 25mph
PG&E | 2017-06-16 22:30 | 22:30 | 38.0373 | -122.1847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101424286 | Unknown | 21000 | Conductor | Overhead | Yes | 42902.9378 | 22:30 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1156 | 2017 | 6 | 16 | 22 | 30 | 17-0055882 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 12000 | 25.2975 | 148_241 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-06-16 22:30:00 | 895 | 25.6656 | FALSE | 25-40mph | UPBC1 | 3.49 | 2017-06-17T05:00:00Z | 32.97 | 21 | 25-40mph | UPBC1 | 3.49 | 2017-06-17T05:00:00Z | 32.97 | 63 | 25-40mph | UPBC1 | 3.49 | 2017-06-17T05:00:00Z | 32.97 | 41 | 25-40mph | UPBC1 | 3.49 | 2017-06-17T05:00:00Z | 32.97 | 122 | 25-40mph
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 0.4 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 14.8685 | 222_261 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 09:36:00 | 925 | 23.4839 | FALSE | <25mph | AT450 | 2.61 | 2017-06-22T17:04:00Z | 4 | 16 | < 25mph | ULBC1 | 6.95 | 2017-06-22T16:33:00Z | 8.99 | 34 | < 25mph | AT450 | 2.61 | 2017-06-22T18:04:00Z | 5.99 | 27 | < 25mph | ULBC1 | 6.95 | 2017-06-22T16:33:00Z | 8.99 | 59 | < 25mph
PG&E | 2017-06-22 17:54 | 18:07 | 38.7583 | -120.7176 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101401088 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.7461 | 0.75486 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1188 | 2017 | 6 | 22 | 18 | 7 | 17-0057857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 8517 | 11.5365 | 212_281 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 18:07:00 | 927 | 16.1873 | FALSE | <25mph | E5691 | 3.88 | 2017-06-23T00:37:00Z | 7 | 22 | < 25mph | E6490 | 7.72 | 2017-06-23T00:14:00Z | 7 | 35 | < 25mph | E5691 | 3.88 | 2017-06-23T00:37:00Z | 7 | 42 | < 25mph | E6490 | 7.72 | 2017-06-23T00:14:00Z | 7 | 67 | < 25mph
PG&E | 2017-06-23 13:01 | 13:00 | 39.3051 | -122.4862 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 100329817 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42909.5421 | 13:00 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | no-match | 1190 | 2017 | 6 | 23 | 13 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 8.6467 | 136_311 | <25mph | <15mph | HFTD - Distribution | 2017-06-23 13:00:00 | 929 | 13.2674 | FALSE | <25mph |  |  |  | 0 | 0 | No data | SYWC1 | 6.32 | 2017-06-23T19:26:00Z | 11.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | SYWC1 | 6.32 | 2017-06-23T20:26:00Z | 11.01 | 2 | < 25mph
PG&E | 2017-06-24 10:32 | 10:31 | 38.9438 | -121.0447 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100090318 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42910.439 | 0.43819 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1193 | 2017 | 6 | 24 | 10 | 31 | 17-0058318 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 582 | 9.5424 | 198_291 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 10:31:00 | 932 | 10.7882 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.98 | 2017-06-24T16:56:00Z | 10 | 22 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.98 | 2017-06-24T17:56:00Z | 10 | 43 | < 25mph
PG&E | 2017-06-24 15:06 | 14:51 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 42910.6292 | 0.61875 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1194 | 2017 | 6 | 24 | 14 | 51 | 17-0058332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 21296 | 10.4286 | 210_259 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 14:51:00 | 933 | 10.7263 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.33 | 2017-06-24T21:56:00Z | 8.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.33 | 2017-06-24T21:56:00Z | 8.99 | 2 | < 25mph
PG&E | 2017-06-24 22:27 | 22:27 | 38.2908 | -120.849 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CONTACT BOBBY BOWMAN | 101238865 | None | 12000 | Conductor | Overhead | Yes | 42910.9354 | 0.93542 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1195 | 2017 | 6 | 24 | 22 | 27 | 17-0058399 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 4529 | 5.1717 | 206_255 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 22:27:00 | 934 | 13.7168 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.57 | 2017-06-25T05:05:00Z | 10 | 10 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.57 | 2017-06-25T05:05:00Z | 10 | 24 | < 25mph
PG&E | 2017-06-25 02:47 | 0:23 | 39.4043 | -123.3869 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102193088 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42911.1159 | 0.015972 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1197 | 2017 | 6 | 25 | 0 | 23 | 17-0058406 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 23100 | 15.6787 | 98_318 | <25mph | <15mph | HFTD - Distribution | 2017-06-25 00:23:00 | 935 | 19.8426 | FALSE | <25mph | AT319 | 3.31 | 2017-06-25T09:44:00Z | 4 | 24 | < 25mph | AU552 | 7.7 | 2017-06-25T09:46:00Z | 4.99 | 54 | < 25mph | AT319 | 3.31 | 2017-06-25T09:44:00Z | 4 | 48 | < 25mph | AU552 | 7.7 | 2017-06-25T10:45:00Z | 4.99 | 104 | < 25mph
PG&E | 2017-06-27 09:28 | 9:23 | 37.9559 | -122.6176 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | marin county fire | 102260068 | UNFILED | 12000 | Conductor | Overhead | Yes | 42913.3944 | 0.39097 | Other | N.A. | N.A. | N.A. | Unknown |  | Fell into (slight defect) | 1203 | 2017 | 6 | 27 | 9 | 23 | 17-0058882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 3920 | 16.1278 | 129_237 | <25mph | <15mph | HFTD - Distribution | 2017-06-27 09:23:00 | 942 | 18.7182 | FALSE | <25mph | MDEC1 | 2.55 | 2017-06-27T15:36:00Z | 24 | 18 | < 25mph | MDEC1 | 2.55 | 2017-06-27T15:36:00Z | 24 | 24 | < 25mph | MDEC1 | 2.55 | 2017-06-27T15:36:00Z | 24 | 35 | < 25mph | MDEC1 | 2.55 | 2017-06-27T15:36:00Z | 24 | 47 | < 25mph
PG&E | 2017-06-30 01:20 | 01:20 | 39.821 | -121.5883 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103840463 | YES | 12000 | Conductor | Overhead | Yes | 42916.0559 | 01:20 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1210 | 2017 | 6 | 30 | 1 | 20 | 17-0059647 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 2888 | 7.4054 | 174_339 | <25mph | <15mph | HFTD - Distribution | 2017-06-30 01:20:00 | 948 | 9.8944 | FALSE | <25mph | C4565 | 1.69 | 2017-06-30T07:43:00Z | 3 | 6 | < 25mph | JBGC1 | 7.9 | 2017-06-30T08:13:00Z | 10 | 20 | < 25mph | C4565 | 1.69 | 2017-06-30T07:43:00Z | 3 | 12 | < 25mph | JBGC1 | 7.9 | 2017-06-30T09:13:00Z | 11.01 | 40 | < 25mph
PG&E | 2017-06-30 23:55 | 23:54 | 38.5794 | -122.8835 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 101958804 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42916.9965 | 23:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1211 | 2017 | 6 | 30 | 23 | 54 | 17-0059922 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2025 | 14.1552 | 118_272 | <25mph | <15mph | HFTD - Distribution | 2017-06-30 23:54:00 | 950 | 23.4555 | FALSE | <25mph | R08WW | 2.5 | 2017-07-01T06:00:00Z | 7.29 | 9 | < 25mph | DRYWW | 4.93 | 2017-07-01T06:00:00Z | 7.61 | 41 | < 25mph | R08WW | 2.5 | 2017-07-01T06:00:00Z | 7.29 | 18 | < 25mph | DRYWW | 4.93 | 2017-07-01T07:00:00Z | 9.19 | 82 | < 25mph
PG&E | 2017-07-01 | 12:02 | 39.8209 | -121.6418 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 003/039 | Unknown | 60000 | Conductor | Overhead | Yes | 42917 | 0.50139 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1212 | 2017 | 7 | 1 | 12 | 2 | INT-09792 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.6345 | 172_339 | <25mph | <15mph | HFTD - Transmission | 2017-07-01 12:02:00 | 954 | 9.664 | FALSE | <25mph | C4565 | 2.41 | 2017-07-01T06:53:00Z | 2.01 | 18 | < 25mph | CSTC1 | 7.61 | 2017-07-01T06:51:00Z | 11.01 | 21 | < 25mph | C4565 | 2.41 | 2017-07-01T07:53:00Z | 3 | 36 | < 25mph | CSTC1 | 7.61 | 2017-07-01T06:51:00Z | 11.01 | 41 | < 25mph
PG&E | 2017-07-01 04:43 | 3:12 | 38.1952 | -122.9197 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103855493 | Unknown | 12000 | Conductor | Overhead | Yes | 42917.1963 | 0.13333 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1214 | 2017 | 7 | 1 | 3 | 12 | 17-0059935 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 41370 | 14.0388 | 116_251 | <25mph | <15mph | HFTD - Distribution | 2017-07-01 03:12:00 | 951 | 27.9197 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PRWC1 | 7.17 | 2017-07-01T10:50:00Z | 27.98 | 13 | 25-40mph |  |  |  | 0 | 0 | No data | PRWC1 | 7.17 | 2017-07-01T10:50:00Z | 27.98 | 26 | 25-40mph
PG&E | 2017-07-02 | 13:28 | 39.8605 | -121.6274 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 000/017c | Unknown | 60000 | Conductor | Overhead | Yes | 42918 | 0.56111 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1216 | 2017 | 7 | 2 | 13 | 28 | INT-09794 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 10.1141 | 173_342 | <25mph | <15mph | HFTD - Transmission | 2017-07-02 13:28:00 | 956 | 11.4462 | FALSE | <25mph | C4565 | 1.76 | 2017-07-02T06:43:00Z | 2.01 | 18 | < 25mph | CSTC1 | 7.55 | 2017-07-02T06:51:00Z | 8.99 | 21 | < 25mph | C4565 | 1.76 | 2017-07-02T07:33:00Z | 2.01 | 36 | < 25mph | CSTC1 | 7.55 | 2017-07-02T06:51:00Z | 8.99 | 41 | < 25mph
PG&E | 2017-07-03 20:28 | 20:26 | 38.7923 | -120.9438 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101388730 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42919.853 | 0.85139 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1218 | 2017 | 7 | 3 | 20 | 26 | 17-0060336 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 8134 | 10.0527 | 202_283 | <25mph | <15mph | HFTD - Distribution | 2017-07-03 20:26:00 | 957 | 12.5378 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 4.45 | 2017-07-04T02:56:00Z | 7 | 25 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 4.45 | 2017-07-04T03:56:00Z | 7 | 50 | < 25mph
PG&E | 2017-07-04 20:17 | 20:16 | 40.4228 | -122.3975 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SCOTT CORN 530-448-2414 | 101481860 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42920.8451 | 20:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1221 | 2017 | 7 | 4 | 20 | 16 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 13.3568 | 141_373 | <25mph | <15mph | HFTD - Distribution | 2017-07-04 20:16:00 | 960 | 18.8443 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6886 | 4.89 | 2017-07-05T02:19:00Z | 11.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6886 | 4.89 | 2017-07-05T02:19:00Z | 11.01 | 8 | < 25mph
PG&E | 2017-07-05 12:11 | 11:58 | 39.2105 | -121.2266 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVE ROBERTSON 530 906 4892 | 100010286 | Unknown | 21000 | Conductor | Overhead | Yes | 42921.5077 | 0.49861 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1223 | 2017 | 7 | 5 | 11 | 58 | 17-0060605 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 10231 | 9.71 | 190_306 | <25mph | <15mph | HFTD - Distribution | 2017-07-05 11:58:00 | 962 | 14.0848 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1789 | 6.76 | 2017-07-05T18:54:00Z | 8.01 | 16 | < 25mph |  |  |  | 0 | 0 | No data | E1789 | 6.76 | 2017-07-05T19:30:00Z | 11.01 | 32 | < 25mph
PG&E | 2017-07-07 | 15:09 | 40.9054 | -122.3806 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101455950 | Unknown | 12000 | Conductor | Overhead | Yes | 42923 | 0.63125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1229 | 2017 | 7 | 7 | 15 | 9 | 17-0061903 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.0906 | 142_400 | <25mph | <15mph | HFTD - Distribution | 2017-07-07 15:09:00 | 969 | 11.4161 | FALSE | <25mph | CTANT | 2.76 | 2017-07-07T06:45:00Z | 13.04 | 11 | < 25mph | CTANT | 2.76 | 2017-07-07T06:45:00Z | 13.04 | 11 | < 25mph | CTANT | 2.76 | 2017-07-07T07:45:00Z | 15.52 | 20 | < 25mph | CTANT | 2.76 | 2017-07-07T07:45:00Z | 15.52 | 20 | < 25mph
PG&E | 2017-07-07 20:49 | 14:31 | 37.499 | -119.799 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVEN WARD OFFICE 209-966-3542 CELL559-706-8811 | 103855637 | Unknown | 21000 | Conductor | Overhead | Yes | 42923.8675 | 0.60486 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1230 | 2017 | 7 | 7 | 14 | 31 | 17-0061288 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 554306 | 11.2535 | 252_212 | <25mph | <15mph | HFTD - Distribution | 2017-07-07 14:31:00 | 968 | 22.3608 | FALSE | <25mph | JSDC1 | 3.81 | 2017-07-08T03:47:00Z | 7 | 1 | < 25mph | C1522 | 5.09 | 2017-07-08T03:01:00Z | 7 | 8 | < 25mph | JSDC1 | 3.81 | 2017-07-08T04:47:00Z | 8.01 | 2 | < 25mph | C1522 | 5.09 | 2017-07-08T04:31:00Z | 8.99 | 17 | < 25mph
PG&E | 2017-07-08 19:23 | 18:49 | 40.2935 | -122.4089 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | TOM STROING, RED BLUFF | 101526269 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42924.8076 | 0.78403 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1234 | 2017 | 7 | 8 | 18 | 49 | 17-0061469 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 157484 | 8.2983 | 140_366 | <25mph | <15mph | HFTD - Distribution | 2017-07-08 18:49:00 | 973 | 15.6109 | FALSE | <25mph | E7114 | 0.65 | 2017-07-09T01:29:00Z | 35.99 | 4 | 25-40mph | E7114 | 0.65 | 2017-07-09T01:29:00Z | 35.99 | 4 | 25-40mph | E7114 | 0.65 | 2017-07-09T01:29:00Z | 35.99 | 8 | 25-40mph | E7114 | 0.65 | 2017-07-09T01:29:00Z | 35.99 | 8 | 25-40mph
PG&E | 2017-07-10 18:00 | 17:00 | 37.3768 | -122.3597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | David Hibdon 831-254-1763 | 100270370 | Unknown | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1240 | 2017 | 7 | 10 | 17 | 0 | 17-0061857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3322 | 11.4741 | 140_205 | <25mph | <15mph | HFTD - Distribution | 2017-07-10 17:00:00 | 979 | 11.9313 | FALSE | <25mph | E4551 | 0.89 | 2017-07-11T00:03:00Z | 5.99 | 1 | < 25mph | PUGC1 | 7.47 | 2017-07-11T00:18:00Z | 14.99 | 17 | < 25mph | E4551 | 0.89 | 2017-07-11T00:03:00Z | 5.99 | 1 | < 25mph | PUGC1 | 7.47 | 2017-07-11T01:18:00Z | 18.01 | 30 | < 25mph
PG&E | 2017-07-11 22:13 | 22:12 | 37.0122 | -121.9497 | Vegetation | Rural | < 3 Meters | Fire Agency | CAPT PHIL CRAMBLET 831-479-6842 | 101676689 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42927.9254 | 22:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1244 | 2017 | 7 | 11 | 22 | 12 | 17-0062198 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 714 | 7.2694 | 158_185 | <25mph | <15mph | HFTD - Distribution | 2017-07-11 22:12:00 | 983 | 9.7577 | FALSE | <25mph | E5038 | 3.28 | 2017-07-12T04:30:00Z | 11.01 | 44 | < 25mph | C8539 | 5.04 | 2017-07-12T04:21:00Z | 14 | 153 | < 25mph | E5038 | 3.28 | 2017-07-12T04:30:00Z | 11.01 | 84 | < 25mph | C8539 | 5.04 | 2017-07-12T04:21:00Z | 14 | 311 | < 25mph
PG&E | 2017-07-12 | 16:04 | 40.6531 | -122.3343 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 000/001 | Unknown | 60000 | Conductor | Overhead | Yes | 42928 | 0.66944 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1245 | 2017 | 7 | 12 | 16 | 4 | INT-09837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 13.5069 | 143_386 | <25mph | <15mph | HFTD - Transmission | 2017-07-12 16:04:00 | 987 | 13.828 | FALSE | <25mph | C5599 | 3.4 | 2017-07-12T06:46:00Z | 0 | 4 | < 25mph | C5599 | 3.4 | 2017-07-12T06:46:00Z | 0 | 4 | < 25mph | C5599 | 3.4 | 2017-07-12T07:46:00Z | 0 | 7 | < 25mph | C5599 | 3.4 | 2017-07-12T07:46:00Z | 0 | 7 | < 25mph
PG&E | 2017-07-12 15:09 | 15:09 | 37.1491 | -122.0037 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 103565794 | Unknown | 21000 | Conductor | Overhead | Yes | 42928.6313 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1248 | 2017 | 7 | 12 | 15 | 9 | 17-0062439 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24690 | 9.5326 | 155_192 | <25mph | <15mph | HFTD - Distribution | 2017-07-12 15:09:00 | 986 | 9.5326 | FALSE | <25mph | D8979 | 3.17 | 2017-07-12T21:47:00Z | 8.01 | 19 | < 25mph | LSGC1 | 4.79 | 2017-07-12T21:32:00Z | 14.99 | 117 | < 25mph | D8979 | 3.17 | 2017-07-12T22:17:00Z | 8.99 | 32 | < 25mph | LSGC1 | 4.79 | 2017-07-12T22:32:00Z | 15.99 | 200 | < 25mph
PG&E | 2017-07-12 20:22 | 20:21 | 40.0808 | -123.8339 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103841917 | Unknown | 12000 | Conductor | Overhead | Yes | 42928.8485 | 20:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1249 | 2017 | 7 | 12 | 20 | 21 | 17-0062445 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 4616 | 11.5535 | 80_355 | <25mph | <15mph | HFTD - Distribution | 2017-07-12 20:21:00 | 988 | 18.1059 | FALSE | <25mph | AV037 | 2.72 | 2017-07-13T02:33:00Z | 11.01 | 3 | < 25mph | AV037 | 2.72 | 2017-07-13T02:33:00Z | 11.01 | 4 | < 25mph | AV037 | 2.72 | 2017-07-13T02:33:00Z | 11.01 | 6 | < 25mph | ERCC1 | 4.01 | 2017-07-13T03:28:00Z | 12.01 | 8 | < 25mph
PG&E | 2017-07-15 14:35 | 14:34 | 39.6231 | -121.5328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | russ fowler | 100404385 | Unknown | 12000 | Conductor | Overhead | Yes | 42931.6076 | 14:34 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1254 | 2017 | 7 | 15 | 14 | 34 | 17-0063126 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 54372 | 7.6156 | 177_329 | <25mph | <15mph | HFTD - Distribution | 2017-07-15 14:34:00 | 993 | 11.3229 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CICC1 | 5.91 | 2017-07-15T20:54:00Z | 12.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CICC1 | 5.91 | 2017-07-15T21:54:00Z | 12.01 | 2 | < 25mph
PG&E | 2017-07-16 11:59 | 11:59 | 36.6669 | -121.7515 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101761892 | None | 21000 | Fuse | Overhead | Yes | 42932.4994 | 11:59 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1259 | 2017 | 7 | 16 | 11 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 22.4318 | 166_166 | <25mph | <15mph | HFTD - Distribution | 2017-07-16 11:59:00 | 998 | 30.0095 | FALSE | 25-40mph | E6666 | 1.85 | 2017-07-16T18:50:00Z | 14.99 | 12 | < 25mph | E6666 | 1.85 | 2017-07-16T18:50:00Z | 14.99 | 16 | < 25mph | E6666 | 1.85 | 2017-07-16T19:50:00Z | 15.99 | 22 | < 25mph | E6666 | 1.85 | 2017-07-16T19:50:00Z | 15.99 | 30 | < 25mph
PG&E | 2017-07-16 12:10 | 12:10 | 35.6613 | -120.922 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101942626 | Unknown | 21000 | Conductor | Overhead | Yes | 42932.5072 | 12:10 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1260 | 2017 | 7 | 16 | 12 | 10 | 17-0063242 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 1304 | 7.6377 | 203_110 | <25mph | <15mph | HFTD - Distribution | 2017-07-16 12:10:00 | 999 | 17.3186 | FALSE | <25mph | TABC1 | 0.35 | 2017-07-16T19:07:00Z | 7 | 1 | < 25mph | D4060 | 6.39 | 2017-07-16T18:30:00Z | 7 | 17 | < 25mph | TABC1 | 0.35 | 2017-07-16T20:07:00Z | 8.99 | 2 | < 25mph | D4060 | 6.39 | 2017-07-16T20:00:00Z | 10 | 33 | < 25mph
PG&E | 2017-07-18 | 11:30 | 38.0484 | -120.5565 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 012/071 | Unknown | 115000 | Conductor | Overhead | Yes | 42934 | 0.47917 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1265 | 2017 | 7 | 18 | 11 | 30 | INT-09873 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 55499 | 7.0574 | 219_242 | <25mph | <15mph | HFTD - Transmission | 2017-07-18 11:30:00 | 1005 | 15.7901 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C9085 | 5.13 | 2017-07-18T06:53:00Z | 2.01 | 65 | < 25mph |  |  |  | 0 | 0 | No data | C9085 | 5.13 | 2017-07-18T06:53:00Z | 2.01 | 122 | < 25mph
PG&E | 2017-07-18 | 21:40 | 38.0031 | -122.2093 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | Pole 000/002 to 000/003 | Unknown | 60000 | Conductor | Overhead | Yes | 42934 | 0.90278 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1266 | 2017 | 7 | 18 | 21 | 40 | INT-09875 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 0 | 11.7142 | 147_239 | <25mph | <15mph | HFTD - Transmission | 2017-07-18 21:40:00 | 1007 | 20.8699 | FALSE | <25mph | E4251 | 2.95 | 2017-07-18T06:15:00Z | 12.01 | 4 | < 25mph | E9944 | 7.08 | 2017-07-18T06:21:00Z | 15.99 | 75 | < 25mph | E4251 | 2.95 | 2017-07-18T06:15:00Z | 12.01 | 9 | < 25mph | MZXC1 | 5.07 | 2017-07-18T07:24:00Z | 18.99 | 146 | < 25mph
PG&E | 2017-07-19 | 5:52 | 37.0905 | -119.6047 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Tower 003/001 | Unknown | 115000 | Conductor | Overhead | Yes | 42935 | 0.24444 | Contact From Object | N.A. | Other | Electric Facility | Unknown |  | no-match | 1269 | 2017 | 7 | 19 | 5 | 52 | INT-09877 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 0 | 0.36815 | 261_189 | <25mph | <15mph | HFTD - Transmission | 2017-07-19 05:52:00 | 1008 | 14.3689 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PRHC1 | 5.59 | 2017-07-19T06:27:00Z | 3 | 1 | < 25mph |  |  |  | 0 | 0 | No data | PRHC1 | 5.59 | 2017-07-19T07:27:00Z | 3 | 2 | < 25mph
PG&E | 2017-07-20 13:46 | 13:45 | 35.0804 | -120.5538 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | PAUL LEE 805 903-3416 INC # 8291 | 101941116 | Unknown | 12000 | Conductor | Overhead | Yes | 42936.5736 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1275 | 2017 | 7 | 20 | 13 | 45 | 17-0064321 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 45999 | 13.843 | 220_78 | <25mph | <15mph | HFTD - Distribution | 2017-07-20 13:45:00 | 1013 | 14.6968 | FALSE | <25mph | D6295 | 2.82 | 2017-07-20T20:33:00Z | 12.01 | 9 | < 25mph | D6295 | 2.82 | 2017-07-20T20:33:00Z | 12.01 | 28 | < 25mph | D6295 | 2.82 | 2017-07-20T20:33:00Z | 12.01 | 17 | < 25mph | D6295 | 2.82 | 2017-07-20T20:33:00Z | 12.01 | 54 | < 25mph
PG&E | 2017-07-22 12:26 | 12:25 | 40.8795 | -123.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Josh , comander chief of forest service. | 100980577 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.518 | 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1279 | 2017 | 7 | 22 | 12 | 25 | 17-0064721 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 23227 | 10.7493 | 84_399 | <25mph | <15mph | HFTD - Distribution | 2017-07-22 12:25:00 | 1018 | 13.5476 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BHTC1 | 5.5 | 2017-07-22T18:46:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | BHTC1 | 5.5 | 2017-07-22T19:46:00Z | 8.01 | 2 | < 25mph
PG&E | 2017-07-22 14:38 | 14:38 | 37.2994 | -122.1631 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100265488 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.6101 | 14:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1280 | 2017 | 7 | 22 | 14 | 38 | 17-0064738 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49181 | 4.6185 | 148_201 | <25mph | <15mph | HFTD - Distribution | 2017-07-22 14:38:00 | 1019 | 12.5156 | FALSE | <25mph | E0516 | 3.56 | 2017-07-22T21:33:00Z | 8.99 | 14 | < 25mph | C6623 | 4.81 | 2017-07-22T21:23:00Z | 12.01 | 87 | < 25mph | E0516 | 3.56 | 2017-07-22T21:49:00Z | 10 | 29 | < 25mph | C6623 | 4.81 | 2017-07-22T21:23:00Z | 12.01 | 168 | < 25mph
PG&E | 2017-07-23 09:22 | 09:22 | 40.642 | -122.2302 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT? | 101459708 | FRONTIER COMMUNICATI | 12000 | Conductor | Overhead | Yes | 42939.3906 | 09:22 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1282 | 2017 | 7 | 23 | 9 | 22 | 17-0064801 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 184712 | 3.9314 | 148_385 | <25mph | <15mph | HFTD - Distribution | 2017-07-23 09:22:00 | 1021 | 13.6933 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C5599 | 5.97 | 2017-07-23T15:31:00Z | 2.01 | 8 | < 25mph |  |  |  | 0 | 0 | No data | C5599 | 5.97 | 2017-07-23T17:02:00Z | 4 | 15 | < 25mph
PG&E | 2017-07-23 18:25 | 18:25 | 39.6723 | -123.5336 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103823226 | Unknown | 12000 | Conductor | Overhead | Yes | 42939.7676 | 18:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1284 | 2017 | 7 | 23 | 18 | 25 | 17-0064854 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 12864 | 11.8402 | 92_333 | <25mph | <15mph | HFTD - Distribution | 2017-07-23 18:25:00 | 1023 | 16.2282 | FALSE | <25mph | LAYC1 | 3.32 | 2017-07-24T00:29:00Z | 11.01 | 1 | < 25mph | LAYC1 | 3.32 | 2017-07-24T00:29:00Z | 11.01 | 7 | < 25mph | LAYC1 | 3.32 | 2017-07-24T00:29:00Z | 11.01 | 2 | < 25mph | LAYC1 | 3.32 | 2017-07-24T00:29:00Z | 11.01 | 14 | < 25mph
PG&E | 2017-07-24 14:02 | 14:01 | 37.2635 | -122.3364 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike klink 650-879-0121 | 100322130 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42940.5845 | 14:01 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1286 | 2017 | 7 | 24 | 14 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 18.4533 | 141_199 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 14:01:00 | 1025 | 18.6394 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 5.31 | 2017-07-24T20:07:00Z | 13 | 1 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 5.31 | 2017-07-24T20:07:00Z | 13 | 2 | < 25mph
PG&E | 2017-07-24 19:31 | 19:31 | 38.3519 | -120.7103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.8134 | 19:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1288 | 2017 | 7 | 24 | 19 | 31 | 17-0065145 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14281 | 10.3402 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 19:31:00 | 1027 | 12.2366 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2017-07-25T01:56:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2017-07-25T01:56:00Z | 7 | 2 | < 25mph
PG&E | 2017-07-24 21:45 | 21:45 | 35.6024 | -120.9211 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101860186 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.9063 | 21:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1289 | 2017 | 7 | 24 | 21 | 45 | 17-0065191 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 21231 | 19.4445 | 203_107 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 21:45:00 | 1028 | 30.0108 | FALSE | 25-40mph | TABC1 | 3.74 | 2017-07-25T04:07:00Z | 3 | 1 | < 25mph | TABC1 | 3.74 | 2017-07-25T04:07:00Z | 3 | 1 | < 25mph | TABC1 | 3.74 | 2017-07-25T05:07:00Z | 4 | 2 | < 25mph | TABC1 | 3.74 | 2017-07-25T05:07:00Z | 4 | 2 | < 25mph
PG&E | 2017-07-25 15:52 | 15:51 | 38.3779 | -122.5388 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102031447 | Unknown | 12000 | Conductor | Overhead | Yes | 42941.6609 | 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1290 | 2017 | 7 | 25 | 15 | 51 | 17-0065437 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 18584 | 12.338 | 133_260 | <25mph | <15mph | HFTD - Distribution | 2017-07-25 15:51:00 | 1029 | 16.6773 | FALSE | <25mph | KENWW | 2.06 | 2017-07-25T22:00:00Z | 15.3 | 4 | < 25mph | KENWW | 2.06 | 2017-07-25T22:00:00Z | 15.3 | 11 | < 25mph | F11WW | 3.22 | 2017-07-25T23:00:00Z | 15.5 | 10 | < 25mph | F11WW | 3.22 | 2017-07-25T23:00:00Z | 15.5 | 24 | < 25mph
PG&E | 2017-07-28 | 14:02 | 40.9997 | -121.9579 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101512624 | Unknown | 12000 | Conductor | Overhead | Yes | 42944 | 0.58472 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1293 | 2017 | 7 | 28 | 14 | 2 | 17-0066367 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 46581 | 11.7167 | 159_405 | <25mph | <15mph | HFTD - Distribution | 2017-07-28 14:02:00 | 1031 | 11.7167 | FALSE | <25mph | OMTC1 | 1.45 | 2017-07-28T06:26:00Z | 2.01 | 1 | < 25mph | OMTC1 | 1.45 | 2017-07-28T06:26:00Z | 2.01 | 1 | < 25mph | OMTC1 | 1.45 | 2017-07-28T06:26:00Z | 2.01 | 2 | < 25mph | OMTC1 | 1.45 | 2017-07-28T06:26:00Z | 2.01 | 2 | < 25mph
PG&E | 2017-07-28 19:21 | 19:20 | 35.7276 | -120.9903 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Luis Obispo CDF | 101945496 | None | 21000 | Conductor | Overhead | Yes | 42944.8062 | 19:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1295 | 2017 | 7 | 28 | 19 | 20 | 17-0066392 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 8300 | 11.4004 | 200_114 | <25mph | <15mph | HFTD - Distribution | 2017-07-28 19:20:00 | 1033 | 13.3732 | FALSE | <25mph | E9175 | 1.53 | 2017-07-29T02:10:00Z | 7 | 12 | < 25mph | TABC1 | 6.16 | 2017-07-29T02:07:00Z | 10 | 13 | < 25mph | E9175 | 1.53 | 2017-07-29T02:10:00Z | 7 | 20 | < 25mph | TABC1 | 6.16 | 2017-07-29T02:07:00Z | 10 | 22 | < 25mph
PG&E | 2017-07-30 09:47 | 09:46 | 38.9132 | -122.6179 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike wink | 102151066 | None | 0 – 750 | Conductor | Overhead | Yes | 42946.4075 | 09:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1302 | 2017 | 7 | 30 | 9 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.2785 | 130_290 | <25mph | <15mph | HFTD - Distribution | 2017-07-30 09:46:00 | 1040 | 13.7198 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 4.76 | 2017-07-30T15:57:00Z | 8.01 | 8 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 4.76 | 2017-07-30T16:57:00Z | 10 | 17 | < 25mph
PG&E | 2017-07-31 14:42 | 14:41 | 38.7967 | -121.1329 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103782414 | Unknown | 12000 | Conductor | Overhead | Yes | 42947.6123 | 14:41 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1305 | 2017 | 7 | 31 | 14 | 41 | 17-0066797 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 210 | 10.6525 | 194_283 | <25mph | <15mph | HFTD - Distribution | 2017-07-31 14:41:00 | 1043 | 12.727 | FALSE | <25mph | D2336 | 3.3 | 2017-07-31T20:45:00Z | 4 | 1 | < 25mph | PLTC1 | 7.08 | 2017-07-31T20:56:00Z | 11.01 | 15 | < 25mph | D2336 | 3.3 | 2017-07-31T21:57:00Z | 7 | 6 | < 25mph | D7393 | 6.59 | 2017-07-31T22:23:00Z | 11.01 | 34 | < 25mph
PG&E | 2017-08-02 | 9:42 | 39.2274 | -123.1081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 5/0 | None | 60000 | Conductor | Overhead | Yes | 42949 | 0.40417 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1307 | 2017 | 8 | 2 | 9 | 42 | INT-09925 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 4.0697 | 109_308 | <25mph | <15mph | HFTD - Transmission | 2017-08-02 09:42:00 | 1047 | 15.4312 | FALSE | <25mph |  |  |  | 0 | 0 | No data | COWC1 | 7.26 | 2017-08-02T06:01:00Z | 14 | 11 | < 25mph |  |  |  | 0 | 0 | No data | COWC1 | 7.26 | 2017-08-02T06:01:00Z | 14 | 23 | < 25mph
PG&E | 2017-08-02 06:01 | 5:54 | 40.7986 | -123.3961 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 100974913 | Unknown | 12000 | Conductor | Overhead | Yes | 42949.251 | 0.24583 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1308 | 2017 | 8 | 2 | 5 | 54 | 17-0067270 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 5832 | 11.2488 | 99_395 | <25mph | <15mph | HFTD - Distribution | 2017-08-02 05:54:00 | 1045 | 15.9988 | FALSE | <25mph |  |  |  | 0 | 0 | No data | UDWC1 | 7.47 | 2017-08-02T12:24:00Z | 1.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | UDWC1 | 7.47 | 2017-08-02T13:24:00Z | 1.01 | 2 | < 25mph
PG&E | 2017-08-03 11:01 | 10:53 | 39.0732 | -121.0868 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100072742 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42950.4588 | 0.45347 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1312 | 2017 | 8 | 3 | 10 | 53 | 17-0067679 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 127440 | 9.5869 | 196_298 | <25mph | <15mph | HFTD - Distribution | 2017-08-03 10:53:00 | 1050 | 11.8038 | FALSE | <25mph | C5488 | 3.14 | 2017-08-03T17:57:00Z | 5.99 | 5 | < 25mph | E1789 | 5.51 | 2017-08-03T18:00:00Z | 7 | 48 | < 25mph | C5488 | 3.14 | 2017-08-03T18:38:00Z | 7 | 8 | < 25mph | E1789 | 5.51 | 2017-08-03T19:00:00Z | 7 | 91 | < 25mph
PG&E | 2017-08-05 08:33 | 08:33 | 38.4583 | -120.8695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JEFF MICHEL- 530 409 2223 | 101236223 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42952.3565 | 08:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1317 | 2017 | 8 | 5 | 8 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 6.5905 | 205_264 | <25mph | <15mph | HFTD - Distribution | 2017-08-05 08:33:00 | 1055 | 14.6063 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 6.33 | 2017-08-05T15:05:00Z | 7 | 10 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 6.33 | 2017-08-05T15:05:00Z | 7 | 17 | < 25mph
PG&E | 2017-08-05 18:13 | 18:08 | 39.0968 | -123.2147 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102196629 | Unknown | 12000 | Conductor | Overhead | Yes | 42952.7592 | 0.75556 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1318 | 2017 | 8 | 5 | 18 | 8 | 17-0068200 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 134239 | 10.1139 | 105_301 | <25mph | <15mph | HFTD - Distribution | 2017-08-05 18:08:00 | 1056 | 16.2126 | FALSE | <25mph | KUKI | 2.28 | 2017-08-06T00:56:00Z | 17.27 | 12 | < 25mph | COWC1 | 7.84 | 2017-08-06T01:01:00Z | 23 | 26 | < 25mph | KUKI | 2.28 | 2017-08-06T01:25:00Z | 19.57 | 13 | < 25mph | COWC1 | 7.84 | 2017-08-06T02:01:00Z | 32.01 | 40 | 25-40mph
PG&E | 2017-08-06 11:38 | 11:38 | 36.5857 | -121.7121 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101747125 | Unknown | 12000 | Conductor | Overhead | Yes | 42953.4849 | 11:38 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1321 | 2017 | 8 | 6 | 11 | 38 | 17-0068279 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 87172 | 7.0101 | 168_161 | <25mph | <15mph | HFTD - Distribution | 2017-08-06 11:38:00 | 1059 | 12.123 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E8875 | 7.87 | 2017-08-06T18:20:00Z | 12.01 | 16 | < 25mph |  |  |  | 0 | 0 | No data | E6666 | 7.23 | 2017-08-06T19:30:00Z | 15.99 | 32 | < 25mph
PG&E | 2017-08-08 04:23 | 4:10 | 38.4949 | -122.6685 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 102025742 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42955.1829 | 0.17361 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1325 | 2017 | 8 | 8 | 4 | 10 | 17-0068642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 2750 | 5.2658 | 127_267 | <25mph | <15mph | HFTD - Distribution | 2017-08-08 04:10:00 | 1062 | 14.7124 | FALSE | <25mph | RSAC1 | 2.6 | 2017-08-08T10:29:00Z | 5.99 | 16 | < 25mph | D9840 | 5.11 | 2017-08-08T10:31:00Z | 5.99 | 63 | < 25mph | C3628 | 3.62 | 2017-08-08T11:46:00Z | 5.99 | 31 | < 25mph | D9840 | 5.11 | 2017-08-08T10:31:00Z | 5.99 | 120 | < 25mph
PG&E | 2017-08-08 20:35 | 20:35 | 37.2637 | -119.7103 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TROY CHEEK1-209-966-3621 | 103793352 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42955.8578 | 20:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1327 | 2017 | 8 | 8 | 20 | 35 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.9357 | 256_199 | <25mph | <15mph | HFTD - Distribution | 2017-08-08 20:35:00 | 1065 | 11.9714 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D7171 | 6.79 | 2017-08-09T02:39:00Z | 5.99 | 32 | < 25mph |  |  |  | 0 | 0 | No data | D7171 | 6.79 | 2017-08-09T03:39:00Z | 7 | 69 | < 25mph
PG&E | 2017-08-09 11:29 | 11:29 | 38.6532 | -120.6273 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101402496 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42956.4786 | 11:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1328 | 2017 | 8 | 9 | 11 | 29 | 17-0069107 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 54216 | 9.4272 | 216_275 | <25mph | <15mph | HFTD - Distribution | 2017-08-09 11:29:00 | 1066 | 11.5652 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GZFC1 | 5.69 | 2017-08-09T18:17:00Z | 8.01 | 3 | < 25mph |  |  |  | 0 | 0 | No data | GZFC1 | 5.69 | 2017-08-09T19:17:00Z | 11.01 | 5 | < 25mph
PG&E | 2017-08-12 09:09 | 09:08 | 34.6689 | -120.0286 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103391912 | Unknown | 12000 | Conductor | Overhead | Yes | 42959.3812 | 09:08 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | wire cut | Other/Unknown | 1330 | 2017 | 8 | 12 | 9 | 8 | 17-0069829 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 26070 | 3.5662 | 244_55 | <25mph | <15mph | HFTD - Distribution | 2017-08-12 09:08:00 | 1068 | 23.4799 | FALSE | <25mph | SXWC1 | 1.34 | 2017-08-12T15:09:00Z | 4 | 7 | < 25mph | SXWC1 | 1.34 | 2017-08-12T15:09:00Z | 4 | 14 | < 25mph | UCSE | 1.88 | 2017-08-12T17:00:00Z | 7.2 | 14 | < 25mph | AP901 | 5.95 | 2017-08-12T17:00:00Z | 8.99 | 32 | < 25mph
PG&E | 2017-08-14 | 6:14 | 40.1164 | -123.8064 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100986364 | Unknown | 12000 | Conductor | Overhead | Yes | 42961 | 0.25972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1332 | 2017 | 8 | 14 | 6 | 14 | 17-0070003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 959989 | 9.3352 | 81_357 | <25mph | <15mph | HFTD - Distribution | 2017-08-14 06:14:00 | 1070 | 20.8696 | FALSE | <25mph | ERCC1 | 1.77 | 2017-08-14T06:28:00Z | 11.01 | 2 | < 25mph | ERCC1 | 1.77 | 2017-08-14T06:28:00Z | 11.01 | 2 | < 25mph | ERCC1 | 1.77 | 2017-08-14T06:28:00Z | 11.01 | 7 | < 25mph | ERCC1 | 1.77 | 2017-08-14T06:28:00Z | 11.01 | 7 | < 25mph
PG&E | 2017-08-14 | 23:52 | 37.1272 | -122.1689 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 015/127 | None | 60000 | Conductor | Overhead | Yes | 42961 | 0.99444 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1333 | 2017 | 8 | 14 | 23 | 52 | INT-09976 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 1790869 | 16.3701 | 148_191 | <25mph | <15mph | HFTD - Transmission | 2017-08-14 23:52:00 | 1072 | 18.2518 | FALSE | <25mph | BNDC1 | 0.33 | 2017-08-14T06:50:00Z | 18.01 | 21 | < 25mph | BNDC1 | 0.33 | 2017-08-14T06:50:00Z | 18.01 | 31 | < 25mph | BNDC1 | 0.33 | 2017-08-14T06:50:00Z | 18.01 | 48 | < 25mph | BNDC1 | 0.33 | 2017-08-14T06:50:00Z | 18.01 | 68 | < 25mph
PG&E | 2017-08-14 07:56 | 07:56 | 39.1794 | -120.9761 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100083743 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42961.3308 | 07:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1334 | 2017 | 8 | 14 | 7 | 56 | 17-0070063 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3012 | 6.4958 | 200_304 | <25mph | <15mph | HFTD - Distribution | 2017-08-14 07:56:00 | 1071 | 15.2686 | FALSE | <25mph | D8321 | 3.61 | 2017-08-14T14:50:00Z | 2.01 | 14 | < 25mph | E5439 | 6.04 | 2017-08-14T14:50:00Z | 8.01 | 69 | < 25mph | D8321 | 3.61 | 2017-08-14T15:40:00Z | 4 | 30 | < 25mph | AT999 | 5.18 | 2017-08-14T15:32:00Z | 11.01 | 144 | < 25mph
PG&E | 2017-08-15 19:29 | 19:28 | 39.5037 | -121.2783 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 100396172 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42962.8116 | 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1335 | 2017 | 8 | 15 | 19 | 28 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.8405 | 188_322 | <25mph | <15mph | HFTD - Distribution | 2017-08-15 19:28:00 | 1073 | 9.7276 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PKCC1 | 4.51 | 2017-08-16T02:10:00Z | 13 | 2 | < 25mph |  |  |  | 0 | 0 | No data | PKCC1 | 4.51 | 2017-08-16T02:10:00Z | 13 | 4 | < 25mph
PG&E | 2017-08-17 | 15:15 | 39.3703 | -121.0484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | PHIL MICHAEL 265-2894 INCIENT # CA NEV 21642 | 100083029 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42964 | 0.63542 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1338 | 2017 | 8 | 17 | 15 | 15 | 17-0071121 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 32850 | 10.6037 | 197_315 | <25mph | <15mph | HFTD - Distribution | 2017-08-17 15:15:00 | 1076 | 10.6037 | FALSE | <25mph | E3651 | 2.23 | 2017-08-17T07:00:00Z | 0 | 13 | < 25mph | RRRC1 | 5.9 | 2017-08-17T06:13:00Z | 5.99 | 14 | < 25mph | E3651 | 2.23 | 2017-08-17T08:00:00Z | 0 | 25 | < 25mph | RRRC1 | 5.9 | 2017-08-17T06:13:00Z | 5.99 | 27 | < 25mph
PG&E | 2017-08-19 | 21:16 | 40.5752 | -122.2985 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464623 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42966 | 0.88611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1341 | 2017 | 8 | 19 | 21 | 16 | 17-0071522 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 19044 | 8.8981 | 145_381 | <25mph | <15mph | HFTD - Distribution | 2017-08-19 21:16:00 | 1079 | 13.341 | FALSE | <25mph | C5599 | 2.67 | 2017-08-19T06:47:00Z | 0 | 4 | < 25mph | RRAC1 | 4.12 | 2017-08-19T06:24:00Z | 4.99 | 11 | < 25mph | C5599 | 2.67 | 2017-08-19T07:16:00Z | 3 | 8 | < 25mph | RRAC1 | 4.12 | 2017-08-19T07:24:00Z | 4.99 | 22 | < 25mph
PG&E | 2017-08-26 | 20:53 | 38.7066 | -121.0193 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101382231 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42973 | 0.87014 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1350 | 2017 | 8 | 26 | 20 | 53 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.4442 | 199_278 | <25mph | <15mph | HFTD - Distribution | 2017-08-26 20:53:00 | 1088 | 14.1326 | FALSE | <25mph | E4740 | 2.39 | 2017-08-26T07:00:00Z | 2.01 | 33 | < 25mph | FSLC1 | 6.06 | 2017-08-26T06:05:00Z | 5.37 | 58 | < 25mph | D7401 | 1.71 | 2017-08-26T07:54:00Z | 4.99 | 65 | < 25mph | FSLC1 | 6.06 | 2017-08-26T07:20:00Z | 5.59 | 115 | < 25mph
PG&E | 2017-08-27 | 20:04 | 38.9165 | -121.151 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-477-0641 x7, log 22629 | 100077184 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42974 | 0.83611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1352 | 2017 | 8 | 27 | 20 | 4 | 17-0073228 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 905 | 9.7822 | 193_290 | <25mph | <15mph | HFTD - Distribution | 2017-08-27 20:04:00 | 1090 | 16.757 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8862 | 4.91 | 2017-08-27T06:02:00Z | 8.99 | 8 | < 25mph |  |  |  | 0 | 0 | No data | D8862 | 4.91 | 2017-08-27T07:47:00Z | 8.99 | 14 | < 25mph
PG&E | 2017-08-28 | 9:14 | 38.7443 | -122.6491 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 103781085 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42975 | 0.38472 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1356 | 2017 | 8 | 28 | 9 | 14 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 4.693 | 128_281 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 09:14:00 | 1094 | 16.6198 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LKRC1 | 6.54 | 2017-08-28T06:05:00Z | 8.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | LKRC1 | 6.54 | 2017-08-28T06:05:00Z | 8.99 | 2 | < 25mph
PG&E | 2017-08-28 | 10:07 | 39.0472 | -120.7859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | FORESTHILL | 100019525 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 0.42153 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1357 | 2017 | 8 | 28 | 10 | 7 | 17-0073379 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 10077 | 5.9792 | 209_297 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 10:07:00 | 1095 | 13.4783 | FALSE | <25mph | AU268 | 3.78 | 2017-08-28T06:44:00Z | 2.01 | 5 | < 25mph | AU268 | 3.78 | 2017-08-28T06:44:00Z | 2.01 | 6 | < 25mph | AU268 | 3.78 | 2017-08-28T07:47:00Z | 2.01 | 8 | < 25mph | AU268 | 3.78 | 2017-08-28T07:47:00Z | 2.01 | 10 | < 25mph
PG&E | 2017-08-28 | 14:06 | 38.634 | -122.4194 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102253236 | Unknown | 21000 | Conductor | Overhead | Yes | 42975 | 0.5875 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1359 | 2017 | 8 | 28 | 14 | 6 | 17-0073526 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 1896 | 12.4455 | 138_274 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 14:06:00 | 1097 | 13.1602 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AT925 | 4.29 | 2017-08-28T06:57:00Z | 1.01 | 12 | < 25mph |  |  |  | 0 | 0 | No data | AT925 | 4.29 | 2017-08-28T07:58:00Z | 1.01 | 24 | < 25mph
PG&E | 2017-08-29 | 12:49 | 37.4507 | -119.6454 | Vegetation | Rural | > 5000 Acres | Fire Agency | USFS | 101017368 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-29 | 0.53403 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1366 | 2017 | 8 | 29 | 12 | 49 | 17-0073823 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | 3rd Party | 3rd Party - Unknown | 5894785 | 7.4398 | 259_209 | <25mph | <15mph | HFTD - Distribution | 2017-08-29 12:49:00 | 1104 | 13.5545 | FALSE | <25mph | D0826 | 0.24 | 2017-08-29T06:01:00Z | 3 | 4 | < 25mph | MIAC1 | 5.9 | 2017-08-29T06:59:00Z | 8.99 | 28 | < 25mph | D0826 | 0.24 | 2017-08-29T06:01:00Z | 3 | 8 | < 25mph | MIAC1 | 5.9 | 2017-08-29T06:59:00Z | 8.99 | 59 | < 25mph
PG&E | 2017-08-29 | 15:54 | 38.302 | -122.5431 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 911 | 102026119 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 42976 | 0.6625 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1367 | 2017 | 8 | 29 | 15 | 54 | 17-0073928 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 485 | 16.1777 | 133_256 | <25mph | <15mph | HFTD - Distribution | 2017-08-29 15:54:00 | 1105 | 18.0049 | FALSE | <25mph | F11WW | 3.32 | 2017-08-29T06:00:00Z | 2.1 | 2 | < 25mph | KENWW | 7.3 | 2017-08-29T06:00:00Z | 6.4 | 21 | < 25mph | F11WW | 3.32 | 2017-08-29T06:00:00Z | 2.1 | 3 | < 25mph | KENWW | 7.3 | 2017-08-29T06:00:00Z | 6.4 | 38 | < 25mph
PG&E | 2017-08-30 | 18:21 | 40.6243 | -122.3039 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CASHU008896 | 103151338 | YES | 12000 | Conductor | Overhead | Yes | 42977 | 0.76458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1369 | 2017 | 8 | 30 | 18 | 21 | 17-0074287 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 76344 | 5.8461 | 145_384 | <25mph | <15mph | HFTD - Distribution | 2017-08-30 18:21:00 | 1107 | 16.2636 | FALSE | <25mph | C5599 | 2.06 | 2017-08-30T06:47:00Z | 1.01 | 8 | < 25mph | RRAC1 | 7.52 | 2017-08-30T06:24:00Z | 7 | 9 | < 25mph | C5599 | 2.06 | 2017-08-30T07:46:00Z | 3 | 17 | < 25mph | RRAC1 | 7.52 | 2017-08-30T06:24:00Z | 7 | 19 | < 25mph
PG&E | 2017-08-30 | 22:37 | 38.9993 | -120.9887 | Vegetation | Rural | < 3 Meters | Fire Agency | Andy 530-889-0111 | 100026238 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42977 | 0.94236 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1370 | 2017 | 8 | 30 | 22 | 37 | 17-0074333 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 3750 | 7.3126 | 200_294 | <25mph | <15mph | HFTD - Distribution | 2017-08-30 22:37:00 | 1108 | 12.9461 | FALSE | <25mph | D9434 | 3.56 | 2017-08-30T06:53:00Z | 2.01 | 15 | < 25mph | AT999 | 7.28 | 2017-08-30T06:33:00Z | 3 | 37 | < 25mph | D9434 | 3.56 | 2017-08-30T07:53:00Z | 3 | 34 | < 25mph | C5488 | 5.56 | 2017-08-30T07:44:00Z | 4 | 82 | < 25mph
PG&E | 2017-08-31 | 6:42 | 35.616 | -120.8577 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Derrick | 101860075 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 0.27917 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1372 | 2017 | 8 | 31 | 6 | 42 | 17-0074386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1620 | 12.088 | 206_107 | <25mph | <15mph | HFTD - Distribution | 2017-08-31 06:42:00 | 1110 | 13.8216 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TABC1 | 4.66 | 2017-08-31T06:07:00Z | 2.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | TABC1 | 4.66 | 2017-08-31T06:07:00Z | 2.01 | 2 | < 25mph
PG&E | 2017-08-31 | 11:33 | 37.1379 | -121.9966 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100519201 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 0.48125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1373 | 2017 | 8 | 31 | 11 | 33 | 17-0074457 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 99153 | 14.3205 | 156_192 | <25mph | <15mph | HFTD - Distribution | 2017-08-31 11:33:00 | 1111 | 14.3569 | FALSE | <25mph | D8979 | 2.5 | 2017-08-31T06:03:00Z | 4.99 | 19 | < 25mph | D3546 | 7.44 | 2017-08-31T06:10:00Z | 7 | 105 | < 25mph | D8979 | 2.5 | 2017-08-31T06:03:00Z | 4.99 | 37 | < 25mph | D3546 | 7.44 | 2017-08-31T06:10:00Z | 7 | 206 | < 25mph
PG&E | 2017-09-01 | 8:00 | 37.3757 | -119.8886 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101067028 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42979 | 0.33333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1378 | 2017 | 9 | 1 | 8 | 0 | 17-0074724 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 680 | 5.98 | 248_205 | <25mph | <15mph | HFTD - Distribution | 2017-09-01 08:00:00 | 1116 | 14.9658 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E9110 | 4.96 | 2017-09-01T06:35:00Z | 8.01 | 6 | < 25mph |  |  |  | 0 | 0 | No data | E9110 | 4.96 | 2017-09-01T07:50:00Z | 8.99 | 12 | < 25mph
PG&E | 2017-09-01 | 17:48 | 36.6518 | -121.7249 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MCFD | 103155761 | Unknown | 12000 | Conductor | Overhead | Yes | 42979 | 0.74167 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1382 | 2017 | 9 | 1 | 17 | 48 | 17-0074898 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 8152 | 14.5474 | 167_165 | <25mph | <15mph | HFTD - Distribution | 2017-09-01 17:48:00 | 1120 | 19.9505 | FALSE | <25mph | E6666 | 3.59 | 2017-09-01T06:25:00Z | 5.99 | 4 | < 25mph | E6666 | 3.59 | 2017-09-01T06:25:00Z | 5.99 | 12 | < 25mph | E6666 | 3.59 | 2017-09-01T07:55:00Z | 8.01 | 9 | < 25mph | E6666 | 3.59 | 2017-09-01T07:55:00Z | 8.01 | 27 | < 25mph
PG&E | 2017-09-02 | 12:01 | 37.6645 | -121.9223 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 100956020 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42980 | 0.50069 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1384 | 2017 | 9 | 2 | 12 | 1 | 17-0075132 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 7152 | 6.3171 | 159_221 | <25mph | <15mph | HFTD - Distribution | 2017-09-02 12:01:00 | 1122 | 21.2394 | FALSE | <25mph | AU719 | 3.94 | 2017-09-02T06:56:00Z | 2.01 | 13 | < 25mph | D3560 | 6.84 | 2017-09-02T07:00:00Z | 8.01 | 31 | < 25mph | AU719 | 3.94 | 2017-09-02T07:56:00Z | 3 | 26 | < 25mph | D3560 | 6.84 | 2017-09-02T07:45:00Z | 8.99 | 65 | < 25mph
PG&E | 2017-09-03 | 12:52 | 37.2162 | -119.4807 | Vegetation | Rural | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103345573 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-09-03 | 0.53611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1388 | 2017 | 9 | 3 | 12 | 52 | 17-0075546 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 2362 | 10.0918 | 266_196 | <25mph | <15mph | HFTD - Distribution | 2017-09-03 12:52:00 | 1126 | 25.526 | FALSE | 25-40mph | NFRC1 | 1.81 | 2017-09-03T06:55:00Z | 11.01 | 5 | < 25mph | NFRC1 | 1.81 | 2017-09-03T06:55:00Z | 11.01 | 5 | < 25mph | C6459 | 2.52 | 2017-09-03T08:00:00Z | 12.01 | 9 | < 25mph | C6459 | 2.52 | 2017-09-03T08:00:00Z | 12.01 | 9 | < 25mph
PG&E | 2017-09-03 | 17:52 | 37.4956 | -119.8367 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101086621 | Unknown | 21000 | Transformer | Overhead | Yes | 42981 | 0.74444 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 1389 | 2017 | 9 | 3 | 17 | 52 | 17-0075617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 4512 | 13.9592 | 250_212 | <25mph | <15mph | HFTD - Distribution | 2017-09-03 17:52:00 | 1127 | 22.0754 | FALSE | <25mph | JSDC1 | 3.33 | 2017-09-03T06:47:00Z | 5.99 | 1 | < 25mph | E9110 | 4.74 | 2017-09-03T06:40:00Z | 8.99 | 6 | < 25mph | JSDC1 | 3.33 | 2017-09-03T07:47:00Z | 5.99 | 2 | < 25mph | E9110 | 4.74 | 2017-09-03T07:55:00Z | 10 | 17 | < 25mph
PG&E | 2017-09-04 | 3:29 | 39.8317 | -121.8444 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102300100 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1392 | 2017 | 9 | 4 | 3 | 29 | 17-0075723 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 214974 | 9.8341 | 164_340 | <25mph | <15mph | HFTD - Distribution | 2017-09-04 03:29:00 | 1130 | 13.8789 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8204 | 5.42 | 2017-09-04T06:37:00Z | 8.99 | 14 | < 25mph |  |  |  | 0 | 0 | No data | D8204 | 5.42 | 2017-09-04T07:13:00Z | 8.99 | 34 | < 25mph
PG&E | 2017-09-05 | 6:58 | 39.6727 | -123.5128 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 102194697 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 42983 | 0.29028 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1395 | 2017 | 9 | 5 | 6 | 58 | 17-0075976 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10528 | 9.1824 | 93_333 | <25mph | <15mph | HFTD - Distribution | 2017-09-05 06:58:00 | 1133 | 14.0364 | FALSE | <25mph | LAYC1 | 2.53 | 2017-09-05T06:29:00Z | 7 | 1 | < 25mph | LAYC1 | 2.53 | 2017-09-05T06:29:00Z | 7 | 8 | < 25mph | LAYC1 | 2.53 | 2017-09-05T07:29:00Z | 7 | 2 | < 25mph | LAYC1 | 2.53 | 2017-09-05T07:29:00Z | 7 | 15 | < 25mph
PG&E | 2017-09-06 | 19:26 | 40.8392 | -122.3635 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103643183 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 0.80972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1399 | 2017 | 9 | 6 | 19 | 26 | 17-0076501 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 23830 | 6.5088 | 142_396 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 19:26:00 | 1137 | 12.365 | FALSE | <25mph | CTANT | 1.93 | 2017-09-06T06:00:00Z | 8.08 | 5 | < 25mph | SLFC1 | 6.48 | 2017-09-06T06:19:00Z | 12.01 | 11 | < 25mph | CTANT | 1.93 | 2017-09-06T06:00:00Z | 8.08 | 9 | < 25mph | SLFC1 | 6.48 | 2017-09-06T07:19:00Z | 18.01 | 20 | < 25mph
PG&E | 2017-09-06 | 20:08 | 37.2925 | -122.294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100256917 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 0.83889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1400 | 2017 | 9 | 6 | 20 | 8 | 17-0076502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4914 | 6.7999 | 143_200 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 20:08:00 | 1138 | 13.6021 | FALSE | <25mph | LAHC1 | 2.3 | 2017-09-06T06:07:00Z | 4 | 1 | < 25mph | LAHC1 | 2.3 | 2017-09-06T06:07:00Z | 4 | 7 | < 25mph | LAHC1 | 2.3 | 2017-09-06T07:07:00Z | 4 | 2 | < 25mph | LAHC1 | 2.3 | 2017-09-06T07:07:00Z | 4 | 13 | < 25mph
PG&E | 2017-09-08 | 4:47 | 38.7478 | -120.859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101391575 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42986 | 0.19931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1401 | 2017 | 9 | 8 | 4 | 47 | 17-0076889 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 39736 | 2.1381 | 205_280 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 04:47:00 | 1139 | 10.5203 | FALSE | <25mph | E5691 | 3.77 | 2017-09-08T06:56:00Z | 0 | 37 | < 25mph | E3165 | 7.16 | 2017-09-08T06:32:00Z | 3 | 78 | < 25mph | E5691 | 3.77 | 2017-09-08T07:56:00Z | 0 | 73 | < 25mph | E3165 | 7.16 | 2017-09-08T06:32:00Z | 3 | 154 | < 25mph
PG&E | 2017-09-08 | 17:21 | 38.6039 | -120.9275 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101379094 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42986 | 0.72292 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1402 | 2017 | 9 | 8 | 17 | 21 | 17-0077122 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 8504 | 10.5347 | 203_272 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 17:21:00 | 1140 | 11.5767 | FALSE | <25mph | BENC1 | 0.96 | 2017-09-08T06:59:00Z | 7 | 14 | < 25mph | BENC1 | 0.96 | 2017-09-08T06:59:00Z | 7 | 59 | < 25mph | BENC1 | 0.96 | 2017-09-08T06:59:00Z | 7 | 27 | < 25mph | BENC1 | 0.96 | 2017-09-08T06:59:00Z | 7 | 116 | < 25mph
PG&E | 2017-09-08 | 21:14 | 37.9604 | -120.3764 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | John Lite 209-984-5623 | 101042521 | Unknown | 17000 | Conductor | Overhead | Yes | 42986 | 0.88472 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1403 | 2017 | 9 | 8 | 21 | 14 | 17-0077137 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49858 | 11.2644 | 227_237 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 21:14:00 | 1141 | 11.9927 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F0305 | 6.4 | 2017-09-08T07:00:00Z | 0 | 17 | < 25mph |  |  |  | 0 | 0 | No data | F0305 | 6.4 | 2017-09-08T08:00:00Z | 0 | 33 | < 25mph
PG&E | 2017-09-11 | 7:18 | 37.0008 | -121.6667 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100621936 | VERIZON CALIFORNIA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1407 | 2017 | 9 | 11 | 7 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.0313 | 170_184 | <25mph | <15mph | HFTD - Distribution | 2017-09-11 07:18:00 | 1145 | 32.6801 | FALSE | 25-40mph | AU710 | 3.82 | 2017-09-11T06:15:00Z | 3 | 5 | < 25mph | C4787 | 7.93 | 2017-09-11T06:33:00Z | 11.01 | 40 | < 25mph | AU710 | 3.82 | 2017-09-11T08:00:00Z | 3 | 9 | < 25mph | C4787 | 7.93 | 2017-09-11T06:33:00Z | 11.01 | 79 | < 25mph
PG&E | 2017-09-11 | 8:50 | 36.9515 | -121.842 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101790954 | PACIFIC BELL | 21000 | Fuse | Overhead | Yes | 42989 | 0.36806 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | no-match | 1408 | 2017 | 9 | 11 | 8 | 50 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | N.A. | 9.6414 | 162_181 | <25mph | <15mph | HFTD - Distribution | 2017-09-11 08:50:00 | 1146 | 17.9559 | FALSE | <25mph | CTOC1 | 3.41 | 2017-09-11T06:27:00Z | 4.99 | 32 | < 25mph | CTOC1 | 3.41 | 2017-09-11T06:27:00Z | 4.99 | 63 | < 25mph | E7291 | 2.85 | 2017-09-11T07:39:00Z | 7 | 65 | < 25mph | E7291 | 2.85 | 2017-09-11T07:39:00Z | 7 | 124 | < 25mph
PG&E | 2017-09-12 | 9:24 | 39.741 | -121.6079 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 911 | 100330302 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42990 | 0.39167 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1410 | 2017 | 9 | 12 | 9 | 24 | 17-0078149 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 402890 | 5.7135 | 174_335 | <25mph | <15mph | HFTD - Distribution | 2017-09-12 09:24:00 | 1148 | 23.672 | FALSE | <25mph | PDEC1 | 1.25 | 2017-09-12T06:00:00Z | 8.99 | 2 | < 25mph | JBGC1 | 6.33 | 2017-09-12T06:13:00Z | 23 | 9 | < 25mph | PDEC1 | 1.25 | 2017-09-12T06:00:00Z | 8.99 | 3 | < 25mph | JBGC1 | 6.33 | 2017-09-12T06:13:00Z | 23 | 17 | < 25mph
PG&E | 2017-09-15 | 14:55 | 39.7461 | -121.4885 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100335239 | Unknown | 12000 | Conductor | Overhead | Yes | 42993 | 0.62153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1415 | 2017 | 9 | 15 | 14 | 55 | 17-0079388 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 8834 | 10.5756 | 179_335 | <25mph | <15mph | HFTD - Distribution | 2017-09-15 14:55:00 | 1153 | 16.2937 | FALSE | <25mph | JBGC1 | 0.7 | 2017-09-15T06:13:00Z | 3 | 1 | < 25mph | JBGC1 | 0.7 | 2017-09-15T06:13:00Z | 3 | 3 | < 25mph | JBGC1 | 0.7 | 2017-09-15T07:13:00Z | 7 | 2 | < 25mph | JBGC1 | 0.7 | 2017-09-15T07:13:00Z | 7 | 5 | < 25mph
PG&E | 2017-09-17 | 17:38 | 38.9946 | -121.0261 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100029537 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42995 | 0.73472 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Branch (OverHanging) | 1417 | 2017 | 9 | 17 | 17 | 38 | 17-0079585 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 28509 | 11.5169 | 198_294 | <25mph | <15mph | HFTD - Distribution | 2017-09-17 17:38:00 | 1155 | 15.8476 | FALSE | <25mph | C0713 | 1.74 | 2017-09-17T06:54:00Z | 0 | 9 | < 25mph | AT999 | 7.97 | 2017-09-17T06:52:00Z | 3 | 18 | < 25mph | C0713 | 1.74 | 2017-09-17T07:54:00Z | 0 | 19 | < 25mph | AT999 | 7.97 | 2017-09-17T07:07:00Z | 3 | 37 | < 25mph
PG&E | 2017-09-18 | 13:01 | 39.3889 | -121.4054 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 103795057 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42996 | 0.54236 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1418 | 2017 | 9 | 18 | 13 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 17.7047 | 182_316 | <25mph | <15mph | HFTD - Distribution | 2017-09-18 13:01:00 | 1156 | 19.5678 | FALSE | <25mph | BNGC1 | 1.17 | 2017-09-18T06:51:00Z | 4.99 | 1 | < 25mph | TT309 | 5.6 | 2017-09-18T06:45:00Z | 7 | 2 | < 25mph | BNGC1 | 1.17 | 2017-09-18T07:51:00Z | 7 | 2 | < 25mph | TT309 | 5.6 | 2017-09-18T06:45:00Z | 7 | 4 | < 25mph
PG&E | 2017-09-18 | 23:50 | 37.9088 | -120.4865 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | incident comander geoff marshall 209-419-4407 | 101040882 | Unknown | 17000 | Conductor | Overhead | Yes | 42996 | 0.99306 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1422 | 2017 | 9 | 18 | 23 | 50 | 17-0079858 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 382303 | 9.0814 | 222_234 | <25mph | <15mph | HFTD - Distribution | 2017-09-18 23:50:00 | 1160 | 16.9339 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.23 | 2017-09-18T06:03:00Z | 4.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.23 | 2017-09-18T07:03:00Z | 4.99 | 2 | < 25mph
PG&E | 2017-09-20 | 2:06 | 37.2597 | -122.3222 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100322388 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42998 | 0.0875 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1424 | 2017 | 9 | 20 | 2 | 6 | 17-0080179 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 36593 | 8.989 | 141_198 | <25mph | <15mph | HFTD - Distribution | 2017-09-20 02:06:00 | 1162 | 20.1127 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.84 | 2017-09-20T06:07:00Z | 4 | 1 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.84 | 2017-09-20T07:07:00Z | 4 | 2 | < 25mph
PG&E | 2017-09-23 | 14:17 | 40.6509 | -122.2974 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DARREN STEWART 448-2421 | 101467221 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43001 | 0.59514 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1429 | 2017 | 9 | 23 | 14 | 17 | 17-0081216 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 98820 | 17.9072 | 145_386 | <25mph | <15mph | HFTD - Distribution | 2017-09-23 14:17:00 | 1167 | 24.6958 | FALSE | <25mph | C5599 | 3.73 | 2017-09-23T06:16:00Z | 4.99 | 4 | < 25mph | C5599 | 3.73 | 2017-09-23T06:16:00Z | 4.99 | 10 | < 25mph | C5599 | 3.73 | 2017-09-23T06:16:00Z | 4.99 | 8 | < 25mph | C5599 | 3.73 | 2017-09-23T06:16:00Z | 4.99 | 20 | < 25mph
PG&E | 2017-09-24 | 16:42 | 38.3869 | -122.9667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DOUG JONES | 101973946 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43002 | 0.69583 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1432 | 2017 | 9 | 24 | 16 | 42 | 17-0081329 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 22574 | 19.6154 | 114_261 | <25mph | <15mph | HFTD - Distribution | 2017-09-24 16:42:00 | 1170 | 19.6154 | FALSE | <25mph | D2849 | 0.23 | 2017-09-24T07:00:00Z | 1.01 | 13 | < 25mph | BGAC1 | 6.8 | 2017-09-24T06:05:00Z | 7 | 71 | < 25mph | D2849 | 0.23 | 2017-09-24T07:55:00Z | 1.01 | 25 | < 25mph | BGAC1 | 6.8 | 2017-09-24T06:05:00Z | 7 | 147 | < 25mph
PG&E | 2017-09-27 | 12:12 | 39.4845 | -121.3545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | bill lopez cell 530 521-8052 | 100429924 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 43005 | 0.50833 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1436 | 2017 | 9 | 27 | 12 | 12 | 17-0082180 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 6370 | 7.6613 | 184_321 | <25mph | <15mph | HFTD - Distribution | 2017-09-27 12:12:00 | 1174 | 27.61 | FALSE | 25-40mph | TT309 | 3.08 | 2017-09-27T06:45:00Z | 4 | 1 | < 25mph | BNGC1 | 7.37 | 2017-09-27T06:51:00Z | 7 | 2 | < 25mph | TT309 | 3.08 | 2017-09-27T07:45:00Z | 4 | 2 | < 25mph | BNGC1 | 7.37 | 2017-09-27T06:51:00Z | 7 | 4 | < 25mph
PG&E | 2017-09-27 | 19:06 | 40.7592 | -123.995 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103660812 | Unknown | 12000 | Conductor | Overhead | Yes | 43005 | 0.79583 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1437 | 2017 | 9 | 27 | 19 | 6 | 17-0082303 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 35394 | 10.6184 | 74_393 | <25mph | <15mph | HFTD - Distribution | 2017-09-27 19:06:00 | 1175 | 13.0154 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KNNC1 | 4.42 | 2017-09-27T06:55:00Z | 10 | 11 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 4.42 | 2017-09-27T07:55:00Z | 10 | 21 | < 25mph
PG&E | 2017-10-02 | 14:56 | 38.9102 | -120.9185 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100110800 | None | 21000 | Other | Overhead | Yes | 43010 | 0.62222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1447 | 2017 | 10 | 2 | 14 | 56 | 17-0083516 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 160 | 17.2967 | 203_289 | <25mph | <15mph | HFTD - Distribution | 2017-10-02 14:56:00 | 1185 | 22.7009 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6476 | 6.41 | 2017-10-02T06:55:00Z | 10 | 14 | < 25mph |  |  |  | 0 | 0 | No data | E6476 | 6.41 | 2017-10-02T06:55:00Z | 10 | 31 | < 25mph
PG&E | 2017-10-02 | 16:05 | 38.7182 | -120.9756 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101375963 | Unknown | 21000 | Conductor | Overhead | Yes | 43010 | 0.67014 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1448 | 2017 | 10 | 2 | 16 | 5 | 17-0083539 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4797 | 14.669 | 201_279 | <25mph | <15mph | HFTD - Distribution | 2017-10-02 16:05:00 | 1186 | 17.4155 | FALSE | <25mph | D7401 | 3.14 | 2017-10-02T06:03:00Z | 4 | 70 | < 25mph | E4740 | 4.79 | 2017-10-02T06:50:00Z | 4 | 92 | < 25mph | D7401 | 3.14 | 2017-10-02T06:03:00Z | 4 | 147 | < 25mph | E4740 | 4.79 | 2017-10-02T07:50:00Z | 4.99 | 190 | < 25mph
PG&E | 2017-10-04 | 23:42 | 38.6554 | -120.9934 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101375442 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 43012 | 0.9875 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1452 | 2017 | 10 | 4 | 23 | 42 | 17-0084323 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7553 | 12.9958 | 200_275 | <25mph | <15mph | HFTD - Distribution | 2017-10-04 23:42:00 | 1190 | 14.755 | FALSE | <25mph | D7401 | 2.11 | 2017-10-04T06:24:00Z | 8.01 | 20 | < 25mph | D7401 | 2.11 | 2017-10-04T06:24:00Z | 8.01 | 106 | < 25mph | D7401 | 2.11 | 2017-10-04T06:24:00Z | 8.01 | 39 | < 25mph | D7401 | 2.11 | 2017-10-04T06:24:00Z | 8.01 | 207 | < 25mph
PG&E | 2017-10-08 | 19:44 | 39.7446 | -121.597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100330456 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 0.82222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1464 | 2017 | 10 | 8 | 19 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 33.2724 | 174_335 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-08 19:44:00 | 1202 | 34.7906 | FALSE | 25-40mph | PDEC1 | 1.6 | 2017-10-08T07:00:00Z | 1.01 | 2 | < 25mph | JBGC1 | 5.77 | 2017-10-08T06:13:00Z | 11.01 | 9 | < 25mph | PDEC1 | 1.6 | 2017-10-08T08:00:00Z | 1.01 | 3 | < 25mph | JBGC1 | 5.77 | 2017-10-08T07:13:00Z | 13 | 17 | < 25mph
PG&E | 2017-10-08 | 22:19 | 39.7371 | -121.6464 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 103319605 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43016 | 0.92986 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1468 | 2017 | 10 | 8 | 22 | 19 | 17-0085504 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 42839 | 9.4272 | 172_335 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 22:19:00 | 1208 | 31.7535 | FALSE | 25-40mph | PDEC1 | 1.62 | 2017-10-08T07:00:00Z | 1.01 | 2 | < 25mph | C4565 | 7.55 | 2017-10-08T06:43:00Z | 3 | 8 | < 25mph | PDEC1 | 1.62 | 2017-10-08T08:00:00Z | 1.01 | 3 | < 25mph | C4565 | 7.55 | 2017-10-08T07:53:00Z | 3 | 15 | < 25mph
PG&E | 2017-10-08 | 22:58 | 39.3642 | -121.1131 | Vegetation | Rural | < 3 Meters | Fire Agency | INCIDENT NUMBER 26268 | 100068104 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43016 | 0.95694 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Fell into (No defect) | 1471 | 2017 | 10 | 8 | 22 | 58 | 17-0085355 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 198802 | 15.5554 | 195_314 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 22:58:00 | 1211 | 22.0344 | FALSE | <25mph | E3651 | 3.94 | 2017-10-08T06:45:00Z | 3 | 13 | < 25mph | RRRC1 | 4.2 | 2017-10-08T06:13:00Z | 8.01 | 20 | < 25mph | E3651 | 3.94 | 2017-10-08T06:45:00Z | 3 | 25 | < 25mph | RRRC1 | 4.2 | 2017-10-08T07:13:00Z | 8.99 | 39 | < 25mph
PG&E | 2017-10-09 | 1:02 | 38.7037 | -120.6725 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101408485 | Unknown | 21000 | Other | Overhead | Yes | 43017 | 0.043056 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1473 | 2017 | 10 | 9 | 1 | 2 | 17-0085324 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 419843 | 26.702 | 214_278 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-10-09 01:02:00 | 1216 | 29.779 | FALSE | 25-40mph | AV185 | 3.98 | 2017-10-09T06:00:00Z | 15.99 | 3 | < 25mph | KPVF | 4.58 | 2017-10-09T06:55:00Z | 33.38 | 28 | 25-40mph | AV185 | 3.98 | 2017-10-09T07:30:00Z | 18.99 | 5 | < 25mph | KPVF | 4.58 | 2017-10-09T06:55:00Z | 33.38 | 55 | 25-40mph
PG&E | 2017-10-09 | 1:45 | 38.8576 | -122.7221 | Vegetation | Rural | < 0.25 Acres | Fire Agency | wink | 103570679 | Unknown | 12000 | Conductor | Overhead | Yes | 43017 | 0.072917 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Other/Unknown | 1477 | 2017 | 10 | 9 | 1 | 45 | 17-0085344 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 219653 | 32.3097 | 125_287 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-09 01:45:00 | 1220 | 32.3097 | FALSE | 25-40mph | LKRC1 | 3.67 | 2017-10-09T06:05:00Z | 34.99 | 2 | 25-40mph | LKRC1 | 3.67 | 2017-10-09T06:05:00Z | 34.99 | 2 | 25-40mph | LKRC1 | 3.67 | 2017-10-09T07:05:00Z | 48 | 4 | 40-55mph | LKRC1 | 3.67 | 2017-10-09T07:05:00Z | 48 | 4 | 40-55mph
PG&E | 2017-10-10 | 13:36 | 38.931 | -123.3023 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 102214553 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43018 | 0.56667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1481 | 2017 | 10 | 10 | 13 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.7263 | 101_291 | <25mph | <15mph | HFTD - Distribution | 2017-10-10 13:36:00 | 1224 | 17.0479 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E4371 | 5.14 | 2017-10-10T06:02:00Z | 10 | 8 | < 25mph |  |  |  | 0 | 0 | No data | BNVC1 | 4.62 | 2017-10-10T07:50:00Z | 13 | 17 | < 25mph
PG&E | 2017-10-11 | 11:57 | 38.5015 | -123.0237 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101974930 | Unknown | 12000 | Conductor | Overhead | Yes | 43019 | 0.49792 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1484 | 2017 | 10 | 11 | 11 | 57 | 17-0086350 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 226925 | 16.5068 | 112_268 | <25mph | <15mph | HFTD - Distribution | 2017-10-11 11:57:00 | 1227 | 19.0479 | FALSE | <25mph | D9841 | 2.93 | 2017-10-11T06:47:00Z | 0 | 31 | < 25mph | R30WW | 7.7 | 2017-10-11T06:00:00Z | 2.51 | 39 | < 25mph | D9841 | 2.93 | 2017-10-11T07:47:00Z | 0 | 61 | < 25mph | R30WW | 7.7 | 2017-10-11T08:00:00Z | 3.2 | 75 | < 25mph
PG&E | 2017-10-16 | 12:10 | 36.5831 | -121.9368 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101781248 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43024 | 0.50694 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | Other/Unknown | 1493 | 2017 | 10 | 16 | 12 | 10 | 17-0087767 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 6313 | 5.0415 | 158_161 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:10:00 | 1236 | 13.6905 | FALSE | <25mph | E6019 | 2.26 | 2017-10-16T06:15:00Z | 12.01 | 22 | < 25mph | E6019 | 2.26 | 2017-10-16T06:15:00Z | 12.01 | 26 | < 25mph | E6019 | 2.26 | 2017-10-16T07:30:00Z | 12.01 | 42 | < 25mph | E6019 | 2.26 | 2017-10-16T07:30:00Z | 12.01 | 50 | < 25mph
PG&E | 2017-10-16 | 12:26 | 36.6641 | -121.0995 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Nick Shawkey E4462 209-402-1645 Cover Engine from Tuolumne Calaveras Unit | 101689865 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43024 | 0.51806 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1495 | 2017 | 10 | 16 | 12 | 26 | 17-0087754 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 519 | 1.3904 | 195_165 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:26:00 | 1238 | 14.8173 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1697 | 6.85 | 2017-10-16T06:58:00Z | 4 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E1697 | 6.85 | 2017-10-16T07:43:00Z | 5.99 | 8 | < 25mph
PG&E | 2017-10-20 | 6:18 | 39.2922 | -121.0157 | Vegetation | Rural | < 3 Meters | Fire Agency | PHILLIP NUNNINK INCIDENT # 27272 | 100087647 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43028 | 0.2625 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1499 | 2017 | 10 | 20 | 6 | 18 | 17-0088957 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 102410 | 6.1464 | 199_310 | <25mph | <15mph | HFTD - Distribution | 2017-10-20 06:18:00 | 1242 | 23.0997 | FALSE | <25mph | E9947 | 3.74 | 2017-10-20T06:59:00Z | 11.01 | 20 | < 25mph | RRRC1 | 5.48 | 2017-10-20T06:13:00Z | 22.01 | 73 | < 25mph | E3651 | 3.59 | 2017-10-20T08:00:00Z | 14.99 | 40 | < 25mph | KGOO | 4.76 | 2017-10-20T07:55:00Z | 35.68 | 145 | 25-40mph
PG&E | 2017-10-20 | 13:45 | 34.5532 | -120.5303 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 101921492 | Unknown | 12000 | Conductor | Overhead | Yes | 43028 | 0.57292 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1502 | 2017 | 10 | 20 | 13 | 45 | 17-0089249 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 173 | 31.847 | 221_49 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-20 13:45:00 | 1245 | 35.5655 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E2332 | 4.19 | 2017-10-20T06:04:00Z | 23 | 21 | < 25mph |  |  |  | 0 | 0 | No data | E2332 | 4.19 | 2017-10-20T06:04:00Z | 23 | 37 | < 25mph
PG&E | 2017-10-23 | 21:24 | 37.3713 | -122.348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100270421 | Unknown | 12000 | Conductor | Overhead | Yes | 43031 | 0.89167 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1507 | 2017 | 10 | 23 | 21 | 24 | 17-0089820 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1768 | 13.1103 | 140_205 | <25mph | <15mph | HFTD - Distribution | 2017-10-23 21:24:00 | 1249 | 22.0037 | FALSE | <25mph | E4551 | 1.61 | 2017-10-23T06:48:00Z | 3 | 6 | < 25mph | LAHC1 | 6.84 | 2017-10-23T06:07:00Z | 7 | 18 | < 25mph | E4551 | 1.61 | 2017-10-23T07:58:00Z | 4 | 12 | < 25mph | E4863 | 4.38 | 2017-10-23T07:49:00Z | 8.99 | 36 | < 25mph
PG&E | 2017-10-28 | 15:26 | 39.4516 | -123.3838 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102209084 | Unknown | 12000 | Conductor | Overhead | Yes | 43036 | 0.64306 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | no-match | 1510 | 2017 | 10 | 28 | 15 | 26 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 10.3107 | 98_320 | <25mph | <15mph | HFTD - Distribution | 2017-10-28 15:26:00 | 1252 | 11.7696 | FALSE | <25mph | E4027 | 3.28 | 2017-10-28T06:58:00Z | 0 | 12 | < 25mph | AT319 | 5.75 | 2017-10-28T06:58:00Z | 2.01 | 24 | < 25mph | E4027 | 3.28 | 2017-10-28T07:58:00Z | 0 | 24 | < 25mph | AT319 | 5.75 | 2017-10-28T07:48:00Z | 2.01 | 48 | < 25mph
PG&E | 2017-10-31 | 21:02 | 39.1119 | -122.9163 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Structure 020/003 | Unknown | 60000 | Conductor | Overhead | Yes | 43039 | 0.87639 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | no-match | 1513 | 2017 | 10 | 31 | 21 | 2 | INT-10325 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | 50730 | 1.8727 | 117_301 | <25mph | <15mph | HFTD - Transmission | 2017-10-31 21:02:00 | 1255 | 9.8895 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5780 | 6.35 | 2017-10-31T06:56:00Z | 3 | 12 | < 25mph |  |  |  | 0 | 0 | No data | E5780 | 6.35 | 2017-10-31T07:57:00Z | 4 | 24 | < 25mph
PG&E | 2017-11-11 12:17 | 11:57 | 35.1191 | -120.3936 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Jordan Dayley ph#929-3911,engine#3467 | 101931190 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43050.5115 | 0.49792 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1518 | 2017 | 11 | 11 | 11 | 57 | 17-0094408 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29093 | 8.6182 | 227_80 | <25mph | <15mph | HFTD - Distribution | 2017-11-11 11:57:00 | 1260 | 14.1707 | FALSE | <25mph | AU609 | 1.13 | 2017-11-11T19:50:00Z | 12.01 | 3 | < 25mph | AU609 | 1.13 | 2017-11-11T19:50:00Z | 12.01 | 9 | < 25mph | AU609 | 1.13 | 2017-11-11T19:50:00Z | 12.01 | 5 | < 25mph | F0412 | 7.06 | 2017-11-11T21:15:00Z | 13 | 17 | < 25mph
PG&E | 2017-11-20 08:33 | 08:32 | 38.7584 | -120.8439 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101389405 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43059.3562 | 08:32 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1522 | 2017 | 11 | 20 | 8 | 32 | 17-0096436 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 12376 | 9.7427 | 206_281 | <25mph | <15mph | HFTD - Distribution | 2017-11-20 08:32:00 | 1264 | 12.0384 | FALSE | <25mph | E5691 | 2.94 | 2017-11-20T16:29:00Z | 0 | 12 | < 25mph | E3165 | 6.09 | 2017-11-20T16:06:00Z | 5.99 | 109 | < 25mph | E5691 | 2.94 | 2017-11-20T17:29:00Z | 0 | 24 | < 25mph | E3165 | 6.09 | 2017-11-20T16:06:00Z | 5.99 | 219 | < 25mph
PG&E | 2017-11-29 17:35 | 17:34 | 38.6841 | -120.6546 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 101419450 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 43068.7326 | 17:34 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1533 | 2017 | 11 | 29 | 17 | 34 | 17-0098456 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 582825 | 2.2539 | 214_277 | <25mph | <15mph | HFTD - Distribution | 2017-11-29 17:34:00 | 1275 | 13.1335 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GZFC1 | 7.93 | 2017-11-30T01:17:00Z | 3 | 8 | < 25mph |  |  |  | 0 | 0 | No data | GZFC1 | 7.93 | 2017-11-30T02:17:00Z | 3 | 17 | < 25mph
PG&E | 2017-12-07 12:26 | 12:25 | 34.7115 | -120.1772 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 015/220 | Unknown | 115000 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1534 | 2017 | 12 | 7 | 12 | 25 | 17-0097211 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 4.373 | 237_58 | <25mph | <15mph | HFTD - Transmission | 2017-12-07 12:25:00 | 1276 | 13.3077 | FALSE | <25mph | TT480 | 2.15 | 2017-12-07T20:20:00Z | 25.99 | 1 | 25-40mph | SXWC1 | 7.67 | 2017-12-07T20:09:00Z | 27 | 9 | 25-40mph | TT480 | 2.15 | 2017-12-07T20:20:00Z | 25.99 | 2 | 25-40mph | SXWC1 | 7.67 | 2017-12-07T20:09:00Z | 27 | 23 | 25-40mph
PG&E | 2017-12-14 | 17:16 | 34.5878 | -120.3566 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101911004 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 43083 | 0.71944 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1538 | 2017 | 12 | 14 | 17 | 16 | 17-0101672 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2896 | 2.7073 | 229_51 | <25mph | <15mph | HFTD - Distribution | 2017-12-14 17:16:00 | 1280 | 11.3138 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2332 | 7.61 | 2017-12-14T08:00:00Z | 15.99 | 7 | < 25mph |  |  |  | 0 | 0 | No data | E2332 | 7.61 | 2017-12-14T08:56:00Z | 22.01 | 24 | < 25mph
PG&E | 2017-12-16 | 11:51 | 38.8171 | -122.7041 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Shawn Ohare | 102167231 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43085 | 0.49375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1540 | 2017 | 12 | 16 | 11 | 51 | 17-0102101 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26120 | 34.3488 | 126_285 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-12-16 11:51:00 | 1282 | 35.345 | FALSE | 25-40mph | LKRC1 | 2.09 | 2017-12-16T07:05:00Z | 17 | 1 | < 25mph | KELC1 | 6.55 | 2017-12-16T07:57:00Z | 23 | 2 | < 25mph | LKRC1 | 2.09 | 2017-12-16T08:05:00Z | 18.99 | 2 | < 25mph | KELC1 | 6.55 | 2017-12-16T07:57:00Z | 23 | 4 | < 25mph
PG&E | 2017-12-19 | 19:45 | 40.7271 | -122.3263 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101457738 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43088 | 0.82292 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1545 | 2017 | 12 | 19 | 19 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 12.0712 | 144_390 | <25mph | <15mph | HFTD - Distribution | 2017-12-19 19:45:00 | 1287 | 14.9625 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F0355 | 7.84 | 2017-12-19T07:51:00Z | 0 | 6 | < 25mph |  |  |  | 0 | 0 | No data | F0355 | 7.84 | 2017-12-19T08:51:00Z | 0 | 12 | < 25mph
PG&E | 2017-12-20 07:55 | 07:54 | 37.4012 | -122.3606 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100318864 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43089.3298 | 07:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1546 | 2017 | 12 | 20 | 7 | 54 | 17-0102756 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6602 | 16.1413 | 140_206 | <25mph | <15mph | HFTD - Distribution | 2017-12-20 07:54:00 | 1288 | 21.2088 | FALSE | <25mph | E4863 | 2.73 | 2017-12-20T15:28:00Z | 17 | 3 | < 25mph | E4863 | 2.73 | 2017-12-20T15:28:00Z | 17 | 13 | < 25mph | E4863 | 2.73 | 2017-12-20T16:38:00Z | 17 | 6 | < 25mph | E4863 | 2.73 | 2017-12-20T16:38:00Z | 17 | 19 | < 25mph
PG&E | 2017-12-29 | 16:31 | 37.8517 | -122.1586 | Vegetation | Rural | < 3 Meters | Fire Agency | 925-933-1313 | 100488954 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1552 | 2017 | 12 | 29 | 16 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 4.4772 | 149_231 | <25mph | <15mph | HFTD - Distribution | 2017-12-29 16:31:00 | 1294 | 9.6531 | FALSE | <25mph | E5555 | 3.67 | 2017-12-29T07:01:00Z | 23 | 31 | < 25mph | E5555 | 3.67 | 2017-12-29T07:01:00Z | 23 | 135 | < 25mph | E5555 | 3.67 | 2017-12-29T07:01:00Z | 23 | 61 | < 25mph | E5555 | 3.67 | 2017-12-29T07:01:00Z | 23 | 263 | < 25mph
PG&E | 2018-01-16 | 14:25 | 34.5703 | -119.9645 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101921689 | Verizon | 12000 | Conductor | Overhead | Yes | 43116 | 0.60069 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1556 | 2018 | 1 | 16 | 14 | 25 | 18-0006506 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 23519 | 5.0963 | 247_50 | <25mph | <15mph | HFTD - Distribution | 2018-01-16 14:25:00 | 1298 | 9.8389 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RHWC1 | 7.32 | 2018-01-16T07:06:00Z | 21 | 6 | < 25mph |  |  |  | 0 | 0 | No data | RHWC1 | 7.32 | 2018-01-16T08:06:00Z | 21 | 11 | < 25mph
PG&E | 2018-02-07 | 5:44 | 40.6543 | -122.5198 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 103922730 | Unknown | 12000 | Conductor | Overhead | Yes | 43138 | 0.23889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1558 | 2018 | 2 | 7 | 5 | 44 | 18-0012073 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 9610 | 17.8768 | 136_386 | <25mph | <15mph | HFTD - Distribution | 2018-02-07 05:44:00 | 1300 | 25.5948 | FALSE | 25-40mph | AU138 | 3.45 | 2018-02-07T07:44:00Z | 10 | 5 | < 25mph | MMOC1 | 5.95 | 2018-02-07T08:00:00Z | 27 | 9 | 25-40mph | AU138 | 3.45 | 2018-02-07T07:44:00Z | 10 | 9 | < 25mph | MMOC1 | 5.95 | 2018-02-07T09:00:00Z | 28.99 | 15 | 25-40mph
PG&E | 2018-02-07 | 9:16 | 38.0369 | -120.2096 | Vegetation | Rural | < 3 meters | Fire Agency | Jason Podesta 209-586-3362 | 101038120 | AT&T | 17000 | Conductor | Overhead | Yes | 43138 | 0.38611 | Contact From Object | N.A. | Other | Electric Facility | Human Error | third-party caused | Other/Unknown | 1559 | 2018 | 2 | 7 | 9 | 16 | 18-0012146 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 78738 | 9.6764 | 234_241 | <25mph | <15mph | HFTD - Distribution | 2018-02-07 09:16:00 | 1301 | 13.44 | FALSE | <25mph | MOUC1 | 2.73 | 2018-02-07T07:02:00Z | 18.99 | 1 | < 25mph | MOUC1 | 2.73 | 2018-02-07T07:02:00Z | 18.99 | 1 | < 25mph | MOUC1 | 2.73 | 2018-02-07T08:02:00Z | 20 | 2 | < 25mph | MOUC1 | 2.73 | 2018-02-07T08:02:00Z | 20 | 2 | < 25mph
PG&E | 2018-02-12 | 20:20 | 39.9395 | -121.6494 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430947 | Unknown | 12000 | Conductor | Overhead | Yes | 43143 | 0.84722 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1561 | 2018 | 2 | 12 | 20 | 20 | 18-0013604 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 149212 | 10.1876 | 172_346 | <25mph | <15mph | HFTD - Distribution | 2018-02-12 20:20:00 | 1303 | 14.6044 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CSTC1 | 7.88 | 2018-02-12T07:51:00Z | 5.99 | 19 | < 25mph |  |  |  | 0 | 0 | No data | CSTC1 | 7.88 | 2018-02-12T08:51:00Z | 14.99 | 38 | < 25mph
PG&E | 2018-03-06 | 17:57 | 38.2811 | -120.8965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-647-5220 | 101238429 | AT&T | 12000 | Conductor | Overhead | Yes | 43165 | 0.74792 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1566 | 2018 | 3 | 6 | 17 | 57 | 18-0020396 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 142000 | 3.9357 | 204_254 | <25mph | <15mph | HFTD - Distribution | 2018-03-06 17:57:00 | 1308 | 12.1612 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.07 | 2018-03-06T07:05:00Z | 13 | 4 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.07 | 2018-03-06T08:05:00Z | 14 | 8 | < 25mph
PG&E | 2018-04-27 | 12:48 | 39.1717 | -120.8652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | incident # 9960 ph # 530-8850111 | 100075314 | Unknown | 12000 | Conductor | Overhead | Yes | 43217 | 0.53333 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Dead | 1577 | 2018 | 4 | 27 | 12 | 48 | 18-0036310 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 28650 | 12.9115 | 205_304 | <25mph | <15mph | HFTD - Distribution | 2018-04-27 12:48:00 | 1319 | 12.9115 | FALSE | <25mph | SETC1 | 1.33 | 2018-04-27T06:28:00Z | 2.01 | 1 | < 25mph | AT999 | 7.76 | 2018-04-27T06:02:00Z | 4 | 14 | < 25mph | SETC1 | 1.33 | 2018-04-27T07:28:00Z | 2.01 | 2 | < 25mph | AT999 | 7.76 | 2018-04-27T07:32:00Z | 4 | 27 | < 25mph
PG&E | 2018-05-09 | 14:00 | 38.5908 | -123.3423 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CASE# 18CALNU 005865 | 101998286 | Unknown | 12000 | Conductor | Overhead | Yes | 43229 | 0.58333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1584 | 2018 | 5 | 9 | 14 | 0 | 18-0039683 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 29522 | 27.1689 | 98_273 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-05-09 14:00:00 | 1326 | 27.3091 | FALSE | 25-40mph | E7021 | 3.81 | 2018-05-09T06:56:00Z | 0 | 6 | < 25mph | HIRWW | 5.18 | 2018-05-09T07:00:00Z | 7.9 | 8 | < 25mph | E7021 | 3.81 | 2018-05-09T07:36:00Z | 8.01 | 12 | < 25mph | E7021 | 3.81 | 2018-05-09T07:36:00Z | 8.01 | 15 | < 25mph
PG&E | 2018-05-11 | 10:13 | 38.387 | -122.9856 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101973909 | Unknown | 12000 | Conductor | Overhead | Yes | 43231 | 0.42569 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1585 | 2018 | 5 | 11 | 10 | 13 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.6545 | 114_261 | <25mph | <15mph | HFTD - Distribution | 2018-05-11 10:13:00 | 1327 | 21.7544 | FALSE | <25mph | D2849 | 0.89 | 2018-05-11T06:52:00Z | 3 | 12 | < 25mph | BGAC1 | 6.17 | 2018-05-11T06:05:00Z | 25.99 | 55 | 25-40mph | D2849 | 0.89 | 2018-05-11T06:52:00Z | 3 | 24 | < 25mph | BGAC1 | 6.17 | 2018-05-11T06:05:00Z | 25.99 | 106 | 25-40mph
PG&E | 2018-05-11 | 17:43 | 38.8218 | -120.9295 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Douglas Ferro. cell-530-708-2715. office-530-677-6192 | 101388939 | AT&T | 21000 | Conductor | Overhead | Yes | 43231 | 0.73819 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1588 | 2018 | 5 | 11 | 17 | 43 | 18-0040415 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 53784 | 23.6414 | 202_284 | <25mph | <15mph | HFTD - Distribution | 2018-05-11 17:43:00 | 1330 | 24.2639 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 4.34 | 2018-05-11T06:56:00Z | 2.01 | 19 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 4.34 | 2018-05-11T07:56:00Z | 3 | 38 | < 25mph
PG&E | 2018-05-19 | 19:44 | 40.2665 | -122.2727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103899310 | Unknown | 12000 | Conductor | Overhead | Yes | 43239 | 0.82222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1599 | 2018 | 5 | 19 | 19 | 44 | 18-0042559 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 31980 | 15.59 | 146_364 | <25mph | <15mph | HFTD - Distribution | 2018-05-19 19:44:00 | 1341 | 18.253 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 7.1 | 2018-05-19T06:14:00Z | 3 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 7.1 | 2018-05-19T08:00:00Z | 3 | 8 | < 25mph
PG&E | 2018-05-28 | 6:30 | 40.4382 | -122.3001 | Building | Rural | Structure Only | Unknown | N.A. | 101495757 | Unknown | 0 – 750 | conductor | Overhead | Yes | 43248 | 0.27083 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1610 | 2018 | 5 | 28 | 6 | 30 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 17.501 | 145_374 | <25mph | <15mph | HFTD - Distribution | 2018-05-28 06:30:00 | 1352 | 26.4092 | FALSE | 25-40mph | AP525 | 2.99 | 2018-05-28T06:55:00Z | 0 | 6 | < 25mph | RRAC1 | 5.38 | 2018-05-28T06:24:00Z | 5.99 | 11 | < 25mph | AP525 | 2.99 | 2018-05-28T07:55:00Z | 0 | 12 | < 25mph | RRAC1 | 5.38 | 2018-05-28T07:24:00Z | 5.99 | 22 | < 25mph
PG&E | 2018-06-04 | 9:25 | 35.4593 | -120.4921 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101895513 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43255 | 0.39236 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1624 | 2018 | 6 | 4 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 12.0315 | 222_99 | <25mph | <15mph | HFTD - Distribution | 2018-06-04 09:25:00 | 1366 | 20.4837 | FALSE | <25mph | TT469 | 2.65 | 2018-06-04T06:14:00Z | 5.99 | 1 | < 25mph | TT469 | 2.65 | 2018-06-04T06:14:00Z | 5.99 | 1 | < 25mph | TT469 | 2.65 | 2018-06-04T06:14:00Z | 5.99 | 2 | < 25mph | TT469 | 2.65 | 2018-06-04T06:14:00Z | 5.99 | 2 | < 25mph
PG&E | 2018-06-05 | 10:13 | 40.6183 | -122.3173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JASON COLLINS 530-225-4628 | 101467801 | None | 12000 | Conductor | Overhead | Yes | 43256 | 0.42569 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1631 | 2018 | 6 | 5 | 10 | 13 | 18-0047539 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 277 | 7.1547 | 144_384 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 10:13:00 | 1373 | 12.6046 | FALSE | <25mph | C5599 | 1.27 | 2018-06-05T06:46:00Z | 4 | 8 | < 25mph | RRAC1 | 7.21 | 2018-06-05T06:24:00Z | 12.01 | 9 | < 25mph | C5599 | 1.27 | 2018-06-05T07:36:00Z | 8.01 | 20 | < 25mph | RRAC1 | 7.21 | 2018-06-05T07:24:00Z | 14 | 22 | < 25mph
PG&E | 2018-06-05 | 13:45 | 38.5432 | -122.7202 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 102031673 | Unknown | 12000 | Conductor | Overhead | Yes | 43256 | 0.57292 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1633 | 2018 | 6 | 5 | 13 | 45 | 18-0047625 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 40599 | 7.3889 | 125_270 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 13:45:00 | 1375 | 15.9614 | FALSE | <25mph | E1553 | 2.52 | 2018-06-05T06:14:00Z | 12.01 | 24 | < 25mph | E1553 | 2.52 | 2018-06-05T06:14:00Z | 12.01 | 86 | < 25mph | E1553 | 2.52 | 2018-06-05T06:14:00Z | 12.01 | 45 | < 25mph | E1553 | 2.52 | 2018-06-05T06:14:00Z | 12.01 | 165 | < 25mph
PG&E | 2018-06-08 | 19:03 | 35.154 | -120.594 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101852092 | AT&T | 12000 | Conductor | Overhead | Yes | 43259 | 0.79375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1644 | 2018 | 6 | 8 | 19 | 3 | 18-0049130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2473 | 24.0333 | 218_82 | <25mph | <15mph | HFTD - Distribution | 2018-06-08 19:03:00 | 1386 | 25.9327 | FALSE | 25-40mph | F0194 | 1.62 | 2018-06-08T06:41:00Z | 3 | 24 | < 25mph | E8214 | 6.18 | 2018-06-08T06:27:00Z | 4.99 | 32 | < 25mph | F0194 | 1.62 | 2018-06-08T06:41:00Z | 3 | 45 | < 25mph | E8214 | 6.18 | 2018-06-08T06:27:00Z | 4.99 | 61 | < 25mph
PG&E | 2018-06-09 | 0:46 | 35.0745 | -120.5167 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101927520 | Unknown | 12000 | Conductor | Overhead | Yes | 43260 | 0.031944 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1645 | 2018 | 6 | 9 | 0 | 46 | 18-0049171 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 16825 | 5.84 | 221_78 | <25mph | <15mph | HFTD - Distribution | 2018-06-09 00:46:00 | 1387 | 22.9582 | FALSE | <25mph | F0412 | 2.71 | 2018-06-09T06:30:00Z | 3 | 16 | < 25mph | F0412 | 2.71 | 2018-06-09T06:30:00Z | 3 | 36 | < 25mph | F0412 | 2.71 | 2018-06-09T06:30:00Z | 3 | 33 | < 25mph | F0412 | 2.71 | 2018-06-09T06:30:00Z | 3 | 73 | < 25mph
PG&E | 2018-06-10 | 17:19 | 38.4157 | -122.9184 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101978419 | AT&T | 12000 | Conductor | Overhead | Yes | 43261 | 0.72153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1647 | 2018 | 6 | 10 | 17 | 19 | 18-0049445 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2386 | 19.6716 | 117_263 | <25mph | <15mph | HFTD - Distribution | 2018-06-10 17:19:00 | 1389 | 23.7271 | FALSE | <25mph | GRWWW | 1.77 | 2018-06-10T06:00:00Z | 14.29 | 43 | < 25mph | DENWW | 6.15 | 2018-06-10T06:00:00Z | 16.4 | 106 | < 25mph | GRWWW | 1.77 | 2018-06-10T06:00:00Z | 14.29 | 87 | < 25mph | DENWW | 6.15 | 2018-06-10T06:00:00Z | 16.4 | 208 | < 25mph
PG&E | 2018-06-11 | 17:49 | 34.7329 | -120.0861 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103015183 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43262 | 0.74236 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1649 | 2018 | 6 | 11 | 17 | 49 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 16.7571 | 241_59 | <25mph | <15mph | HFTD - Distribution | 2018-06-11 17:49:00 | 1391 | 18.839 | FALSE | <25mph | UCSE | 3.69 | 2018-06-11T06:50:00Z | 7.81 | 7 | < 25mph | FGMC1 | 4.52 | 2018-06-11T06:35:00Z | 20 | 9 | < 25mph | UCSE | 3.69 | 2018-06-11T07:30:00Z | 8.3 | 13 | < 25mph | FGMC1 | 4.52 | 2018-06-11T06:35:00Z | 20 | 17 | < 25mph
PG&E | 2018-06-13 | 22:40 | 38.4901 | -122.6661 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SRS181640125 | 101966547 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 0.94444 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1656 | 2018 | 6 | 13 | 22 | 40 | 18-0050782 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 295146 | 2.5247 | 128_267 | <25mph | <15mph | HFTD - Distribution | 2018-06-13 22:40:00 | 1398 | 17.8767 | FALSE | <25mph | E1582 | 2.84 | 2018-06-13T06:43:00Z | 3 | 15 | < 25mph | CRIWW | 6.91 | 2018-06-13T06:00:00Z | 3.8 | 69 | < 25mph | E1582 | 2.84 | 2018-06-13T06:43:00Z | 3 | 30 | < 25mph | CRIWW | 6.91 | 2018-06-13T06:00:00Z | 3.8 | 134 | < 25mph
PG&E | 2018-06-15 | 2:56 | 37.4869 | -122.4223 | Vegetation | Rural | < 0.25 Acres | Utility: PG&E | N.A. | Pole 10/5 | None | 60000 | Conductor | Overhead | Yes | 43266 | 0.12222 | Contamination | N.A. | N.A. | N.A. | Unknown |  | no-match | 1659 | 2018 | 6 | 15 | 2 | 56 | INT-11115 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 0 | 6.5721 | 137_211 | <25mph | <15mph | HFTD - Transmission | 2018-06-15 02:56:00 | 1401 | 18.0175 | FALSE | <25mph | C3295 | 3.73 | 2018-06-15T06:23:00Z | 3 | 1 | < 25mph | HSPC1 | 5.28 | 2018-06-15T06:18:00Z | 18.99 | 78 | < 25mph | C3295 | 3.73 | 2018-06-15T07:13:00Z | 8.99 | 4 | < 25mph | HSPC1 | 5.28 | 2018-06-15T07:18:00Z | 21 | 154 | < 25mph
PG&E | 2018-06-15 | 9:51 | 37.1986 | -119.4709 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RANCHARIA ENGINE 4255 USFS ENG 52 | 101058060 | Unknown | 12000 | Conductor | Overhead | Yes | 43266 | 0.41042 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1660 | 2018 | 6 | 15 | 9 | 51 | 18-0051354 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 35146 | 7.0865 | 267_195 | <25mph | <15mph | HFTD - Distribution | 2018-06-15 09:51:00 | 1402 | 16.2916 | FALSE | <25mph | NFRC1 | 3.06 | 2018-06-15T06:55:00Z | 8.01 | 1 | < 25mph | NFRC1 | 3.06 | 2018-06-15T06:55:00Z | 8.01 | 1 | < 25mph | NFRC1 | 3.06 | 2018-06-15T06:55:00Z | 8.01 | 2 | < 25mph | NFRC1 | 3.06 | 2018-06-15T06:55:00Z | 8.01 | 2 | < 25mph
PG&E | 2018-06-15 | 10:05 | 38.6238 | -121.0221 | Vegetation | Rural | < 3 meters | Customer | N.A. | 101376538 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43266 | 0.42014 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1661 | 2018 | 6 | 15 | 10 | 5 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 10.3423 | 199_273 | <25mph | <15mph | HFTD - Distribution | 2018-06-15 10:05:00 | 1403 | 17.1425 | FALSE | <25mph | E8856 | 3.9 | 2018-06-15T07:00:00Z | 0 | 13 | < 25mph | FSLC1 | 7.47 | 2018-06-15T06:25:00Z | 9.26 | 57 | < 25mph | E8856 | 3.9 | 2018-06-15T08:00:00Z | 0 | 25 | < 25mph | FSLC1 | 7.47 | 2018-06-15T07:25:00Z | 10.63 | 112 | < 25mph
PG&E | 2018-06-16 | 19:58 | 37.907 | -121.8063 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100483910 | Unknown | 21000 | Conductor | Overhead | Yes | 43267 | 0.83194 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1670 | 2018 | 6 | 16 | 19 | 58 | 18-0051687 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 3322 | 40.9858 | 164_234 | 40-55mph | 30-45mph | HFTD - Distribution | 2018-06-16 19:58:00 | 1412 | 43.1884 | FALSE | 40-55mph | PG071 | 2.97 | 2018-06-16T06:00:00Z | 33.11 | 14 | 25-40mph | PG071 | 2.97 | 2018-06-16T06:00:00Z | 33.11 | 106 | 25-40mph | PG071 | 2.97 | 2018-06-16T06:00:00Z | 33.11 | 26 | 25-40mph | PG071 | 2.97 | 2018-06-16T06:00:00Z | 33.11 | 219 | 25-40mph
PG&E | 2018-06-16 | 20:33 | 38.0494 | -122.206 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Contra Costa FD | 101423963 | Unknown | 21000 | Conductor | Overhead | Yes | 43267 | 0.85625 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 1671 | 2018 | 6 | 16 | 20 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 31.0273 | 147_242 | 25-40mph | 30-45mph | HFTD - Distribution | 2018-06-16 20:33:00 | 1413 | 35.6333 | FALSE | 25-40mph | DPXC1 | 2.96 | 2018-06-16T06:42:00Z | 20.98 | 15 | < 25mph | PG064 | 7.4 | 2018-06-16T06:10:00Z | 35.95 | 95 | 25-40mph | DPXC1 | 2.96 | 2018-06-16T07:30:00Z | 20.98 | 28 | < 25mph | PG064 | 7.4 | 2018-06-16T06:10:00Z | 35.95 | 190 | 25-40mph
PG&E | 2018-06-19 | 0:27 | 38.7604 | -120.8224 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101388356 | Unknown | 12000 | Conductor | Overhead | Yes | 43270 | 0.01875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1675 | 2018 | 6 | 19 | 0 | 27 | 18-0052111 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 141652 | 7.2853 | 207_281 | <25mph | <15mph | HFTD - Distribution | 2018-06-19 00:27:00 | 1417 | 13.5304 | FALSE | <25mph | E5691 | 1.82 | 2018-06-19T06:59:00Z | 0 | 12 | < 25mph | TS903 | 6.68 | 2018-06-19T06:37:00Z | 2.01 | 75 | < 25mph | E5691 | 1.82 | 2018-06-19T07:59:00Z | 0 | 24 | < 25mph | E3165 | 5.03 | 2018-06-19T07:41:00Z | 2.01 | 147 | < 25mph
PG&E | 2018-06-19 | 14:41 | 37.2158 | -119.6811 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JOE QUINSTORFF 559-683-8008 | 103372829 | Unknown | 21000 | Conductor | Overhead | Yes | 43270 | 0.61181 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1679 | 2018 | 6 | 19 | 14 | 41 | 18-0052327 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 123838 | 9.7956 | 257_196 | <25mph | <15mph | HFTD - Distribution | 2018-06-19 14:41:00 | 1421 | 11.6304 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5766 | 6.85 | 2018-06-19T06:58:00Z | 0 | 20 | < 25mph |  |  |  | 0 | 0 | No data | E5766 | 6.85 | 2018-06-19T07:53:00Z | 0 | 33 | < 25mph
PG&E | 2018-06-21 | 18:58 | 35.1224 | -120.3938 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101878933 | AT&T | 12000 | Conductor | Overhead | Yes | 43272 | 0.79028 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1683 | 2018 | 6 | 21 | 18 | 58 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 13.9909 | 227_80 | <25mph | <15mph | HFTD - Distribution | 2018-06-21 18:58:00 | 1425 | 15.3983 | FALSE | <25mph | AU609 | 1.36 | 2018-06-21T06:48:00Z | 0 | 4 | < 25mph | F0412 | 7.22 | 2018-06-21T07:00:00Z | 4 | 11 | < 25mph | AU609 | 1.36 | 2018-06-21T07:48:00Z | 0 | 8 | < 25mph | F0412 | 7.22 | 2018-06-21T08:00:00Z | 4 | 21 | < 25mph
PG&E | 2018-06-22 | 17:44 | 37.2485 | -119.5625 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Madera County | 101117749 | None | 0 – 750 | Conductor | Overhead | Yes | 43273 | 0.73889 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1686 | 2018 | 6 | 22 | 17 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 10.123 | 263_198 | <25mph | <15mph | HFTD - Distribution | 2018-06-22 17:44:00 | 1428 | 12.3323 | FALSE | <25mph | NFRC1 | 3.29 | 2018-06-22T06:55:00Z | 8.01 | 1 | < 25mph | NFRC1 | 3.29 | 2018-06-22T06:55:00Z | 8.01 | 42 | < 25mph | NFRC1 | 3.29 | 2018-06-22T07:55:00Z | 8.01 | 2 | < 25mph | NFRC1 | 3.29 | 2018-06-22T07:55:00Z | 8.01 | 84 | < 25mph
PG&E | 2018-06-23 | 9:31 | 40.8632 | -122.3962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | RYAN MEANS 530-238-2416 | 101472252 | AT&T | 12000 | Conductor | Overhead | Yes | 43274 | 0.39653 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1688 | 2018 | 6 | 23 | 9 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2018-06-23 09:31:00 | NA | 0 | FALSE | <25mph | CTANT | 1.62 | 2018-06-23T06:15:00Z | 9.93 | 4 | < 25mph | SLFC1 | 4.17 | 2018-06-23T06:19:00Z | 21 | 9 | < 25mph | CTANT | 1.62 | 2018-06-23T06:15:00Z | 9.93 | 7 | < 25mph | SLFC1 | 4.17 | 2018-06-23T06:19:00Z | 21 | 17 | < 25mph
PG&E | 2018-06-27 | 18:46 | 40.218 | -123.7989 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TJ alderpoint fire | 100990381 | Unknown | 12000 | Conductor | Overhead | Yes | 43278 | 0.78194 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1700 | 2018 | 6 | 27 | 18 | 46 | 18-0055205 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 21357 | 17.7599 | 81_363 | <25mph | <15mph | HFTD - Distribution | 2018-06-27 18:46:00 | 1441 | 20.5507 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ERCC1 | 5.65 | 2018-06-27T06:28:00Z | 8.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | ERCC1 | 5.65 | 2018-06-27T06:28:00Z | 8.99 | 2 | < 25mph
PG&E | 2018-06-28 | 12:27 | 38.5982 | -121.0081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | John Reis, 530-622-3858 | 101376954 | Unknown | 21000 | Conductor | Overhead | Yes | 43279 | 0.51875 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1702 | 2018 | 6 | 28 | 12 | 27 | 18-0055479 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 24671 | 12.7651 | 199_272 | <25mph | <15mph | HFTD - Distribution | 2018-06-28 12:27:00 | 1443 | 13.4512 | FALSE | <25mph | E8856 | 2.62 | 2018-06-28T07:00:00Z | 7 | 13 | < 25mph | BENC1 | 4.05 | 2018-06-28T06:59:00Z | 8.01 | 28 | < 25mph | E8856 | 2.62 | 2018-06-28T07:15:00Z | 7 | 25 | < 25mph | BENC1 | 4.05 | 2018-06-28T06:59:00Z | 8.01 | 55 | < 25mph
PG&E | 2018-06-30 | 11:14 | 39.3621 | -121.0809 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ENGINEER YUREK | 100091354 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 0.46806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1713 | 2018 | 6 | 30 | 11 | 14 | 18-0055945 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5724 | 3.7745 | 196_314 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 11:14:00 | 1454 | 12.1468 | FALSE | <25mph | E3651 | 2.44 | 2018-06-30T06:30:00Z | 2.01 | 13 | < 25mph | RRRC1 | 4.49 | 2018-06-30T06:13:00Z | 7 | 28 | < 25mph | E3651 | 2.44 | 2018-06-30T07:50:00Z | 3 | 25 | < 25mph | PG030 | 6.5 | 2018-06-30T08:00:00Z | 10.51 | 54 | < 25mph
PG&E | 2018-06-30 | 22:18 | 40.6043 | -122.24 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101469808 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43281 | 0.92917 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1716 | 2018 | 6 | 30 | 22 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 10.6263 | 147_383 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 22:18:00 | 1457 | 24.79 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C5599 | 4.85 | 2018-06-30T06:17:00Z | 12.01 | 10 | < 25mph |  |  |  | 0 | 0 | No data | C5599 | 4.85 | 2018-06-30T06:17:00Z | 12.01 | 23 | < 25mph
PG&E | 2018-06-30 | 22:36 | 39.1141 | -121.077 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Matt Wallen (530) 277-3312 Incident # NEU015486 | 100105380 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 0.94167 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1717 | 2018 | 6 | 30 | 22 | 36 | 18-0056039 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 8004 | 7.8488 | 196_300 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 22:36:00 | 1458 | 15.8656 | FALSE | <25mph | E1789 | 3.68 | 2018-06-30T06:30:00Z | 4 | 21 | < 25mph | E1789 | 3.68 | 2018-06-30T06:30:00Z | 4 | 64 | < 25mph | E1789 | 3.68 | 2018-06-30T07:48:00Z | 4 | 41 | < 25mph | AT999 | 5.18 | 2018-06-30T07:57:00Z | 8.99 | 121 | < 25mph
PG&E | 2018-07-01 | 0:23 | 40.2697 | -124.2386 | Vegetation | Rural | < 3 meters | Fire Agency | fire chief | 100986962 | Unknown | 12000 | Conductor | Overhead | Yes | 43282 | 0.015972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1718 | 2018 | 7 | 1 | 0 | 23 | 18-0056043 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 22872 | 20.9894 | 63_366 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 00:23:00 | 1459 | 27.5371 | FALSE | 25-40mph | PTEC1 | 1.7 | 2018-07-01T06:08:00Z | 44.98 | 1 | 40-55mph | PTEC1 | 1.7 | 2018-07-01T06:08:00Z | 44.98 | 1 | 40-55mph | PTEC1 | 1.7 | 2018-07-01T06:08:00Z | 44.98 | 2 | 40-55mph | PTEC1 | 1.7 | 2018-07-01T06:08:00Z | 44.98 | 2 | 40-55mph
PG&E | 2018-07-01 | 0:45 | 38.8842 | -120.847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Brian Mackwood (530)708-2711 | 100109003 | None | 21000 | Conductor | Overhead | Yes | 43282 | 0.03125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1719 | 2018 | 7 | 1 | 0 | 45 | 18-0056045 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5760 | 9.2878 | 206_288 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 00:45:00 | 1460 | 12.1055 | FALSE | <25mph | PG033 | 2.7 | 2018-07-01T07:00:00Z | 3.29 | 33 | < 25mph | BDMC1 | 7.75 | 2018-07-01T06:36:00Z | 10 | 41 | < 25mph | PG033 | 2.7 | 2018-07-01T07:00:00Z | 3.29 | 63 | < 25mph | BDMC1 | 7.75 | 2018-07-01T07:36:00Z | 21 | 79 | < 25mph
PG&E | 2018-07-01 | 8:13 | 39.4154 | -121.5122 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430344 | AT&T | 12000 | Conductor | Overhead | Yes | 43282 | 0.34236 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1720 | 2018 | 7 | 1 | 8 | 13 | 18-0056061 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 7848 | 6.5616 | 178_317 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 08:13:00 | 1461 | 14.6967 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TT309 | 6.67 | 2018-07-01T06:45:00Z | 5.99 | 2 | < 25mph |  |  |  | 0 | 0 | No data | TT309 | 6.67 | 2018-07-01T06:45:00Z | 5.99 | 4 | < 25mph
PG&E | 2018-07-02 | 5:12 | 38.6092 | -122.4595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 707-967-1467 | 102252558 | AT&T | 21000 | Conductor | Overhead | Yes | 43283 | 0.21667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1722 | 2018 | 7 | 2 | 5 | 12 | 18-0056178 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 403 | 6.1424 | 137_273 | <25mph | <15mph | HFTD - Distribution | 2018-07-02 05:12:00 | 1463 | 24.2981 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG045 | 7.68 | 2018-07-02T06:30:00Z | 5.48 | 11 | < 25mph |  |  |  | 0 | 0 | No data | PG045 | 7.68 | 2018-07-02T07:50:00Z | 10.09 | 21 | < 25mph
PG&E | 2018-07-09 | 7:27 | 35.0785 | -120.3948 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101861366 | Unknown | 12000 | Conductor | Overhead | Yes | 43290 | 0.31042 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1735 | 2018 | 7 | 9 | 7 | 27 | 18-0057904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 21045 | 9.782 | 227_78 | <25mph | <15mph | HFTD - Distribution | 2018-07-09 07:27:00 | 1475 | 17.5911 | FALSE | <25mph | AU609 | 1.69 | 2018-07-09T06:48:00Z | 0 | 4 | < 25mph | AU609 | 1.69 | 2018-07-09T06:48:00Z | 0 | 4 | < 25mph | AU609 | 1.69 | 2018-07-09T07:48:00Z | 0 | 8 | < 25mph | F0412 | 5.4 | 2018-07-09T07:55:00Z | 1.01 | 10 | < 25mph
PG&E | 2018-07-14 | 11:34 | 38.4026 | -122.5489 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103141862 | Verizon | 12000 | Conductor | Overhead | Yes | 43295 | 0.48194 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1745 | 2018 | 7 | 14 | 11 | 34 | 18-0059821 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 6426 | 11.4725 | 133_262 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 11:34:00 | 1485 | 15.7933 | FALSE | <25mph | KENWW | 0.52 | 2018-07-14T06:00:00Z | 9.19 | 2 | < 25mph | BVYWW | 5.16 | 2018-07-14T06:00:00Z | 11.79 | 16 | < 25mph | KENWW | 0.52 | 2018-07-14T06:00:00Z | 9.19 | 3 | < 25mph | BVYWW | 5.16 | 2018-07-14T06:00:00Z | 11.79 | 29 | < 25mph
PG&E | 2018-07-14 | 12:40 | 38.5793 | -122.878 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103122744 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 0.52778 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1746 | 2018 | 7 | 14 | 12 | 40 | 18-0059799 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20804 | 12.0574 | 118_272 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 12:40:00 | 1486 | 14.4502 | FALSE | <25mph | R08WW | 2.26 | 2018-07-14T06:00:00Z | 8.59 | 11 | < 25mph | DRYWW | 5.04 | 2018-07-14T06:00:00Z | 10.69 | 57 | < 25mph | R08WW | 2.26 | 2018-07-14T06:00:00Z | 8.59 | 20 | < 25mph | DRYWW | 5.04 | 2018-07-14T06:00:00Z | 10.69 | 103 | < 25mph
PG&E | 2018-07-14 | 12:56 | 39.2093 | -121.197 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE DEPT LEFT BEFORE UPTAINING THAT INFO | 100086833 | None | 21000 | Conductor | Overhead | Yes | 43295 | 0.53889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1747 | 2018 | 7 | 14 | 12 | 56 | 18-0059841 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 3720 | 10.2359 | 191_306 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 12:56:00 | 1487 | 12.6903 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RRRC1 | 7.78 | 2018-07-14T06:13:00Z | 4.99 | 35 | < 25mph |  |  |  | 0 | 0 | No data | RRRC1 | 7.78 | 2018-07-14T07:13:00Z | 5.99 | 70 | < 25mph
PG&E | 2018-07-14 | 14:44 | 38.9524 | -121.2467 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100035452 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 0.61389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1748 | 2018 | 7 | 14 | 14 | 44 | 18-0059847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2430 | 9.5304 | 189_291 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 14:44:00 | 1488 | 13.6375 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LICC1 | 5.05 | 2018-07-14T06:13:00Z | 4 | 6 | < 25mph |  |  |  | 0 | 0 | No data | E6168 | 5.24 | 2018-07-14T07:13:00Z | 4 | 11 | < 25mph
PG&E | 2018-07-17 | 11:11 | 35.6986 | -120.9777 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | dennis byrnes 8055434244 inc # = 18ca-slu-007640 | 103886652 | Unknown | 21000 | Conductor | Overhead | Yes | 43298 | 0.46597 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1755 | 2018 | 7 | 17 | 11 | 11 | 18-0060637 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 9121 | 4.768 | 201_112 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 11:11:00 | 1495 | 12.6145 | FALSE | <25mph | E9175 | 3.58 | 2018-07-17T06:15:00Z | 4.99 | 12 | < 25mph | D4060 | 6.73 | 2018-07-17T06:25:00Z | 8.01 | 17 | < 25mph | E9175 | 3.58 | 2018-07-17T07:25:00Z | 5.99 | 24 | < 25mph | D4060 | 6.73 | 2018-07-17T07:10:00Z | 8.99 | 34 | < 25mph
PG&E | 2018-07-17 | 11:58 | 37.2217 | -121.6778 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Luis Morado state arson fire fighter | 100601345 | Unknown | 12000 | Conductor | Overhead | Yes | 43298 | 0.49861 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1756 | 2018 | 7 | 17 | 11 | 58 | 18-0060617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 5865 | 5.1834 | 170_196 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 11:58:00 | 1496 | 14.408 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C7794 | 7.07 | 2018-07-17T06:00:00Z | 1.01 | 23 | < 25mph |  |  |  | 0 | 0 | No data | C7794 | 7.07 | 2018-07-17T06:00:00Z | 1.01 | 45 | < 25mph
PG&E | 2018-07-17 | 16:53 | 38.3955 | -122.9212 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101978449 | AT&T | 12000 | Conductor | Overhead | Yes | 43298 | 0.70347 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1759 | 2018 | 7 | 17 | 16 | 53 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 13.5832 | 116_262 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 16:53:00 | 1499 | 13.5832 | FALSE | <25mph | DUTWW | 3.53 | 2018-07-17T07:00:00Z | 9.19 | 36 | < 25mph | DUTWW | 3.53 | 2018-07-17T07:00:00Z | 9.19 | 80 | < 25mph | DUTWW | 3.53 | 2018-07-17T08:00:00Z | 10.69 | 68 | < 25mph | DUTWW | 3.53 | 2018-07-17T08:00:00Z | 10.69 | 154 | < 25mph
PG&E | 2018-07-17 | 19:40 | 40.5927 | -122.4886 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101477082 | AT&T | 12000 | Conductor | Overhead | Yes | 43298 | 0.81944 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1760 | 2018 | 7 | 17 | 19 | 40 | 18-0060840 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 30162 | 14.3022 | 137_382 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 19:40:00 | 1500 | 21.6282 | FALSE | <25mph | MMOC1 | 1.8 | 2018-07-17T07:00:00Z | 10 | 7 | < 25mph | MMOC1 | 1.8 | 2018-07-17T07:00:00Z | 10 | 13 | < 25mph | MMOC1 | 1.8 | 2018-07-17T07:00:00Z | 10 | 12 | < 25mph | MMOC1 | 1.8 | 2018-07-17T07:00:00Z | 10 | 23 | < 25mph
PG&E | 2018-07-18 | 1:14 | 38.3671 | -120.5578 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101247987 | Unknown | 12000 | Conductor | Overhead | Yes | 43299 | 0.051389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1761 | 2018 | 7 | 18 | 1 | 14 | 18-0060882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6420 | 6.6576 | 219_259 | <25mph | <15mph | HFTD - Distribution | 2018-07-18 01:14:00 | 1501 | 11.9385 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ESPC1 | 6.8 | 2018-07-18T06:13:00Z | 8.01 | 14 | < 25mph |  |  |  | 0 | 0 | No data | ESPC1 | 6.8 | 2018-07-18T06:13:00Z | 8.01 | 28 | < 25mph
PG&E | 2018-07-19 | 0:08 | 36.9372 | -119.4557 | Vegetation | Rural | < 0.25 Acres | Fire Agency | incident # 10559 | 100677019 | AT&T | 12000 | Conductor | Overhead | Yes | 43300 | 0.0055556 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1766 | 2018 | 7 | 19 | 0 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 10.281 | 268_181 | <25mph | <15mph | HFTD - Distribution | 2018-07-19 00:08:00 | 1506 | 18.2382 | FALSE | <25mph | FCHC1 | 3.86 | 2018-07-19T07:00:00Z | 5.99 | 2 | < 25mph | FCHC1 | 3.86 | 2018-07-19T07:00:00Z | 5.99 | 2 | < 25mph | FCHC1 | 3.86 | 2018-07-19T07:00:00Z | 5.99 | 3 | < 25mph | FCHC1 | 3.86 | 2018-07-19T07:00:00Z | 5.99 | 3 | < 25mph
PG&E | 2018-07-19 | 5:29 | 40.1918 | -123.5373 | Vegetation | Rural | < 0.25 Acres | Fire Agency | fire captain | 103909820 | Unknown | 12000 | Conductor | Overhead | Yes | 43300 | 0.22847 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1767 | 2018 | 7 | 19 | 5 | 29 | 18-0061308 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 73380 | 5.6109 | 92_361 | <25mph | <15mph | HFTD - Distribution | 2018-07-19 05:29:00 | 1507 | 13.8917 | FALSE | <25mph | ALDC1 | 2.86 | 2018-07-19T06:51:00Z | 4 | 1 | < 25mph | ALDC1 | 2.86 | 2018-07-19T06:51:00Z | 4 | 1 | < 25mph | ALDC1 | 2.86 | 2018-07-19T07:51:00Z | 4 | 2 | < 25mph | ALDC1 | 2.86 | 2018-07-19T07:51:00Z | 4 | 2 | < 25mph
PG&E | 2018-07-20 | 6:31 | 37.4318 | -119.9441 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ZACH RUTHERFORD 209-966-3621 | 103909942 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43301 | 0.27153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1771 | 2018 | 7 | 20 | 6 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2004 | 246_208 | <25mph | <15mph | HFTD - Distribution | 2018-07-20 06:31:00 | 1511 | 13.5994 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E9110 | 6.48 | 2018-07-20T06:47:00Z | 5.99 | 9 | < 25mph |  |  |  | 0 | 0 | No data | E9110 | 6.48 | 2018-07-20T07:02:00Z | 5.99 | 18 | < 25mph
PG&E | 2018-07-21 | 0:23 | 38.6927 | -120.7921 | Vegetation | Rural | < 3 meters | Fire Agency | CAMINO | 101415904 | AT&T | 12000 | Conductor | Overhead | Yes | 43302 | 0.015972 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1774 | 2018 | 7 | 21 | 0 | 23 | 18-0062206 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 107552 | 9.7365 | 208_277 | <25mph | <15mph | HFTD - Distribution | 2018-07-21 00:23:00 | 1514 | 11.1911 | FALSE | <25mph | C6129 | 3.07 | 2018-07-21T06:24:00Z | 2.01 | 30 | < 25mph | C6129 | 3.07 | 2018-07-21T06:24:00Z | 2.01 | 60 | < 25mph | C6129 | 3.07 | 2018-07-21T06:24:00Z | 2.01 | 60 | < 25mph | E3165 | 7.94 | 2018-07-21T07:58:00Z | 3 | 120 | < 25mph
PG&E | 2018-07-21 | 14:51 | 35.6846 | -120.9427 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101943190 | Unknown | 21000 | Conductor | Overhead | Yes | 43302 | 0.61875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1775 | 2018 | 7 | 21 | 14 | 51 | 18-0062364 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 110814 | 14.9597 | 202_111 | <25mph | <15mph | HFTD - Distribution | 2018-07-21 14:51:00 | 1515 | 21.9627 | FALSE | <25mph | TABC1 | 2.21 | 2018-07-21T06:07:00Z | 3 | 1 | < 25mph | E9175 | 5.16 | 2018-07-21T06:50:00Z | 4 | 18 | < 25mph | TABC1 | 2.21 | 2018-07-21T06:07:00Z | 3 | 2 | < 25mph | E9175 | 5.16 | 2018-07-21T06:50:00Z | 4 | 35 | < 25mph
PG&E | 2018-07-23 | 17:27 | 39.734 | -121.4965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103843963 | AT&T | 12000 | Conductor | Overhead | Yes | 43304 | 0.72708 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1782 | 2018 | 7 | 23 | 17 | 27 | 18-0062874 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 183629 | 9.1915 | 178_335 | <25mph | <15mph | HFTD - Distribution | 2018-07-23 17:27:00 | 1522 | 13.4352 | FALSE | <25mph | JBGC1 | 0.42 | 2018-07-23T06:13:00Z | 5.99 | 1 | < 25mph | JBGC1 | 0.42 | 2018-07-23T06:13:00Z | 5.99 | 3 | < 25mph | JBGC1 | 0.42 | 2018-07-23T07:13:00Z | 11.01 | 2 | < 25mph | JBGC1 | 0.42 | 2018-07-23T07:13:00Z | 11.01 | 5 | < 25mph
PG&E | 2018-07-24 | 13:47 | 39.0606 | -123.4456 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102212216 | Unknown | 12000 | Conductor | Overhead | Yes | 43305 | 0.57431 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1786 | 2018 | 7 | 24 | 13 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 16.5971 | 95_299 | <25mph | <15mph | HFTD - Distribution | 2018-07-24 13:47:00 | 1526 | 19.7448 | FALSE | <25mph | E1763 | 3.79 | 2018-07-24T06:13:00Z | 1.01 | 4 | < 25mph | BNVC1 | 7.27 | 2018-07-24T06:50:00Z | 4 | 8 | < 25mph | E1763 | 3.79 | 2018-07-24T06:13:00Z | 1.01 | 8 | < 25mph | BNVC1 | 7.27 | 2018-07-24T06:50:00Z | 4 | 17 | < 25mph
PG&E | 2018-07-25 | 0:42 | 39.7791 | -121.6173 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100327443 | Unknown | 12000 | Conductor | Overhead | Yes | 43306 | 0.029167 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1788 | 2018 | 7 | 25 | 0 | 42 | 18-0063320 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6742 | 1.3279 | 173_337 | <25mph | <15mph | HFTD - Distribution | 2018-07-25 00:42:00 | 1528 | 11.7229 | FALSE | <25mph | PDEC1 | 1.8 | 2018-07-25T07:00:00Z | 1.01 | 2 | < 25mph | JBGC1 | 7.44 | 2018-07-25T06:13:00Z | 10 | 21 | < 25mph | PDEC1 | 1.8 | 2018-07-25T08:00:00Z | 1.01 | 3 | < 25mph | JBGC1 | 7.44 | 2018-07-25T07:13:00Z | 10 | 37 | < 25mph
PG&E | 2018-07-27 | 23:12 | 37.18 | -122.029 | Vegetation | Rural | < 3 meters | Fire Agency | Jeremy Wise 408-378-4010 Incident # C182080066 | 100518365 | Unknown | 12000 | Conductor | Overhead | Yes | 43308 | 0.96667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1793 | 2018 | 7 | 27 | 23 | 12 | 18-0064525 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 30475 | 3.2895 | 154_194 | <25mph | <15mph | HFTD - Distribution | 2018-07-27 23:12:00 | 1533 | 9.1823 | FALSE | <25mph | PG050 | 2.33 | 2018-07-27T06:10:00Z | 12.93 | 11 | < 25mph | PG050 | 2.33 | 2018-07-27T06:10:00Z | 12.93 | 125 | < 25mph | PG050 | 2.33 | 2018-07-27T06:10:00Z | 12.93 | 21 | < 25mph | PG050 | 2.33 | 2018-07-27T06:10:00Z | 12.93 | 240 | < 25mph
PG&E | 2018-07-28 | 6:51 | 38.7473 | -120.7866 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101418155 | AT&T | 21000 | Conductor | Overhead | Yes | 43309 | 0.28542 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1794 | 2018 | 7 | 28 | 6 | 51 | 18-0064545 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 15429 | 14.6813 | 209_280 | <25mph | <15mph | HFTD - Distribution | 2018-07-28 06:51:00 | 1534 | 14.6813 | FALSE | <25mph | E5691 | 0.5 | 2018-07-28T06:01:00Z | 2.01 | 16 | < 25mph | E3165 | 4.37 | 2018-07-28T06:55:00Z | 4.99 | 54 | < 25mph | E5691 | 0.5 | 2018-07-28T06:01:00Z | 2.01 | 25 | < 25mph | E3165 | 4.37 | 2018-07-28T07:35:00Z | 8.01 | 97 | < 25mph
PG&E | 2018-07-29 | 11:39 | 39.0968 | -123.5018 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102177329 | Unknown | 12000 | Conductor | Overhead | Yes | 43310 | 0.48542 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1796 | 2018 | 7 | 29 | 11 | 39 | 18-0064779 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4329 | 14.6452 | 92_301 | <25mph | <15mph | HFTD - Distribution | 2018-07-29 11:39:00 | 1536 | 18.4465 | FALSE | <25mph | E1763 | 2 | 2018-07-29T06:59:00Z | 0 | 2 | < 25mph | E1763 | 2 | 2018-07-29T06:59:00Z | 0 | 2 | < 25mph | E1763 | 2 | 2018-07-29T07:29:00Z | 2.01 | 6 | < 25mph | E1763 | 2 | 2018-07-29T07:29:00Z | 2.01 | 6 | < 25mph
PG&E | 2018-07-29 | 17:29 | 38.5777 | -120.8556 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101383255 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43310 | 0.72847 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1797 | 2018 | 7 | 29 | 17 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.882 | 206_271 | <25mph | <15mph | HFTD - Distribution | 2018-07-29 17:29:00 | 1537 | 11.0812 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BENC1 | 4.31 | 2018-07-29T06:59:00Z | 4.99 | 30 | < 25mph |  |  |  | 0 | 0 | No data | BENC1 | 4.31 | 2018-07-29T07:59:00Z | 4.99 | 58 | < 25mph
PG&E | 2018-07-30 | 14:36 | 38.1987 | -120.3638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NICK WEBB ( 209) 532-7424 | 103336176 | Unknown | 17000 | Conductor | Overhead | Yes | 43311 | 0.60833 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1800 | 2018 | 7 | 30 | 14 | 36 | 18-0065131 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18530 | 10.5817 | 227_250 | <25mph | <15mph | HFTD - Distribution | 2018-07-30 14:36:00 | 1540 | 14.4256 | FALSE | <25mph | E8204 | 0 | 2018-07-30T06:48:00Z | 0 | 4 | < 25mph | E9838 | 7.59 | 2018-07-30T06:39:00Z | 4.99 | 20 | < 25mph | E8204 | 0 | 2018-07-30T07:48:00Z | 0 | 7 | < 25mph | E9838 | 7.59 | 2018-07-30T06:39:00Z | 4.99 | 37 | < 25mph
PG&E | 2018-07-31 | 7:57 | 38.9559 | -122.7274 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102162351 | AT&T | 12000 | Conductor | Overhead | Yes | 43312 | 0.33125 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1803 | 2018 | 7 | 31 | 7 | 57 | 18-0065276 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 89832 | 7.6131 | 125_292 | <25mph | <15mph | HFTD - Distribution | 2018-07-31 07:57:00 | 1543 | 16.0718 | FALSE | <25mph | KELC1 | 3.24 | 2018-07-31T06:57:00Z | 17 | 1 | < 25mph | KELC1 | 3.24 | 2018-07-31T06:57:00Z | 17 | 1 | < 25mph | KELC1 | 3.24 | 2018-07-31T07:57:00Z | 18.99 | 2 | < 25mph | KELC1 | 3.24 | 2018-07-31T07:57:00Z | 18.99 | 2 | < 25mph
PG&E | 2018-08-01 | 17:58 | 38.9155 | -122.799 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102156435 | Unknown | 12000 | Conductor | Overhead | Yes | 43313 | 0.74861 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1805 | 2018 | 8 | 1 | 17 | 58 | 18-0065921 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2744 | 14.8702 | 122_290 | <25mph | <15mph | HFTD - Distribution | 2018-08-01 17:58:00 | 1545 | 14.8702 | FALSE | <25mph | E4393 | 3.97 | 2018-08-01T06:15:00Z | 7 | 4 | < 25mph | KELC1 | 4.99 | 2018-08-01T06:57:00Z | 14.99 | 5 | < 25mph | E4393 | 3.97 | 2018-08-01T06:15:00Z | 7 | 8 | < 25mph | KELC1 | 4.99 | 2018-08-01T06:57:00Z | 14.99 | 10 | < 25mph
PG&E | 2018-08-05 | 13:56 | 37.4005 | -119.7532 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | JIM FORGA 209-966-3621 | 101017235 | Unknown | 12000 | Conductor | Overhead | Yes | 43317 | 0.58056 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1821 | 2018 | 8 | 5 | 13 | 56 | 18-0066905 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 7325 | 10.7759 | 254_206 | <25mph | <15mph | HFTD - Distribution | 2018-08-05 13:56:00 | 1561 | 13.3386 | FALSE | <25mph | MIAC1 | 1.36 | 2018-08-05T06:59:00Z | 10 | 2 | < 25mph | MIAC1 | 1.36 | 2018-08-05T06:59:00Z | 10 | 28 | < 25mph | MIAC1 | 1.36 | 2018-08-05T06:59:00Z | 10 | 4 | < 25mph | MIAC1 | 1.36 | 2018-08-05T06:59:00Z | 10 | 56 | < 25mph
PG&E | 2018-08-07 | 15:46 | 40.4465 | -122.446 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464611 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43319 | 0.65694 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1826 | 2018 | 8 | 7 | 15 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 7.2812 | 139_374 | <25mph | <15mph | HFTD - Distribution | 2018-08-07 15:46:00 | 1566 | 14.3471 | FALSE | <25mph | E6886 | 2.81 | 2018-08-07T06:31:00Z | 2.01 | 4 | < 25mph | E6886 | 2.81 | 2018-08-07T06:31:00Z | 2.01 | 4 | < 25mph | E6886 | 2.81 | 2018-08-07T07:16:00Z | 2.01 | 8 | < 25mph | E6886 | 2.81 | 2018-08-07T07:16:00Z | 2.01 | 8 | < 25mph
PG&E | 2018-08-07 | 17:15 | 37.1181 | -122.1093 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101670606 | AT&T | 12000 | Conductor | Overhead | Yes | 43319 | 0.71875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1827 | 2018 | 8 | 7 | 17 | 15 | 18-0067641 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1988 | 17.3453 | 151_191 | <25mph | <15mph | HFTD - Distribution | 2018-08-07 17:15:00 | 1567 | 17.3453 | FALSE | <25mph | BNDC1 | 3.6 | 2018-08-07T06:50:00Z | 18.01 | 34 | < 25mph | BNDC1 | 3.6 | 2018-08-07T06:50:00Z | 18.01 | 67 | < 25mph | BNDC1 | 3.6 | 2018-08-07T07:50:00Z | 20 | 65 | < 25mph | BNDC1 | 3.6 | 2018-08-07T07:50:00Z | 20 | 124 | < 25mph
PG&E | 2018-08-07 | 21:03 | 38.2129 | -120.9184 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102042811 | Unknown | 12000 | Conductor | Overhead | Yes | 43319 | 0.87708 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1828 | 2018 | 8 | 7 | 21 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2018-08-07 21:03:00 | NA | 0 | FALSE | <25mph | CMAC1 | 2.92 | 2018-08-07T06:59:00Z | 3 | 1 | < 25mph | CMAC1 | 2.92 | 2018-08-07T06:59:00Z | 3 | 1 | < 25mph | CMAC1 | 2.92 | 2018-08-07T07:59:00Z | 3 | 2 | < 25mph | CMAC1 | 2.92 | 2018-08-07T07:59:00Z | 3 | 2 | < 25mph
PG&E | 2018-08-08 | 10:03 | 40.7933 | -124.0242 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CHIEF | 100983089 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 0.41875 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1829 | 2018 | 8 | 8 | 10 | 3 | 18-0067921 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 27379 | 3.1403 | 73_395 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 10:03:00 | 1568 | 7.3376 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.13 | 2018-08-08T06:55:00Z | 7 | 30 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.13 | 2018-08-08T06:55:00Z | 7 | 61 | < 25mph
PG&E | 2018-08-08 | 16:02 | 36.4703 | -121.7143 | Vegetation | Rural | < 3 meters | Customer | N.A. | 103910535 | None | 12000 | Conductor | Overhead | Yes | 43320 | 0.66806 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1830 | 2018 | 8 | 8 | 16 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 14.7322 | 168_155 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:02:00 | 1569 | 15.5625 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F1964 | 7.27 | 2018-08-08T07:00:00Z | 2.01 | 5 | < 25mph |  |  |  | 0 | 0 | No data | F1964 | 7.27 | 2018-08-08T08:00:00Z | 2.01 | 8 | < 25mph
PG&E | 2018-08-08 | 16:03 | 37.2974 | -122.2651 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 100307515 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 0.66875 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1831 | 2018 | 8 | 8 | 16 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.1654 | 144_201 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:03:00 | 1570 | 9.1654 | FALSE | <25mph | LAHC1 | 0.77 | 2018-08-08T06:07:00Z | 4 | 1 | < 25mph | PG003 | 5.06 | 2018-08-08T06:00:00Z | 12.93 | 57 | < 25mph | LAHC1 | 0.77 | 2018-08-08T06:07:00Z | 4 | 2 | < 25mph | PG003 | 5.06 | 2018-08-08T06:00:00Z | 12.93 | 111 | < 25mph
PG&E | 2018-08-10 | 12:54 | 38.799 | -120.73 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101386272 | AT&T | 12000 | Conductor | Overhead | Yes | 43322 | 0.5375 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1832 | 2018 | 8 | 10 | 12 | 54 | 18-0068798 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 26532 | 10.1607 | 211_283 | <25mph | <15mph | HFTD - Distribution | 2018-08-10 12:54:00 | 1571 | 17.3224 | FALSE | <25mph | E3165 | 0.86 | 2018-08-10T06:10:00Z | 4.99 | 8 | < 25mph | PG068 | 4.31 | 2018-08-10T07:00:00Z | 5.03 | 47 | < 25mph | E3165 | 0.86 | 2018-08-10T08:00:00Z | 4.99 | 15 | < 25mph | PG068 | 4.31 | 2018-08-10T07:10:00Z | 6.13 | 91 | < 25mph
PG&E | 2018-08-12 | 14:46 | 38.6443 | -120.9211 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101410516 | Unknown | 21000 | Conductor | Overhead | Yes | 43324 | 0.61528 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1838 | 2018 | 8 | 12 | 14 | 46 | 18-0069084 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4032 | 11.2318 | 203_274 | <25mph | <15mph | HFTD - Distribution | 2018-08-12 14:46:00 | 1577 | 12.412 | FALSE | <25mph | E8856 | 3.96 | 2018-08-12T06:35:00Z | 8.01 | 27 | < 25mph | PG073 | 7.47 | 2018-08-12T07:00:00Z | 14.92 | 118 | < 25mph | E8856 | 3.96 | 2018-08-12T06:35:00Z | 8.01 | 52 | < 25mph | PG073 | 7.47 | 2018-08-12T07:30:00Z | 19.06 | 228 | < 25mph
PG&E | 2018-08-13 | 15:33 | 38.708 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101377799 | Unknown | 21000 | Conductor | Overhead | Yes | 43325 | 0.64792 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1840 | 2018 | 8 | 13 | 15 | 33 | 18-0069470 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1004 | 11.7134 | 201_278 | <25mph | <15mph | HFTD - Distribution | 2018-08-13 15:33:00 | 1579 | 13.7748 | FALSE | <25mph | PG073 | 2.99 | 2018-08-13T06:40:00Z | 13.8 | 60 | < 25mph | PG073 | 2.99 | 2018-08-13T06:40:00Z | 13.8 | 117 | < 25mph | PG073 | 2.99 | 2018-08-13T06:40:00Z | 13.8 | 116 | < 25mph | PG073 | 2.99 | 2018-08-13T06:40:00Z | 13.8 | 226 | < 25mph
PG&E | 2018-08-14 | 15:46 | 38.0878 | -122.6002 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103916882 | Verizon | 0 – 750 | Conductor | Overhead | Yes | 43326 | 0.65694 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1844 | 2018 | 8 | 14 | 15 | 46 | 18-0069929 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 546 | 20.6189 | 130_244 | <25mph | <15mph | HFTD - Distribution | 2018-08-14 15:46:00 | 1583 | 26.2074 | FALSE | 25-40mph | E0433 | 1.95 | 2018-08-14T06:35:00Z | 15.99 | 35 | < 25mph | WDAC1 | 7.14 | 2018-08-14T06:51:00Z | 20 | 64 | < 25mph | E0433 | 1.95 | 2018-08-14T06:35:00Z | 15.99 | 70 | < 25mph | WDAC1 | 7.14 | 2018-08-14T06:51:00Z | 20 | 125 | < 25mph
PG&E | 2018-08-17 | 9:38 | 40.2997 | -122.3322 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chief | 101509747 | AT&T | 12000 | Conductor | Overhead | Yes | 43329 | 0.40139 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1845 | 2018 | 8 | 17 | 9 | 38 | 18-0071042 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 15510 | 1.1849 | 143_366 | <25mph | <15mph | HFTD - Distribution | 2018-08-17 09:38:00 | 1584 | 12.2164 | FALSE | <25mph | E7114 | 3.57 | 2018-08-17T06:47:00Z | 4.99 | 4 | < 25mph | E7114 | 3.57 | 2018-08-17T06:47:00Z | 4.99 | 4 | < 25mph | E7114 | 3.57 | 2018-08-17T07:47:00Z | 5.99 | 8 | < 25mph | E7114 | 3.57 | 2018-08-17T07:47:00Z | 5.99 | 8 | < 25mph
PG&E | 2018-08-20 | 9:34 | 39.8014 | -121.5813 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100400441 | Unknown | 12000 | Conductor | Overhead | Yes | 43332 | 0.39861 | Contact From Object | N.A. | Other | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1849 | 2018 | 8 | 20 | 9 | 34 | 18-0071596 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 394259 | 5.4464 | 175_338 | <25mph | <15mph | HFTD - Distribution | 2018-08-20 09:34:00 | 1588 | 11.8754 | FALSE | <25mph | C4565 | 3.06 | 2018-08-20T06:53:00Z | 3 | 6 | < 25mph | JBGC1 | 6.67 | 2018-08-20T06:13:00Z | 11.01 | 28 | < 25mph | C4565 | 3.06 | 2018-08-20T07:53:00Z | 3 | 12 | < 25mph | JBGC1 | 6.67 | 2018-08-20T07:13:00Z | 11.01 | 54 | < 25mph
PG&E | 2018-08-21 | 10:13 | 38.6972 | -120.889 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101385436 | Unknown | 12000 | Conductor | Overhead | Yes | 43333 | 0.42569 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1852 | 2018 | 8 | 21 | 10 | 13 | 18-0072055 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4572 | 5.9109 | 204_277 | <25mph | <15mph | HFTD - Distribution | 2018-08-21 10:13:00 | 1591 | 12.0437 | FALSE | <25mph | PG106 | 1.36 | 2018-08-21T06:40:00Z | 9.22 | 57 | < 25mph | PG073 | 6.99 | 2018-08-21T06:40:00Z | 11.63 | 142 | < 25mph | PG106 | 1.36 | 2018-08-21T06:40:00Z | 9.22 | 111 | < 25mph | PG073 | 6.99 | 2018-08-21T06:40:00Z | 11.63 | 274 | < 25mph
PG&E | 2018-08-22 | 17:24 | 37.9519 | -120.3103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101030620 | Unknown | 17000 | Conductor | Overhead | Yes | 43334 | 0.725 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | dampeners | no-match | 1853 | 2018 | 8 | 22 | 17 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 10.7586 | 229_236 | <25mph | <15mph | HFTD - Distribution | 2018-08-22 17:24:00 | 1592 | 13.1476 | FALSE | <25mph | PG029 | 2.2 | 2018-08-22T06:00:00Z | 4.61 | 18 | < 25mph | PG061 | 6.32 | 2018-08-22T06:40:00Z | 5.03 | 39 | < 25mph | PG031 | 2.51 | 2018-08-22T08:00:00Z | 6.58 | 34 | < 25mph | PG031 | 2.51 | 2018-08-22T08:00:00Z | 6.58 | 73 | < 25mph
PG&E | 2018-08-22 | 21:56 | 39.0425 | -120.9695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100024728 | Verizon | 12000 | Conductor | Overhead | Yes | 43334 | 0.91389 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1854 | 2018 | 8 | 22 | 21 | 56 | 18-0072654 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29727 | 9.3137 | 201_296 | <25mph | <15mph | HFTD - Distribution | 2018-08-22 21:56:00 | 1593 | 10.5291 | FALSE | <25mph | D9434 | 1.28 | 2018-08-22T07:00:00Z | 0 | 11 | < 25mph | PG032 | 6.31 | 2018-08-22T06:40:00Z | 7 | 44 | < 25mph | D9434 | 1.28 | 2018-08-22T08:00:00Z | 0 | 21 | < 25mph | PG032 | 6.31 | 2018-08-22T07:40:00Z | 7 | 84 | < 25mph
PG&E | 2018-08-24 | 5:03 | 39.1184 | -121.0154 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JIM SMITH BATT CHIEF 3 | 100097647 | Unknown | 12000 | Conductor | Overhead | Yes | 43336 | 0.21042 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1858 | 2018 | 8 | 24 | 5 | 3 | 18-0073024 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 4048 | 6.5682 | 199_301 | <25mph | <15mph | HFTD - Distribution | 2018-08-24 05:03:00 | 1597 | 12.3049 | FALSE | <25mph | AT999 | 2.07 | 2018-08-24T07:00:00Z | 0 | 11 | < 25mph | PG059 | 6.98 | 2018-08-24T06:40:00Z | 6.58 | 79 | < 25mph | AT999 | 2.07 | 2018-08-24T07:15:00Z | 2.01 | 21 | < 25mph | PG059 | 6.98 | 2018-08-24T07:10:00Z | 8.12 | 153 | < 25mph
PG&E | 2018-08-26 | 15:29 | 39.3599 | -121.1209 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100107472 | Unknown | 12000 | Conductor | Overhead | Yes | 43338 | 0.64514 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1860 | 2018 | 8 | 26 | 15 | 29 | 18-0073601 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 36162 | 13.8191 | 194_314 | <25mph | <15mph | HFTD - Distribution | 2018-08-26 15:29:00 | 1599 | 13.8191 | FALSE | <25mph | RRRC1 | 3.9 | 2018-08-26T06:13:00Z | 4.99 | 1 | < 25mph | RRRC1 | 3.9 | 2018-08-26T06:13:00Z | 4.99 | 27 | < 25mph | RRRC1 | 3.9 | 2018-08-26T07:13:00Z | 7 | 2 | < 25mph | RRRC1 | 3.9 | 2018-08-26T07:13:00Z | 7 | 52 | < 25mph
PG&E | 2018-08-28 | 12:50 | 40.2139 | -123.5966 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100994840 | Unknown | 12000 | Conductor | Overhead | Yes | 43340 | 0.53472 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1866 | 2018 | 8 | 28 | 12 | 50 | 18-0074371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 82754 | 9.6027 | 90_363 | <25mph | <15mph | HFTD - Distribution | 2018-08-28 12:50:00 | 1605 | 19.5452 | FALSE | <25mph | ALDC1 | 1.95 | 2018-08-28T06:51:00Z | 3 | 1 | < 25mph | ALDC1 | 1.95 | 2018-08-28T06:51:00Z | 3 | 1 | < 25mph | ALDC1 | 1.95 | 2018-08-28T06:51:00Z | 3 | 2 | < 25mph | ALDC1 | 1.95 | 2018-08-28T06:51:00Z | 3 | 2 | < 25mph
PG&E | 2018-08-31 | 13:02 | 40.4775 | -122.4847 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103918932 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 0.54306 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1872 | 2018 | 8 | 31 | 13 | 2 | 18-0075616 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18300 | 0.9461 | 137_376 | <25mph | <15mph | HFTD - Distribution | 2018-08-31 13:02:00 | 1611 | 11.7486 | FALSE | <25mph | PG086 | 3.07 | 2018-08-31T07:00:00Z | 0 | 12 | < 25mph | MMOC1 | 6.41 | 2018-08-31T06:00:00Z | 11.01 | 14 | < 25mph | PG086 | 3.07 | 2018-08-31T08:00:00Z | 1.74 | 22 | < 25mph | MMOC1 | 6.41 | 2018-08-31T06:00:00Z | 11.01 | 25 | < 25mph
PG&E | 2018-08-31 | 18:04 | 39.5785 | -123.3842 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102196393 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 0.75278 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1873 | 2018 | 8 | 31 | 18 | 4 | 18-0075741 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18540 | 15.395 | 98_327 | <25mph | <15mph | HFTD - Distribution | 2018-08-31 18:04:00 | 1612 | 16.0884 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RDVC1 | 7.03 | 2018-08-31T06:28:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | RDVC1 | 7.03 | 2018-08-31T07:28:00Z | 7 | 2 | < 25mph
PG&E | 2018-09-01 | 14:25 | 36.8088 | -121.5916 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Twr 35/222 | None | 115000 | Conductor | Overhead | Yes | 43344 | 0.60069 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1875 | 2018 | 9 | 1 | 14 | 25 | INT-11331 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 702145 | 13.8683 | 173_173 | <25mph | <15mph | HFTD - Transmission | 2018-09-01 14:25:00 | 1614 | 16.3299 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AP200 | 7.05 | 2018-09-01T06:58:00Z | 0 | 3 | < 25mph |  |  |  | 0 | 0 | No data | AP200 | 7.05 | 2018-09-01T07:53:00Z | 0 | 6 | < 25mph
PG&E | 2018-09-02 | 15:36 | 37.4714 | -122.4248 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Arie Delay 659-740-4636 | 103808872 | Unknown | 12000 | Capacitor Bank | Overhead | Yes | 43345 | 0.65 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1876 | 2018 | 9 | 2 | 15 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 11.73 | 137_210 | <25mph | <15mph | HFTD - Distribution | 2018-09-02 15:36:00 | 1615 | 13.6047 | FALSE | <25mph |  |  |  | 0 | 0 | No data | HSPC1 | 6.33 | 2018-09-02T06:18:00Z | 13 | 45 | < 25mph |  |  |  | 0 | 0 | No data | HSPC1 | 6.33 | 2018-09-02T07:18:00Z | 13 | 90 | < 25mph
PG&E | 2018-09-03 | 18:29 | 39.4547 | -121.4955 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100395672 | Unknown | 12000 | Conductor | Overhead | Yes | 43346 | 0.77014 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1880 | 2018 | 9 | 3 | 18 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 6.2719 | 178_319 | <25mph | <15mph | HFTD - Distribution | 2018-09-03 18:29:00 | 1619 | 14.7897 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TT309 | 4.73 | 2018-09-03T06:45:00Z | 4 | 2 | < 25mph |  |  |  | 0 | 0 | No data | TT309 | 4.73 | 2018-09-03T06:45:00Z | 4 | 4 | < 25mph
PG&E | 2018-09-05 | 16:55 | 37.4655 | -119.9005 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JON BERRY 209-966-4700 | 101087053 | Unknown | 21000 | Conductor | Overhead | Yes | 43348 | 0.70486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1882 | 2018 | 9 | 5 | 16 | 55 | 18-0076909 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 4017 | 13.8551 | 248_210 | <25mph | <15mph | HFTD - Distribution | 2018-09-05 16:55:00 | 1621 | 17.3022 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E9110 | 4.85 | 2018-09-05T06:36:00Z | 8.01 | 6 | < 25mph |  |  |  | 0 | 0 | No data | E9110 | 4.85 | 2018-09-05T06:36:00Z | 8.01 | 12 | < 25mph
PG&E | 2018-09-06 | 16:19 | 39.0904 | -120.9464 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 100020676 | Unknown | 12000 | Conductor | Overhead | Yes | 43349 | 0.67986 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1886 | 2018 | 9 | 6 | 16 | 19 | 18-0077280 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 30780 | 10.0605 | 202_299 | <25mph | <15mph | HFTD - Distribution | 2018-09-06 16:19:00 | 1625 | 12.3694 | FALSE | <25mph | D9434 | 3.62 | 2018-09-06T06:00:00Z | 4 | 9 | < 25mph | PG032 | 7.62 | 2018-09-06T06:50:00Z | 7 | 46 | < 25mph | D9434 | 3.62 | 2018-09-06T06:00:00Z | 4 | 17 | < 25mph | PG032 | 7.62 | 2018-09-06T07:10:00Z | 7.25 | 89 | < 25mph
PG&E | 2018-09-09 | 4:25 | 38.6534 | -122.8538 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 13/1 | None | 60000 | Conductor | Overhead | Yes | 43352 | 0.18403 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1887 | 2018 | 9 | 9 | 4 | 25 | INT-11353 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 7.8888 | 120_276 | <25mph | <15mph | HFTD - Transmission | 2018-09-09 04:25:00 | 1626 | 22.3261 | FALSE | <25mph | PICWW | 2.16 | 2018-09-09T06:00:00Z | 11.21 | 15 | < 25mph | PG082 | 5.77 | 2018-09-09T06:30:00Z | 19.95 | 38 | < 25mph | PICWW | 2.16 | 2018-09-09T06:00:00Z | 11.21 | 26 | < 25mph | PG082 | 5.77 | 2018-09-09T06:30:00Z | 19.95 | 65 | < 25mph
PG&E | 2018-09-10 | 20:37 | 38.0188 | -122.7225 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 102252760 | Unknown | 12000 | Conductor | Overhead | Yes | 43353 | 0.85903 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1889 | 2018 | 9 | 10 | 20 | 37 | 18-0078359 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 219903 | 12.2581 | 125_241 | <25mph | <15mph | HFTD - Distribution | 2018-09-10 20:37:00 | 1628 | 18.8462 | FALSE | <25mph | BBEC1 | 1.27 | 2018-09-10T06:11:00Z | 14.99 | 8 | < 25mph | WDAC1 | 4.66 | 2018-09-10T06:51:00Z | 18.99 | 50 | < 25mph | BBEC1 | 1.27 | 2018-09-10T06:11:00Z | 14.99 | 15 | < 25mph | WDAC1 | 4.66 | 2018-09-10T07:51:00Z | 22.01 | 95 | < 25mph
PG&E | 2018-09-11 | 5:23 | 37.376 | -119.6304 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | TROY CHEEK 209-966-3621 | 101023184 | Unknown | 12000 | Conductor | Overhead | Yes | 43354 | 0.22431 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1891 | 2018 | 9 | 11 | 5 | 23 | 18-0078387 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 288 | 4.3046 | 260_205 | <25mph | <15mph | HFTD - Distribution | 2018-09-11 05:23:00 | 1630 | 11.3584 | FALSE | <25mph | BSNC1 | 0.17 | 2018-09-11T06:48:00Z | 8.01 | 23 | < 25mph | MIAC1 | 6.99 | 2018-09-11T06:59:00Z | 8.99 | 67 | < 25mph | BSNC1 | 0.17 | 2018-09-11T07:48:00Z | 10 | 49 | < 25mph | MIAC1 | 6.99 | 2018-09-11T07:59:00Z | 10 | 134 | < 25mph
PG&E | 2018-09-14 | 15:08 | 35.328 | -120.6982 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Sean Hernandez Cell # 805 903 3423 | 103400199 | Unknown | 12000 | Conductor | Overhead | Yes | 43357 | 0.63056 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1898 | 2018 | 9 | 14 | 15 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 24.1105 | 213_92 | <25mph | <15mph | HFTD - Distribution | 2018-09-14 15:08:00 | 1637 | 24.1304 | FALSE | <25mph | ARGC1 | 2.05 | 2018-09-14T06:54:00Z | 2.01 | 1 | < 25mph | F2489 | 7.42 | 2018-09-14T06:30:00Z | 8.01 | 17 | < 25mph | ARGC1 | 2.05 | 2018-09-14T07:54:00Z | 3 | 2 | < 25mph | F2489 | 7.42 | 2018-09-14T06:30:00Z | 8.01 | 35 | < 25mph
PG&E | 2018-09-16 | 8:26 | 35.3046 | -120.6389 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | Pole 4/23A | None | 70000 | Conductor | Overhead | Yes | 43359 | 0.35139 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1903 | 2018 | 9 | 16 | 8 | 26 | INT-11371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 29925 | 32.6873 | 216_90 | 25-40mph | 30-45mph | HFTD - Transmission | 2018-09-16 08:26:00 | 1642 | 35.3808 | FALSE | 25-40mph | ARGC1 | 2.25 | 2018-09-16T06:54:00Z | 2.01 | 1 | < 25mph | ARGC1 | 2.25 | 2018-09-16T06:54:00Z | 2.01 | 5 | < 25mph | ARGC1 | 2.25 | 2018-09-16T07:54:00Z | 3 | 2 | < 25mph | ARGC1 | 2.25 | 2018-09-16T07:54:00Z | 3 | 10 | < 25mph
PG&E | 2018-09-21 | 21:10 | 39.0273 | -122.6627 | Vegetation | Rural | < 3 meters | Customer | N.A. | 102147414 | Unknown | 12000 | Conductor | Overhead | Yes | 43364 | 0.88194 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1908 | 2018 | 9 | 21 | 21 | 10 | 18-0082278 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 281055 | 11.7868 | 128_296 | <25mph | <15mph | HFTD - Distribution | 2018-09-21 21:10:00 | 1647 | 15.5314 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG097 | 7.92 | 2018-09-21T06:50:00Z | 2.19 | 14 | < 25mph |  |  |  | 0 | 0 | No data | PG115 | 4.77 | 2018-09-21T07:20:00Z | 3.51 | 26 | < 25mph
PG&E | 2018-09-21 | 23:02 | 38.6428 | -122.7453 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102218862 | Unknown | 12000 | Conductor | Overhead | Yes | 43364 | 0.95972 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1909 | 2018 | 9 | 21 | 23 | 2 | 18-0082304 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 9470 | 7.2054 | 124_275 | <25mph | <15mph | HFTD - Distribution | 2018-09-21 23:02:00 | 1648 | 14.1592 | FALSE | <25mph | E3235 | 2.39 | 2018-09-21T06:59:00Z | 0 | 12 | < 25mph | PG038 | 6.21 | 2018-09-21T07:00:00Z | 3.51 | 41 | < 25mph | E3235 | 2.39 | 2018-09-21T07:59:00Z | 0 | 23 | < 25mph | PG038 | 6.21 | 2018-09-21T07:40:00Z | 3.51 | 78 | < 25mph
PG&E | 2018-09-24 | 0:35 | 39.8152 | -121.6438 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Pole 3/42B | None | 60000 | Conductor | Overhead | Yes | 43367 | 0.024306 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1913 | 2018 | 9 | 24 | 0 | 35 | INT-11388 | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 2407691 | 10.8571 | 172_339 | <25mph | <15mph | HFTD - Transmission | 2018-09-24 00:35:00 | 1652 | 11.6135 | FALSE | <25mph | C8878 | 3.93 | 2018-09-24T06:58:00Z | 3 | 25 | < 25mph | CSTC1 | 7.71 | 2018-09-24T06:51:00Z | 5.99 | 40 | < 25mph | C8878 | 3.93 | 2018-09-24T07:43:00Z | 4 | 47 | < 25mph | CSTC1 | 7.71 | 2018-09-24T07:51:00Z | 8.01 | 75 | < 25mph
PG&E | 2018-09-27 | 12:43 | 38.5148 | -122.4463 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Twr 000/010 | None | 60000 | Conductor | Overhead | Yes | 43370 | 0.52986 | Contact From Object | N.A. | Other | Electric Facility | Human Error | helicopter | no-match | 1917 | 2018 | 9 | 27 | 12 | 43 | INT-11394 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1488992 | 4.4433 | 137_268 | <25mph | <15mph | HFTD - Transmission | 2018-09-27 12:43:00 | 1656 | 10.4879 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG018 | 4.41 | 2018-09-27T06:10:00Z | 3.51 | 21 | < 25mph |  |  |  | 0 | 0 | No data | PG018 | 4.41 | 2018-09-27T08:00:00Z | 3.51 | 39 | < 25mph
PG&E | 2018-09-29 | 16:16 | 41.0219 | -123.655 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Hoopa Fire Dept | 100962165 | Unknown | 12000 | Conductor | Overhead | Yes | 43372 | 0.67778 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1923 | 2018 | 9 | 29 | 16 | 16 | 18-0084877 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 16028 | 7.8421 | 89_407 | <25mph | <15mph | HFTD - Distribution | 2018-09-29 16:16:00 | 1662 | 11.5265 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BHTC1 | 7.5 | 2018-09-29T06:46:00Z | 13 | 6 | < 25mph |  |  |  | 0 | 0 | No data | BHTC1 | 7.5 | 2018-09-29T07:46:00Z | 21 | 9 | < 25mph
PG&E | 2018-10-07 | 1:44 | 37.178 | -122.0267 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Mike Mathiesen 408-472-1613 Incident # SCU7096 | 100518363 | Unknown | 12000 | Conductor | Overhead | Yes | 43380 | 0.072222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1929 | 2018 | 10 | 7 | 1 | 44 | 18-0087807 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 224444 | 25.0906 | 154_194 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-07 01:44:00 | 1668 | 25.864 | FALSE | 25-40mph | PG050 | 2.46 | 2018-10-07T06:30:00Z | 14.25 | 11 | < 25mph | PG057 | 6.61 | 2018-10-07T06:20:00Z | 21.92 | 140 | < 25mph | PG050 | 2.46 | 2018-10-07T07:50:00Z | 16.67 | 21 | < 25mph | PG057 | 6.61 | 2018-10-07T07:40:00Z | 23.67 | 274 | < 25mph
PG&E | 2018-10-08 | 11:03 | 38.2621 | -122.7881 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101987186 | AT&T | 12000 | Conductor | Overhead | No | N.A. | N.A. | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1933 | 2018 | 10 | 8 | 11 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 15.6859 | 122_254 | <25mph | <15mph | HFTD - Distribution | 2018-10-08 11:03:00 | 1672 | 17.3485 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F2270 | 5.08 | 2018-10-08T06:04:00Z | 10 | 16 | < 25mph |  |  |  | 0 | 0 | No data | F2270 | 5.08 | 2018-10-08T06:04:00Z | 10 | 32 | < 25mph
PG&E | 2018-10-14 | 11:40 | 40.3598 | -122.4388 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TOM STROING 530-200-5113 | 101506416 | AT&T | 12000 | Conductor | Overhead | Yes | 43387 | 0.48611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1938 | 2018 | 10 | 14 | 11 | 40 | 18-0090193 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 945 | 30.6414 | 139_370 | 25-40mph | 30-45mph | HFTD - Distribution | 2018-10-14 11:40:00 | 1677 | 30.6414 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E7114 | 4.61 | 2018-10-14T06:00:00Z | 10 | 5 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 4.61 | 2018-10-14T07:45:00Z | 10 | 8 | < 25mph
PG&E | 2018-10-14 | 19:39 | 38.446 | -120.5147 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | IC- Dillon Gissell- 209-295-7735 | 103384485 | Unknown | 12000 | Conductor | Overhead | Yes | 43387 | 0.81875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1939 | 2018 | 10 | 14 | 19 | 39 | 18-0090288 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3497327 | 25.4932 | 220_264 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-14 19:39:00 | 1678 | 30.9108 | FALSE | 25-40mph | C9148 | 3.52 | 2018-10-14T06:34:00Z | 22.01 | 18 | < 25mph | C9148 | 3.52 | 2018-10-14T06:34:00Z | 22.01 | 37 | < 25mph | C9148 | 3.52 | 2018-10-14T06:34:00Z | 22.01 | 34 | < 25mph | C9148 | 3.52 | 2018-10-14T06:34:00Z | 22.01 | 69 | < 25mph
PG&E | 2018-10-14 | 20:08 | 38.8935 | -120.8497 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103674516 | Unknown | 21000 | Conductor | Overhead | Yes | 43387 | 0.83889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1940 | 2018 | 10 | 14 | 20 | 8 | 18-0090299 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 48095 | 8.663 | 206_288 | <25mph | <15mph | HFTD - Distribution | 2018-10-14 20:08:00 | 1679 | 24.0259 | FALSE | <25mph | PG033 | 2.11 | 2018-10-14T07:00:00Z | 6.13 | 27 | < 25mph | BDMC1 | 7.81 | 2018-10-14T06:36:00Z | 17 | 35 | < 25mph | PG033 | 2.11 | 2018-10-14T07:00:00Z | 6.13 | 51 | < 25mph | BDMC1 | 7.81 | 2018-10-14T06:36:00Z | 17 | 66 | < 25mph
PG&E | 2018-10-15 | 3:23 | 38.2897 | -120.5803 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103378003 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43388 | 0.14097 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1941 | 2018 | 10 | 15 | 3 | 23 | 18-0090342 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1464 | 26.0611 | 218_255 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-15 03:23:00 | 1680 | 26.2858 | FALSE | 25-40mph | AT317 | 3.74 | 2018-10-15T06:50:00Z | 23 | 13 | < 25mph | ESPC1 | 4.93 | 2018-10-15T06:13:00Z | 44.98 | 26 | 40-55mph | AT317 | 3.74 | 2018-10-15T06:50:00Z | 23 | 25 | < 25mph | ESPC1 | 4.93 | 2018-10-15T07:13:00Z | 47 | 50 | 40-55mph
PG&E | 2018-10-16 | 10:44 | 40.5097 | -124.1624 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101004106 | Unknown | 12000 | Conductor | Overhead | Yes | 43389 | 0.44722 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1942 | 2018 | 10 | 16 | 10 | 44 | 18-0090952 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 2081 | 4.5851 | 67_380 | <25mph | <15mph | HFTD - Distribution | 2018-10-16 10:44:00 | 1681 | 13.3626 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C5061 | 4.32 | 2018-10-16T07:00:00Z | 0 | 7 | < 25mph |  |  |  | 0 | 0 | No data | C5061 | 4.32 | 2018-10-16T07:59:00Z | 0 | 14 | < 25mph
PG&E | 2018-10-16 | 16:30 | 38.7754 | -122.8976 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MARK GRADEK (707) 889-4303 | 101962692 | AT&T | 12000 | Conductor | Overhead | Yes | 43389 | 0.6875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1943 | 2018 | 10 | 16 | 16 | 30 | 18-0091127 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 744 | 10.3513 | 118_282 | <25mph | <15mph | HFTD - Distribution | 2018-10-16 16:30:00 | 1682 | 19.9126 | FALSE | <25mph | PG090 | 1.05 | 2018-10-16T06:20:00Z | 4.38 | 7 | < 25mph | PG125 | 5.67 | 2018-10-16T07:00:00Z | 14.25 | 26 | < 25mph | PG090 | 1.05 | 2018-10-16T07:20:00Z | 10.29 | 13 | < 25mph | HWKC1 | 4.29 | 2018-10-16T07:56:00Z | 18.99 | 49 | < 25mph
PG&E | 2018-10-20 | 14:31 | 40.5218 | -124.1137 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Str. 003/000 | None | 60000 | Conductor | Overhead | Yes | 43393 | 0.60486 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1947 | 2018 | 10 | 20 | 14 | 31 | INT-11477 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 410982 | 9.6901 | 69_380 | <25mph | <15mph | HFTD - Transmission | 2018-10-20 14:31:00 | 1686 | 10.3412 | FALSE | <25mph | AT493 | 3.34 | 2018-10-20T06:58:00Z | 4.99 | 22 | < 25mph | AT493 | 3.34 | 2018-10-20T06:58:00Z | 4.99 | 22 | < 25mph | AT493 | 3.34 | 2018-10-20T07:18:00Z | 4.99 | 43 | < 25mph | AT493 | 3.34 | 2018-10-20T07:18:00Z | 4.99 | 43 | < 25mph
PG&E | 2018-10-21 | 0:32 | 35.5035 | -120.6025 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101886776 | Unknown | 21000 | Conductor | Overhead | Yes | 43394 | 0.022222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1948 | 2018 | 10 | 21 | 0 | 32 | 18-0092526 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 302559 | 9.0366 | 217_101 | <25mph | <15mph | HFTD - Distribution | 2018-10-21 00:32:00 | 1687 | 16.4549 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TT469 | 4.38 | 2018-10-21T06:14:00Z | 4 | 28 | < 25mph |  |  |  | 0 | 0 | No data | TT469 | 4.38 | 2018-10-21T07:14:00Z | 4 | 55 | < 25mph
PG&E | 2018-10-24 | 7:08 | 37.9475 | -120.2671 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SCOTT PITTMAN 209-768-8182 TCU INCIDENT# 012528 | 101047865 | Unknown | 17000 | Conductor | Overhead | Yes | 43397 | 0.29722 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1949 | 2018 | 10 | 24 | 7 | 8 | 18-0093599 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 13433 | 8.6394 | 231_236 | <25mph | <15mph | HFTD - Distribution | 2018-10-24 07:08:00 | 1688 | 12.0171 | FALSE | <25mph | PG031 | 1.92 | 2018-10-24T07:00:00Z | 6.35 | 19 | < 25mph | PG166 | 7.04 | 2018-10-24T06:50:00Z | 11.83 | 54 | < 25mph | PG031 | 1.92 | 2018-10-24T07:40:00Z | 7.9 | 35 | < 25mph | PG166 | 7.04 | 2018-10-24T06:50:00Z | 11.83 | 100 | < 25mph
PG&E | 2018-10-24 | 14:18 | 36.7265 | -119.1086 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CHRIS CHRISTOPHERSON (559)493-4320 I.C #18CAFKUO15649 | 100691946 | None | 12000 | Conductor | Overhead | Yes | 43397 | 0.59583 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1950 | 2018 | 10 | 24 | 14 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 7.8375 | 283_170 | <25mph | <15mph | HFTD - Distribution | 2018-10-24 14:18:00 | 1689 | 7.8887 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PHRC1 | 5.37 | 2018-10-24T06:58:00Z | 8.99 | 17 | < 25mph |  |  |  | 0 | 0 | No data | PHRC1 | 5.37 | 2018-10-24T07:58:00Z | 10 | 34 | < 25mph
PG&E | 2018-11-01 | 20:45 | 38.372 | -123.0507 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103852431 | AT&T | 12000 | Conductor | Overhead | Yes | 43405 | 0.86458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1958 | 2018 | 11 | 1 | 20 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.9426 | 111_260 | <25mph | <15mph | HFTD - Distribution | 2018-11-01 20:45:00 | 1697 | 13.8199 | FALSE | <25mph | BBYC1 | 3.77 | 2018-11-01T07:00:00Z | 0.51 | 2 | < 25mph | BDZC1 | 4.05 | 2018-11-01T06:10:00Z | 6.51 | 20 | < 25mph | BBYC1 | 3.77 | 2018-11-01T08:00:00Z | 0.85 | 3 | < 25mph | BDZC1 | 4.05 | 2018-11-01T08:00:00Z | 7.02 | 38 | < 25mph
PG&E | 2018-11-09 | 4:49 | 39.8234 | -121.8382 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100402367 | AT&T | 12000 | Conductor | Overhead | Yes | 43413 | 0.20069 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1963 | 2018 | 11 | 9 | 4 | 49 | 18-0098482 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 11900 | 0.23999 | 164_340 | <25mph | <15mph | HFTD - Distribution | 2018-11-09 04:49:00 | 1703 | 7.1467 | FALSE | <25mph | D8132 | 3.69 | 2018-11-09T07:15:00Z | 2.01 | 5 | < 25mph | CSTC1 | 4.96 | 2018-11-09T07:51:00Z | 8.01 | 13 | < 25mph | D8132 | 3.69 | 2018-11-09T08:45:00Z | 3 | 8 | < 25mph | CSTC1 | 4.96 | 2018-11-09T07:51:00Z | 8.01 | 23 | < 25mph
PG&E | 2018-11-09 | 8:59 | 37.2809 | -122.1214 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100546562 | AT&T | 12000 | Conductor | Overhead | Yes | 43413 | 0.37431 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1964 | 2018 | 11 | 9 | 8 | 59 | 18-0098521 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 77077 | 5.2345 | 150_200 | <25mph | <15mph | HFTD - Distribution | 2018-11-09 08:59:00 | 1704 | 17.3931 | FALSE | <25mph | E0516 | 1.72 | 2018-11-09T08:00:00Z | 17 | 39 | < 25mph | PG152 | 4.64 | 2018-11-09T07:20:00Z | 31.14 | 172 | 25-40mph | E0516 | 1.72 | 2018-11-09T09:00:00Z | 21 | 75 | < 25mph | PG152 | 4.64 | 2018-11-09T07:20:00Z | 31.14 | 331 | 25-40mph
PG&E | 2018-11-10 | 13:31 | 37.0467 | -121.9853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101671641 | Unknown | 21000 | Conductor | Overhead | Yes | 43414 | 0.56319 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1966 | 2018 | 11 | 10 | 13 | 31 | 18-0098856 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 1482 | 7.3629 | 156_187 | <25mph | <15mph | HFTD - Distribution | 2018-11-10 13:31:00 | 1706 | 13.8913 | FALSE | <25mph | PG062 | 2.37 | 2018-11-10T08:00:00Z | 9.86 | 45 | < 25mph | PG004 | 7.89 | 2018-11-10T07:10:00Z | 11.83 | 186 | < 25mph | PG062 | 2.37 | 2018-11-10T08:20:00Z | 10.96 | 84 | < 25mph | PG004 | 7.89 | 2018-11-10T07:10:00Z | 11.83 | 356 | < 25mph
PG&E | 2018-11-11 | 4:18 | 38.4341 | -122.5522 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102032588 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43415 | 0.17917 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1967 | 2018 | 11 | 11 | 4 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.8216 | 132_263 | <25mph | <15mph | HFTD - Distribution | 2018-11-11 04:18:00 | 1707 | 11.1813 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG091 | 4.41 | 2018-11-11T07:10:00Z | 23.24 | 26 | < 25mph |  |  |  | 0 | 0 | No data | PG091 | 4.41 | 2018-11-11T07:10:00Z | 23.24 | 50 | < 25mph
PG&E | 2018-11-13 | 15:41 | 37.0644 | -121.9578 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101680441 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43417 | 0.65347 | Other | N.A. | N.A. | N.A. | Human Error | Grow house | Other/Unknown | 1973 | 2018 | 11 | 13 | 15 | 41 | 18-0099492 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 21484 | 1.9347 | 157_188 | <25mph | <15mph | HFTD - Distribution | 2018-11-13 15:41:00 | 1713 | 13.1257 | FALSE | <25mph | PG062 | 0.72 | 2018-11-13T08:00:00Z | 5.91 | 41 | < 25mph | PG057 | 4.36 | 2018-11-13T07:20:00Z | 9.86 | 181 | < 25mph | PG062 | 0.72 | 2018-11-13T08:10:00Z | 6.35 | 79 | < 25mph | PG057 | 4.36 | 2018-11-13T07:20:00Z | 9.86 | 351 | < 25mph
PG&E | 2018-11-15 | 6:09 | 38.3599 | -122.3682 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102241814 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43419 | 0.25625 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1974 | 2018 | 11 | 15 | 6 | 9 | 18-0099862 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 441 | 10.2454 | 140_259 | <25mph | <15mph | HFTD - Distribution | 2018-11-15 06:09:00 | 1714 | 12.9788 | FALSE | <25mph | PG021 | 1.9 | 2018-11-15T07:20:00Z | 2.42 | 7 | < 25mph | PG021 | 1.9 | 2018-11-15T07:20:00Z | 2.42 | 21 | < 25mph | PG021 | 1.9 | 2018-11-15T08:20:00Z | 2.64 | 13 | < 25mph | PG021 | 1.9 | 2018-11-15T08:20:00Z | 2.64 | 39 | < 25mph
PG&E | 2018-11-15 | 6:34 | 38.6082 | -120.9532 | Vegetation | Rural | < 0.25 Acres | Self Extinguished | N.A. | 101414740 | Unknown | 12000 | Conductor | Overhead | Yes | 43419 | 0.27361 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1975 | 2018 | 11 | 15 | 6 | 34 | 18-0099901 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 5325 | 11.5356 | 201_273 | <25mph | <15mph | HFTD - Distribution | 2018-11-15 06:34:00 | 1715 | 14.51 | FALSE | <25mph | BENC1 | 1.6 | 2018-11-15T07:59:00Z | 7 | 21 | < 25mph | BENC1 | 1.6 | 2018-11-15T07:59:00Z | 7 | 108 | < 25mph | BENC1 | 1.6 | 2018-11-15T08:59:00Z | 7 | 40 | < 25mph | E4740 | 7.49 | 2018-11-15T08:58:00Z | 8.99 | 206 | < 25mph
PG&E | 2018-11-16 | 17:02 | 38.7574 | -120.9012 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101409894 | AT&T | 21000 | Conductor | Overhead | Yes | 43420 | 0.70972 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1976 | 2018 | 11 | 16 | 17 | 2 | 18-0100490 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 119860 | 5.5125 | 204_281 | <25mph | <15mph | HFTD - Distribution | 2018-11-16 17:02:00 | 1716 | 12.5682 | FALSE | <25mph | PG106 | 3.02 | 2018-11-16T07:40:00Z | 5.03 | 33 | < 25mph | PG068 | 7.29 | 2018-11-16T08:00:00Z | 6.8 | 136 | < 25mph | PG106 | 3.02 | 2018-11-16T09:00:00Z | 5.26 | 63 | < 25mph | PG068 | 7.29 | 2018-11-16T08:10:00Z | 8.55 | 264 | < 25mph
PG&E | 2018-11-17 | 17:20 | 38.7082 | -120.6927 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101421319 | Unknown | 12000 | Conductor | Overhead | Yes | 43421 | 0.72222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1977 | 2018 | 11 | 17 | 17 | 20 | 18-0100697 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 35749 | 6.6792 | 213_278 | <25mph | <15mph | HFTD - Distribution | 2018-11-17 17:20:00 | 1717 | 12.841 | FALSE | <25mph | PG077 | 1.14 | 2018-11-17T07:50:00Z | 1.32 | 14 | < 25mph | PG104 | 6.43 | 2018-11-17T08:00:00Z | 13.8 | 72 | < 25mph | PG077 | 1.14 | 2018-11-17T07:50:00Z | 1.32 | 25 | < 25mph | PG104 | 6.43 | 2018-11-17T08:10:00Z | 14.03 | 137 | < 25mph
PG&E | 2018-12-12 | 12:09 | 38.727 | -120.7947 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 101404403 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43446 | 0.50625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1984 | 2018 | 12 | 12 | 12 | 9 | No ILIS or TOTL available | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.1462 | 208_279 | <25mph | <15mph | HFTD - Distribution | 2018-12-12 12:09:00 | 1724 | 13.5134 | FALSE | <25mph | PG068 | 1.89 | 2018-12-12T08:00:00Z | 4.16 | 37 | < 25mph | PG027 | 6.17 | 2018-12-12T08:00:00Z | 7 | 76 | < 25mph | PG068 | 1.89 | 2018-12-12T08:00:00Z | 4.16 | 73 | < 25mph | PG027 | 6.17 | 2018-12-12T08:50:00Z | 8.32 | 148 | < 25mph
PG&E | 2018-12-14 | 10:32 | 40.4379 | -123.7834 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101009136 | Unknown | 12000 | Conductor | Overhead | Yes | 43448 | 0.43889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1985 | 2018 | 12 | 14 | 10 | 32 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 36.1442 | 82_375 | 25-40mph | 30-45mph | HFTD - Distribution | 2018-12-14 10:32:00 | 1725 | 36.1442 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PG204 | 5.47 | 2018-12-14T07:50:00Z | 2.64 | 7 | < 25mph |  |  |  | 0 | 0 | No data | PG204 | 5.47 | 2018-12-14T08:40:00Z | 3.51 | 13 | < 25mph
1. Butte | 2015-09-09 | 14:26 | 38.3297 | -120.7042 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1987 | 2015 | 9 | 9 | 14 | 26 |  | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 1353755 | 12.0917 | 212_257 | <25mph | <15mph | HFTD - Distribution | 2015-09-09 14:26:00 | 332 | 14.8248 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 5.02 | 2015-09-09T06:56:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 5.02 | 2015-09-09T07:56:00Z | 8.99 | 2 | < 25mph
2. Cascade (Neu Wind Complex) | 2017-10-08 | 23:45 | 39.322 | -121.4021 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1988 | 2017 | 10 | 8 | 23 | 45 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Equip Failure | Conductor | 0 | 17.3686 | 182_312 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 23:45:00 | 1213 | 29.7104 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | BNGC1 | 4.15 | 2017-10-08T06:51:00Z | 3 | 1 | < 25mph |  |  |  | 0 | 0 | No data | BNGC1 | 4.15 | 2017-10-08T07:51:00Z | 3 | 2 | < 25mph
3. Redwood Valley (Mendocino Lake Complex) | 2017-10-08 | 23:36 | 39.2487 | -123.1663 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1989 | 2017 | 10 | 8 | 23 | 36 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 24.7673 | 107_309 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 23:36:00 | 1212 | 30.3049 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E7513 | 5.24 | 2017-10-08T06:28:00Z | 3 | 25 | < 25mph |  |  |  | 0 | 0 | No data | E7513 | 5.24 | 2017-10-08T06:28:00Z | 3 | 49 | < 25mph
4. Nuns (Central LNU Complex) | 2017-10-08 | 22:00 | 38.4041 | -122.5209 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1990 | 2017 | 10 | 8 | 22 | 0 |  | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 45.6439 | 134_262 | 40-55mph | >=45mph | HFTD - Distribution | 2017-10-08 22:00:00 | 1207 | 46.2981 | FALSE | 40-55mph | KENWW | 1.15 | 2017-10-08T07:00:00Z | 4.61 | 6 | < 25mph | F11WW | 4.55 | 2017-10-08T07:00:00Z | 14.2 | 16 | < 25mph | KENWW | 1.15 | 2017-10-08T07:00:00Z | 4.61 | 11 | < 25mph | F11WW | 4.55 | 2017-10-08T07:00:00Z | 14.2 | 29 | < 25mph
5. Atlas (Southern LNU Complex) | 2017-10-08 | 21:52 | 38.3921 | -122.2437 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1991 | 2017 | 10 | 8 | 21 | 52 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 37.6357 | 146_261 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-08 21:52:00 | 1206 | 41.3099 | FALSE | 40-55mph | F0187 | 3.03 | 2017-10-08T07:00:00Z | 2.01 | 5 | < 25mph | ATLC1 | 5.83 | 2017-10-08T06:29:00Z | 10 | 6 | < 25mph | F0187 | 3.03 | 2017-10-08T07:00:00Z | 2.01 | 8 | < 25mph | ATLC1 | 5.83 | 2017-10-08T06:29:00Z | 10 | 15 | < 25mph
7. Camp Fire | 2018-11-08 | 6:33 | 39.8134 | -121.4347 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 60000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1993 | 2018 | 11 | 8 | 6 | 33 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Conductor | 826291590 | 33.1236 | 181_339 | 25-40mph | 30-45mph | HFTD - Transmission | 2018-11-08 06:33:00 | 1699 | 39.0185 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | JBGC1 | 6.08 | 2018-11-08T07:13:00Z | 44 | 1 | 40-55mph |  |  |  | 0 | 0 | No data | JBGC1 | 6.08 | 2018-11-08T08:13:00Z | 44.98 | 2 | 40-55mph
PG&E | 2019-01-16 | 0:17 | 38.0621 | -120.1964 | Vegetation | Conifer Forest | Structure Only | Cal Fire |  | 163661701 |  | 17000 | Conductor | Overhead | Yes | 43481 | 0.011806 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-01 | 2019 | 1 | 16 | 0 | 17 | 19-0010443 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1041827 | 14.8061 | 234_243 | <25mph | <15mph | HFTD - Distribution | 2019-01-16 00:17:00 | 1728 | 28.2081 | FALSE | 25-40mph | MOUC1 | 2.77 | 2019-01-16T07:02:00Z | 38.01 | 1 | 25-40mph | MOUC1 | 2.77 | 2019-01-16T07:02:00Z | 38.01 | 22 | 25-40mph | MOUC1 | 2.77 | 2019-01-16T07:02:00Z | 38.01 | 2 | 25-40mph | MOUC1 | 2.77 | 2019-01-16T07:02:00Z | 38.01 | 41 | 25-40mph
PG&E | 2019-03-13 | 16:08 | 39.8831 | -122.5498 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 6Fn0313191607 |  | 12000 | Conductor | Overhead | Yes | 43537 | 0.67222 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-194 | 2019 | 3 | 13 | 16 | 8 | 19-0033617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 21012 | 20.7105 | 134_343 | <25mph | <15mph | HFTD - Distribution | 2019-03-13 16:08:00 | 1734 | 26.4067 | FALSE | 25-40mph | TCKC1 | 3.76 | 2019-03-13T06:28:00Z | 13 | 1 | < 25mph | EPKC1 | 5.75 | 2019-03-13T06:03:00Z | 28.01 | 9 | 25-40mph | TCKC1 | 3.76 | 2019-03-13T07:28:00Z | 15.99 | 2 | < 25mph | EPKC1 | 5.75 | 2019-03-13T06:03:00Z | 28.01 | 17 | 25-40mph
PG&E | 2019-03-19 | 12:52 | 37.9956 | -120.3244 | Tree - cutting, 3rd party | Hardwood Forest | 1 meter - < 3 meters | Self Extinguished |  | 101045032 |  | 17000 | Conductor | Overhead | Yes | 43543 | 0.53611 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-187 | 2019 | 3 | 19 | 12 | 52 | 19-0035101 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 70602 | 12.9023 | 229_239 | <25mph | <15mph | HFTD - Distribution | 2019-03-19 12:52:00 | 1736 | 14.3226 | FALSE | <25mph | PG061 | 3.8 | 2019-03-19T07:00:00Z | 8.99 | 21 | < 25mph | PG166 | 7.85 | 2019-03-19T07:00:00Z | 18.86 | 68 | < 25mph | PG061 | 3.8 | 2019-03-19T08:00:00Z | 9.22 | 39 | < 25mph | PG166 | 7.85 | 2019-03-19T07:50:00Z | 20.4 | 127 | < 25mph
PG&E | 2019-04-09 | 14:07 | 34.6311 | -119.9813 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Fire Dept | Santa Barbra County FD | 101863014 |  | 12000 | Conductor | Overhead | Yes | 43564 | 0.58819 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-263 | 2019 | 4 | 9 | 14 | 7 | 19-0040969 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 70756 | 38.5369 | 246_53 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-09 14:07:00 | 1737 | 43.1384 | FALSE | 40-55mph |  |  |  | 0 | 0 | No data | SXWC1 | 5.08 | 2019-04-09T06:09:00Z | 7 | 13 | < 25mph |  |  |  | 0 | 0 | No data | UCSE | 5.53 | 2019-04-09T07:40:00Z | 7.2 | 23 | < 25mph
PG&E | 2019-04-09 | 15:27 | 37.7341 | -120.0776 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 101076921 |  | 21000 | Pole | Overhead | Yes | 43564 | 0.64375 | Vegetation |  | Veg. contact | Pole |  |  | Branch (Not overhanging, > 12ft) | 2019-313 | 2019 | 4 | 9 | 15 | 27 | 19-0041008 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 179862 | 22.8983 | 240_225 | <25mph | <15mph | HFTD - Distribution | 2019-04-09 15:27:00 | 1738 | 29.8749 | FALSE | 25-40mph | PG112 | 3.29 | 2019-04-09T06:20:00Z | 10.51 | 14 | < 25mph | PG155 | 7.32 | 2019-04-09T06:50:00Z | 12.71 | 29 | < 25mph | PG112 | 3.29 | 2019-04-09T07:50:00Z | 13.8 | 26 | < 25mph | PG155 | 7.32 | 2019-04-09T07:50:00Z | 19.51 | 54 | < 25mph
PG&E | 2019-04-20 | 6:57 | 37.8686 | -121.6843 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | East County FD | Unknown |  | 17000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-321 | 2019 | 4 | 20 | 6 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 39.0116 | 170_232 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-20 06:57:00 | 1744 | 39.0116 | FALSE | 25-40mph | D3588 | 2.98 | 2019-04-20T07:00:00Z | 10 | 6 | < 25mph | PG066 | 6.23 | 2019-04-20T06:30:00Z | 37.04 | 109 | 25-40mph | D3588 | 2.98 | 2019-04-20T07:51:00Z | 18.01 | 11 | < 25mph | KC83 | 4.32 | 2019-04-20T07:35:00Z | 43.73 | 207 | 40-55mph
PG&E | 2019-04-28 | 12:36 | 39.6756 | -121.5677 |  | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 100404366 |  | 12000 | Conductor | Overhead | Yes | 43583 | 0.525 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-166 | 2019 | 4 | 28 | 12 | 36 | 19-0046853 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 79810 | 6.7497 | 175_331 | <25mph | <15mph | HFTD - Distribution | 2019-04-28 12:36:00 | 1752 | 11.2512 | FALSE | <25mph | PG295 | 0.21 | 2019-04-28T06:50:00Z | 9.22 | 7 | < 25mph | PG295 | 0.21 | 2019-04-28T06:50:00Z | 9.22 | 25 | < 25mph | PG295 | 0.21 | 2019-04-28T06:50:00Z | 9.22 | 13 | < 25mph | JBGC1 | 5.9 | 2019-04-28T07:13:00Z | 11.01 | 46 | < 25mph
PG&E | 2019-05-08 | 10:23 | 39.3851 | -122.557 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | Colusa FD | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-312 | 2019 | 5 | 8 | 10 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 11.1721 | 133_316 | <25mph | <15mph | HFTD - Distribution | 2019-05-08 10:23:00 | 1764 | 11.4886 | FALSE | <25mph | SYWC1 | 1.49 | 2019-05-08T06:26:00Z | 4 | 1 | < 25mph | PG294 | 6.56 | 2019-05-08T06:00:00Z | 10.74 | 16 | < 25mph | SYWC1 | 1.49 | 2019-05-08T07:26:00Z | 4.99 | 2 | < 25mph | PG294 | 6.56 | 2019-05-08T06:00:00Z | 10.74 | 30 | < 25mph
PG&E | 2019-05-10 | 14:52 | 40.704 | -122.8314 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Fire Dept | Lewiston FD | Keswick-Trinity 60Kv Line |  | 60000 | Conductor | Overhead | Yes | 43595 | 0.61944 | Vegetation |  | Contact from Object - Other | Electric Facility |  |  | no-match | 2019-301 | 2019 | 5 | 10 | 14 | 52 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.0535 | 123_389 | <25mph | <15mph | HFTD - Transmission | 2019-05-10 14:52:00 | 1766 | 13.0849 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TCAC1 | 5.87 | 2019-05-10T06:28:00Z | 14.99 | 5 | < 25mph |  |  |  | 0 | 0 | No data | TCAC1 | 5.87 | 2019-05-10T06:28:00Z | 14.99 | 8 | < 25mph
PG&E | 2019-05-15 | 21:31 | 38.5731 | -122.9603 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Unknown |  | 103931177 |  | 12000 | Conductor | Overhead | Yes | 43600 | 0.89653 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-316 | 2019 | 5 | 15 | 21 | 31 | 19-0052480 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 27780 | 16.5892 | 115_271 | <25mph | <15mph | HFTD - Distribution | 2019-05-15 21:31:00 | 1774 | 23.8094 | FALSE | <25mph | D9841 | 3.34 | 2019-05-15T07:00:00Z | 1.01 | 5 | < 25mph | AR798 | 4.72 | 2019-05-15T06:56:00Z | 10 | 43 | < 25mph | D9841 | 3.34 | 2019-05-15T07:00:00Z | 1.01 | 8 | < 25mph | AR798 | 4.72 | 2019-05-15T06:56:00Z | 10 | 84 | < 25mph
PG&E | 2019-05-17 | 15:12 | 38.4797 | -123.1486 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 42811111 |  | 12000 | Conductor | Overhead | Yes | 43602 | 0.63333 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-200 | 2019 | 5 | 17 | 15 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 19.5511 | 107_266 | <25mph | <15mph | HFTD - Distribution | 2019-05-17 15:12:00 | 1775 | 20.334 | FALSE | <25mph | E8483 | 3.61 | 2019-05-17T06:30:00Z | 8.99 | 5 | < 25mph | E8483 | 3.61 | 2019-05-17T06:30:00Z | 8.99 | 17 | < 25mph | E8483 | 3.61 | 2019-05-17T06:30:00Z | 8.99 | 9 | < 25mph | E8483 | 3.61 | 2019-05-17T06:30:00Z | 8.99 | 29 | < 25mph
PG&E | 2019-05-24 | 15:03 | 35.1696 | -120.5103 |  | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 40589503 |  | 500000 | Pole | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-100 | 2019 | 5 | 24 | 15 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 14.866 | 222_83 | <25mph | <15mph | HFTD - Transmission | 2019-05-24 15:03:00 | 1780 | 15.7146 | FALSE | <25mph | C9687 | 3.56 | 2019-05-24T06:55:00Z | 0 | 12 | < 25mph | PG168 | 5.97 | 2019-05-24T07:00:00Z | 4.83 | 46 | < 25mph | C9687 | 3.56 | 2019-05-24T07:55:00Z | 0 | 24 | < 25mph | PG168 | 5.97 | 2019-05-24T07:00:00Z | 4.83 | 90 | < 25mph
PG&E | 2019-05-29 | 16:54 | 37.0371 | -119.5209 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 100680674 |  | 12000 | Pole | Overhead | Yes | 43614 | 0.70417 | Vegetation |  | Veg. contact | Pole |  |  | Dead | 2019-202 | 2019 | 5 | 29 | 16 | 54 | 19-0059237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 6780 | 6.6167 | 265_186 | <25mph | <15mph | HFTD - Distribution | 2019-05-29 16:54:00 | 1787 | 9.3593 | FALSE | <25mph | PG219 | 2.84 | 2019-05-29T06:40:00Z | 3.06 | 8 | < 25mph | PG202 | 6.2 | 2019-05-29T06:30:00Z | 7.25 | 57 | < 25mph | PG219 | 2.84 | 2019-05-29T08:00:00Z | 4.16 | 15 | < 25mph | PG202 | 6.2 | 2019-05-29T06:30:00Z | 7.25 | 97 | < 25mph
PG&E | 2019-05-29 | 20:25 | 39.0194 | -121.0608 |  | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match |  | 2019 | 5 | 29 | 20 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 14.177 | 197_295 | <25mph | <15mph | HFTD - Distribution | 2019-05-29 20:25:00 | 1789 | 14.177 | FALSE | <25mph | PG349 | 3.78 | 2019-05-29T06:50:00Z | 4.83 | 23 | < 25mph | PG367 | 7.83 | 2019-05-29T06:20:00Z | 7 | 59 | < 25mph | PG349 | 3.78 | 2019-05-29T07:50:00Z | 5.91 | 42 | < 25mph | PG332 | 6.22 | 2019-05-29T07:40:00Z | 8.77 | 111 | < 25mph
PG&E | 2019-05-30 | 8:18 | 35.7005 | -120.8104 | Vehicle | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 101871463 |  | 12000 | Pole | Overhead | Yes | 43615 | 0.34583 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-274 | 2019 | 5 | 30 | 8 | 18 | 19-0059906 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 171603 | 10.8019 | 208_112 | <25mph | <15mph | HFTD - Distribution | 2019-05-30 08:18:00 | 1791 | 17.2262 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D4060 | 4.58 | 2019-05-30T06:02:00Z | 8.01 | 12 | < 25mph |  |  |  | 0 | 0 | No data | D4060 | 4.58 | 2019-05-30T06:02:00Z | 8.01 | 23 | < 25mph
PG&E | 2019-05-31 | 15:25 | 40.4431 | -121.8211 |  | Hardwood Woodland | 1 meter - < 3 meters | Self Extinguished |  | 101556319 |  | 12000 | Conductor | Overhead | Yes | 43616 | 0.64236 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-88 | 2019 | 5 | 31 | 15 | 25 | 19-0060901 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 55546 | 8.5736 | 165_374 | <25mph | <15mph | HFTD - Distribution | 2019-05-31 15:25:00 | 1795 | 18.5418 | FALSE | <25mph | PG313 | 2.94 | 2019-05-31T06:50:00Z | 16.22 | 15 | < 25mph | PG193 | 6.12 | 2019-05-31T06:40:00Z | 18.41 | 22 | < 25mph | PG130 | 1.76 | 2019-05-31T07:50:00Z | 17.54 | 33 | < 25mph | PG193 | 6.12 | 2019-05-31T08:00:00Z | 22.57 | 52 | < 25mph
PG&E | 2019-06-03 | 14:31 | 40.6822 | -122.2806 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 101466598 |  | 12000 | Transformer | Overhead | Yes | 43619 | 0.60486 | Equipment - Overloaded | Transformer |  |  |  |  | no-match | 2019-161 | 2019 | 6 | 3 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 6.522 | 146_387 | <25mph | <15mph | HFTD - Distribution | 2019-06-03 14:31:00 | 1798 | 12.4331 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG307 | 4.7 | 2019-06-03T06:50:00Z | 2.42 | 19 | < 25mph |  |  |  | 0 | 0 | No data | PG307 | 4.7 | 2019-06-03T08:00:00Z | 3.94 | 38 | < 25mph
PG&E | 2019-06-03 | 14:47 | 40.4419 | -122.3036 |  | Herbaceous | 1 meter - < 3 meters | Fire Dept | Anderson FD | 101495889 |  | 12000 | Insulator | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-456 | 2019 | 6 | 3 | 14 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 9.9807 | 145_374 | <25mph | <15mph | HFTD - Distribution | 2019-06-03 14:47:00 | 1799 | 16.209 | FALSE | <25mph | AP525 | 3.17 | 2019-06-03T06:55:00Z | 0 | 6 | < 25mph | PG174 | 6.35 | 2019-06-03T06:00:00Z | 10.29 | 17 | < 25mph | AP525 | 3.17 | 2019-06-03T07:55:00Z | 0 | 12 | < 25mph | PG174 | 6.35 | 2019-06-03T06:00:00Z | 10.29 | 33 | < 25mph
PG&E | 2019-06-06 | 9:01 | 35.6384 | -118.9687 | Bird Found | Herbaceous | 0.25 - 10 Acres | Fire Dept | Kern County FD | 100216096 |  | 21000 | Conductor | Overhead | No |  |  | Contact - Animal - Other |  | Animal contact |  | Animal Contact |  | no-match | 2019-228 | 2019 | 6 | 6 | 9 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 4.6796 | 291_110 | <25mph | <15mph | HFTD - Distribution | 2019-06-06 09:01:00 | 1803 | 21.162 | FALSE | <25mph | PG159 | 2.52 | 2019-06-06T06:50:00Z | 9.86 | 14 | < 25mph | PG159 | 2.52 | 2019-06-06T06:50:00Z | 9.86 | 28 | < 25mph | PG159 | 2.52 | 2019-06-06T06:50:00Z | 9.86 | 26 | < 25mph | PG159 | 2.52 | 2019-06-06T06:50:00Z | 9.86 | 52 | < 25mph
PG&E | 2019-06-06 | 20:30 | 38.4969 | -122.6435 |  | Barren/Other | < 1 meter | Self Extinguished |  | Unknown |  | 230000 | Circuit Breaker | Overhead | Yes | 43622 | 0.85417 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | no-match | 2019-102 | 2019 | 6 | 6 | 20 | 30 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 16.883 | 129_267 | <25mph | <15mph | HFTD - Transmission | 2019-06-06 20:30:00 | 1804 | 23.129 | FALSE | <25mph | RSAC1 | 3.91 | 2019-06-06T06:29:00Z | 8.01 | 17 | < 25mph | PG162 | 5.7 | 2019-06-06T06:00:00Z | 23.02 | 91 | < 25mph | RSAC1 | 3.91 | 2019-06-06T07:29:00Z | 11.01 | 34 | < 25mph | PG162 | 5.7 | 2019-06-06T06:00:00Z | 23.02 | 172 | < 25mph
PG&E | 2019-06-07 | 9:58 | 38.7285 | -123.3528 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 042861101 |  | 21000 | Conductor | Overhead | Yes | 43623 | 0.41528 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-358 | 2019 | 6 | 7 | 9 | 58 | 19-0064216 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 5301 | 16.456 | 98_280 | <25mph | <15mph | HFTD - Distribution | 2019-06-07 09:58:00 | 1805 | 19.4921 | FALSE | <25mph | OAAC1 | 2.48 | 2019-06-07T06:33:00Z | 35.99 | 1 | 25-40mph | OAAC1 | 2.48 | 2019-06-07T06:33:00Z | 35.99 | 13 | 25-40mph | OAAC1 | 2.48 | 2019-06-07T06:33:00Z | 35.99 | 2 | 25-40mph | OAAC1 | 2.48 | 2019-06-07T06:33:00Z | 35.99 | 25 | 25-40mph
PG&E | 2019-06-08 | 18:51 | 38.6105 | -122.9732 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 42751113 |  | 12000 | Conductor | Overhead | Yes | 43624 | 0.78542 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-355 | 2019 | 6 | 8 | 18 | 51 | 19-0064689 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 44664 | 14.8219 | 114_273 | <25mph | <15mph | HFTD - Distribution | 2019-06-08 18:51:00 | 1812 | 19.8533 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG243 | 5.7 | 2019-06-08T06:20:00Z | 12.48 | 51 | < 25mph |  |  |  | 0 | 0 | No data | PG243 | 5.7 | 2019-06-08T07:10:00Z | 14.47 | 100 | < 25mph
PG&E | 2019-06-10 | 13:29 | 38.8137 | -120.9433 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Other | Customer | 153652109 |  | 21000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-243 | 2019 | 6 | 10 | 13 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.2437 | 202_284 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 13:29:00 | 1823 | 9.9566 | FALSE | <25mph | PLTC1 | 3.76 | 2019-06-10T06:56:00Z | 4 | 15 | < 25mph | PG073 | 7.24 | 2019-06-10T07:00:00Z | 11.18 | 62 | < 25mph | PLTC1 | 3.76 | 2019-06-10T07:56:00Z | 4 | 28 | < 25mph | PG073 | 7.24 | 2019-06-10T07:10:00Z | 14.25 | 117 | < 25mph
PG&E | 2019-06-10 | 16:18 | 38.1107 | -122.9025 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 42291101 |  | 12000 | Conductor | Overhead | Yes | 43626 | 0.67917 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-401 | 2019 | 6 | 10 | 16 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.6937 | 117_246 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 16:18:00 | 1826 | 12.047 | FALSE | <25mph | PG046 | 2.87 | 2019-06-10T06:40:00Z | 12.93 | 21 | < 25mph | PG046 | 2.87 | 2019-06-10T06:40:00Z | 12.93 | 21 | < 25mph | PG046 | 2.87 | 2019-06-10T06:40:00Z | 12.93 | 39 | < 25mph | PG046 | 2.87 | 2019-06-10T06:40:00Z | 12.93 | 39 | < 25mph
PG&E | 2019-06-10 | 16:34 | 38.821 | -120.846 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Garden Valley FD | 153082106 |  | 21000 | Conductor | Overhead | Yes | 43626 | 0.69028 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-372 | 2019 | 6 | 10 | 16 | 34 | 19-0065481 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14169 | 8.5329 | 206_284 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 16:34:00 | 1827 | 15.7607 | FALSE | <25mph | PG180 | 3.67 | 2019-06-10T07:00:00Z | 6.35 | 14 | < 25mph | PG104 | 6.61 | 2019-06-10T07:00:00Z | 14.47 | 81 | < 25mph | PG180 | 3.67 | 2019-06-10T08:00:00Z | 6.58 | 26 | < 25mph | PG104 | 6.61 | 2019-06-10T07:00:00Z | 14.47 | 154 | < 25mph
PG&E | 2019-06-15 | 14:08 | 38.8802 | -122.6125 | Tree - cutting, 3rd party | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 43361103 |  | 12000 | Pole | Overhead | Yes | 43631 | 0.58889 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | Other/Unknown | 2019-19 | 2019 | 6 | 15 | 14 | 8 | 19-0068074 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 259562 | 11.2331 | 130_288 | <25mph | <15mph | HFTD - Distribution | 2019-06-15 14:08:00 | 1841 | 15.703 | FALSE | <25mph | PG110 | 3.62 | 2019-06-15T06:00:00Z | 7 | 14 | < 25mph | KELC1 | 5.5 | 2019-06-15T06:57:00Z | 14.99 | 58 | < 25mph | PG110 | 3.62 | 2019-06-15T06:00:00Z | 7 | 26 | < 25mph | KELC1 | 5.5 | 2019-06-15T07:57:00Z | 14.99 | 106 | < 25mph
PG&E | 2019-06-17 | 10:25 | 38.511 | -122.2134 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 43051101 |  | 12000 | Conductor | Overhead | Yes | 43633 | 0.43403 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-84 | 2019 | 6 | 17 | 10 | 25 | 19-0068579 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 306900 | 10.2943 | 147_267 | <25mph | <15mph | HFTD - Distribution | 2019-06-17 10:25:00 | 1843 | 15.8677 | FALSE | <25mph | PG048 | 0.14 | 2019-06-17T06:30:00Z | 11.63 | 8 | < 25mph | PG048 | 0.14 | 2019-06-17T06:30:00Z | 11.63 | 50 | < 25mph | PG048 | 0.14 | 2019-06-17T06:30:00Z | 11.63 | 15 | < 25mph | PG048 | 0.14 | 2019-06-17T06:30:00Z | 11.63 | 93 | < 25mph
PG&E | 2019-06-18 | 19:49 | 35.8876 | -120.9217 | Bird Found | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Pole | Overhead | Yes | 43634 | 0.82569 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | no-match | 2019-55 | 2019 | 6 | 18 | 19 | 49 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 15.5935 | 203_122 | <25mph | <15mph | HFTD - Distribution | 2019-06-18 19:49:00 | 1852 | 21.7258 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG360 | 6.27 | 2019-06-18T06:10:00Z | 16.89 | 15 | < 25mph |  |  |  | 0 | 0 | No data | RBYC1 | 6.84 | 2019-06-18T07:12:00Z | 17 | 28 | < 25mph
PG&E | 2019-06-19 | 11:44 | 39.8612 | -121.6907 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100400933 |  | 12000 | Conductor | Overhead | Yes | 43635 | 0.48889 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-224 | 2019 | 6 | 19 | 11 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.9144 | 170_342 | <25mph | <15mph | HFTD - Distribution | 2019-06-19 11:44:00 | 1855 | 12.1329 | FALSE | <25mph | PG337 | 3.36 | 2019-06-19T06:10:00Z | 5.48 | 26 | < 25mph | PG339 | 7.65 | 2019-06-19T06:40:00Z | 10.29 | 73 | < 25mph | PG337 | 3.36 | 2019-06-19T07:20:00Z | 7.25 | 50 | < 25mph | CSTC1 | 4.21 | 2019-06-19T07:51:00Z | 11.01 | 132 | < 25mph
PG&E | 2019-06-26 | 13:14 | 40.0185 | -122.4107 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | Circuit Id 103331101 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43642 | 0.55139 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-331 | 2019 | 6 | 26 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2684 | 140_351 | <25mph | <15mph | HFTD - Distribution | 2019-06-26 13:14:00 | 1870 | 19.4401 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG276 | 6.5 | 2019-06-26T07:00:00Z | 13.6 | 14 | < 25mph |  |  |  | 0 | 0 | No data | PG276 | 6.5 | 2019-06-26T07:00:00Z | 13.6 | 26 | < 25mph
PG&E | 2019-06-27 | 2:23 | 36.8198 | -119.3334 | Bird Found | Hardwood Woodland | 0.25 - 10 Acres | Self Extinguished |  | Kings River-Sanger-Reedley 115Kv At 16/089 |  | 115000 | Insulator | Overhead | Yes | 43643 | 0.099306 | Equipment - PG&E | Insulator |  |  |  |  | no-match | 2019-104 | 2019 | 6 | 27 | 2 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | N.A. | 13.572 | 273_175 | <25mph | <15mph | HFTD - Transmission | 2019-06-27 02:23:00 | 1872 | 13.572 | FALSE | <25mph | PG408 | 3.33 | 2019-06-27T06:40:00Z | 4.83 | 7 | < 25mph | PG233 | 6.47 | 2019-06-27T06:20:00Z | 7.67 | 21 | < 25mph | PG408 | 3.33 | 2019-06-27T06:40:00Z | 4.83 | 13 | < 25mph | PG233 | 6.47 | 2019-06-27T06:20:00Z | 7.67 | 40 | < 25mph
PG&E | 2019-07-01 | 2:15 | 38.2955 | -120.8335 |  | Shrub | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-252 | 2019 | 7 | 1 | 2 | 15 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.9479 | 207_255 | <25mph | <15mph | HFTD - Distribution | 2019-07-01 02:15:00 | 1878 | 14.184 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TS389 | 4.67 | 2019-07-01T06:53:00Z | 14 | 32 | < 25mph |  |  |  | 0 | 0 | No data | TS389 | 4.67 | 2019-07-01T06:53:00Z | 14 | 60 | < 25mph
PG&E | 2019-07-06 | 14:22 | 34.6388 | -119.9695 |  | Herbaceous | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | 182721104 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43652 | 0.59861 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-153 | 2019 | 7 | 6 | 14 | 22 | 19-0074960 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 14213 | 21.2189 | 246_54 | <25mph | <15mph | HFTD - Distribution | 2019-07-06 14:22:00 | 1888 | 23.8361 | FALSE | <25mph |  |  |  | 0 | 0 | No data | FGMC1 | 6.93 | 2019-07-06T06:35:00Z | 8.99 | 22 | < 25mph |  |  |  | 0 | 0 | No data | FGMC1 | 6.93 | 2019-07-06T07:35:00Z | 8.99 | 42 | < 25mph
PG&E | 2019-07-13 | 13:13 | 34.7273 | -120.4357 |  | Shrub | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | Y44 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43659 | 0.55069 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-154 | 2019 | 7 | 13 | 13 | 13 | 19-0077070 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 18256 | 12.2026 | 225_58 | <25mph | <15mph | HFTD - Distribution | 2019-07-13 13:13:00 | 1900 | 12.8932 | FALSE | <25mph | VDBC1 | 3.58 | 2019-07-13T06:22:00Z | 4.99 | 5 | < 25mph | VDBC1 | 3.58 | 2019-07-13T06:22:00Z | 4.99 | 24 | < 25mph | VDBC1 | 3.58 | 2019-07-13T07:22:00Z | 4.99 | 10 | < 25mph | VDBC1 | 3.58 | 2019-07-13T07:22:00Z | 4.99 | 47 | < 25mph
PG&E | 2019-07-15 | 7:51 | 38.3266 | -122.568 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 42721104 |  | 12000 | Conductor | Overhead | Yes | 43661 | 0.32708 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-343 | 2019 | 7 | 15 | 7 | 51 | 19-0077351 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2348 | 31.0114 | 132_257 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-07-15 07:51:00 | 1903 | 35.3209 | FALSE | 25-40mph | PG177 | 1.33 | 2019-07-15T07:00:00Z | 23.02 | 11 | < 25mph | PG177 | 1.33 | 2019-07-15T07:00:00Z | 23.02 | 46 | < 25mph | PG177 | 1.33 | 2019-07-15T08:00:00Z | 23.24 | 21 | < 25mph | PG177 | 1.33 | 2019-07-15T08:00:00Z | 23.24 | 90 | < 25mph
PG&E | 2019-07-17 | 7:49 | 34.5066 | -120.2247 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Santa Barbara County FD | 4Bx0717190747 |  | 12000 | Other | Overhead | Yes | 43663 | 0.32569 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-425 | 2019 | 7 | 17 | 7 | 49 | 19-0078239 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 19608 | 17.3045 | 235_46 | <25mph | <15mph | HFTD - Distribution | 2019-07-17 07:49:00 | 1908 | 28.4942 | FALSE | 25-40mph | GVTC1 | 1.4 | 2019-07-17T06:09:00Z | 40 | 8 | 40-55mph | GVTC1 | 1.4 | 2019-07-17T06:09:00Z | 40 | 8 | 40-55mph | GVTC1 | 1.4 | 2019-07-17T07:09:00Z | 40 | 15 | 40-55mph | GVTC1 | 1.4 | 2019-07-17T07:09:00Z | 40 | 15 | 40-55mph
PG&E | 2019-07-18 | 19:57 | 37.081 | -119.4865 |  | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | No |  |  | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-09 | 2019 | 7 | 18 | 19 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.8761 | 266_189 | <25mph | <15mph | HFTD - Distribution | 2019-07-18 19:57:00 | 1914 | 14.7588 | FALSE | <25mph | PG389 | 1.62 | 2019-07-18T06:00:00Z | 8.77 | 39 | < 25mph | SE370 | 7.06 | 2019-07-18T06:10:00Z | 11.41 | 104 | < 25mph | PG389 | 1.62 | 2019-07-18T06:00:00Z | 8.77 | 74 | < 25mph | SE370 | 7.06 | 2019-07-18T06:10:00Z | 11.41 | 195 | < 25mph
PG&E | 2019-07-18 | 10:27 | 38.3033 | -120.6718 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | B561 |  | 12000 | Other | Overhead | Yes | 43664 | 0.43542 | Equipment - PG&E | Other |  |  |  |  | Other/Unknown | 2019-68 | 2019 | 7 | 18 | 10 | 27 | 19-0078904 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45558 | 8.6789 | 214_256 | <25mph | <15mph | HFTD - Distribution | 2019-07-18 10:27:00 | 1910 | 16.0413 | FALSE | <25mph | PG372 | 0.86 | 2019-07-18T07:00:00Z | 4.83 | 14 | < 25mph | TS389 | 7.11 | 2019-07-18T06:53:00Z | 7 | 59 | < 25mph | PG372 | 0.86 | 2019-07-18T07:50:00Z | 7.67 | 26 | < 25mph | PG372 | 0.86 | 2019-07-18T07:50:00Z | 7.67 | 110 | < 25mph
PG&E | 2019-07-19 | 11:59 | 37.9162 | -120.349 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 163351703 |  | 17000 | Conductor | Overhead | Yes | 43665 | 0.49931 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-376 | 2019 | 7 | 19 | 11 | 59 | 19-0079030 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24042 | 10.7946 | 228_234 | <25mph | <15mph | HFTD - Distribution | 2019-07-19 11:59:00 | 1915 | 10.8841 | FALSE | <25mph | PG166 | 2.3 | 2019-07-19T06:00:00Z | 10.96 | 32 | < 25mph | PG166 | 2.3 | 2019-07-19T06:00:00Z | 10.96 | 51 | < 25mph | PG166 | 2.3 | 2019-07-19T06:00:00Z | 10.96 | 60 | < 25mph | PG166 | 2.3 | 2019-07-19T06:00:00Z | 10.96 | 95 | < 25mph
PG&E | 2019-07-21 | 10:14 | 38.9716 | -120.9991 |  | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire | Placer Hill FD | 152241102 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43667 | 0.42639 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-127 | 2019 | 7 | 21 | 10 | 14 | 19-0079578 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 32850 | 6.8026 | 199_293 | <25mph | <15mph | HFTD - Distribution | 2019-07-21 10:14:00 | 1916 | 10.8012 | FALSE | <25mph | C0713 | 3.87 | 2019-07-21T07:00:00Z | 0 | 16 | < 25mph | PG349 | 6.34 | 2019-07-21T06:40:00Z | 3.94 | 45 | < 25mph | C0713 | 3.87 | 2019-07-21T07:59:00Z | 0 | 31 | < 25mph | PG349 | 6.34 | 2019-07-21T08:00:00Z | 5.03 | 90 | < 25mph
PG&E | 2019-07-22 | 8:11 | 38.7687 | -120.9633 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | El Dorado County FD | 6Ht0722190809 |  | 21000 | Other | Overhead | Yes | 43668 | 0.34097 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-49 | 2019 | 7 | 22 | 8 | 11 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.6529 | 201_281 | <25mph | <15mph | HFTD - Distribution | 2019-07-22 08:11:00 | 1920 | 11.9774 | FALSE | <25mph | PG027 | 3.71 | 2019-07-22T06:20:00Z | 5.48 | 14 | < 25mph | PG111 | 5.58 | 2019-07-22T06:00:00Z | 5.48 | 121 | < 25mph | PG027 | 3.71 | 2019-07-22T07:30:00Z | 8.32 | 26 | < 25mph | PG027 | 3.71 | 2019-07-22T07:30:00Z | 8.32 | 231 | < 25mph
PG&E | 2019-07-22 | 21:39 | 38.8618 | -121.1044 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 152561103 |  | 12000 | Conductor | Overhead | Yes | 43668 | 0.90208 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-336 | 2019 | 7 | 22 | 21 | 39 | 19-0080025 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 9842 | 9.5984 | 195_286 | <25mph | <15mph | HFTD - Distribution | 2019-07-22 21:39:00 | 1921 | 13.5446 | FALSE | <25mph | D8862 | 2.4 | 2019-07-22T06:15:00Z | 4 | 5 | < 25mph | F5165 | 7.23 | 2019-07-22T06:55:00Z | 4 | 29 | < 25mph | D8862 | 2.4 | 2019-07-22T07:15:00Z | 4 | 8 | < 25mph | F5165 | 7.23 | 2019-07-22T07:40:00Z | 4 | 53 | < 25mph
PG&E | 2019-07-23 | 16:55 | 37.2128 | -119.505 | Gun Shot | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | 252521103 |  | 12000 | Conductor | Overhead | Yes | 43669 | 0.70486 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-434 | 2019 | 7 | 23 | 16 | 55 | 19-0080383 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 513358 | 13.6168 | 265_196 | <25mph | <15mph | HFTD - Distribution | 2019-07-23 16:55:00 | 1923 | 13.6168 | FALSE | <25mph | PG467 | 3.77 | 2019-07-23T06:40:00Z | 15.99 | 9 | < 25mph | PG467 | 3.77 | 2019-07-23T06:40:00Z | 15.99 | 30 | < 25mph | PG467 | 3.77 | 2019-07-23T07:20:00Z | 15.99 | 16 | < 25mph | PG467 | 3.77 | 2019-07-23T07:20:00Z | 15.99 | 55 | < 25mph
PG&E | 2019-07-25 | 0:15 | 39.0662 | -120.9754 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Placer Hills FD | 152491101 |  | 12000 | Conductor | Overhead | Yes | 43671 | 0.010417 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-379 | 2019 | 7 | 25 | 0 | 15 | 19-0080924 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7845 | 8.7511 | 200_298 | <25mph | <15mph | HFTD - Distribution | 2019-07-25 00:15:00 | 1927 | 11.2312 | FALSE | <25mph | PG377 | 2.2 | 2019-07-25T07:00:00Z | 4.16 | 31 | < 25mph | PG032 | 7.47 | 2019-07-25T06:30:00Z | 5.91 | 54 | < 25mph | PG377 | 2.2 | 2019-07-25T07:10:00Z | 5.7 | 61 | < 25mph | PG032 | 7.47 | 2019-07-25T07:10:00Z | 8.55 | 108 | < 25mph
PG&E | 2019-07-25 | 7:39 | 39.1735 | -123.5763 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Oj 2 P/Ss Of Cgc# 215532055340 |  | 12000 | Other | Overhead | Yes | 43671 | 0.31875 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-380 | 2019 | 7 | 25 | 7 | 39 | 19-0080947 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 790 | 2.0398 | 89_305 | <25mph | <15mph | HFTD - Distribution | 2019-07-25 07:39:00 | 1928 | 13.3511 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG485 | 4.89 | 2019-07-25T06:30:00Z | 3.74 | 18 | < 25mph |  |  |  | 0 | 0 | No data | PG485 | 4.89 | 2019-07-25T06:30:00Z | 3.74 | 35 | < 25mph
PG&E | 2019-07-27 | 8:22 | 40.3789 | -122.1873 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Self Extinguished |  | 103461102 |  | 12000 | Conductor | Overhead | Yes | 43673 | 0.34861 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-382 | 2019 | 7 | 27 | 8 | 22 | 19-0081756 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 456 | 4.4493 | 149_370 | <25mph | <15mph | HFTD - Distribution | 2019-07-27 08:22:00 | 1935 | 12.5056 | FALSE | <25mph | PG335 | 2.07 | 2019-07-27T06:00:00Z | 9.64 | 7 | < 25mph | PG320 | 4.66 | 2019-07-27T06:50:00Z | 11.41 | 21 | < 25mph | PG335 | 2.07 | 2019-07-27T06:00:00Z | 9.64 | 13 | < 25mph | PG320 | 4.66 | 2019-07-27T06:50:00Z | 11.41 | 39 | < 25mph
PG&E | 2019-07-27 | 4:51 | 37.9486 | -120.4656 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 163781705 |  | 17000 | Conductor | Overhead | Yes | 43673 | 0.20208 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-385 | 2019 | 7 | 27 | 4 | 51 | 19-0081744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 1364 | 13.5826 | 223_236 | <25mph | <15mph | HFTD - Distribution | 2019-07-27 04:51:00 | 1934 | 16.9934 | FALSE | <25mph | PG167 | 3.88 | 2019-07-27T06:40:00Z | 5.26 | 14 | < 25mph | PG166 | 6.57 | 2019-07-27T07:00:00Z | 12.06 | 35 | < 25mph | PG167 | 3.88 | 2019-07-27T06:40:00Z | 5.26 | 26 | < 25mph | PG166 | 6.57 | 2019-07-27T07:00:00Z | 12.06 | 65 | < 25mph
PG&E | 2019-07-30 | 15:15 | 39.1207 | -121.072 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 152691104 |  | 12000 | Conductor | Overhead | Yes | 43676 | 0.63542 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-386 | 2019 | 7 | 30 | 15 | 15 | 19-0082713 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 31302 | 12.2921 | 196_301 | <25mph | <15mph | HFTD - Distribution | 2019-07-30 15:15:00 | 1942 | 13.0851 | FALSE | <25mph | E1789 | 3.69 | 2019-07-30T06:24:00Z | 8.01 | 11 | < 25mph | PG429 | 7.54 | 2019-07-30T06:20:00Z | 8.32 | 88 | < 25mph | E1789 | 3.69 | 2019-07-30T06:24:00Z | 8.01 | 21 | < 25mph | PG367 | 7.57 | 2019-07-30T07:40:00Z | 16.44 | 171 | < 25mph
PG&E | 2019-08-01 | 13:28 | 38.5721 | -120.6803 | Equipment Failure/Involved, Overhead | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 153662102 |  | 21000 | Conductor | Overhead | Yes | 43678 | 0.56111 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-170 | 2019 | 8 | 1 | 13 | 28 | 19-0083500 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1374 | 13.6823 | 213_271 | <25mph | <15mph | HFTD - Distribution | 2019-08-01 13:28:00 | 1945 | 13.6823 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG433 | 7.73 | 2019-08-01T07:00:00Z | 11.83 | 31 | < 25mph |  |  |  | 0 | 0 | No data | PG433 | 7.73 | 2019-08-01T07:20:00Z | 15.77 | 59 | < 25mph
PG&E | 2019-08-05 | 22:38 | 37.1869 | -119.7902 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Unknown |  | 322066125092 |  | 21000 | Transformer | Overhead | Yes | 43682 | 0.94306 | Equipment - Overloaded | Transformer |  |  |  |  | Other/Unknown | 2019-134 | 2019 | 8 | 5 | 22 | 38 | 19-0084586 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 996 | 7.0886 | 253_195 | <25mph | <15mph | HFTD - Distribution | 2019-08-05 22:38:00 | 1952 | 12.3468 | FALSE | <25mph | PG434 | 0.93 | 2019-08-05T06:50:00Z | 6.13 | 19 | < 25mph | PG425 | 4.53 | 2019-08-05T06:30:00Z | 7.9 | 47 | < 25mph | PG434 | 0.93 | 2019-08-05T07:40:00Z | 6.35 | 37 | < 25mph | PG460 | 7.2 | 2019-08-05T07:30:00Z | 11.63 | 89 | < 25mph
PG&E | 2019-08-11 | 1:19 | 39.1152 | -121.001 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100097796 |  | 12000 | Other | Overhead | Yes | 43688 | 0.054861 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-387 | 2019 | 8 | 11 | 1 | 19 | 19-0086613 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6200 | 9.9563 | 199_300 | <25mph | <15mph | HFTD - Distribution | 2019-08-11 01:19:00 | 1965 | 18.5914 | FALSE | <25mph | PG377 | 1.68 | 2019-08-11T07:00:00Z | 1.52 | 13 | < 25mph | AV504 | 7.68 | 2019-08-11T06:55:00Z | 7 | 79 | < 25mph | PG377 | 1.68 | 2019-08-11T08:00:00Z | 2.86 | 25 | < 25mph | AV504 | 7.68 | 2019-08-11T07:05:00Z | 8.01 | 151 | < 25mph
PG&E | 2019-08-12 | 20:06 | 39.0952 | -123.4937 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 102177212 |  | 12000 | Conductor | Overhead | Yes | 43689 | 0.8375 | Vegetation |  | Veg. contact |  |  |  | Fell into (No defect) | 2019-400 | 2019 | 8 | 12 | 20 | 6 | 19-0087090 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2508 | 13.5331 | 93_301 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 20:06:00 | 1970 | 19.4805 | FALSE | <25mph | PG256 | 1.12 | 2019-08-12T06:10:00Z | 1.74 | 10 | < 25mph | PG248 | 4.67 | 2019-08-12T06:10:00Z | 4.16 | 17 | < 25mph | PG256 | 1.12 | 2019-08-12T06:10:00Z | 1.74 | 20 | < 25mph | PG248 | 4.67 | 2019-08-12T07:40:00Z | 4.38 | 33 | < 25mph
PG&E | 2019-08-12 | 17:42 | 38.6618 | -120.7451 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 101415488, 101404439 |  | 12000 | Pole | Overhead | Yes | 43689 | 0.7375 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (slight defect) | 2019-241 | 2019 | 8 | 12 | 17 | 42 | 19-0087080 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 54604 | 8.3029 | 210_275 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 17:42:00 | 1968 | 11.2889 | FALSE | <25mph | PG354 | 3.38 | 2019-08-12T07:00:00Z | 7.67 | 16 | < 25mph | PG354 | 3.38 | 2019-08-12T07:00:00Z | 7.67 | 57 | < 25mph | PG354 | 3.38 | 2019-08-12T07:40:00Z | 11.41 | 28 | < 25mph | PG354 | 3.38 | 2019-08-12T07:40:00Z | 11.41 | 106 | < 25mph
PG&E | 2019-08-14 | 10:16 | 35.379 | -120.4232 | Vegetation | Hardwood Woodland | < 1 meter | Cal Fire |  | 512769069280 |  | 21000 | Conductor | Overhead | Yes | 43691 | 0.42778 | Vegetation | [5 empty] | no-match |  | 2019 | 8 | 14 | 10 | 16 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.0314 | 226_94 | <25mph | <15mph | HFTD - Distribution | 2019-08-14 10:16:00 | 1976 | 14.3934 | FALSE | <25mph | PG235 | 1.2 | 2019-08-14T06:30:00Z | 5.48 | 28 | < 25mph | PG190 | 6.24 | 2019-08-14T06:00:00Z | 12.06 | 56 | < 25mph | PG235 | 1.2 | 2019-08-14T06:30:00Z | 5.48 | 52 | < 25mph | PG190 | 6.24 | 2019-08-14T06:00:00Z | 12.06 | 104 | < 25mph
PG&E | 2019-08-16 | 8:19 | 40.1235 | -123.8758 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Self Extinguished |  | 192221102-2101118022{5563} |  | 12000 | Conductor | Overhead | Yes | 43693 | 0.34653 | Vegetation | [5 empty] | Other/Unknown |  | 2019 | 8 | 16 | 8 | 19 | 19-0088744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 2979 | 5.7689 | 78_358 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 08:19:00 | 1983 | 18.468 | FALSE | <25mph | ERCC1 | 2.93 | 2019-08-16T06:28:00Z | 12.01 | 1 | < 25mph | ERCC1 | 2.93 | 2019-08-16T06:28:00Z | 12.01 | 33 | < 25mph | ERCC1 | 2.93 | 2019-08-16T06:28:00Z | 12.01 | 2 | < 25mph | ERCC1 | 2.93 | 2019-08-16T06:28:00Z | 12.01 | 62 | < 25mph
PG&E | 2019-08-16 | 10:31 | 39.3714 | -121.3221 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103191101 |  | 12000 | Conductor | Overhead | Yes | 43693 | 0.43819 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-397 | 2019 | 8 | 16 | 10 | 31 | 19-0088805 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4580 | 6.4736 | 186_315 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 10:31:00 | 1984 | 15.7456 | FALSE | <25mph | PG298 | 3.48 | 2019-08-16T06:50:00Z | 6.8 | 8 | < 25mph | PG381 | 4.94 | 2019-08-16T07:00:00Z | 14.25 | 43 | < 25mph | PG298 | 3.48 | 2019-08-16T08:00:00Z | 7.25 | 15 | < 25mph | PG381 | 4.94 | 2019-08-16T07:00:00Z | 14.25 | 80 | < 25mph
PG&E | 2019-08-20 | 9:03 | 41.1088 | -121.5034 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-297 | 2019 | 8 | 20 | 9 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 2.4258 | 178_411 | <25mph | <15mph | HFTD - Distribution | 2019-08-20 09:03:00 | 1990 | 15.6046 | FALSE | <25mph | PG384 | 3.7 | 2019-08-20T06:40:00Z | 2.64 | 7 | < 25mph | PG499 | 7.38 | 2019-08-20T06:00:00Z | 9.42 | 14 | < 25mph | PG384 | 3.7 | 2019-08-20T07:20:00Z | 3.06 | 13 | < 25mph | PG499 | 7.38 | 2019-08-20T06:00:00Z | 9.42 | 26 | < 25mph
PG&E | 2019-08-22 | 22:23 | 39.139 | -121.0194 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 152481106 |  | 12000 | Conductor | Overhead | Yes | 43699 | 0.93264 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-346 | 2019 | 8 | 22 | 22 | 23 | 19-0091224 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38628 | 9.4944 | 199_302 | <25mph | <15mph | HFTD - Distribution | 2019-08-22 22:23:00 | 1993 | 12.3163 | FALSE | <25mph | PG377 | 3.46 | 2019-08-22T07:00:00Z | 5.48 | 11 | < 25mph | E1789 | 6.14 | 2019-08-22T07:00:00Z | 5.99 | 93 | < 25mph | PG377 | 3.46 | 2019-08-22T07:00:00Z | 5.48 | 21 | < 25mph | E1789 | 6.14 | 2019-08-22T08:00:00Z | 5.99 | 184 | < 25mph
PG&E | 2019-08-31 | 10:20 | 40.661 | -122.356 | Vehicle | Barren/Other | 3 meters - 0.25 Acres | Fire Dept | Shasta Lake FD | 103571671 | Yes | 12000 | Fuse | Overbuild | Yes | 43708 | 0.43056 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-421 | 2019 | 8 | 31 | 10 | 20 | 19-0094332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3050 | 3.1396 | 143_386 | <25mph | <15mph | HFTD - Distribution | 2019-08-31 10:20:00 | 2007 | 12.9011 | FALSE | <25mph | F5970 | 1.07 | 2019-08-31T06:00:00Z | 3 | 23 | < 25mph | PG519 | 6.72 | 2019-08-31T06:30:00Z | 5.55 | 62 | < 25mph | F5970 | 1.07 | 2019-08-31T07:16:00Z | 4 | 45 | < 25mph | PG519 | 6.72 | 2019-08-31T08:00:00Z | 11.99 | 118 | < 25mph
PG&E | 2019-09-01 | 16:50 | 35.908 | -121.011 |  | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 103477437 |  | 12000 | Pole | Overhead | Yes | 43709 | 0.70139 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-17 | 2019 | 9 | 1 | 16 | 50 | 19-0094475 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45432 | 5.8888 | 199_124 | <25mph | <15mph | HFTD - Distribution | 2019-09-01 16:50:00 | 2009 | 25.5842 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PG140 | 7.9 | 2019-09-01T06:20:00Z | 3.74 | 21 | < 25mph |  |  |  | 0 | 0 | No data | PG171 | 7.31 | 2019-09-01T08:00:00Z | 4.83 | 39 | < 25mph
PG&E | 2019-09-05 | 23:02 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire | California Department of Forestry | 101670112 |  | 12000 | Fuse | Overhead | Yes | 43713 | 0.95972 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-388 | 2019 | 9 | 5 | 23 | 2 | 19-0095858 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 17920 | 6.8605 | 147_193 | <25mph | <15mph | HFTD - Distribution | 2019-09-05 23:02:00 | 2016 | 8.0768 | FALSE | <25mph | BNDC1 | 2.84 | 2019-09-05T06:50:00Z | 3 | 15 | < 25mph | BNDC1 | 2.84 | 2019-09-05T06:50:00Z | 3 | 66 | < 25mph | BNDC1 | 2.84 | 2019-09-05T07:50:00Z | 3 | 28 | < 25mph | C1844 | 4.46 | 2019-09-05T07:29:00Z | 3 | 128 | < 25mph
PG&E | 2019-09-10 | 7:13 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 82841102 |  | 12000 | Conductor | Overhead | Yes | 43718 | 0.30069 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-369 | 2019 | 9 | 10 | 7 | 13 | 19-0097264 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 23500 | 14.6244 | 147_193 | <25mph | <15mph | HFTD - Distribution | 2019-09-10 07:13:00 | 2029 | 17.7422 | FALSE | <25mph | PG472 | 2.91 | 2019-09-10T07:00:00Z | 23.44 | 15 | < 25mph | PG472 | 2.91 | 2019-09-10T07:00:00Z | 23.44 | 65 | < 25mph | PG472 | 2.91 | 2019-09-10T07:00:00Z | 23.44 | 28 | < 25mph | PG472 | 2.91 | 2019-09-10T07:00:00Z | 23.44 | 125 | < 25mph
PG&E | 2019-09-11 | 21:03 | 38.3132 | -120.9809 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 163341103 |  | 12000 | Conductor | Overhead | Yes | 43719 | 0.87708 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-370 | 2019 | 9 | 11 | 21 | 3 | 19-0098003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25994 | 11.7888 | 200_256 | <25mph | <15mph | HFTD - Distribution | 2019-09-11 21:03:00 | 2035 | 13.1911 | FALSE | <25mph | PG401 | 2.35 | 2019-09-11T06:00:00Z | 3.06 | 7 | < 25mph | CFAC1 | 5.36 | 2019-09-11T06:05:00Z | 7 | 25 | < 25mph | PG401 | 2.35 | 2019-09-11T06:00:00Z | 3.06 | 13 | < 25mph | CFAC1 | 5.36 | 2019-09-11T06:05:00Z | 7 | 51 | < 25mph
PG&E | 2019-09-11 | 18:56 | 37.9937 | -122.137 | Bird Found | Hardwood Woodland | Other | Unknown |  | Unknown |  | 115000 | Other | Overhead | Yes | 43719 | 0.78889 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-42 | 2019 | 9 | 11 | 18 | 56 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | N.A. | 16.9097 | 150_239 | <25mph | <15mph | HFTD - Transmission | 2019-09-11 18:56:00 | 2034 | 19.7995 | FALSE | <25mph | PG064 | 2.53 | 2019-09-11T06:00:00Z | 16.15 | 54 | < 25mph | PG064 | 2.53 | 2019-09-11T06:00:00Z | 16.15 | 209 | < 25mph | PG064 | 2.53 | 2019-09-11T06:00:00Z | 16.15 | 103 | < 25mph | PG064 | 2.53 | 2019-09-11T06:00:00Z | 16.15 | 396 | < 25mph
PG&E | 2019-09-12 | 14:25 | 37.3144 | -122.1865 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 024131103 |  | 12000 | Conductor | Overhead | Yes | 43720 | 0.60069 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-217 | 2019 | 9 | 12 | 14 | 25 | 19-0098386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 89097 | 5.2412 | 147_201 | <25mph | <15mph | HFTD - Distribution | 2019-09-12 14:25:00 | 2036 | 15.0249 | FALSE | <25mph | PG152 | 1.17 | 2019-09-12T06:00:00Z | 9.28 | 49 | < 25mph | PG150 | 4.6 | 2019-09-12T06:40:00Z | 10.16 | 161 | < 25mph | PG152 | 1.17 | 2019-09-12T06:00:00Z | 9.28 | 100 | < 25mph | PG150 | 4.6 | 2019-09-12T06:40:00Z | 10.16 | 318 | < 25mph
PG&E | 2019-09-13 | 6:30 | 37.3348 | -121.7716 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 83392110 |  | 21000 | Splice/Clamp/Connector | Overhead | Yes | 43721 | 0.27083 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-444 | 2019 | 9 | 13 | 6 | 30 | 19-0098560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 35534 | 3.3882 | 166_202 | <25mph | <15mph | HFTD - Distribution | 2019-09-13 06:30:00 | 2037 | 14.1926 | FALSE | <25mph | PG477 | 2.08 | 2019-09-13T06:30:00Z | 9.35 | 54 | < 25mph | PG477 | 2.08 | 2019-09-13T06:30:00Z | 9.35 | 122 | < 25mph | PG477 | 2.08 | 2019-09-13T06:30:00Z | 9.35 | 101 | < 25mph | PG477 | 2.08 | 2019-09-13T06:30:00Z | 9.35 | 231 | < 25mph
PG&E | 2019-09-13 | 8:53 | 39.0754 | -121.1717 | Bird Found | Herbaceous | 0.25 - 10 Acres | Fire Dept | Consolidated FD | Etr0913190810 |  | 12000 | Other | Overhead | Yes | 43721 | 0.37014 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-46 | 2019 | 9 | 13 | 8 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 10.4382 | 192_298 | <25mph | <15mph | HFTD - Distribution | 2019-09-13 08:53:00 | 2038 | 13.5808 | FALSE | <25mph | PG367 | 1.38 | 2019-09-13T06:00:00Z | 8.68 | 10 | < 25mph | PG367 | 1.38 | 2019-09-13T06:00:00Z | 8.68 | 45 | < 25mph | PG367 | 1.38 | 2019-09-13T06:00:00Z | 8.68 | 22 | < 25mph | PG367 | 1.38 | 2019-09-13T06:00:00Z | 8.68 | 89 | < 25mph
PG&E | 2019-09-15 | 12:38 | 38.1194 | -120.8013 | Vehicle | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103959405 |  | 12000 | Pole | Overhead | Yes | 43723 | 0.52639 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-118 | 2019 | 9 | 15 | 12 | 38 | 19-0099234 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 5378 | 7.5852 | 208_246 | <25mph | <15mph | HFTD - Distribution | 2019-09-15 12:38:00 | 2043 | 14.1961 | FALSE | <25mph | F0465 | 3.04 | 2019-09-15T06:31:00Z | 2.01 | 12 | < 25mph | PG375 | 4.65 | 2019-09-15T06:40:00Z | 5.19 | 26 | < 25mph | F0465 | 3.04 | 2019-09-15T07:36:00Z | 3 | 24 | < 25mph | PG375 | 4.65 | 2019-09-15T08:00:00Z | 7.61 | 50 | < 25mph
PG&E | 2019-09-16 | 14:39 | 37.3762 | -119.8729 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 254452102 |  | 21000 | Conductor | Overhead | Yes | 43724 | 0.61042 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-417 | 2019 | 9 | 16 | 14 | 39 | 19-0099772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 121254 | 13.3091 | 249_205 | <25mph | <15mph | HFTD - Distribution | 2019-09-16 14:39:00 | 2045 | 14.9838 | FALSE | <25mph | PG571 | 0.83 | 2019-09-16T06:10:00Z | 7.74 | 14 | < 25mph | MIAC1 | 7.6 | 2019-09-16T06:59:00Z | 8.01 | 55 | < 25mph | PG571 | 0.83 | 2019-09-16T06:10:00Z | 7.74 | 26 | < 25mph | MIAC1 | 7.6 | 2019-09-16T06:59:00Z | 8.01 | 103 | < 25mph
PG&E | 2019-09-22 | 11:56 | 37.5168 | -119.9159 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103967994 |  | 21000 | Pole | Overhead | Yes | 43730 | 0.49722 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-452 | 2019 | 9 | 22 | 11 | 56 | 19-0102232 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 133232 | 11.5782 | 247_213 | <25mph | <15mph | HFTD - Distribution | 2019-09-22 11:56:00 | 2051 | 13.905 | FALSE | <25mph | PG189 | 1.46 | 2019-09-22T06:10:00Z | 6.22 | 15 | < 25mph | PG575 | 7.53 | 2019-09-22T06:00:00Z | 6.35 | 68 | < 25mph | PG189 | 1.46 | 2019-09-22T06:10:00Z | 6.22 | 28 | < 25mph | PG575 | 7.53 | 2019-09-22T06:00:00Z | 6.35 | 127 | < 25mph
PG&E | 2019-09-26 | 14:12 | 36.9517 | -121.8278 | Vegetation | Shrub | 1 meter - < 3 meters | Cal Fire |  | 2287 |  | 21000 | Conductor | Overhead | Yes | 43734 | 0.59167 | Vegetation |  | Veg. contact |  |  |  | Branch (OverHanging) | 2019-352 | 2019 | 9 | 26 | 14 | 12 | 19-0104163 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 2856 | 23.4173 | 163_181 | <25mph | <15mph | HFTD - Distribution | 2019-09-26 14:12:00 | 2060 | 23.8621 | FALSE | <25mph | E7291 | 3.61 | 2019-09-26T07:00:00Z | 8.01 | 35 | < 25mph | E7291 | 3.61 | 2019-09-26T07:00:00Z | 8.01 | 99 | < 25mph | E7291 | 3.61 | 2019-09-26T07:00:00Z | 8.01 | 66 | < 25mph | E7291 | 3.61 | 2019-09-26T07:00:00Z | 8.01 | 188 | < 25mph
PG&E | 2019-09-27 | 10:30 | 36.5336 | -121.1464 | Vegetation | Barren/Other | 0.25 - 10 Acres | Cal Fire |  | 182492105 |  | 21000 | Conductor | Overhead | Yes | 43735 | 0.4375 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-359 | 2019 | 9 | 27 | 10 | 30 | 19-0104536 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20631 | 5.3593 | 193_158 | <25mph | <15mph | HFTD - Distribution | 2019-09-27 10:30:00 | 2062 | 16.3021 | FALSE | <25mph | PG406 | 3.05 | 2019-09-27T06:00:00Z | 11.41 | 14 | < 25mph | PG406 | 3.05 | 2019-09-27T06:00:00Z | 11.41 | 22 | < 25mph | PG406 | 3.05 | 2019-09-27T06:00:00Z | 11.41 | 26 | < 25mph | PG406 | 3.05 | 2019-09-27T06:00:00Z | 11.41 | 41 | < 25mph
PG&E | 2019-09-28 | 13:16 | 37.2553 | -119.5057 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 252531103 |  | 12000 | Conductor | Overhead | Yes | 43736 | 0.55278 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-36 | 2019 | 9 | 28 | 13 | 16 | 19-0104972 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 1296 | 12.1111 | 265_198 | <25mph | <15mph | HFTD - Distribution | 2019-09-28 13:16:00 | 2064 | 13.545 | FALSE | <25mph | PG573 | 3.43 | 2019-09-28T07:00:00Z | 8.61 | 8 | < 25mph | PG573 | 3.43 | 2019-09-28T07:00:00Z | 8.61 | 68 | < 25mph | PG573 | 3.43 | 2019-09-28T07:00:00Z | 8.61 | 16 | < 25mph | PG573 | 3.43 | 2019-09-28T07:00:00Z | 8.61 | 140 | < 25mph
PG&E | 2019-09-30 | 14:29 | 34.6139 | -120.1799 | Contact with High Voltage, 3rd party | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 183041102 |  | 12000 | Conductor | Overhead | Yes | 43738 | 0.60347 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-13 | 2019 | 9 | 30 | 14 | 29 | 19-0105582 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 4080 | 26.8876 | 237_52 | 25-40mph | 15-30mph | HFTD - Distribution | 2019-09-30 14:29:00 | 2072 | 27.9753 | FALSE | 25-40mph | C9206 | 2.6 | 2019-09-30T06:56:00Z | 0 | 12 | < 25mph | TT480 | 6.42 | 2019-09-30T06:20:00Z | 12.01 | 16 | < 25mph | C9206 | 2.6 | 2019-09-30T07:56:00Z | 0 | 24 | < 25mph | TT480 | 6.42 | 2019-09-30T06:20:00Z | 12.01 | 32 | < 25mph
PG&E | 2019-10-04 | 19:07 | 40.4964 | -122.0448 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | Yes | 43742 | 0.79653 | Equipment - Overloaded | Other |  |  |  |  | no-match | 2019-257 | 2019 | 10 | 4 | 19 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 6.2955 | 155_377 | <25mph | <15mph | HFTD - Distribution | 2019-10-04 19:07:00 | 2076 | 10.3362 | FALSE | <25mph | PG107 | 2.58 | 2019-10-04T06:10:00Z | 4.54 | 7 | < 25mph | PG322 | 7.46 | 2019-10-04T06:50:00Z | 6.44 | 42 | < 25mph | PG107 | 2.58 | 2019-10-04T06:10:00Z | 4.54 | 13 | < 25mph | PG322 | 7.46 | 2019-10-04T06:50:00Z | 6.44 | 78 | < 25mph
PG&E | 2019-10-08 | 17:59 | 35.2979 | -120.4868 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 182541103 |  | 12000 | Conductor | Overhead | Yes | 43746 | 0.74931 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-207 | 2019 | 10 | 8 | 17 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.8254 | 223_90 | <25mph | <15mph | HFTD - Distribution | 2019-10-08 17:59:00 | 2082 | 10.8694 | FALSE | <25mph | PG240 | 3.72 | 2019-10-08T06:40:00Z | 1.61 | 7 | < 25mph | PG235 | 6.78 | 2019-10-08T06:00:00Z | 9.64 | 35 | < 25mph | PG240 | 3.72 | 2019-10-08T07:20:00Z | 2.77 | 13 | < 25mph | PG235 | 6.78 | 2019-10-08T06:00:00Z | 9.64 | 65 | < 25mph
PG&E | 2019-10-15 | 0:41 | 37.3237 | -119.6173 |  | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | Circuit 254432102 |  | 21000 | Insulator | Overhead | Yes | 43753 | 0.028472 | Equipment - PG&E | Insulator |  |  |  |  | Other/Unknown | 2019-168 | 2019 | 10 | 15 | 0 | 41 | 19-0111571 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 741 | 8.1986 | 260_202 | <25mph | <15mph | HFTD - Distribution | 2019-10-15 00:41:00 | 2092 | 11.0003 | FALSE | <25mph | BSNC1 | 3.84 | 2019-10-15T06:48:00Z | 8.99 | 54 | < 25mph | BSNC1 | 3.84 | 2019-10-15T06:48:00Z | 8.99 | 80 | < 25mph | BSNC1 | 3.84 | 2019-10-15T06:48:00Z | 8.99 | 106 | < 25mph | BSNC1 | 3.84 | 2019-10-15T06:48:00Z | 8.99 | 156 | < 25mph
PG&E | 2019-10-17 | 19:44 | 37.6494 | -120.357 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 5Tr1017191903 |  | 12000 | Conductor | Overhead | Yes | 43755 | 0.82222 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-423 | 2019 | 10 | 17 | 19 | 44 | 19-0113175 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 10105 | 17.2183 | 228_220 | <25mph | <15mph | HFTD - Distribution | 2019-10-17 19:44:00 | 2093 | 19.6404 | FALSE | <25mph | PG459 | 0.92 | 2019-10-17T06:20:00Z | 15.93 | 7 | < 25mph | PG186 | 7.71 | 2019-10-17T06:20:00Z | 16.28 | 21 | < 25mph | PG459 | 0.92 | 2019-10-17T07:40:00Z | 23.17 | 13 | < 25mph | PG186 | 7.71 | 2019-10-17T07:50:00Z | 25.05 | 39 | 25-40mph
PG&E | 2019-10-20 | 17:09 | 37.1585 | -122.1339 |  | Conifer Forest | 1 meter - < 3 meters | Employee |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match |  | 2019 | 10 | 20 | 17 | 9 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 13.248 | 150_193 | <25mph | <15mph | HFTD - Distribution | 2019-10-20 17:09:00 | 2098 | 15.6656 | FALSE | <25mph | PG472 | 2.84 | 2019-10-20T06:30:00Z | 12.28 | 41 | < 25mph | AV151 | 4.67 | 2019-10-20T06:05:00Z | 14 | 104 | < 25mph | PG472 | 2.84 | 2019-10-20T06:30:00Z | 12.28 | 79 | < 25mph | AV151 | 4.67 | 2019-10-20T06:05:00Z | 14 | 201 | < 25mph
PG&E | 2019-10-23 | 21:27 | 38.7959 | -122.7673 |  | Herbaceous | 100+ Acres | Cal Fire |  | 001/006 |  | 230000 | Jumper | Overhead | Yes | 43761 | 0.88819 | Under Investigation | Jumper |  |  |  | This ignition relates to the Kincade Fire, which is reported in compliance with D.19-05-037. The origin and cause of the Kincade Fire is under investigation by CAL FIRE and PG&E. At this time, PG&E has not formed a conclusion about the origin or cause of the Kincade Fire. | no-match |  | 2019 | 10 | 23 | 21 | 27 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 35.6848 | 123_284 | 25-40mph | 30-45mph | HFTD - Transmission | 2019-10-23 21:27:00 | 2102 | 39.9048 | FALSE | 25-40mph | PG305 | 2.22 | 2019-10-23T06:40:00Z | 21.18 | 21 | < 25mph | PG303 | 4.59 | 2019-10-23T06:40:00Z | 30.53 | 71 | 25-40mph | PG305 | 2.22 | 2019-10-23T06:40:00Z | 21.18 | 39 | < 25mph | PG303 | 4.59 | 2019-10-23T06:40:00Z | 30.53 | 132 | 25-40mph
PG&E | 2019-10-28 | 17:48 | 37.0309 | -121.7788 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 101682849 |  | 21000 | Conductor | Overhead | Yes | 43766 | 0.74167 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-389 | 2019 | 10 | 28 | 17 | 48 | 19-0118112 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 16698 | 8.4978 | 165_186 | <25mph | <15mph | HFTD - Distribution | 2019-10-28 17:48:00 | 2135 | 19.9036 | FALSE | <25mph | PG370 | 3.22 | 2019-10-28T06:00:00Z | 42.17 | 22 | 40-55mph | PG370 | 3.22 | 2019-10-28T06:00:00Z | 42.17 | 43 | 40-55mph | PG370 | 3.22 | 2019-10-28T06:00:00Z | 42.17 | 41 | 40-55mph | PG370 | 3.22 | 2019-10-28T06:00:00Z | 42.17 | 80 | 40-55mph
PG&E | 2019-10-28 | 18:46 | 38.5646 | -122.4642 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 43432104 |  | 21000 | Conductor | Overhead | Yes | 43766 | 0.78194 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-357 | 2019 | 10 | 28 | 18 | 46 | 19-0118147 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 496944 | 12.9758 | 136_271 | <25mph | <15mph | HFTD - Distribution | 2019-10-28 18:46:00 | 2136 | 31.1526 | FALSE | 25-40mph | PG199 | 2.69 | 2019-10-28T07:00:00Z | 32.21 | 23 | 25-40mph | PG162 | 6.69 | 2019-10-28T06:30:00Z | 35.08 | 79 | 25-40mph | PG199 | 2.69 | 2019-10-28T07:00:00Z | 32.21 | 44 | 25-40mph | PG162 | 6.69 | 2019-10-28T06:30:00Z | 35.08 | 148 | 25-40mph
PG&E | 2019-10-28 | 13:00 | 39.3208 | -121.1273 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 100099164 |  | 12000 | Transformer | Overbuild | Yes | 43766 | 0.54167 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-398 | 2019 | 10 | 28 | 13 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.567 | 194_312 | <25mph | <15mph | HFTD - Distribution | 2019-10-28 13:00:00 | 2133 | 16.9711 | FALSE | <25mph | RRRC1 | 1.31 | 2019-10-28T06:13:00Z | 7 | 8 | < 25mph | PG348 | 4.93 | 2019-10-28T07:00:00Z | 15.28 | 62 | < 25mph | RRRC1 | 1.31 | 2019-10-28T06:13:00Z | 7 | 15 | < 25mph | PG424 | 7.74 | 2019-10-28T07:20:00Z | 23.6 | 112 | < 25mph
PG&E | 2019-10-29 | 3:29 | 37.0374 | -121.5207 | Animal Found | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 1471 |  | 21000 | Fuse | Overhead | Yes | 43767 | 0.14514 | Contact - Animal - Other |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-283 | 2019 | 10 | 29 | 3 | 29 | 19-0118370 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 3294 | 2.601 | 177_186 | <25mph | <15mph | HFTD - Distribution | 2019-10-29 03:29:00 | 2137 | 15.317 | FALSE | <25mph | PG509 | 2.27 | 2019-10-29T06:00:00Z | 7.09 | 31 | < 25mph | PG509 | 2.27 | 2019-10-29T06:00:00Z | 7.09 | 46 | < 25mph | PG509 | 2.27 | 2019-10-29T06:00:00Z | 7.09 | 61 | < 25mph | PG509 | 2.27 | 2019-10-29T06:00:00Z | 7.09 | 88 | < 25mph
PG&E | 2019-10-30 | 13:32 | 38.4792 | -122.0302 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 063681102 |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact |  |  |  | no-match | 2019-338 | 2019 | 10 | 30 | 13 | 32 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.8557 | 155_266 | <25mph | <15mph | HFTD - Distribution | 2019-10-30 13:32:00 | 2143 | 17.0659 | FALSE | <25mph | PG431 | 3.57 | 2019-10-30T06:20:00Z | 30.4 | 7 | 25-40mph | PG583 | 4.98 | 2019-10-30T06:00:00Z | 32.82 | 14 | 25-40mph | PG431 | 3.57 | 2019-10-30T06:20:00Z | 30.4 | 13 | 25-40mph | PG583 | 4.98 | 2019-10-30T06:00:00Z | 32.82 | 26 | 25-40mph
PG&E | 2019-10-31 | 17:23 | 38.0458 | -122.1905 |  | Herbaceous | 1 meter - < 3 meters | Fire Dept | Crockett FD | 13432207 |  | 21000 | Conductor | Overhead | Yes | 43769 | 0.72431 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-05 | 2019 | 10 | 31 | 17 | 23 | 19-0119756 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 138161 | 2.9536 | 148_242 | <25mph | <15mph | HFTD - Distribution | 2019-10-31 17:23:00 | 2147 | 12.6781 | FALSE | <25mph | DPXC1 | 3.83 | 2019-10-31T06:30:00Z | 10 | 40 | < 25mph | DPXC1 | 3.83 | 2019-10-31T06:30:00Z | 10 | 108 | < 25mph | DPXC1 | 3.83 | 2019-10-31T06:30:00Z | 10 | 74 | < 25mph | DPXC1 | 3.83 | 2019-10-31T06:30:00Z | 10 | 206 | < 25mph
PG&E | 2019-10-31 | 16:09 | 38.3845 | -122.1893 | Vegetation | Agriculture | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact |  |  |  | no-match | 2019-396 | 2019 | 10 | 31 | 16 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 5.3253 | 148_260 | <25mph | <15mph | HFTD - Distribution | 2019-10-31 16:09:00 | 2146 | 18.7786 | FALSE | <25mph | F0187 | 2.71 | 2019-10-31T06:15:00Z | 8.99 | 10 | < 25mph | PG185 | 4.03 | 2019-10-31T06:50:00Z | 17.83 | 66 | < 25mph | F0187 | 2.71 | 2019-10-31T06:15:00Z | 8.99 | 21 | < 25mph | PG185 | 4.03 | 2019-10-31T07:10:00Z | 18.99 | 126 | < 25mph
PG&E | 2019-11-03 | 18:26 | 36.2323 | -121.7622 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 182941102 |  | 12000 | Conductor | Overhead | Yes | 43772 | 0.76806 | Vegetation |  | Veg. contact |  |  |  | Fell into (Moderate-Severe defect) | 2019-371 | 2019 | 11 | 3 | 18 | 26 | 19-0120570 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 59211 | 9.4075 | 166_142 | <25mph | <15mph | HFTD - Distribution | 2019-11-03 18:26:00 | 2152 | 16.3887 | FALSE | <25mph | PG362 | 1.69 | 2019-11-03T06:30:00Z | 20.18 | 13 | < 25mph | PG362 | 1.69 | 2019-11-03T06:30:00Z | 20.18 | 13 | < 25mph | PG362 | 1.69 | 2019-11-03T07:50:00Z | 20.18 | 23 | < 25mph | PG362 | 1.69 | 2019-11-03T07:50:00Z | 20.18 | 23 | < 25mph
PG&E | 2019-11-04 | 23:32 | 34.6619 | -120.0852 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 8145 |  | 12000 | Conductor | Overhead | Yes | 43773 | 0.98056 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-125 | 2019 | 11 | 4 | 23 | 32 | 19-0121150 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 20066 | 2.0041 | 241_55 | <25mph | <15mph | HFTD - Distribution | 2019-11-04 23:32:00 | 2155 | 13.4228 | FALSE | <25mph | SXWC1 | 2.51 | 2019-11-04T07:09:00Z | 4.99 | 15 | < 25mph | TT594 | 4.6 | 2019-11-04T07:46:00Z | 5.99 | 40 | < 25mph | SXWC1 | 2.51 | 2019-11-04T08:09:00Z | 4.99 | 28 | < 25mph | TT480 | 7.81 | 2019-11-04T08:20:00Z | 8.99 | 77 | < 25mph
PG&E | 2019-11-10 | 9:47 | 35.0787 | -120.4974 |  | Herbaceous | 1 meter - < 3 meters | Cal Fire |  | 4Bx1110190931 |  | 12000 | Conductor | Overhead | Yes | 43779 | 0.40764 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-431 | 2019 | 11 | 10 | 9 | 47 | 19-0123396 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 19943 | 5.9544 | 222_78 | <25mph | <15mph | HFTD - Distribution | 2019-11-10 09:47:00 | 2161 | 16.9334 | FALSE | <25mph | PG168 | 0.77 | 2019-11-10T07:00:00Z | 8.05 | 14 | < 25mph | PG168 | 0.77 | 2019-11-10T07:00:00Z | 8.05 | 63 | < 25mph | PG168 | 0.77 | 2019-11-10T09:00:00Z | 11.34 | 26 | < 25mph | PG168 | 0.77 | 2019-11-10T09:00:00Z | 11.34 | 126 | < 25mph
PG&E | 2019-11-11 | 6:52 | 36.6822 | -119.1806 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 4Tj1111191656 |  | 12000 | Other | Overhead | Yes | 43780 | 0.28611 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-453 | 2019 | 11 | 11 | 6 | 52 | 19-0123468 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 109129 | 2.952 | 280_167 | <25mph | <15mph | HFTD - Distribution | 2019-11-11 06:52:00 | 2162 | 12.1773 | FALSE | <25mph | PG258 | 2.49 | 2019-11-11T07:50:00Z | 7 | 21 | < 25mph | PG374 | 4.84 | 2019-11-11T07:20:00Z | 7.61 | 62 | < 25mph | PG258 | 2.49 | 2019-11-11T07:50:00Z | 7 | 39 | < 25mph | PG374 | 4.84 | 2019-11-11T08:20:00Z | 7.81 | 116 | < 25mph
PG&E | 2019-11-21 | 16:26 | 40.3231 | -123.9202 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 192311141 |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-416 | 2019 | 11 | 21 | 16 | 26 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 5.8466 | 77_369 | <25mph | <15mph | HFTD - Distribution | 2019-11-21 16:26:00 | 2173 | 12.9212 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG274 | 5.92 | 2019-11-21T07:30:00Z | 2.26 | 7 | < 25mph |  |  |  | 0 | 0 | No data | PG274 | 5.92 | 2019-11-21T08:40:00Z | 2.55 | 13 | < 25mph
PG&E | 2019-11-22 | 4:43 | 39.6736 | -121.3855 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 103751102 |  | 12000 | Conductor | Overhead | Yes | 43791 | 0.19653 | Vegetation |  | Veg. contact |  |  |  | Fell into (slight defect) | 2019-428 | 2019 | 11 | 22 | 4 | 43 | 19-0127475 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3712 | 7.9177 | 183_331 | <25mph | <15mph | HFTD - Distribution | 2019-11-22 04:43:00 | 2174 | 11.8215 | FALSE | <25mph | PG099 | 3.33 | 2019-11-22T08:00:00Z | 0 | 7 | < 25mph | JBGC1 | 6.99 | 2019-11-22T07:13:00Z | 13 | 36 | < 25mph | PG099 | 3.33 | 2019-11-22T09:00:00Z | 0 | 13 | < 25mph | JBGC1 | 6.99 | 2019-11-22T08:13:00Z | 13 | 67 | < 25mph
PG&E | 2019-11-27 | 15:39 | 40.6579 | -122.4211 |  | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 103521102-2101107406{2413} |  | 12000 | Fuse | Overhead | Yes | 43796 | 0.65208 | Other Fire: Non-PG&E related | [5 empty] | Other/Unknown |  | 2019 | 11 | 27 | 15 | 39 | 19-0130770 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip failure | Fuse | 8302 | 6.9489 | 140_386 | <25mph | <15mph | HFTD - Distribution | 2019-11-27 15:39:00 | 2179 | 14.036 | FALSE | <25mph | F5970 | 3 | 2019-11-27T07:47:00Z | 17 | 11 | < 25mph | PG265 | 7.46 | 2019-11-27T08:00:00Z | 38.07 | 75 | 25-40mph | F5970 | 3 | 2019-11-27T09:00:00Z | 17 | 22 | < 25mph | PG265 | 7.46 | 2019-11-27T08:00:00Z | 38.07 | 142 | 25-40mph
PG&E | 2019-11-27 | 6:37 | 37.2717 | -122.3078 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 24101103 |  | 12000 | Conductor | Overhead | Yes | 43796 | 0.27569 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-362 | 2019 | 11 | 27 | 6 | 37 | 19-0130047 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 16680 | 9.7328 | 142_199 | <25mph | <15mph | HFTD - Distribution | 2019-11-27 06:37:00 | 2178 | 32.4983 | FALSE | 25-40mph | LAHC1 | 3.7 | 2019-11-27T07:07:00Z | 11.01 | 1 | < 25mph | PG150 | 6.93 | 2019-11-27T07:40:00Z | 32.37 | 33 | 25-40mph | LAHC1 | 3.7 | 2019-11-27T08:07:00Z | 14.99 | 2 | < 25mph | PG150 | 6.93 | 2019-11-27T08:10:00Z | 32.73 | 61 | 25-40mph
PG&E | 2019-11-29 | 20:18 | 39.8503 | -121.6312 |  | Shrub | 1 meter - < 3 meters | Unknown |  | 40700248, 42578814, 42578813 |  | 60000 | Pole | Overhead | Yes | 43798 | 0.84583 | Equipment - PG&E | Pole |  |  |  |  | no-match | 2019-10 | 2019 | 11 | 29 | 20 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Pole | N.A. | 13.1829 | 173_341 | <25mph | <15mph | HFTD - Transmission | 2019-11-29 20:18:00 | 2180 | 13.969 | FALSE | <25mph | PG333 | 3.51 | 2019-11-29T07:00:00Z | 10.38 | 54 | < 25mph | PG333 | 3.51 | 2019-11-29T07:00:00Z | 10.38 | 99 | < 25mph | PG333 | 3.51 | 2019-11-29T07:00:00Z | 10.38 | 102 | < 25mph | PG333 | 3.51 | 2019-11-29T07:00:00Z | 10.38 | 185 | < 25mph
PG&E | 2019-12-18 | 5:25 | 38.2817 | -120.517 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 101273893 |  | 12000 | Pole | Overhead | Yes | 43817 | 0.22569 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (No defect) | 2019-361 | 2019 | 12 | 18 | 5 | 25 | 19-0137065 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3185 | 6.993 | 220_255 | <25mph | <15mph | HFTD - Distribution | 2019-12-18 05:25:00 | 2183 | 18.6148 | FALSE | <25mph | ESPC1 | 1.49 | 2019-12-18T07:13:00Z | 15.99 | 25 | < 25mph | ESPC1 | 1.49 | 2019-12-18T07:13:00Z | 15.99 | 51 | < 25mph | ESPC1 | 1.49 | 2019-12-18T08:13:00Z | 15.99 | 48 | < 25mph | ESPC1 | 1.49 | 2019-12-18T08:13:00Z | 15.99 | 95 | < 25mph
Note on AP4: Based on the max wind gust speed in the hour of ignition. used wind gust speed factor of 1.6.
Note on AW4: Based on the max wind gust speed +/- 12 hours of ignition. Used wind gust speed factor of 1.6.
Note on AY4: based on mph_day_max
Note on AM560: Chong, Yanping: was under investigation, Kincade

## Random Wind
CPUC Reportable Ignitions from 2015-2019 + 7 fires ¦ HFTD + Wind Station Analysis
Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations | [7 empty] | Used in the pivot | [7 empty] | Used in Pivot | Used for Tranche | Used in the Risk Input Sheet | Used in Pivot | Used in the Risk Input Sheet | Used in the Risk Input | Used in EO-WF-14 | [7 empty] | 1
Utility Name | Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | Notes (Optional): | Veg Subdriver | 0_Ignition ID | 0_Year | 0_Month | 0_Day | 0_Hour | 0_Minute | 0_Outage ID | 0_HFTD Zone | 0_HFTD | 0_RFW Applicable | 0_Transmission/Distribution | 0_Tranche | 0_Fire Greater than 300 Acres | 0_Driver | 0_Subdriver | 0_Customer Minutes Interrupted | 1_wg_mph | 1_we_sn | 1_Wind Categorization | 1_Wind Category | 1_Tranche | 2_dt_local | 2_wg_row | 2_wg_mph_day_max | 1_same date and time as other ignition | 2_Wind Category | 4m/1h stid | 4m/1h time | 4m/1h dist | 4m/1h gust mph | 4m/1h count | 4m/1h Category | 8m/1h stid | 8m/1h time | 8m/1h dist | 8m/1h gust mph | 8m/1h count | 8m/1h Category | 4m/2h stid | 4m/2h time | 4m/2h dist | 4m/2h gust mph | 4m/2h count | 4m/2h Category | 8m/2h stid | 8m/2h time | 8m/2h dist | 8m/2h gust mph | 8m/2h count | 8m/2h Category
PG&E | 2018-06-19 | 0.01875 | 38.7604 | -120.8224 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101388356 | Unknown | 12000 | Conductor | Overhead | Yes | 43270 | 0.01875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1675 | 2018 | 6 | 19 | 0 | 27 | 18-0052111 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 141652 | 7.2853 | 207_281 | <25mph | <15mph | HFTD - Distribution | 2018-06-19 00:27:00 | 1417 | 13.5304 | FALSE | <25mph | PG068 | 3.2 | 2019-11-05T19:30:00Z | 6.8 | 18 | < 25mph | C6129 | 4.72 | 2019-11-05T19:44:00Z | 12.01 | 104 | < 25mph | PG068 | 3.2 | 2019-11-05T20:30:00Z | 7.61 | 36 | < 25mph | C6129 | 4.72 | 2019-11-05T19:59:00Z | 12.01 | 208 | < 25mph
PG&E | 2018-07-21 | 0.61875 | 35.6846 | -120.9427 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101943190 | Unknown | 21000 | Conductor | Overhead | Yes | 43302 | 0.61875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1775 | 2018 | 7 | 21 | 14 | 51 | 18-0062364 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 110814 | 14.9597 | 202_111 | <25mph | <15mph | HFTD - Distribution | 2018-07-21 14:51:00 | 1515 | 21.9627 | FALSE | <25mph | TABC1 | 2.21 | 2016-05-26T15:07:00Z | 4 | 1 | < 25mph | TABC1 | 2.21 | 2016-05-26T15:07:00Z | 4 | 17 | < 25mph | TABC1 | 2.21 | 2016-05-26T16:07:00Z | 5.99 | 2 | < 25mph | D4060 | 5.73 | 2016-05-26T16:18:00Z | 8.01 | 34 | < 25mph
PG&E | 2017-04-25 12:39 | 0.52639 | 38.6583 | -120.9762 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101376746 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 42850.5271 | 0.52639 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1072 | 2017 | 4 | 25 | 12 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 9.948 | 200_275 | <25mph | <15mph | HFTD - Distribution | 2017-04-25 12:38:00 | 812 | 10.5664 | FALSE | <25mph | D7401 | 2.53 | 2016-12-16T07:15:00Z | 14 | 8 | < 25mph | BENC1 | 5.2 | 2016-12-16T06:59:00Z | 30 | 69 | 25-40mph | D7401 | 2.53 | 2016-12-16T07:15:00Z | 14 | 16 | < 25mph | BENC1 | 5.2 | 2016-12-16T07:59:00Z | 32.99 | 138 | 25-40mph
PG&E | 2018-02-12 | 20:20 | 39.9395 | -121.6494 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430947 | Unknown | 12000 | Conductor | Overhead | Yes | 43143 | 20:20 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1561 | 2018 | 2 | 12 | 20 | 20 | 18-0013604 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 149212 | 10.1876 | 172_346 | <25mph | <15mph | HFTD - Distribution | 2018-02-12 20:20:00 | 1303 | 14.6044 | FALSE | <25mph | PG134 | 2.86 | 2019-05-10T01:10:00Z | 6.13 | 2 | < 25mph | CSTC1 | 7.88 | 2019-05-10T00:51:00Z | 13 | 22 | < 25mph | PG134 | 2.86 | 2019-05-10T01:10:00Z | 6.13 | 6 | < 25mph | CSTC1 | 7.88 | 2019-05-10T00:51:00Z | 13 | 51 | < 25mph
PG&E | 2015-03-04 18:44 | 2015-03-04 18:44 | 38.9995 | -122.7545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kelseyville FD | 102156367 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42067.7806 | 2015-03-04 18:44 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0271 | 2015 | 3 | 4 | 18 | 44 | 15-0017374 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29532 | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2015-03-04 18:44:00 | NA | 0 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.58 | 2018-06-24T09:57:00Z | 5.99 | 5 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.58 | 2018-06-24T10:57:00Z | 5.99 | 10 | < 25mph
PG&E | 2015-04-02 09:44 | 42096.4056 | 39.6772 | -121.492 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100338726 |  | 12000 | Conductor | Overhead | Yes | 42096.4056 | 42096.4056 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0284 | 2015 | 4 | 2 | 9 | 44 | 15-0023747 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 100204 | 15.7458 | 178_332 | <25mph | <15mph | HFTD - Distribution | 2015-04-02 09:44:00 | 30 | 15.7458 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JBGC1 | 4.06 | 2015-09-14T04:13:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | JBGC1 | 4.06 | 2015-09-14T04:13:00Z | 7 | 2 | < 25mph
PG&E | 2018-06-05 | 10:13 | 40.6183 | -122.3173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JASON COLLINS 530-225-4628 | 101467801 | None | 12000 | Conductor | Overhead | Yes | 43256 | 10:13 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1631 | 2018 | 6 | 5 | 10 | 13 | 18-0047539 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 277 | 7.1547 | 144_384 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 10:13:00 | 1373 | 12.6046 | FALSE | <25mph | C5599 | 1.27 | 2015-07-16T07:33:00Z | 0 | 2 | < 25mph | RRAC1 | 7.21 | 2015-07-16T07:24:00Z | 7 | 7 | < 25mph | C5599 | 1.27 | 2015-07-16T08:33:00Z | 0 | 4 | < 25mph | RRAC1 | 7.21 | 2015-07-16T07:24:00Z | 7 | 14 | < 25mph
PG&E | 2017-07-23 18:25 | 18:25 | 39.6723 | -123.5336 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103823226 | Unknown | 12000 | Conductor | Overhead | Yes | 42939.7676 | 18:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1284 | 2017 | 7 | 23 | 18 | 25 | 17-0064854 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 12864 | 11.8402 | 92_333 | <25mph | <15mph | HFTD - Distribution | 2017-07-23 18:25:00 | 1023 | 16.2282 | FALSE | <25mph | LAYC1 | 3.32 | 2019-04-02T18:29:00Z | 5.99 | 1 | < 25mph | LAYC1 | 3.32 | 2019-04-02T18:29:00Z | 5.99 | 1 | < 25mph | LAYC1 | 3.32 | 2019-04-02T19:29:00Z | 5.99 | 2 | < 25mph | LAYC1 | 3.32 | 2019-04-02T19:29:00Z | 5.99 | 2 | < 25mph
PG&E | 2018-08-10 | 12:54 | 38.799 | -120.73 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101386272 | AT&T | 12000 | Conductor | Overhead | Yes | 43322 | 12:54 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1832 | 2018 | 8 | 10 | 12 | 54 | 18-0068798 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 26532 | 10.1607 | 211_283 | <25mph | <15mph | HFTD - Distribution | 2018-08-10 12:54:00 | 1571 | 17.3224 | FALSE | <25mph | PG104 | 0.2 | 2018-09-07T02:40:00Z | 4.38 | 12 | < 25mph | PG104 | 0.2 | 2018-09-07T02:40:00Z | 4.38 | 66 | < 25mph | PG104 | 0.2 | 2018-09-07T02:40:00Z | 4.38 | 24 | < 25mph | PG104 | 0.2 | 2018-09-07T02:40:00Z | 4.38 | 132 | < 25mph
2. Cascade (Neu Wind Complex) | 2017-10-08 | 23:45 | 39.322 | -121.4021 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1988 | 2017 | 10 | 8 | 23 | 45 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Equip Failure | Conductor | 0 | 17.3686 | 182_312 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 23:45:00 | 1213 | 29.7104 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | BNGC1 | 4.15 | 2016-09-26T10:51:00Z | 1.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | BNGC1 | 4.15 | 2016-09-26T10:51:00Z | 1.01 | 2 | < 25mph
PG&E | 2017-04-25 12:39 | 12:38 | 38.6583 | -120.9762 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101376746 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 42850.5271 | 12:38 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1072 | 2017 | 4 | 25 | 12 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 9.948 | 200_275 | <25mph | <15mph | HFTD - Distribution | 2017-04-25 12:38:00 | 812 | 10.5664 | FALSE | <25mph | PG181 | 2.67 | 2018-11-24T04:00:00Z | 25.21 | 30 | 25-40mph | PG181 | 2.67 | 2018-11-24T04:00:00Z | 25.21 | 140 | 25-40mph | PG181 | 2.67 | 2018-11-24T05:10:00Z | 25.43 | 56 | 25-40mph | PG181 | 2.67 | 2018-11-24T05:10:00Z | 25.43 | 269 | 25-40mph
PG&E | 2016-07-21 21:45 | 2016-07-21 21:45 | 40.8566 | -122.3387 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101455670 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0870 | 2016 | 7 | 21 | 21 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.7351 | 143_397 | <25mph | <15mph | HFTD - Distribution | 2016-07-21 21:45:00 | 613 | 15.1303 | FALSE | <25mph | PG514 | 0.73 | 2019-12-07T11:40:00Z | 23.53 | 10 | < 25mph | PG519 | 7.5 | 2019-12-07T12:00:00Z | 50.71 | 27 | 40-55mph | PG514 | 0.73 | 2019-12-07T11:40:00Z | 23.53 | 20 | < 25mph | PG519 | 7.5 | 2019-12-07T12:50:00Z | 50.71 | 54 | 40-55mph
PG&E | 2015-09-24 04:30 | 2015-09-24 04:30 | 38.6769 | -123.314 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Str. 041/007 |  | 60000 | Conductor | Overhead | Yes | 42271.1875 | 2015-09-24 04:30 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0613 | 2015 | 9 | 24 | 4 | 30 | FU-2015-057 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 22680 | 6.5939 | 100_277 | <25mph | <15mph | HFTD - Transmission | 2015-09-24 04:30:00 | 358 | 13.8122 | FALSE | <25mph |  |  |  | 0 | 0 | No data | OAAC1 | 4.24 | 2018-11-05T00:33:00Z | 22.01 | 13 | < 25mph |  |  |  | 0 | 0 | No data | OAAC1 | 4.24 | 2018-11-05T01:33:00Z | 24.99 | 25 | < 25mph
PG&E | 2017-07-18 | 11:30 | 38.0484 | -120.5565 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 012/071 | Unknown | 115000 | Conductor | Overhead | Yes | 42934 | 11:30 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1265 | 2017 | 7 | 18 | 11 | 30 | INT-09873 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 55499 | 7.0574 | 219_242 | <25mph | <15mph | HFTD - Transmission | 2017-07-18 11:30:00 | 1005 | 15.7901 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KO22 | 7.54 | 2017-01-22T14:35:00Z | 23.02 | 27 | < 25mph |  |  |  | 0 | 0 | No data | KO22 | 7.54 | 2017-01-22T14:55:00Z | 24.16 | 54 | < 25mph
PG&E | 2018-07-17 | 11:58 | 37.2217 | -121.6778 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Luis Morado state arson fire fighter | 100601345 | Unknown | 12000 | Conductor | Overhead | Yes | 43298 | 11:58 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1756 | 2018 | 7 | 17 | 11 | 58 | 18-0060617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 5865 | 5.1834 | 170_196 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 11:58:00 | 1496 | 14.408 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E4742 | 5.37 | 2016-01-26T17:39:00Z | 3 | 33 | < 25mph |  |  |  | 0 | 0 | No data | C7794 | 7.07 | 2016-01-26T18:45:00Z | 4.99 | 64 | < 25mph
PG&E | 2019-06-17 | 10:25 | 38.511 | -122.2134 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 43051101 |  | 12000 | Conductor | Overhead | Yes | 43633 | 10:25 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-84 | 2019 | 6 | 17 | 10 | 25 | 19-0068579 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 306900 | 10.2943 | 147_267 | <25mph | <15mph | HFTD - Distribution | 2019-06-17 10:25:00 | 1843 | 15.8677 | FALSE | <25mph | ATLC1 | 3.74 | 2018-01-15T16:29:00Z | 14.99 | 1 | < 25mph | ATLC1 | 3.74 | 2018-01-15T16:29:00Z | 14.99 | 1 | < 25mph | ATLC1 | 3.74 | 2018-01-15T16:29:00Z | 14.99 | 2 | < 25mph | ATLC1 | 3.74 | 2018-01-15T16:29:00Z | 14.99 | 2 | < 25mph
PG&E | 2016-04-13 19:28 | 2016-04-13 19:28 | 40.4954 | -124.1219 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103659313 |  | 12000 | Conductor | Overhead | Yes | 42473.8111 | 2016-04-13 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0706 | 2016 | 4 | 13 | 19 | 28 | 16-0028421 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 688 | 19.0823 | 68_379 | <25mph | <15mph | HFTD - Distribution | 2016-04-13 19:28:00 | 450 | 22.9769 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C5061 | 4.94 | 2015-12-30T13:27:00Z | 10 | 26 | < 25mph |  |  |  | 0 | 0 | No data | C5061 | 4.94 | 2015-12-30T14:07:00Z | 12.01 | 50 | < 25mph
PG&E | 2019-09-27 | 10:30 | 36.5336 | -121.1464 | Vegetation | Barren/Other | 0.25 - 10 Acres | Cal Fire |  | 182492105 |  | 21000 | Conductor | Overhead | Yes | 43735 | 10:30 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-359 | 2019 | 9 | 27 | 10 | 30 | 19-0104536 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20631 | 5.3593 | 193_158 | <25mph | <15mph | HFTD - Distribution | 2019-09-27 10:30:00 | 2062 | 16.3021 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.34 | 2016-06-23T10:37:00Z | 8.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.34 | 2016-06-23T10:37:00Z | 8.01 | 2 | < 25mph
PG&E | 2016-10-14 19:45 | 0.82222 | 39.6245 | -121.5382 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100435570 |  | 0 – 750 | Conductor | Overhead | Yes | 42657.8228 | 0.82222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1036 | 2016 | 10 | 14 | 19 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.5623 | 177_329 | <25mph | <15mph | HFTD - Distribution | 2016-10-14 19:44:00 | 777 | 22.2526 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG463 | 4.72 | 2019-07-04T19:30:00Z | 14.7 | 43 | < 25mph |  |  |  | 0 | 0 | No data | PG427 | 6.09 | 2019-07-04T20:40:00Z | 16.22 | 84 | < 25mph
PG&E | 2019-08-20 | 9:03 | 41.1088 | -121.5034 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-297 | 2019 | 8 | 20 | 9 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 2.4258 | 178_411 | <25mph | <15mph | HFTD - Distribution | 2019-08-20 09:03:00 | 1990 | 15.6046 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2015-04-30 00:26 | 2015-04-30 00:26 | 37.2401 | -122.2472 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 1145 VERDE R |  | 12000 | Conductor | Overhead | Yes | 42124.0181 | 2015-04-30 00:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0304 | 2015 | 4 | 30 | 0 | 26 | 15-0030607 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1256 | 5.7566 | 145_197 | <25mph | <15mph | HFTD - Distribution | 2015-04-30 00:26:00 | 50 | 15.5915 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6800 | 5.71 | 2017-10-03T06:33:00Z | 5.99 | 13 | < 25mph |  |  |  | 0 | 0 | No data | E6800 | 5.71 | 2017-10-03T06:33:00Z | 5.99 | 26 | < 25mph
PG&E | 2019-06-19 | 11:44 | 39.8612 | -121.6907 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100400933 |  | 12000 | Conductor | Overhead | Yes | 43635 | 11:44 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-224 | 2019 | 6 | 19 | 11 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.9144 | 170_342 | <25mph | <15mph | HFTD - Distribution | 2019-06-19 11:44:00 | 1855 | 12.1329 | FALSE | <25mph | C8878 | 2.27 | 2016-04-16T11:28:00Z | 0 | 13 | < 25mph | CSTC1 | 4.21 | 2016-04-16T10:51:00Z | 7 | 21 | < 25mph | C8878 | 2.27 | 2016-04-16T12:28:00Z | 0 | 25 | < 25mph | E4833 | 5.86 | 2016-04-16T12:11:00Z | 8.99 | 40 | < 25mph
PG&E | 2016-08-22 | 2016-08-22 16:10 | 37.9666 | -120.2395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Toulumne City FD | 101043683 |  | 17000 | Conductor | Overhead | Yes | 42604 | 2016-08-22 16:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0941 | 2016 | 8 | 22 | 16 | 10 | 16-0059149 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 78534 | 13.4322 | 233_237 | <25mph | <15mph | HFTD - Distribution | 2016-08-22 16:10:00 | 684 | 13.7297 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.67 | 2016-10-13T17:02:00Z | 15.99 | 5 | < 25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.67 | 2016-10-13T18:02:00Z | 15.99 | 10 | < 25mph
PG&E | 2016-10-19 10:42 | 10:42 | 38.5098 | -122.45 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | st helena | 102242552 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42662.4459 | 10:42 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1040 | 2016 | 10 | 19 | 10 | 42 | 16-0073955 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 693 | 4.5329 | 137_268 | <25mph | <15mph | HFTD - Distribution | 2016-10-19 10:42:00 | 781 | 13.4953 | FALSE | <25mph | PG091 | 3.91 | 2019-02-25T05:00:00Z | 8.12 | 7 | < 25mph | PG199 | 6.48 | 2019-02-25T04:20:00Z | 12.28 | 40 | < 25mph | PG091 | 3.91 | 2019-02-25T05:00:00Z | 8.12 | 13 | < 25mph | PG199 | 6.48 | 2019-02-25T04:20:00Z | 12.28 | 76 | < 25mph
PG&E | 2018-10-07 | 0.072222 | 37.178 | -122.0267 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Mike Mathiesen 408-472-1613 Incident # SCU7096 | 100518363 | Unknown | 12000 | Conductor | Overhead | Yes | 43380 | 0.072222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1929 | 2018 | 10 | 7 | 1 | 44 | 18-0087807 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 224444 | 25.0906 | 154_194 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-07 01:44:00 | 1668 | 25.864 | FALSE | 25-40mph | AV151 | 2.69 | 2016-03-30T03:15:00Z | 8.01 | 12 | < 25mph | AS952 | 7.57 | 2016-03-30T02:47:00Z | 14 | 125 | < 25mph | AV151 | 2.69 | 2016-03-30T03:45:00Z | 8.01 | 24 | < 25mph | AS952 | 7.57 | 2016-03-30T02:47:00Z | 14 | 257 | < 25mph
PG&E | 2019-09-22 | 11:56 | 37.5168 | -119.9159 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103967994 |  | 21000 | Pole | Overhead | Yes | 43730 | 11:56 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-452 | 2019 | 9 | 22 | 11 | 56 | 19-0102232 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 133232 | 11.5782 | 247_213 | <25mph | <15mph | HFTD - Distribution | 2019-09-22 11:56:00 | 2051 | 13.905 | FALSE | <25mph | MPOC1 | 3.98 | 2019-05-04T11:07:00Z | 8.99 | 7 | < 25mph | MPOC1 | 3.98 | 2019-05-04T11:07:00Z | 8.99 | 15 | < 25mph | MPOC1 | 3.98 | 2019-05-04T12:07:00Z | 10 | 14 | < 25mph | MPOC1 | 3.98 | 2019-05-04T12:07:00Z | 10 | 30 | < 25mph
PG&E | 2016-08-02 | 2016-08-02 16:15 | 37.0312 | -119.4395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Fresno County FD | 100675986 |  | 12000 | Conductor | Overhead | Yes | 42584 | 2016-08-02 16:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0900 | 2016 | 8 | 2 | 16 | 15 | 16-0054552 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 265566 | 14.0604 | 268_186 | <25mph | <15mph | HFTD - Distribution | 2016-08-02 16:15:00 | 643 | 14.6638 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTQC1 | 4.04 | 2015-02-22T00:52:00Z | 10 | 11 | < 25mph |  |  |  | 0 | 0 | No data | MTQC1 | 4.04 | 2015-02-22T00:52:00Z | 10 | 19 | < 25mph
PG&E | 2015-08-31 14:28 | 2015-08-31 14:28 | 36.5325 | -121.1462 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 29401 Hwy 25 |  | 21000 | Conductor | Overhead | Yes | 42247.6028 | 2015-08-31 14:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0568 | 2015 | 8 | 31 | 14 | 28 | 15-0058455 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25668 | 4.8975 | 193_158 | <25mph | <15mph | HFTD - Distribution | 2015-08-31 14:28:00 | 312 | 19.6836 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.27 | 2018-05-12T07:37:00Z | 4.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.27 | 2018-05-12T07:37:00Z | 4.99 | 2 | < 25mph
PG&E | 2017-07-12 15:09 | 15:09 | 37.1491 | -122.0037 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 103565794 | Unknown | 21000 | Conductor | Overhead | Yes | 42928.6313 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1248 | 2017 | 7 | 12 | 15 | 9 | 17-0062439 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24690 | 9.5326 | 155_192 | <25mph | <15mph | HFTD - Distribution | 2017-07-12 15:09:00 | 986 | 9.5326 | FALSE | <25mph | D8979 | 3.17 | 2016-02-23T08:03:00Z | 8.99 | 26 | < 25mph | E6085 | 6.59 | 2016-02-23T08:24:00Z | 13 | 131 | < 25mph | D8979 | 3.17 | 2016-02-23T09:03:00Z | 12.01 | 52 | < 25mph | E6085 | 6.59 | 2016-02-23T08:39:00Z | 14.99 | 254 | < 25mph
PG&E | 2018-06-05 | 13:45 | 38.5432 | -122.7202 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 102031673 | Unknown | 12000 | Conductor | Overhead | Yes | 43256 | 13:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1633 | 2018 | 6 | 5 | 13 | 45 | 18-0047625 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 40599 | 7.3889 | 125_270 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 13:45:00 | 1375 | 15.9614 | FALSE | <25mph | E6724 | 3.93 | 2017-04-04T23:40:00Z | 11.01 | 16 | < 25mph | C0677 | 6.65 | 2017-04-05T00:12:00Z | 12.01 | 71 | < 25mph | E6724 | 3.93 | 2017-04-04T23:40:00Z | 11.01 | 30 | < 25mph | C0677 | 6.65 | 2017-04-05T01:07:00Z | 12.01 | 139 | < 25mph
PG&E | 2017-12-29 | 16:31 | 37.8517 | -122.1586 | Vegetation | Rural | < 3 Meters | Fire Agency | 925-933-1313 | 100488954 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1552 | 2017 | 12 | 29 | 16 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 4.4772 | 149_231 | <25mph | <15mph | HFTD - Distribution | 2017-12-29 16:31:00 | 1294 | 9.6531 | FALSE | <25mph | F2503 | 2.91 | 2019-02-10T21:16:00Z | 24 | 58 | < 25mph | F2503 | 2.91 | 2019-02-10T21:16:00Z | 24 | 167 | < 25mph | F2503 | 2.91 | 2019-02-10T21:16:00Z | 24 | 114 | < 25mph | F2503 | 2.91 | 2019-02-10T21:16:00Z | 24 | 334 | < 25mph
PG&E | 2015-06-09 16:20 | 2015-06-09 16:20 | 38.3822 | -122.4316 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102269716 | Pacific Bell | 21000 | Unknown | Overhead | Yes | 42164.6806 | 2015-06-09 16:20 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0369 | 2015 | 6 | 9 | 16 | 20 | 15-0039860 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 4184 | 20.783 | 138_260 | <25mph | <15mph | HFTD - Distribution | 2015-06-09 16:20:00 | 115 | 24.1918 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KENWW | 6.21 | 2017-08-30T20:00:00Z | 8.21 | 8 | < 25mph |  |  |  | 0 | 0 | No data | KENWW | 6.21 | 2017-08-30T21:00:00Z | 9.89 | 17 | < 25mph
PG&E | 2018-10-16 | 16:30 | 38.7754 | -122.8976 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MARK GRADEK (707) 889-4303 | 101962692 | AT&T | 12000 | Conductor | Overhead | Yes | 43389 | 16:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1943 | 2018 | 10 | 16 | 16 | 30 | 18-0091127 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 744 | 10.3513 | 118_282 | <25mph | <15mph | HFTD - Distribution | 2018-10-16 16:30:00 | 1682 | 19.9126 | FALSE | <25mph |  |  |  | 0 | 0 | No data | HWKC1 | 4.29 | 2016-01-21T16:56:00Z | 18.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | HWKC1 | 4.29 | 2016-01-21T17:56:00Z | 20 | 2 | < 25mph
PG&E | 2018-08-05 | 13:56 | 37.4005 | -119.7532 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | JIM FORGA 209-966-3621 | 101017235 | Unknown | 12000 | Conductor | Overhead | Yes | 43317 | 13:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1821 | 2018 | 8 | 5 | 13 | 56 | 18-0066905 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 7325 | 10.7759 | 254_206 | <25mph | <15mph | HFTD - Distribution | 2018-08-05 13:56:00 | 1561 | 13.3386 | FALSE | <25mph | MCFC1 | 1.01 | 2017-07-13T06:02:00Z | 4.99 | 2 | < 25mph | E9110 | 4.41 | 2017-07-13T06:12:00Z | 8.01 | 30 | < 25mph | MCFC1 | 1.01 | 2017-07-13T06:02:00Z | 4.99 | 4 | < 25mph | E9110 | 4.41 | 2017-07-13T06:42:00Z | 8.01 | 63 | < 25mph
PG&E | 2015-08-29 03:30 | 2015-08-29 03:30 | 38.6302 | -122.8327 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Dirt road across from 3204 Rio Lindo Rd, Healdsburg |  | 12000 | Conductor | Overhead | Yes | 42245.1458 | 2015-08-29 03:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0566 | 2015 | 8 | 29 | 3 | 30 | 15-0058127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4780 | 9.2134 | 120_274 | <25mph | <15mph | HFTD - Distribution | 2015-08-29 03:30:00 | 310 | 15.1029 | FALSE | <25mph | F39WW | 3.02 | 2017-06-04T09:15:00Z | 2.1 | 13 | < 25mph | HWKC1 | 7.25 | 2017-06-04T08:56:00Z | 10 | 39 | < 25mph | F39WW | 3.02 | 2017-06-04T10:30:00Z | 2.42 | 27 | < 25mph | HWKC1 | 7.25 | 2017-06-04T09:56:00Z | 11.01 | 80 | < 25mph
5. Atlas (Southern LNU Complex) | 2017-10-08 | 21:52 | 38.3921 | -122.2437 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1991 | 2017 | 10 | 8 | 21 | 52 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 37.6357 | 146_261 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-08 21:52:00 | 1206 | 41.3099 | FALSE | 40-55mph | F0187 | 3.03 | 2017-04-12T09:34:00Z | 5.99 | 4 | < 25mph | ATLC1 | 5.83 | 2017-04-12T09:29:00Z | 24.99 | 10 | < 25mph | F0187 | 3.03 | 2017-04-12T09:34:00Z | 5.99 | 8 | < 25mph | ATLC1 | 5.83 | 2017-04-12T10:29:00Z | 24.99 | 16 | < 25mph
PG&E | 2018-07-31 | 7:57 | 38.9559 | -122.7274 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102162351 | AT&T | 12000 | Conductor | Overhead | Yes | 43312 | 7:57 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1803 | 2018 | 7 | 31 | 7 | 57 | 18-0065276 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 89832 | 7.6131 | 125_292 | <25mph | <15mph | HFTD - Distribution | 2018-07-31 07:57:00 | 1543 | 16.0718 | FALSE | <25mph | KELC1 | 3.24 | 2019-10-17T13:57:00Z | 27 | 1 | 25-40mph | KELC1 | 3.24 | 2019-10-17T13:57:00Z | 27 | 31 | 25-40mph | KELC1 | 3.24 | 2019-10-17T13:57:00Z | 27 | 2 | 25-40mph | KELC1 | 3.24 | 2019-10-17T13:57:00Z | 27 | 62 | 25-40mph
PG&E | 2017-10-28 | 15:26 | 39.4516 | -123.3838 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102209084 | Unknown | 12000 | Conductor | Overhead | Yes | 43036 | 15:26 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | no-match | 1510 | 2017 | 10 | 28 | 15 | 26 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 10.3107 | 98_320 | <25mph | <15mph | HFTD - Distribution | 2017-10-28 15:26:00 | 1252 | 11.7696 | FALSE | <25mph | E4027 | 3.28 | 2018-03-27T08:53:00Z | 3 | 12 | < 25mph | E4027 | 3.28 | 2018-03-27T08:53:00Z | 3 | 23 | < 25mph | E4027 | 3.28 | 2018-03-27T08:53:00Z | 3 | 24 | < 25mph | E4027 | 3.28 | 2018-03-27T08:53:00Z | 3 | 46 | < 25mph
3. Redwood Valley (Mendocino Lake Complex) | 2017-10-08 | 23:36 | 39.2487 | -123.1663 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1989 | 2017 | 10 | 8 | 23 | 36 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 24.7673 | 107_309 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 23:36:00 | 1212 | 30.3049 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | D9878 | 7.09 | 2016-02-20T17:40:00Z | 4 | 24 | < 25mph |  |  |  | 0 | 0 | No data | D9878 | 7.09 | 2016-02-20T19:00:00Z | 5.99 | 48 | < 25mph
PG&E | 2017-11-11 12:17 | 11:57 | 35.1191 | -120.3936 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Jordan Dayley ph#929-3911,engine#3467 | 101931190 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43050.5115 | 11:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1518 | 2017 | 11 | 11 | 11 | 57 | 17-0094408 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29093 | 8.6182 | 227_80 | <25mph | <15mph | HFTD - Distribution | 2017-11-11 11:57:00 | 1260 | 14.1707 | FALSE | <25mph | AU609 | 1.13 | 2018-11-21T19:15:00Z | 13 | 4 | < 25mph | F0412 | 7.06 | 2018-11-21T18:35:00Z | 14.99 | 10 | < 25mph | AU609 | 1.13 | 2018-11-21T19:45:00Z | 14 | 8 | < 25mph | F0412 | 7.06 | 2018-11-21T18:35:00Z | 14.99 | 20 | < 25mph
PG&E | 2018-08-08 | 16:03 | 37.2974 | -122.2651 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 100307515 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 16:03 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1831 | 2018 | 8 | 8 | 16 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.1654 | 144_201 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:03:00 | 1570 | 9.1654 | FALSE | <25mph | PG605 | 3.12 | 2019-09-15T21:50:00Z | 18.99 | 18 | < 25mph | PG605 | 3.12 | 2019-09-15T21:50:00Z | 18.99 | 66 | < 25mph | PG605 | 3.12 | 2019-09-15T21:50:00Z | 18.99 | 35 | < 25mph | PG150 | 4.42 | 2019-09-15T22:20:00Z | 20.89 | 126 | < 25mph
PG&E | 2016-07-31 12:11 | 2016-07-31 12:11 | 38.7827 | -120.9168 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101417359 |  | 21000 | Conductor | Overhead | Yes | 42582.5076 | 2016-07-31 12:11 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0895 | 2016 | 7 | 31 | 12 | 11 | 16-0053949 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 10.9662 | 203_282 | <25mph | <15mph | HFTD - Distribution | 2016-07-31 12:11:00 | 638 | 14.1387 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D4464 | 7.25 | 2015-10-30T05:57:00Z | 7 | 47 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 6.02 | 2015-10-30T06:56:00Z | 8.01 | 94 | < 25mph
PG&E | 2016-07-03 15:00 | 2016-07-03 15:00 | 38.0348 | -120.3809 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101050507 |  | 17000 | Conductor | Overhead | Yes | 42554.625 | 2016-07-03 15:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0837 | 2016 | 7 | 3 | 15 | 0 | 16-0047689 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38812 | 10.6263 | 226_241 | <25mph | <15mph | HFTD - Distribution | 2016-07-03 15:00:00 | 580 | 12.5395 | FALSE | <25mph | PG058 | 3.89 | 2019-06-19T13:50:00Z | 1.32 | 6 | < 25mph | PG156 | 6.39 | 2019-06-19T13:10:00Z | 18.41 | 43 | < 25mph | PG058 | 3.89 | 2019-06-19T15:00:00Z | 1.32 | 12 | < 25mph | PG156 | 6.39 | 2019-06-19T13:10:00Z | 18.41 | 86 | < 25mph
PG&E | 2016-07-03 15:00 | 2016-07-03 15:00 | 38.0348 | -120.3809 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101050507 |  | 17000 | Conductor | Overhead | Yes | 42554.625 | 2016-07-03 15:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0837 | 2016 | 7 | 3 | 15 | 0 | 16-0047689 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38812 | 10.6263 | 226_241 | <25mph | <15mph | HFTD - Distribution | 2016-07-03 15:00:00 | 580 | 12.5395 | FALSE | <25mph | F0305 | 3.78 | 2017-01-26T21:10:00Z | 0 | 11 | < 25mph | MOUC1 | 7.53 | 2017-01-26T21:02:00Z | 14 | 12 | < 25mph | F0305 | 3.78 | 2017-01-26T22:10:00Z | 0 | 23 | < 25mph | MOUC1 | 7.53 | 2017-01-26T22:02:00Z | 14 | 25 | < 25mph
PG&E | 2019-05-10 | 14:52 | 40.704 | -122.8314 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Fire Dept | Lewiston FD | Keswick-Trinity 60Kv Line |  | 60000 | Conductor | Overhead | Yes | 43595 | 14:52 | Vegetation |  | Contact from Object - Other | Electric Facility |  |  | no-match | 2019-301 | 2019 | 5 | 10 | 14 | 52 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.0535 | 123_389 | <25mph | <15mph | HFTD - Transmission | 2019-05-10 14:52:00 | 1766 | 13.0849 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TCAC1 | 5.87 | 2015-11-04T23:28:00Z | 10 | 7 | < 25mph |  |  |  | 0 | 0 | No data | TCAC1 | 5.87 | 2015-11-04T23:28:00Z | 10 | 14 | < 25mph
PG&E | 2017-08-14 07:56 | 07:56 | 39.1794 | -120.9761 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100083743 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42961.3308 | 07:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1334 | 2017 | 8 | 14 | 7 | 56 | 17-0070063 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3012 | 6.4958 | 200_304 | <25mph | <15mph | HFTD - Distribution | 2017-08-14 07:56:00 | 1071 | 15.2686 | FALSE | <25mph | D8321 | 3.61 | 2017-12-06T09:55:00Z | 2.01 | 18 | < 25mph | SETC1 | 4.92 | 2017-12-06T10:28:00Z | 4 | 67 | < 25mph | D8321 | 3.61 | 2017-12-06T11:30:00Z | 3 | 36 | < 25mph | SETC1 | 4.92 | 2017-12-06T10:28:00Z | 4 | 133 | < 25mph
PG&E | 2017-07-01 | 12:02 | 39.8209 | -121.6418 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 003/039 | Unknown | 60000 | Conductor | Overhead | Yes | 42917 | 12:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1212 | 2017 | 7 | 1 | 12 | 2 | INT-09792 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.6345 | 172_339 | <25mph | <15mph | HFTD - Transmission | 2017-07-01 12:02:00 | 954 | 9.664 | FALSE | <25mph | C8878 | 3.55 | 2016-10-25T15:28:00Z | 13 | 18 | < 25mph | CSTC1 | 7.61 | 2016-10-25T14:51:00Z | 18.99 | 28 | < 25mph | C8878 | 3.55 | 2016-10-25T16:13:00Z | 14.99 | 36 | < 25mph | CSTC1 | 7.61 | 2016-10-25T15:51:00Z | 25.99 | 56 | 25-40mph
PG&E | 2016-06-21 | 2016-06-21 10:09 | 39.0294 | -121.2927 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100024816 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | no-match | 0813 | 2016 | 6 | 21 | 10 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 5.0939 | 187_296 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 10:09:00 | 555 | 12.3682 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D7902 | 7.03 | 2016-12-07T10:04:00Z | 4 | 16 | < 25mph |  |  |  | 0 | 0 | No data | D7902 | 7.03 | 2016-12-07T11:09:00Z | 4 | 32 | < 25mph
PG&E | 2019-05-24 | 15:03 | 35.1696 | -120.5103 |  | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 40589503 |  | 500000 | Pole | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-100 | 2019 | 5 | 24 | 15 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 14.866 | 222_83 | <25mph | <15mph | HFTD - Transmission | 2019-05-24 15:03:00 | 1780 | 15.7146 | FALSE | <25mph | C9687 | 3.56 | 2018-11-17T08:40:00Z | 0 | 13 | < 25mph | F0194 | 5.22 | 2018-11-17T08:26:00Z | 3 | 37 | < 25mph | C9687 | 3.56 | 2018-11-17T09:40:00Z | 2.01 | 25 | < 25mph | F0194 | 5.22 | 2018-11-17T09:36:00Z | 4.99 | 76 | < 25mph
PG&E | 2016-06-19 | 2016-06-19 17:19 | 38.4508 | -122.3546 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire--napa fire | 102256859 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 17:19 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0808 | 2016 | 6 | 19 | 17 | 19 | 16-0044337 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 672 | 13.296 | 141_264 | <25mph | <15mph | HFTD - Distribution | 2016-06-19 17:19:00 | 552 | 13.7776 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.13 | 2015-09-20T06:29:00Z | 0 | 1 | < 25mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.13 | 2015-09-20T07:29:00Z | 0 | 2 | < 25mph
PG&E | 2015-09-10 18:39 | 2015-09-10 18:39 | 40.7569 | -123.7958 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 096/004 |  | 115000 | Conductor | Overhead | Yes | 42257.7771 | 2015-09-10 18:39 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0590 | 2015 | 9 | 10 | 18 | 39 | RM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 2.2423 | 82_393 | <25mph | <15mph | HFTD - Transmission | 2015-09-10 18:39:00 | 335 | 12.4043 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.39 | 2015-02-10T23:55:00Z | 12.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.39 | 2015-02-10T23:55:00Z | 12.01 | 2 | < 25mph
PG&E | 2019-07-23 | 16:55 | 37.2128 | -119.505 | Gun Shot | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | 252521103 |  | 12000 | Conductor | Overhead | Yes | 43669 | 16:55 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-434 | 2019 | 7 | 23 | 16 | 55 | 19-0080383 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 513358 | 13.6168 | 265_196 | <25mph | <15mph | HFTD - Distribution | 2019-07-23 16:55:00 | 1923 | 13.6168 | FALSE | <25mph | C6459 | 1.76 | 2016-08-18T17:20:00Z | 5.99 | 3 | < 25mph | C6459 | 1.76 | 2016-08-18T17:20:00Z | 5.99 | 3 | < 25mph | NFRC1 | 1.4 | 2016-08-18T17:55:00Z | 8.01 | 4 | < 25mph | NFRC1 | 1.4 | 2016-08-18T17:55:00Z | 8.01 | 4 | < 25mph
PG&E | 2018-02-12 | 20:20 | 39.9395 | -121.6494 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430947 | Unknown | 12000 | Conductor | Overhead | Yes | 43143 | 20:20 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1561 | 2018 | 2 | 12 | 20 | 20 | 18-0013604 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 149212 | 10.1876 | 172_346 | <25mph | <15mph | HFTD - Distribution | 2018-02-12 20:20:00 | 1303 | 14.6044 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CSTC1 | 7.88 | 2018-02-17T00:51:00Z | 11.01 | 21 | < 25mph |  |  |  | 0 | 0 | No data | CSTC1 | 7.88 | 2018-02-17T01:51:00Z | 11.01 | 40 | < 25mph
PG&E | 2018-06-30 | 22:36 | 39.1141 | -121.077 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Matt Wallen (530) 277-3312 Incident # NEU015486 | 100105380 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 22:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1717 | 2018 | 6 | 30 | 22 | 36 | 18-0056039 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 8004 | 7.8488 | 196_300 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 22:36:00 | 1458 | 15.8656 | FALSE | <25mph | E1789 | 3.68 | 2016-09-02T11:36:00Z | 3 | 28 | < 25mph | E1789 | 3.68 | 2016-09-02T11:36:00Z | 3 | 74 | < 25mph | E1789 | 3.68 | 2016-09-02T12:54:00Z | 3 | 56 | < 25mph | E1789 | 3.68 | 2016-09-02T12:54:00Z | 3 | 149 | < 25mph
PG&E | 2017-07-18 | 11:30 | 38.0484 | -120.5565 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 012/071 | Unknown | 115000 | Conductor | Overhead | Yes | 42934 | 11:30 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1265 | 2017 | 7 | 18 | 11 | 30 | INT-09873 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 55499 | 7.0574 | 219_242 | <25mph | <15mph | HFTD - Transmission | 2017-07-18 11:30:00 | 1005 | 15.7901 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C9085 | 5.13 | 2015-03-23T14:05:00Z | 0 | 5 | < 25mph |  |  |  | 0 | 0 | No data | C9085 | 5.13 | 2015-03-23T15:05:00Z | 0 | 9 | < 25mph
PG&E | 2018-10-20 | 14:31 | 40.5218 | -124.1137 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Str. 003/000 | None | 60000 | Conductor | Overhead | Yes | 43393 | 14:31 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1947 | 2018 | 10 | 20 | 14 | 31 | INT-11477 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 410982 | 9.6901 | 69_380 | <25mph | <15mph | HFTD - Transmission | 2018-10-20 14:31:00 | 1686 | 10.3412 | FALSE | <25mph | AT493 | 3.34 | 2015-03-20T22:33:00Z | 4.99 | 24 | < 25mph | AT493 | 3.34 | 2015-03-20T22:33:00Z | 4.99 | 24 | < 25mph | AT493 | 3.34 | 2015-03-21T00:04:00Z | 10 | 48 | < 25mph | AT493 | 3.34 | 2015-03-21T00:04:00Z | 10 | 48 | < 25mph
PG&E | 2018-10-07 | 1:44 | 37.178 | -122.0267 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Mike Mathiesen 408-472-1613 Incident # SCU7096 | 100518363 | Unknown | 12000 | Conductor | Overhead | Yes | 43380 | 1:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1929 | 2018 | 10 | 7 | 1 | 44 | 18-0087807 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 224444 | 25.0906 | 154_194 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-07 01:44:00 | 1668 | 25.864 | FALSE | 25-40mph | AV005 | 3.71 | 2015-02-28T06:47:00Z | 8.99 | 10 | < 25mph | D3546 | 4.3 | 2015-02-28T07:05:00Z | 20 | 105 | < 25mph | AV005 | 3.71 | 2015-02-28T06:47:00Z | 8.99 | 20 | < 25mph | D3546 | 4.3 | 2015-02-28T07:45:00Z | 22.97 | 208 | < 25mph
PG&E | 2017-07-19 | 0.24444 | 37.0905 | -119.6047 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Tower 003/001 | Unknown | 115000 | Conductor | Overhead | Yes | 42935 | 0.24444 | Contact From Object | N.A. | Other | Electric Facility | Unknown |  | no-match | 1269 | 2017 | 7 | 19 | 5 | 52 | INT-09877 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 0 | 0.36815 | 261_189 | <25mph | <15mph | HFTD - Transmission | 2017-07-19 05:52:00 | 1008 | 14.3689 | FALSE | <25mph | PG484 | 0.44 | 2019-08-17T00:20:00Z | 17.09 | 12 | < 25mph | PG484 | 0.44 | 2019-08-17T00:20:00Z | 17.09 | 79 | < 25mph | PG484 | 0.44 | 2019-08-17T00:20:00Z | 17.09 | 24 | < 25mph | PG484 | 0.44 | 2019-08-17T00:20:00Z | 17.09 | 158 | < 25mph
PG&E | 2017-09-17 | 17:38 | 38.9946 | -121.0261 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100029537 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42995 | 17:38 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Branch (OverHanging) | 1417 | 2017 | 9 | 17 | 17 | 38 | 17-0079585 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 28509 | 11.5169 | 198_294 | <25mph | <15mph | HFTD - Distribution | 2017-09-17 17:38:00 | 1155 | 15.8476 | FALSE | <25mph | C0713 | 1.74 | 2018-10-16T17:19:00Z | 0 | 15 | < 25mph | C5488 | 5.47 | 2018-10-16T16:32:00Z | 5.99 | 29 | < 25mph | C0713 | 1.74 | 2018-10-16T18:19:00Z | 7 | 31 | < 25mph | C0713 | 1.74 | 2018-10-16T18:19:00Z | 7 | 60 | < 25mph
PG&E | 2018-08-07 | 21:03 | 38.2129 | -120.9184 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102042811 | Unknown | 12000 | Conductor | Overhead | Yes | 43319 | 21:03 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1828 | 2018 | 8 | 7 | 21 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2018-08-07 21:03:00 | NA | 0 | FALSE | <25mph | CMAC1 | 2.92 | 2015-07-21T02:59:00Z | 13 | 1 | < 25mph | CMAC1 | 2.92 | 2015-07-21T02:59:00Z | 13 | 1 | < 25mph | CMAC1 | 2.92 | 2015-07-21T02:59:00Z | 13 | 2 | < 25mph | CMAC1 | 2.92 | 2015-07-21T02:59:00Z | 13 | 2 | < 25mph
PG&E | 2018-06-22 | 0.73889 | 37.2485 | -119.5625 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Madera County | 101117749 | None | 0 – 750 | Conductor | Overhead | Yes | 43273 | 0.73889 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1686 | 2018 | 6 | 22 | 17 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 10.123 | 263_198 | <25mph | <15mph | HFTD - Distribution | 2018-06-22 17:44:00 | 1428 | 12.3323 | FALSE | <25mph | NFRC1 | 3.29 | 2017-02-10T10:55:00Z | 8.99 | 4 | < 25mph | NFRC1 | 3.29 | 2017-02-10T10:55:00Z | 8.99 | 40 | < 25mph | NFRC1 | 3.29 | 2017-02-10T10:55:00Z | 8.99 | 8 | < 25mph | NFRC1 | 3.29 | 2017-02-10T10:55:00Z | 8.99 | 81 | < 25mph
PG&E | 2019-01-16 | 0.011806 | 38.0621 | -120.1964 | Vegetation | Conifer Forest | Structure Only | Cal Fire |  | 163661701 |  | 17000 | Conductor | Overhead | Yes | 43481 | 0.011806 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-01 | 2019 | 1 | 16 | 0 | 17 | 19-0010443 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1041827 | 14.8061 | 234_243 | <25mph | <15mph | HFTD - Distribution | 2019-01-16 00:17:00 | 1728 | 28.2081 | FALSE | 25-40mph | MOUC1 | 2.77 | 2016-07-09T00:02:00Z | 14.99 | 1 | < 25mph | MOUC1 | 2.77 | 2016-07-09T00:02:00Z | 14.99 | 1 | < 25mph | MOUC1 | 2.77 | 2016-07-09T00:02:00Z | 14.99 | 2 | < 25mph | MOUC1 | 2.77 | 2016-07-09T00:02:00Z | 14.99 | 2 | < 25mph
PG&E | 2017-04-25 12:39 | 12:38 | 38.6583 | -120.9762 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101376746 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 42850.5271 | 12:38 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1072 | 2017 | 4 | 25 | 12 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 9.948 | 200_275 | <25mph | <15mph | HFTD - Distribution | 2017-04-25 12:38:00 | 812 | 10.5664 | FALSE | <25mph | D7401 | 2.53 | 2016-02-01T06:17:00Z | 17 | 8 | < 25mph | BENC1 | 5.2 | 2016-02-01T05:59:00Z | 27 | 51 | 25-40mph | D7401 | 2.53 | 2016-02-01T06:32:00Z | 18.01 | 16 | < 25mph | BENC1 | 5.2 | 2016-02-01T06:59:00Z | 28.99 | 102 | 25-40mph
PG&E | 2019-07-23 | 16:55 | 37.2128 | -119.505 | Gun Shot | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | 252521103 |  | 12000 | Conductor | Overhead | Yes | 43669 | 16:55 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-434 | 2019 | 7 | 23 | 16 | 55 | 19-0080383 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 513358 | 13.6168 | 265_196 | <25mph | <15mph | HFTD - Distribution | 2019-07-23 16:55:00 | 1923 | 13.6168 | FALSE | <25mph | C6459 | 1.76 | 2019-06-13T10:20:00Z | 8.01 | 2 | < 25mph | C6459 | 1.76 | 2019-06-13T10:20:00Z | 8.01 | 8 | < 25mph | C6459 | 1.76 | 2019-06-13T10:20:00Z | 8.01 | 3 | < 25mph | C6459 | 1.76 | 2019-06-13T10:20:00Z | 8.01 | 15 | < 25mph
PG&E | 2019-09-28 | 13:16 | 37.2553 | -119.5057 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 252531103 |  | 12000 | Conductor | Overhead | Yes | 43736 | 13:16 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-36 | 2019 | 9 | 28 | 13 | 16 | 19-0104972 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 1296 | 12.1111 | 265_198 | <25mph | <15mph | HFTD - Distribution | 2019-09-28 13:16:00 | 2064 | 13.545 | FALSE | <25mph | NFRC1 | 1.54 | 2019-05-18T17:55:00Z | 8.99 | 2 | < 25mph | D7778 | 7.57 | 2019-05-18T17:31:00Z | 8.99 | 38 | < 25mph | NFRC1 | 1.54 | 2019-05-18T17:55:00Z | 8.99 | 3 | < 25mph | AT344 | 5.5 | 2019-05-18T19:00:00Z | 10 | 71 | < 25mph
1. Butte | 2015-09-09 | 14:26 | 38.3297 | -120.7042 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1987 | 2015 | 9 | 9 | 14 | 26 |  | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 1353755 | 12.0917 | 212_257 | <25mph | <15mph | HFTD - Distribution | 2015-09-09 14:26:00 | 332 | 14.8248 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 5.02 | 2016-08-11T07:56:00Z | 3 | 2 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 5.02 | 2016-08-11T08:56:00Z | 5.99 | 4 | < 25mph
PG&E | 2015-07-30 19:11 | 2015-07-30 19:11 | 37.8102 | -120.1287 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE |  |  | 17000 | Conductor | Overhead | Yes | 42215.7993 | 2015-07-30 19:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0500 | 2015 | 7 | 30 | 19 | 11 | 15-0051772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26776 | 10.007 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2015-07-30 19:11:00 | 245 | 11.7658 | FALSE | <25mph | SEWC1 | 1.66 | 2018-07-05T19:16:00Z | 15.99 | 5 | < 25mph | SEWC1 | 1.66 | 2018-07-05T19:16:00Z | 15.99 | 5 | < 25mph | SEWC1 | 1.66 | 2018-07-05T20:16:00Z | 15.99 | 10 | < 25mph | SEWC1 | 1.66 | 2018-07-05T20:16:00Z | 15.99 | 11 | < 25mph
PG&E | 2019-09-15 | 12:38 | 38.1194 | -120.8013 | Vehicle | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103959405 |  | 12000 | Pole | Overhead | Yes | 43723 | 12:38 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-118 | 2019 | 9 | 15 | 12 | 38 | 19-0099234 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 5378 | 7.5852 | 208_246 | <25mph | <15mph | HFTD - Distribution | 2019-09-15 12:38:00 | 2043 | 14.1961 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2017-08-29 | 15:54 | 38.302 | -122.5431 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 911 | 102026119 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 42976 | 15:54 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1367 | 2017 | 8 | 29 | 15 | 54 | 17-0073928 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 485 | 16.1777 | 133_256 | <25mph | <15mph | HFTD - Distribution | 2017-08-29 15:54:00 | 1105 | 18.0049 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KO69 | 4.55 | 2016-08-22T01:35:00Z | 17.27 | 29 | < 25mph |  |  |  | 0 | 0 | No data | KO69 | 4.55 | 2016-08-22T02:55:00Z | 19.57 | 63 | < 25mph
PG&E | 2017-09-18 | 13:01 | 39.3889 | -121.4054 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 103795057 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42996 | 13:01 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1418 | 2017 | 9 | 18 | 13 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 17.7047 | 182_316 | <25mph | <15mph | HFTD - Distribution | 2017-09-18 13:01:00 | 1156 | 19.5678 | FALSE | <25mph | BNGC1 | 1.17 | 2019-10-25T17:51:00Z | 7 | 7 | < 25mph | PG309 | 7.97 | 2019-10-25T17:20:00Z | 8.99 | 49 | < 25mph | PG290 | 0.32 | 2019-10-25T18:30:00Z | 9.42 | 14 | < 25mph | PG298 | 4.25 | 2019-10-25T19:10:00Z | 11.34 | 98 | < 25mph
PG&E | 2019-06-07 | 9:58 | 38.7285 | -123.3528 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 042861101 |  | 21000 | Conductor | Overhead | Yes | 43623 | 9:58 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-358 | 2019 | 6 | 7 | 9 | 58 | 19-0064216 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 5301 | 16.456 | 98_280 | <25mph | <15mph | HFTD - Distribution | 2019-06-07 09:58:00 | 1805 | 19.4921 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D2695 | 5.46 | 2016-01-27T05:03:00Z | 4.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | D2695 | 5.46 | 2016-01-27T05:03:00Z | 4.99 | 8 | < 25mph
PG&E | 2016-07-28 13:19 | 2016-07-28 13:19 | 39.7127 | -123.4973 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102195566 |  | 12000 | Conductor | Overhead | Yes | 42579.5549 | 2016-07-28 13:19 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0886 | 2016 | 7 | 28 | 13 | 19 | 16-0053369 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 4447 | 11.1949 | 93_335 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 13:19:00 | 629 | 12.238 | FALSE | <25mph | LAYC1 | 0.97 | 2016-10-31T20:29:00Z | 10 | 1 | < 25mph | LAYC1 | 0.97 | 2016-10-31T20:29:00Z | 10 | 1 | < 25mph | LAYC1 | 0.97 | 2016-10-31T21:29:00Z | 10 | 2 | < 25mph | LAYC1 | 0.97 | 2016-10-31T21:29:00Z | 10 | 2 | < 25mph
PG&E | 2015-05-02 16:51 | 2015-05-02 16:51 | 37.3284 | -119.643 | Vegetation | Rural | < 0.25 Acres | Fire Agency | MADERA COUNTY | 103768995 |  | 12000 | Conductor | Overhead | Yes | 42126.7021 | 2015-05-02 16:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0305 | 2015 | 5 | 2 | 16 | 51 | 15-0031285 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 79805 | 9.7158 | 259_202 | <25mph | <15mph | HFTD - Distribution | 2015-05-02 16:51:00 | 51 | 12.4769 | FALSE | <25mph | AT301 | 1.62 | 2019-05-27T11:37:00Z | 4.99 | 40 | < 25mph | AT301 | 1.62 | 2019-05-27T11:37:00Z | 4.99 | 71 | < 25mph | AT301 | 1.62 | 2019-05-27T11:37:00Z | 4.99 | 75 | < 25mph | AT301 | 1.62 | 2019-05-27T11:37:00Z | 4.99 | 136 | < 25mph
PG&E | 2015-09-24 04:30 | 2015-09-24 04:30 | 38.6769 | -123.314 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Str. 041/007 |  | 60000 | Conductor | Overhead | Yes | 42271.1875 | 2015-09-24 04:30 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0613 | 2015 | 9 | 24 | 4 | 30 | FU-2015-057 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 22680 | 6.5939 | 100_277 | <25mph | <15mph | HFTD - Transmission | 2015-09-24 04:30:00 | 358 | 13.8122 | FALSE | <25mph |  |  |  | 0 | 0 | No data | OAAC1 | 4.24 | 2017-04-26T18:33:00Z | 13 | 6 | < 25mph |  |  |  | 0 | 0 | No data | OAAC1 | 4.24 | 2017-04-26T19:33:00Z | 14 | 9 | < 25mph
PG&E | 2017-09-18 | 23:50 | 37.9088 | -120.4865 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | incident comander geoff marshall 209-419-4407 | 101040882 | Unknown | 17000 | Conductor | Overhead | Yes | 42996 | 23:50 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1422 | 2017 | 9 | 18 | 23 | 50 | 17-0079858 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 382303 | 9.0814 | 222_234 | <25mph | <15mph | HFTD - Distribution | 2017-09-18 23:50:00 | 1160 | 16.9339 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.23 | 2015-10-09T22:03:00Z | 14 | 8 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.23 | 2015-10-09T23:03:00Z | 15.99 | 15 | < 25mph
PG&E | 2015-09-04 07:49 | 2015-09-04 07:49 | 40.2318 | -122.3643 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | E/O FRONTIER RD & N/O WAGON WAY |  | 12000 | Conductor | Overhead | Yes | 42251.3257 | 2015-09-04 07:49 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0577 | 2015 | 9 | 4 | 7 | 49 | 15-0059323 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 9563 | 2.343 | 142_362 | <25mph | <15mph | HFTD - Distribution | 2015-09-04 07:49:00 | 321 | 17.9748 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 5.07 | 2017-12-30T09:09:00Z | 8.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 5.07 | 2017-12-30T09:55:00Z | 8.99 | 8 | < 25mph
PG&E | 2015-12-03 12:10 | 2015-12-03 12:10 | 40.0277 | -120.9652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | usfs | spanish creek campground |  | 12000 | Conductor | Overhead | Yes | 42341.5069 | 2015-12-03 12:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0683 | 2015 | 12 | 3 | 12 | 10 | 15-0082505 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 196854 | 26.293 | 201_351 | 25-40mph | 15-30mph | HFTD - Distribution | 2015-12-03 12:10:00 | 427 | 26.9543 | FALSE | 25-40mph | CHAC1 | 3.2 | 2018-01-30T11:47:00Z | 4 | 2 | < 25mph | CHAC1 | 3.2 | 2018-01-30T11:47:00Z | 4 | 3 | < 25mph | CHAC1 | 3.2 | 2018-01-30T11:47:00Z | 4 | 4 | < 25mph | CHAC1 | 3.2 | 2018-01-30T11:47:00Z | 4 | 6 | < 25mph
PG&E | 2018-09-02 | 15:36 | 37.4714 | -122.4248 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Arie Delay 659-740-4636 | 103808872 | Unknown | 12000 | Capacitor Bank | Overhead | Yes | 43345 | 15:36 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1876 | 2018 | 9 | 2 | 15 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 11.73 | 137_210 | <25mph | <15mph | HFTD - Distribution | 2018-09-02 15:36:00 | 1615 | 13.6047 | FALSE | <25mph | D9259 | 3.46 | 2018-11-12T09:16:00Z | 4 | 4 | < 25mph | HSPC1 | 6.33 | 2018-11-12T09:18:00Z | 7 | 48 | < 25mph | D9259 | 3.46 | 2018-11-12T09:16:00Z | 4 | 8 | < 25mph | HSPC1 | 6.33 | 2018-11-12T09:18:00Z | 7 | 95 | < 25mph
PG&E | 2019-07-23 | 16:55 | 37.2128 | -119.505 | Gun Shot | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | 252521103 |  | 12000 | Conductor | Overhead | Yes | 43669 | 16:55 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-434 | 2019 | 7 | 23 | 16 | 55 | 19-0080383 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 513358 | 13.6168 | 265_196 | <25mph | <15mph | HFTD - Distribution | 2019-07-23 16:55:00 | 1923 | 13.6168 | FALSE | <25mph | NFRC1 | 1.4 | 2017-06-24T00:55:00Z | 10 | 4 | < 25mph | NFRC1 | 1.4 | 2017-06-24T00:55:00Z | 10 | 4 | < 25mph | NFRC1 | 1.4 | 2017-06-24T00:55:00Z | 10 | 8 | < 25mph | NFRC1 | 1.4 | 2017-06-24T00:55:00Z | 10 | 8 | < 25mph
PG&E | 2019-08-20 | 0.37708 | 41.1088 | -121.5034 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-297 | 2019 | 8 | 20 | 9 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 2.4258 | 178_411 | <25mph | <15mph | HFTD - Distribution | 2019-08-20 09:03:00 | 1990 | 15.6046 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-10-11 23:17 | 23:16 | 39.0201 | -120.8294 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire.foresthill fire | 100025501 |  | 60000 | Conductor | Overhead | Yes | 42654.9701 | 23:16 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error |  | no-match | 1028 | 2016 | 10 | 11 | 23 | 16 | INT-08640 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 0 | 7.6312 | 207_295 | <25mph | <15mph | HFTD - Transmission | 2016-10-11 23:16:00 | 769 | 11.1078 | FALSE | <25mph | AU268 | 0.89 | 2015-03-16T19:29:00Z | 4.99 | 4 | < 25mph | FSHC1 | 7.19 | 2015-03-16T19:33:00Z | 7 | 11 | < 25mph | AU268 | 0.89 | 2015-03-16T19:29:00Z | 4.99 | 6 | < 25mph | FSHC1 | 7.19 | 2015-03-16T20:33:00Z | 8.01 | 20 | < 25mph
PG&E | 2017-06-15 08:08 | 7:39 | 39.2276 | -121.2348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE CHIEF | 103676075 | Unknown | 21000 | Conductor | Overhead | Yes | 42901.3391 | 7:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1147 | 2017 | 6 | 15 | 7 | 39 | 17-0055387 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 740 | 10.5195 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 07:39:00 | 886 | 12.4202 | FALSE | <25mph | E2572 | 2.6 | 2015-10-20T06:13:00Z | 2.01 | 12 | < 25mph | E1789 | 7.9 | 2015-10-20T06:00:00Z | 4 | 28 | < 25mph | E2572 | 2.6 | 2015-10-20T07:18:00Z | 2.01 | 23 | < 25mph | E1789 | 7.9 | 2015-10-20T07:00:00Z | 8.01 | 55 | < 25mph
PG&E | 2017-07-16 11:59 | 11:59 | 36.6669 | -121.7515 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101761892 | None | 21000 | Fuse | Overhead | Yes | 42932.4994 | 11:59 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1259 | 2017 | 7 | 16 | 11 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 22.4318 | 166_166 | <25mph | <15mph | HFTD - Distribution | 2017-07-16 11:59:00 | 998 | 30.0095 | FALSE | 25-40mph | E6666 | 1.85 | 2017-03-18T17:05:00Z | 3 | 12 | < 25mph | E8875 | 6.38 | 2017-03-18T17:36:00Z | 4.99 | 16 | < 25mph | E6666 | 1.85 | 2017-03-18T18:25:00Z | 4 | 24 | < 25mph | E8875 | 6.38 | 2017-03-18T18:36:00Z | 5.99 | 32 | < 25mph
PG&E | 2018-06-10 | 17:19 | 38.4157 | -122.9184 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101978419 | AT&T | 12000 | Conductor | Overhead | Yes | 43261 | 17:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1647 | 2018 | 6 | 10 | 17 | 19 | 18-0049445 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2386 | 19.6716 | 117_263 | <25mph | <15mph | HFTD - Distribution | 2018-06-10 17:19:00 | 1389 | 23.7271 | FALSE | <25mph | D3838 | 1.59 | 2018-10-31T02:32:00Z | 1.01 | 28 | < 25mph | AR323 | 5.66 | 2018-10-31T01:49:00Z | 4 | 82 | < 25mph | D3838 | 1.59 | 2018-10-31T02:47:00Z | 1.01 | 51 | < 25mph | AR323 | 5.66 | 2018-10-31T02:59:00Z | 4 | 158 | < 25mph
PG&E | 2018-11-16 | 17:02 | 38.7574 | -120.9012 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101409894 | AT&T | 21000 | Conductor | Overhead | Yes | 43420 | 17:02 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1976 | 2018 | 11 | 16 | 17 | 2 | 18-0100490 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 119860 | 5.5125 | 204_281 | <25mph | <15mph | HFTD - Distribution | 2018-11-16 17:02:00 | 1716 | 12.5682 | FALSE | <25mph | D2736 | 3.3 | 2016-12-19T04:00:00Z | 0 | 13 | < 25mph | D4464 | 6.31 | 2016-12-19T03:35:00Z | 4.99 | 67 | < 25mph | D2736 | 3.3 | 2016-12-19T05:00:00Z | 0 | 25 | < 25mph | D4464 | 6.31 | 2016-12-19T03:35:00Z | 4.99 | 137 | < 25mph
PG&E | 2017-05-25 15:05 | 15:05 | 36.5217 | -121.8473 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Buddy Bloxham 831-236-5659 | 101778611 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42880.6288 | 15:05 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1113 | 2017 | 5 | 25 | 15 | 5 | 17-0050761 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 13965 | 25.8899 | 162_158 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-05-25 15:05:00 | 853 | 26.2648 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E4129 | 5.3 | 2018-08-19T12:20:00Z | 4.99 | 38 | < 25mph |  |  |  | 0 | 0 | No data | E8875 | 6.61 | 2018-08-19T12:56:00Z | 4.99 | 77 | < 25mph
PG&E | 2015-07-07 10:42 | 2015-07-07 10:42 | 39.1138 | -121.0655 | Vegetation | Rural | < 0.25 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42192.4458 | 2015-07-07 10:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0448 | 2015 | 7 | 7 | 10 | 42 | 15-0045985 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 46738 | 10.1548 | 197_300 | <25mph | <15mph | HFTD - Distribution | 2015-07-07 10:42:00 | 193 | 12.5396 | FALSE | <25mph | AV369 | 3.22 | 2019-05-14T08:46:00Z | 0 | 10 | < 25mph | E1789 | 4.22 | 2019-05-14T08:48:00Z | 5.99 | 59 | < 25mph | C5488 | 3.42 | 2019-05-14T09:20:00Z | 4 | 20 | < 25mph | E1789 | 4.22 | 2019-05-14T09:54:00Z | 5.99 | 120 | < 25mph
PG&E | 2019-09-10 | 7:13 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 82841102 |  | 12000 | Conductor | Overhead | Yes | 43718 | 7:13 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-369 | 2019 | 9 | 10 | 7 | 13 | 19-0097264 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 23500 | 14.6244 | 147_193 | <25mph | <15mph | HFTD - Distribution | 2019-09-10 07:13:00 | 2029 | 17.7422 | FALSE | <25mph | BNDC1 | 2.84 | 2015-08-03T07:50:00Z | 4.99 | 1 | < 25mph | E6800 | 5.35 | 2015-08-03T08:01:00Z | 4.99 | 24 | < 25mph | BNDC1 | 2.84 | 2015-08-03T07:50:00Z | 4.99 | 2 | < 25mph | E6800 | 5.35 | 2015-08-03T08:01:00Z | 4.99 | 49 | < 25mph
PG&E | 2016-07-08 10:49 | 2016-07-08 10:49 | 38.3373 | -122.1211 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 102291118 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42559.4507 | 2016-07-08 10:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0842 | 2016 | 7 | 8 | 10 | 49 | 16-0048647 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 19469 | 8.3702 | 151_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-08 10:49:00 | 585 | 20.6133 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6079 | 6.28 | 2018-04-19T14:44:00Z | 7 | 16 | < 25mph |  |  |  | 0 | 0 | No data | E6079 | 6.28 | 2018-04-19T16:23:00Z | 7 | 32 | < 25mph
PG&E | 2017-09-06 | 19:26 | 40.8392 | -122.3635 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103643183 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 19:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1399 | 2017 | 9 | 6 | 19 | 26 | 17-0076501 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 23830 | 6.5088 | 142_396 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 19:26:00 | 1137 | 12.365 | FALSE | <25mph | CTANT | 1.93 | 2018-08-21T13:15:00Z | 8.7 | 5 | < 25mph | CTANT | 1.93 | 2018-08-21T13:15:00Z | 8.7 | 10 | < 25mph | CTANT | 1.93 | 2018-08-21T13:15:00Z | 8.7 | 9 | < 25mph | SLFC1 | 6.48 | 2018-08-21T14:19:00Z | 8.99 | 19 | < 25mph
PG&E | 2018-08-08 | 16:02 | 36.4703 | -121.7143 | Vegetation | Rural | < 3 meters | Customer | N.A. | 103910535 | None | 12000 | Conductor | Overhead | Yes | 43320 | 16:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1830 | 2018 | 8 | 8 | 16 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 14.7322 | 168_155 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:02:00 | 1569 | 15.5625 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F1964 | 7.27 | 2018-12-23T14:00:00Z | 0 | 4 | < 25mph |  |  |  | 0 | 0 | No data | F1964 | 7.27 | 2018-12-23T15:00:00Z | 0 | 8 | < 25mph
PG&E | 2018-07-01 | 0:23 | 40.2697 | -124.2386 | Vegetation | Rural | < 3 meters | Fire Agency | fire chief | 100986962 | Unknown | 12000 | Conductor | Overhead | Yes | 43282 | 0:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1718 | 2018 | 7 | 1 | 0 | 23 | 18-0056043 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 22872 | 20.9894 | 63_366 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 00:23:00 | 1459 | 27.5371 | FALSE | 25-40mph | PTEC1 | 1.7 | 2016-05-20T03:08:00Z | 34.99 | 1 | 25-40mph | PTEC1 | 1.7 | 2016-05-20T03:08:00Z | 34.99 | 1 | 25-40mph | PTEC1 | 1.7 | 2016-05-20T04:08:00Z | 34.99 | 2 | 25-40mph | PTEC1 | 1.7 | 2016-05-20T04:08:00Z | 34.99 | 2 | 25-40mph
PG&E | 2018-08-20 | 9:34 | 39.8014 | -121.5813 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100400441 | Unknown | 12000 | Conductor | Overhead | Yes | 43332 | 9:34 | Contact From Object | N.A. | Other | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1849 | 2018 | 8 | 20 | 9 | 34 | 18-0071596 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 394259 | 5.4464 | 175_338 | <25mph | <15mph | HFTD - Distribution | 2018-08-20 09:34:00 | 1588 | 11.8754 | FALSE | <25mph | C4565 | 3.06 | 2017-01-09T08:33:00Z | 11.01 | 6 | < 25mph | JBGC1 | 6.67 | 2017-01-09T08:13:00Z | 15.99 | 18 | < 25mph | C4565 | 3.06 | 2017-01-09T08:33:00Z | 11.01 | 10 | < 25mph | JBGC1 | 6.67 | 2017-01-09T09:13:00Z | 17 | 35 | < 25mph
PG&E | 2018-07-01 | 0:45 | 38.8842 | -120.847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Brian Mackwood (530)708-2711 | 100109003 | None | 21000 | Conductor | Overhead | Yes | 43282 | 0:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1719 | 2018 | 7 | 1 | 0 | 45 | 18-0056045 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5760 | 9.2878 | 206_288 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 00:45:00 | 1460 | 12.1055 | FALSE | <25mph | PG180 | 3.22 | 2019-03-31T13:00:00Z | 5.7 | 30 | < 25mph | PG180 | 3.22 | 2019-03-31T13:00:00Z | 5.7 | 36 | < 25mph | PG180 | 3.22 | 2019-03-31T14:20:00Z | 6.13 | 60 | < 25mph | PG180 | 3.22 | 2019-03-31T14:20:00Z | 6.13 | 72 | < 25mph
PG&E | 2016-07-24 16:24 | 2016-07-24 16:24 | 38.0105 | -122.1941 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | CCD | 103049639 |  | 115000 | Conductor | Overhead | Yes | 42575.6833 | 2016-07-24 16:24 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0876 | 2016 | 7 | 24 | 16 | 24 | PS-2016-013 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 0 | 18.9534 | 148_240 | <25mph | <15mph | HFTD - Transmission | 2016-07-24 16:24:00 | 619 | 23.7155 | FALSE | <25mph | E4251 | 3.92 | 2015-01-20T10:30:00Z | 4.99 | 17 | < 25mph | UPBC1 | 4.44 | 2015-01-20T10:24:00Z | 5.99 | 69 | < 25mph | E4251 | 3.92 | 2015-01-20T10:30:00Z | 4.99 | 35 | < 25mph | DPXC1 | 4.78 | 2015-01-20T12:18:00Z | 7 | 138 | < 25mph
PG&E | 2019-08-16 | 8:19 | 40.1235 | -123.8758 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Self Extinguished |  | 192221102-2101118022{5563} |  | 12000 | Conductor | Overhead | Yes | 43693 | 8:19 | Vegetation | [5 empty] | Other/Unknown |  | 2019 | 8 | 16 | 8 | 19 | 19-0088744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 2979 | 5.7689 | 78_358 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 08:19:00 | 1983 | 18.468 | FALSE | <25mph | ERCC1 | 2.93 | 2016-06-04T19:28:00Z | 4 | 1 | < 25mph | ERCC1 | 2.93 | 2016-06-04T19:28:00Z | 4 | 3 | < 25mph | ERCC1 | 2.93 | 2016-06-04T20:28:00Z | 5.99 | 2 | < 25mph | ERCC1 | 2.93 | 2016-06-04T20:28:00Z | 5.99 | 5 | < 25mph
PG&E | 2018-08-21 | 10:13 | 38.6972 | -120.889 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101385436 | Unknown | 12000 | Conductor | Overhead | Yes | 43333 | 10:13 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1852 | 2018 | 8 | 21 | 10 | 13 | 18-0072055 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4572 | 5.9109 | 204_277 | <25mph | <15mph | HFTD - Distribution | 2018-08-21 10:13:00 | 1591 | 12.0437 | FALSE | <25mph | PG027 | 2.89 | 2018-09-03T00:00:00Z | 10.96 | 55 | < 25mph | BENC1 | 7.73 | 2018-09-02T23:59:00Z | 12.01 | 131 | < 25mph | PG027 | 2.89 | 2018-09-03T00:00:00Z | 10.96 | 109 | < 25mph | BENC1 | 7.73 | 2018-09-03T00:59:00Z | 12.01 | 260 | < 25mph
PG&E | 2019-08-11 | 0.054861 | 39.1152 | -121.001 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100097796 |  | 12000 | Other | Overhead | Yes | 43688 | 0.054861 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-387 | 2019 | 8 | 11 | 1 | 19 | 19-0086613 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6200 | 9.9563 | 199_300 | <25mph | <15mph | HFTD - Distribution | 2019-08-11 01:19:00 | 1965 | 18.5914 | FALSE | <25mph | PG377 | 1.68 | 2019-08-29T00:50:00Z | 8.55 | 24 | < 25mph | E1789 | 7.39 | 2019-08-29T00:54:00Z | 8.99 | 81 | < 25mph | PG377 | 1.68 | 2019-08-29T00:50:00Z | 8.55 | 48 | < 25mph | E1789 | 7.39 | 2019-08-29T00:54:00Z | 8.99 | 164 | < 25mph
PG&E | 2015-11-15 16:30 | 2015-11-15 16:30 | 37.0007 | -121.885 | Vegetation | Rural | < 3 meters | Customer |  | 101691004 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42323.6875 | 2015-11-15 16:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0676 | 2015 | 11 | 15 | 16 | 30 | 15-0077978 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 25920 | 24.6094 | 161_184 | <25mph | <15mph | HFTD - Distribution | 2015-11-15 16:30:00 | 420 | 25.3186 | FALSE | 25-40mph | E7291 | 2.82 | 2017-02-12T08:01:00Z | 4.99 | 44 | < 25mph | E6085 | 7.67 | 2017-02-12T07:47:00Z | 14 | 131 | < 25mph | E7291 | 2.82 | 2017-02-12T08:01:00Z | 4.99 | 84 | < 25mph | E6085 | 7.67 | 2017-02-12T09:33:00Z | 14.99 | 254 | < 25mph
PG&E | 2019-08-16 | 10:31 | 39.3714 | -121.3221 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103191101 |  | 12000 | Conductor | Overhead | Yes | 43693 | 10:31 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-397 | 2019 | 8 | 16 | 10 | 31 | 19-0088805 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4580 | 6.4736 | 186_315 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 10:31:00 | 1984 | 15.7456 | FALSE | <25mph | BNGC1 | 3.48 | 2016-01-10T13:51:00Z | 4 | 1 | < 25mph | BNGC1 | 3.48 | 2016-01-10T13:51:00Z | 4 | 1 | < 25mph | BNGC1 | 3.48 | 2016-01-10T13:51:00Z | 4 | 2 | < 25mph | BNGC1 | 3.48 | 2016-01-10T13:51:00Z | 4 | 2 | < 25mph
PG&E | 2016-07-08 10:49 | 2016-07-08 10:49 | 38.3373 | -122.1211 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 102291118 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42559.4507 | 2016-07-08 10:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0842 | 2016 | 7 | 8 | 10 | 49 | 16-0048647 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 19469 | 8.3702 | 151_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-08 10:49:00 | 585 | 20.6133 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F0187 | 5.39 | 2018-09-17T16:30:00Z | 8.01 | 21 | < 25mph |  |  |  | 0 | 0 | No data | PG083 | 4.57 | 2018-09-17T17:30:00Z | 10.29 | 43 | < 25mph
PG&E | 2019-03-19 | 12:52 | 37.9956 | -120.3244 | Tree - cutting, 3rd party | Hardwood Forest | 1 meter - < 3 meters | Self Extinguished |  | 101045032 |  | 17000 | Conductor | Overhead | Yes | 43543 | 12:52 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-187 | 2019 | 3 | 19 | 12 | 52 | 19-0035101 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 70602 | 12.9023 | 229_239 | <25mph | <15mph | HFTD - Distribution | 2019-03-19 12:52:00 | 1736 | 14.3226 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.27 | 2015-07-15T03:02:00Z | 12.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.27 | 2015-07-15T03:02:00Z | 12.01 | 5 | < 25mph
PG&E | 2018-08-01 | 0.74861 | 38.9155 | -122.799 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102156435 | Unknown | 12000 | Conductor | Overhead | Yes | 43313 | 0.74861 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1805 | 2018 | 8 | 1 | 17 | 58 | 18-0065921 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2744 | 14.8702 | 122_290 | <25mph | <15mph | HFTD - Distribution | 2018-08-01 17:58:00 | 1545 | 14.8702 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 4.99 | 2018-03-13T19:57:00Z | 21 | 1 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 4.99 | 2018-03-13T20:57:00Z | 24 | 2 | < 25mph
PG&E | 2017-10-20 | 13:45 | 34.5532 | -120.5303 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 101921492 | Unknown | 12000 | Conductor | Overhead | Yes | 43028 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1502 | 2017 | 10 | 20 | 13 | 45 | 17-0089249 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 173 | 31.847 | 221_49 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-20 13:45:00 | 1245 | 35.5655 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PTGC1 | 6.9 | 2015-11-16T06:00:00Z | 50.73 | 7 | 40-55mph |  |  |  | 0 | 0 | No data | PTGC1 | 6.9 | 2015-11-16T07:00:00Z | 51.85 | 14 | 40-55mph
PG&E | 2019-09-28 | 13:16 | 37.2553 | -119.5057 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 252531103 |  | 12000 | Conductor | Overhead | Yes | 43736 | 13:16 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-36 | 2019 | 9 | 28 | 13 | 16 | 19-0104972 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 1296 | 12.1111 | 265_198 | <25mph | <15mph | HFTD - Distribution | 2019-09-28 13:16:00 | 2064 | 13.545 | FALSE | <25mph | C6459 | 1.57 | 2017-01-24T17:00:00Z | 5.99 | 4 | < 25mph | C6459 | 1.57 | 2017-01-24T17:00:00Z | 5.99 | 36 | < 25mph | C6459 | 1.57 | 2017-01-24T17:00:00Z | 5.99 | 8 | < 25mph | C6459 | 1.57 | 2017-01-24T17:00:00Z | 5.99 | 64 | < 25mph
PG&E | 2015-03-14 02:30 | 2015-03-14 02:30 | 38.9038 | -122.7579 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 9210 Wildcat Road, Kelseyville |  | 12000 | Conductor | Overhead | Yes | 42077.1042 | 2015-03-14 02:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0274 | 2015 | 3 | 14 | 2 | 30 | 15-0019556 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2280 | 8.9688 | 124_289 | <25mph | <15mph | HFTD - Distribution | 2015-03-14 02:30:00 | 20 | 8.9688 | FALSE | <25mph | KELC1 | 2.83 | 2018-12-13T06:57:00Z | 8.99 | 7 | < 25mph | LKRC1 | 6.79 | 2018-12-13T07:05:00Z | 12.01 | 30 | < 25mph | KELC1 | 2.83 | 2018-12-13T06:57:00Z | 8.99 | 14 | < 25mph | PG125 | 6.63 | 2018-12-13T08:00:00Z | 12.93 | 60 | < 25mph
PG&E | 2018-11-13 | 15:41 | 37.0644 | -121.9578 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101680441 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43417 | 15:41 | Other | N.A. | N.A. | N.A. | Human Error | Grow house | Other/Unknown | 1973 | 2018 | 11 | 13 | 15 | 41 | 18-0099492 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 21484 | 1.9347 | 157_188 | <25mph | <15mph | HFTD - Distribution | 2018-11-13 15:41:00 | 1713 | 13.1257 | FALSE | <25mph | E5965 | 0.43 | 2015-09-18T19:43:00Z | 13 | 38 | < 25mph | E5965 | 0.43 | 2015-09-18T19:43:00Z | 13 | 124 | < 25mph | E5965 | 0.43 | 2015-09-18T20:33:00Z | 14 | 78 | < 25mph | E5965 | 0.43 | 2015-09-18T20:33:00Z | 14 | 253 | < 25mph
PG&E | 2016-10-13 23:23 | 23:14 | 40.4901 | -122.3729 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | SHASTA COUNTY FIRE | 101502366 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42656.9745 | 23:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1029 | 2016 | 10 | 13 | 23 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 30.3025 | 142_377 | 25-40mph | 30-45mph | HFTD - Distribution | 2016-10-13 23:14:00 | 770 | 30.3025 | FALSE | 25-40mph | E6886 | 3.41 | 2016-04-19T00:08:00Z | 8.01 | 9 | < 25mph | RRAC1 | 4.59 | 2016-04-18T23:24:00Z | 10 | 16 | < 25mph | E6886 | 3.41 | 2016-04-19T00:54:00Z | 8.01 | 19 | < 25mph | RRAC1 | 4.59 | 2016-04-18T23:24:00Z | 10 | 33 | < 25mph
PG&E | 2017-05-05 15:52 | 15:52 | 40.3776 | -123.0019 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101501566 | None | 12000 | Conductor | Overhead | Yes | 42860.6614 | 15:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1084 | 2017 | 5 | 5 | 15 | 52 | 17-0045707 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 56893 | 24.5621 | 115_371 | <25mph | <15mph | HFTD - Distribution | 2017-05-05 15:52:00 | 824 | 35.0644 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | YOBC1 | 4.35 | 2018-07-26T23:35:00Z | 8.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | YOBC1 | 4.35 | 2018-07-26T23:35:00Z | 8.01 | 2 | < 25mph
PG&E | 2015-03-07 13:35 | 2015-03-07 13:35 | 38.7091 | -122.6484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 14417 western mine rd, Middletown |  | 12000 | Conductor | Overhead | Yes | 42070.566 | 2015-03-07 13:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0272 | 2015 | 3 | 7 | 13 | 35 | 15-0018003 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2263 | 3.8777 | 128_279 | <25mph | <15mph | HFTD - Distribution | 2015-03-07 13:35:00 | 18 | 14.4715 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2050 | 7.98 | 2016-04-10T14:10:00Z | 3 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E2050 | 7.98 | 2016-04-10T14:25:00Z | 4 | 8 | < 25mph
PG&E | 2016-08-22 | 2016-08-22 16:10 | 37.9666 | -120.2395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Toulumne City FD | 101043683 |  | 17000 | Conductor | Overhead | Yes | 42604 | 2016-08-22 16:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0941 | 2016 | 8 | 22 | 16 | 10 | 16-0059149 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 78534 | 13.4322 | 233_237 | <25mph | <15mph | HFTD - Distribution | 2016-08-22 16:10:00 | 684 | 13.7297 | FALSE | <25mph | PG031 | 3.85 | 2018-08-05T14:10:00Z | 5.48 | 18 | < 25mph | MOUC1 | 6.67 | 2018-08-05T14:02:00Z | 8.99 | 35 | < 25mph | PG031 | 3.85 | 2018-08-05T15:20:00Z | 6.8 | 36 | < 25mph | MOUC1 | 6.67 | 2018-08-05T15:02:00Z | 10 | 70 | < 25mph
PG&E | 2019-07-22 | 8:11 | 38.7687 | -120.9633 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | El Dorado County FD | 6Ht0722190809 |  | 21000 | Other | Overhead | Yes | 43668 | 8:11 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-49 | 2019 | 7 | 22 | 8 | 11 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.6529 | 201_281 | <25mph | <15mph | HFTD - Distribution | 2019-07-22 08:11:00 | 1920 | 11.9774 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 5.01 | 2015-06-08T01:56:00Z | 12.01 | 53 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 5.01 | 2015-06-08T02:56:00Z | 12.01 | 104 | < 25mph
PG&E | 2017-05-09 18:41 | 18:26 | 40.8689 | -123.5156 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | todd wright fire chief. 5307392493 | 103796045 | Unknown | 12000 | Conductor | Overhead | Yes | 42864.7782 | 18:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1092 | 2017 | 5 | 9 | 18 | 26 | 17-0046642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 108117 | 15.9566 | 94_399 | <25mph | <15mph | HFTD - Distribution | 2017-05-09 18:26:00 | 832 | 17.9691 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8984 | 6.51 | 2019-08-09T16:15:00Z | 4 | 3 | < 25mph |  |  |  | 0 | 0 | No data | D8984 | 6.51 | 2019-08-09T16:15:00Z | 4 | 7 | < 25mph
PG&E | 2018-05-19 | 19:44 | 40.2665 | -122.2727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103899310 | Unknown | 12000 | Conductor | Overhead | Yes | 43239 | 19:44 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1599 | 2018 | 5 | 19 | 19 | 44 | 18-0042559 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 31980 | 15.59 | 146_364 | <25mph | <15mph | HFTD - Distribution | 2018-05-19 19:44:00 | 1341 | 18.253 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 7.1 | 2019-07-02T02:01:00Z | 11.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 7.1 | 2019-07-02T02:01:00Z | 11.01 | 8 | < 25mph
PG&E | 2018-09-14 | 15:08 | 35.328 | -120.6982 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Sean Hernandez Cell # 805 903 3423 | 103400199 | Unknown | 12000 | Conductor | Overhead | Yes | 43357 | 15:08 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1898 | 2018 | 9 | 14 | 15 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 24.1105 | 213_92 | <25mph | <15mph | HFTD - Distribution | 2018-09-14 15:08:00 | 1637 | 24.1304 | FALSE | <25mph | ARGC1 | 2.05 | 2017-07-24T00:54:00Z | 13 | 1 | < 25mph | ARGC1 | 2.05 | 2017-07-24T00:54:00Z | 13 | 5 | < 25mph | ARGC1 | 2.05 | 2017-07-24T00:54:00Z | 13 | 2 | < 25mph | ARGC1 | 2.05 | 2017-07-24T00:54:00Z | 13 | 10 | < 25mph
PG&E | 2016-07-25 15:32 | 2016-07-25 15:32 | 38.3522 | -120.7107 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42576.6472 | 2016-07-25 15:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0878 | 2016 | 7 | 25 | 15 | 32 | 16-0052398 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 19951 | 10.4912 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-25 15:32:00 | 621 | 14.4675 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2016-07-13T22:56:00Z | 8.99 | 2 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2016-07-13T23:56:00Z | 12.01 | 4 | < 25mph
PG&E | 2018-11-11 | 4:18 | 38.4341 | -122.5522 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102032588 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43415 | 4:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1967 | 2018 | 11 | 11 | 4 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.8216 | 132_263 | <25mph | <15mph | HFTD - Distribution | 2018-11-11 04:18:00 | 1707 | 11.1813 | FALSE | <25mph | KENWW | 1.92 | 2017-05-30T23:00:00Z | 11.7 | 5 | < 25mph | D9840 | 7.78 | 2017-05-30T23:14:00Z | 14 | 23 | < 25mph | KENWW | 1.92 | 2017-05-31T00:00:00Z | 11.7 | 10 | < 25mph | D9840 | 7.78 | 2017-05-30T23:14:00Z | 14 | 48 | < 25mph
PG&E | 2019-09-15 | 12:38 | 38.1194 | -120.8013 | Vehicle | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103959405 |  | 12000 | Pole | Overhead | Yes | 43723 | 12:38 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-118 | 2019 | 9 | 15 | 12 | 38 | 19-0099234 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 5378 | 7.5852 | 208_246 | <25mph | <15mph | HFTD - Distribution | 2019-09-15 12:38:00 | 2043 | 14.1961 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-08-12 | 14:46 | 38.6443 | -120.9211 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101410516 | Unknown | 21000 | Conductor | Overhead | Yes | 43324 | 14:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1838 | 2018 | 8 | 12 | 14 | 46 | 18-0069084 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4032 | 11.2318 | 203_274 | <25mph | <15mph | HFTD - Distribution | 2018-08-12 14:46:00 | 1577 | 12.412 | FALSE | <25mph | PG074 | 3.85 | 2018-11-20T07:30:00Z | 7.67 | 25 | < 25mph | E4740 | 7.6 | 2018-11-20T08:08:00Z | 10 | 131 | < 25mph | PG074 | 3.85 | 2018-11-20T09:00:00Z | 8.99 | 50 | < 25mph | PG073 | 7.47 | 2018-11-20T09:10:00Z | 13.15 | 260 | < 25mph
PG&E | 2017-05-05 15:52 | 15:52 | 40.3776 | -123.0019 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101501566 | None | 12000 | Conductor | Overhead | Yes | 42860.6614 | 15:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1084 | 2017 | 5 | 5 | 15 | 52 | 17-0045707 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 56893 | 24.5621 | 115_371 | <25mph | <15mph | HFTD - Distribution | 2017-05-05 15:52:00 | 824 | 35.0644 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PG299 | 6.16 | 2019-07-08T19:30:00Z | 19.28 | 7 | < 25mph |  |  |  | 0 | 0 | No data | PG299 | 6.16 | 2019-07-08T20:30:00Z | 20.6 | 14 | < 25mph
PG&E | 2015-04-02 09:44 | 2015-04-02 09:44 | 39.6772 | -121.492 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100338726 |  | 12000 | Conductor | Overhead | Yes | 42096.4056 | 2015-04-02 09:44 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0284 | 2015 | 4 | 2 | 9 | 44 | 15-0023747 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 100204 | 15.7458 | 178_332 | <25mph | <15mph | HFTD - Distribution | 2015-04-02 09:44:00 | 30 | 15.7458 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JBGC1 | 4.06 | 2017-03-07T00:13:00Z | 12.01 | 12 | < 25mph |  |  |  | 0 | 0 | No data | JBGC1 | 4.06 | 2017-03-07T01:13:00Z | 12.01 | 23 | < 25mph
PG&E | 2017-10-08 | 22:58 | 39.3642 | -121.1131 | Vegetation | Rural | < 3 Meters | Fire Agency | INCIDENT NUMBER 26268 | 100068104 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43016 | 22:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Fell into (No defect) | 1471 | 2017 | 10 | 8 | 22 | 58 | 17-0085355 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 198802 | 15.5554 | 195_314 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 22:58:00 | 1211 | 22.0344 | FALSE | <25mph | E3651 | 3.94 | 2018-05-19T09:30:00Z | 0 | 12 | < 25mph | RRRC1 | 4.2 | 2018-05-19T09:13:00Z | 8.01 | 19 | < 25mph | E3651 | 3.94 | 2018-05-19T10:30:00Z | 0 | 24 | < 25mph | RRRC1 | 4.2 | 2018-05-19T10:13:00Z | 8.01 | 38 | < 25mph
PG&E | 2017-08-09 11:29 | 11:29 | 38.6532 | -120.6273 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101402496 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42956.4786 | 11:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1328 | 2017 | 8 | 9 | 11 | 29 | 17-0069107 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 54216 | 9.4272 | 216_275 | <25mph | <15mph | HFTD - Distribution | 2017-08-09 11:29:00 | 1066 | 11.5652 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GZFC1 | 5.69 | 2015-11-20T12:17:00Z | 4 | 5 | < 25mph |  |  |  | 0 | 0 | No data | GZFC1 | 5.69 | 2015-11-20T13:17:00Z | 4 | 10 | < 25mph
PG&E | 2016-08-05 | 2016-08-05 14:46 | 40.4797 | -123.7803 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103572261 |  | 12000 | Conductor | Overhead | Yes | 42587 | 2016-08-05 14:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0907 | 2016 | 8 | 5 | 14 | 46 | 16-0055425 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 7019 | 13.7408 | 83_377 | <25mph | <15mph | HFTD - Distribution | 2016-08-05 14:46:00 | 650 | 14.7579 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-04-30 | 17:59 | 38.3142 | -120.9015 | Vegetation | RURAL | < 3 meters | Fire Agency | Kern County FD |  |  | 12000 | Conductor | Overhead | Yes | 42490 | 17:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0719 | 2016 | 4 | 30 | 17 | 59 | 16-0032910 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 722 | 19.7396 | 204_256 | <25mph | <15mph | HFTD - Distribution | 2016-04-30 17:59:00 | 465 | 19.7396 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 4.81 | 2017-03-05T20:05:00Z | 21 | 3 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 4.81 | 2017-03-05T21:05:00Z | 34 | 6 | 25-40mph
PG&E | 2017-10-16 | 12:10 | 36.5831 | -121.9368 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101781248 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43024 | 12:10 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | Other/Unknown | 1493 | 2017 | 10 | 16 | 12 | 10 | 17-0087767 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 6313 | 5.0415 | 158_161 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:10:00 | 1236 | 13.6905 | FALSE | <25mph | MTYC1 | 3.1 | 2016-03-30T20:54:00Z | 17.98 | 58 | < 25mph | MTYC1 | 3.1 | 2016-03-30T20:54:00Z | 17.98 | 62 | < 25mph | MTYC1 | 3.1 | 2016-03-30T21:48:00Z | 17.98 | 117 | < 25mph | MTYC1 | 3.1 | 2016-03-30T21:48:00Z | 17.98 | 125 | < 25mph
PG&E | 2016-07-15 14:26 | 2016-07-15 14:26 | 38.1366 | -122.7092 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | NOVATO FIRE AND OTHERS | 102013570 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.6014 | 2016-07-15 14:26 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0853 | 2016 | 7 | 15 | 14 | 26 | 16-0050269 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 758 | 13.1533 | 125_247 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 14:26:00 | 596 | 15.659 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BBEC1 | 7.51 | 2015-10-01T06:11:00Z | 13 | 30 | < 25mph |  |  |  | 0 | 0 | No data | BBEC1 | 7.51 | 2015-10-01T06:11:00Z | 13 | 60 | < 25mph
PG&E | 2018-10-15 | 3:23 | 38.2897 | -120.5803 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103378003 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43388 | 3:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1941 | 2018 | 10 | 15 | 3 | 23 | 18-0090342 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1464 | 26.0611 | 218_255 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-15 03:23:00 | 1680 | 26.2858 | FALSE | 25-40mph | AT317 | 3.74 | 2017-07-19T08:45:00Z | 3 | 12 | < 25mph | MTZC1 | 7.96 | 2017-07-19T07:56:00Z | 5.99 | 27 | < 25mph | AT317 | 3.74 | 2017-07-19T09:45:00Z | 4 | 24 | < 25mph | MTZC1 | 7.96 | 2017-07-19T08:56:00Z | 5.99 | 54 | < 25mph
PG&E | 2018-07-20 | 6:31 | 37.4318 | -119.9441 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ZACH RUTHERFORD 209-966-3621 | 103909942 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43301 | 6:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1771 | 2018 | 7 | 20 | 6 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2004 | 246_208 | <25mph | <15mph | HFTD - Distribution | 2018-07-20 06:31:00 | 1511 | 13.5994 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E9110 | 6.48 | 2018-12-14T18:16:00Z | 11.01 | 12 | < 25mph |  |  |  | 0 | 0 | No data | E9110 | 6.48 | 2018-12-14T18:16:00Z | 11.01 | 23 | < 25mph
PG&E | 2015-09-10 05:42 | 2015-09-10 05:42 | 37.4609 | -121.8434 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100619766 | None | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0588 | 2015 | 9 | 10 | 5 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 1.7354 | 163_209 | <25mph | <15mph | HFTD - Distribution | 2015-09-10 05:42:00 | 333 | 13.8129 | FALSE | <25mph | E3968 | 2.89 | 2015-04-22T22:16:00Z | 14 | 13 | < 25mph | PEAC1 | 6.37 | 2015-04-22T22:18:00Z | 18.99 | 17 | < 25mph | E3968 | 2.89 | 2015-04-22T23:32:00Z | 14.99 | 25 | < 25mph | PEAC1 | 6.37 | 2015-04-22T23:18:00Z | 20 | 33 | < 25mph
PG&E | 2016-05-20 15:01 | 15:01 | 39.0559 | -123.4581 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102198323 |  | 12000 | Conductor | Overhead | Yes | 42510.6257 | 15:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0741 | 2016 | 5 | 20 | 15 | 1 | 16-0037479 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2720 | 20.9117 | 94_299 | <25mph | <15mph | HFTD - Distribution | 2016-05-20 15:01:00 | 484 | 20.9117 | FALSE | <25mph | E1763 | 3.93 | 2018-03-26T03:45:00Z | 2.01 | 4 | < 25mph | E4777 | 6.25 | 2018-03-26T03:30:00Z | 15.99 | 8 | < 25mph | E1763 | 3.93 | 2018-03-26T05:15:00Z | 2.01 | 8 | < 25mph | E4777 | 6.25 | 2018-03-26T03:30:00Z | 15.99 | 16 | < 25mph
PG&E | 2015-08-16 07:35 | 2015-08-16 07:35 | 35.4572 | -120.6567 | Vegetation | Rural | < 3 meters | Utility: PG&E |  | 8932 SAN GABRIEL RD. SW C/O OF LOT, Atascadero | None | 0 – 750 | Conductor | Overhead | Yes | 42232.316 | 2015-08-16 07:35 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0534 | 2015 | 8 | 16 | 7 | 35 | 15-0055284 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.0129 | 215_99 | <25mph | <15mph | HFTD - Distribution | 2015-08-16 07:35:00 | 278 | 16.9932 | FALSE | <25mph | E1179 | 1.71 | 2018-02-10T20:49:00Z | 8.01 | 23 | < 25mph | TT469 | 6.73 | 2018-02-10T20:14:00Z | 8.99 | 28 | < 25mph | E1179 | 1.71 | 2018-02-10T21:19:00Z | 8.01 | 46 | < 25mph | TT469 | 6.73 | 2018-02-10T21:14:00Z | 14.99 | 56 | < 25mph
PG&E | 2018-11-17 | 17:20 | 38.7082 | -120.6927 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101421319 | Unknown | 12000 | Conductor | Overhead | Yes | 43421 | 17:20 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1977 | 2018 | 11 | 17 | 17 | 20 | 18-0100697 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 35749 | 6.6792 | 213_278 | <25mph | <15mph | HFTD - Distribution | 2018-11-17 17:20:00 | 1717 | 12.841 | FALSE | <25mph | C5121 | 3.47 | 2016-12-30T17:16:00Z | 2.01 | 8 | < 25mph | E3165 | 7.06 | 2016-12-30T17:13:00Z | 4.99 | 34 | < 25mph | C5121 | 3.47 | 2016-12-30T17:16:00Z | 2.01 | 13 | < 25mph | E5691 | 6.11 | 2016-12-30T18:47:00Z | 7 | 67 | < 25mph
PG&E | 2017-09-18 | 23:50 | 37.9088 | -120.4865 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | incident comander geoff marshall 209-419-4407 | 101040882 | Unknown | 17000 | Conductor | Overhead | Yes | 42996 | 23:50 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1422 | 2017 | 9 | 18 | 23 | 50 | 17-0079858 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 382303 | 9.0814 | 222_234 | <25mph | <15mph | HFTD - Distribution | 2017-09-18 23:50:00 | 1160 | 16.9339 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG166 | 6.38 | 2019-08-05T13:20:00Z | 15.35 | 32 | < 25mph |  |  |  | 0 | 0 | No data | PG166 | 6.38 | 2019-08-05T13:20:00Z | 15.35 | 64 | < 25mph
PG&E | 2015-07-01 12:57 | 2015-07-01 12:57 | 39.4146 | -121.379 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42186.5396 | 2015-07-01 12:57 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0434 | 2015 | 7 | 1 | 12 | 57 | 15-0044609 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 12.6482 | 183_317 | <25mph | <15mph | HFTD - Distribution | 2015-07-01 12:57:00 | 179 | 18.7031 | FALSE | <25mph | BNGC1 | 2.37 | 2019-03-28T21:51:00Z | 18.99 | 1 | < 25mph | TT309 | 4.14 | 2019-03-28T21:45:00Z | 20 | 8 | < 25mph | BNGC1 | 2.37 | 2019-03-28T21:51:00Z | 18.99 | 2 | < 25mph | TT309 | 4.14 | 2019-03-28T21:45:00Z | 20 | 16 | < 25mph
PG&E | 2018-11-01 | 20:45 | 38.372 | -123.0507 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103852431 | AT&T | 12000 | Conductor | Overhead | Yes | 43405 | 20:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1958 | 2018 | 11 | 1 | 20 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.9426 | 111_260 | <25mph | <15mph | HFTD - Distribution | 2018-11-01 20:45:00 | 1697 | 13.8199 | FALSE | <25mph | BBYC1 | 3.77 | 2015-11-03T09:10:00Z | 14.97 | 1 | < 25mph | UCBM | 4.05 | 2015-11-03T09:10:00Z | 19.1 | 34 | < 25mph | BBYC1 | 3.77 | 2015-11-03T09:10:00Z | 14.97 | 2 | < 25mph | UCBM | 4.05 | 2015-11-03T09:30:00Z | 25.39 | 67 | 25-40mph
PG&E | 2016-08-30 | 2016-08-30 16:01 | 36.5941 | -121.9212 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Unknown | 101734977 |  | 21000 | Conductor | Overhead | Yes | 42612 | 2016-08-30 16:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0951 | 2016 | 8 | 30 | 16 | 1 | 16-0061130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 199327 | 14.6893 | 159_162 | <25mph | <15mph | HFTD - Distribution | 2016-08-30 16:01:00 | 694 | 14.6893 | FALSE | <25mph | E6407 | 1.51 | 2019-03-21T02:03:00Z | 10 | 37 | < 25mph | E8875 | 4.34 | 2019-03-21T02:00:00Z | 12.01 | 41 | < 25mph | E6407 | 1.51 | 2019-03-21T02:03:00Z | 10 | 73 | < 25mph | E8875 | 4.34 | 2019-03-21T02:00:00Z | 12.01 | 81 | < 25mph
PG&E | 2019-03-13 | 16:08 | 39.8831 | -122.5498 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 6Fn0313191607 |  | 12000 | Conductor | Overhead | Yes | 43537 | 16:08 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-194 | 2019 | 3 | 13 | 16 | 8 | 19-0033617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 21012 | 20.7105 | 134_343 | <25mph | <15mph | HFTD - Distribution | 2019-03-13 16:08:00 | 1734 | 26.4067 | FALSE | 25-40mph | TCKC1 | 3.76 | 2016-06-12T06:28:00Z | 17 | 1 | < 25mph | EPKC1 | 5.75 | 2016-06-12T06:03:00Z | 28.01 | 2 | 25-40mph | TCKC1 | 3.76 | 2016-06-12T07:28:00Z | 18.01 | 2 | < 25mph | EPKC1 | 5.75 | 2016-06-12T07:03:00Z | 32.01 | 4 | 25-40mph
PG&E | 2016-10-23 18:44 | 18:10 | 38.021 | -120.5991 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101272943 |  | 115000 | Conductor | Overhead | Yes | 42666.7804 | 18:10 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1043 | 2016 | 10 | 23 | 18 | 10 | INT-08709 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 0 | 9.2045 | 217_240 | <25mph | <15mph | HFTD - Transmission | 2016-10-23 18:10:00 | 784 | 15.0974 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2861 | 6.79 | 2015-11-24T06:10:00Z | 2.01 | 8 | < 25mph |  |  |  | 0 | 0 | No data | E2861 | 6.79 | 2015-11-24T07:13:00Z | 8.01 | 17 | < 25mph
PG&E | 2015-06-09 15:24 | 2015-06-09 15:24 | 38.3651 | -122.2541 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | load side 2987 | Yes | 21000 | Conductor | Overhead | Yes | 42164.6417 | 2015-06-09 15:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0368 | 2015 | 6 | 9 | 15 | 24 | 15-0039825 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 651298 | 15.2247 | 145_259 | <25mph | <15mph | HFTD - Distribution | 2015-06-09 15:24:00 | 114 | 15.4726 | FALSE | <25mph | PG083 | 3.53 | 2018-10-12T04:30:00Z | 6.8 | 19 | < 25mph | ATLC1 | 7.61 | 2018-10-12T05:29:00Z | 11.01 | 48 | < 25mph | PG083 | 3.53 | 2018-10-12T04:30:00Z | 6.8 | 35 | < 25mph | ATLC1 | 7.61 | 2018-10-12T06:29:00Z | 15.99 | 90 | < 25mph
PG&E | 2015-06-04 13:17 | 2015-06-04 13:17 | 39.2694 | -123.7841 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42159.5535 | 2015-06-04 13:17 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0344 | 2015 | 6 | 4 | 13 | 17 | 15-0038501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20525 | 22.1312 | 81_311 | <25mph | <15mph | HFTD - Distribution | 2015-06-04 13:17:00 | 90 | 22.6218 | FALSE | <25mph | E6025 | 1.61 | 2016-11-01T18:30:00Z | 3 | 4 | < 25mph | E6025 | 1.61 | 2016-11-01T18:30:00Z | 3 | 5 | < 25mph | E6025 | 1.61 | 2016-11-01T19:30:00Z | 4 | 8 | < 25mph | E6025 | 1.61 | 2016-11-01T19:30:00Z | 4 | 9 | < 25mph
PG&E | 2018-07-01 | 0:23 | 40.2697 | -124.2386 | Vegetation | Rural | < 3 meters | Fire Agency | fire chief | 100986962 | Unknown | 12000 | Conductor | Overhead | Yes | 43282 | 0:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1718 | 2018 | 7 | 1 | 0 | 23 | 18-0056043 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 22872 | 20.9894 | 63_366 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 00:23:00 | 1459 | 27.5371 | FALSE | 25-40mph | PTEC1 | 1.7 | 2017-06-20T10:08:00Z | 55.01 | 1 | 55mph+ | PTEC1 | 1.7 | 2017-06-20T10:08:00Z | 55.01 | 1 | 55mph+ | PTEC1 | 1.7 | 2017-06-20T10:08:00Z | 55.01 | 2 | 55mph+ | PTEC1 | 1.7 | 2017-06-20T10:08:00Z | 55.01 | 2 | 55mph+
PG&E | 2016-10-14 04:33 | 4:32 | 40.5228 | -121.6813 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101513661 |  | 12000 | Conductor | Overhead | Yes | 42657.1893 | 4:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1032 | 2016 | 10 | 14 | 4 | 32 | 16-0071897 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 38950 | 28.7152 | 171_378 | 25-40mph | 15-30mph | HFTD - Distribution | 2016-10-14 04:32:00 | 773 | 31.1927 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | VIOC1 | 5.45 | 2019-02-27T10:52:00Z | 21 | 1 | < 25mph |  |  |  | 0 | 0 | No data | VIOC1 | 5.45 | 2019-02-27T10:52:00Z | 21 | 2 | < 25mph
PG&E | 2017-07-30 09:47 | 09:46 | 38.9132 | -122.6179 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike wink | 102151066 | None | 0 – 750 | Conductor | Overhead | Yes | 42946.4075 | 09:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1302 | 2017 | 7 | 30 | 9 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.2785 | 130_290 | <25mph | <15mph | HFTD - Distribution | 2017-07-30 09:46:00 | 1040 | 13.7198 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 4.76 | 2017-01-05T18:57:00Z | 8.99 | 6 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 4.76 | 2017-01-05T18:57:00Z | 8.99 | 14 | < 25mph
PG&E | 2019-06-07 | 9:58 | 38.7285 | -123.3528 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 042861101 |  | 21000 | Conductor | Overhead | Yes | 43623 | 9:58 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-358 | 2019 | 6 | 7 | 9 | 58 | 19-0064216 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 5301 | 16.456 | 98_280 | <25mph | <15mph | HFTD - Distribution | 2019-06-07 09:58:00 | 1805 | 19.4921 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D2695 | 5.46 | 2017-10-27T15:04:00Z | 4 | 4 | < 25mph |  |  |  | 0 | 0 | No data | D2695 | 5.46 | 2017-10-27T15:04:00Z | 4 | 8 | < 25mph
PG&E | 2018-08-20 | 9:34 | 39.8014 | -121.5813 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100400441 | Unknown | 12000 | Conductor | Overhead | Yes | 43332 | 9:34 | Contact From Object | N.A. | Other | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1849 | 2018 | 8 | 20 | 9 | 34 | 18-0071596 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 394259 | 5.4464 | 175_338 | <25mph | <15mph | HFTD - Distribution | 2018-08-20 09:34:00 | 1588 | 11.8754 | FALSE | <25mph | E2076 | 2.84 | 2017-04-02T20:27:00Z | 12.01 | 12 | < 25mph | JBGC1 | 6.67 | 2017-04-02T20:13:00Z | 18.01 | 26 | < 25mph | E2076 | 2.84 | 2017-04-02T20:27:00Z | 12.01 | 25 | < 25mph | JBGC1 | 6.67 | 2017-04-02T20:13:00Z | 18.01 | 52 | < 25mph
PG&E | 2016-04-21 09:25 | 2016-04-21 09:25 | 39.293 | -123.769 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 103312287 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0711 | 2016 | 4 | 21 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 8.8774 | 81_312 | <25mph | <15mph | HFTD - Distribution | 2016-04-21 09:25:00 | 455 | 20.2474 | FALSE | <25mph | E6025 | 0.21 | 2015-10-10T06:01:00Z | 3 | 4 | < 25mph | E6025 | 0.21 | 2015-10-10T06:01:00Z | 3 | 4 | < 25mph | E6025 | 0.21 | 2015-10-10T06:01:00Z | 3 | 8 | < 25mph | E6025 | 0.21 | 2015-10-10T06:01:00Z | 3 | 9 | < 25mph
PG&E | 2019-09-11 | 18:56 | 37.9937 | -122.137 | Bird Found | Hardwood Woodland | Other | Unknown |  | Unknown |  | 115000 | Other | Overhead | Yes | 43719 | 18:56 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-42 | 2019 | 9 | 11 | 18 | 56 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | N.A. | 16.9097 | 150_239 | <25mph | <15mph | HFTD - Transmission | 2019-09-11 18:56:00 | 2034 | 19.7995 | FALSE | <25mph | UPBC1 | 3.21 | 2017-05-02T06:18:00Z | 18.1 | 38 | < 25mph | UPBC1 | 3.21 | 2017-05-02T06:18:00Z | 18.1 | 129 | < 25mph | UPBC1 | 3.21 | 2017-05-02T06:18:00Z | 18.1 | 74 | < 25mph | UPBC1 | 3.21 | 2017-05-02T06:18:00Z | 18.1 | 252 | < 25mph
PG&E | 2018-09-05 | 16:55 | 37.4655 | -119.9005 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JON BERRY 209-966-4700 | 101087053 | Unknown | 21000 | Conductor | Overhead | Yes | 43348 | 16:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1882 | 2018 | 9 | 5 | 16 | 55 | 18-0076909 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 4017 | 13.8551 | 248_210 | <25mph | <15mph | HFTD - Distribution | 2018-09-05 16:55:00 | 1621 | 17.3022 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C1522 | 4.69 | 2015-08-15T16:47:00Z | 7 | 6 | < 25mph |  |  |  | 0 | 0 | No data | C1522 | 4.69 | 2015-08-15T17:37:00Z | 10 | 14 | < 25mph
PG&E | 2017-10-23 | 21:24 | 37.3713 | -122.348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100270421 | Unknown | 12000 | Conductor | Overhead | Yes | 43031 | 21:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1507 | 2017 | 10 | 23 | 21 | 24 | 17-0089820 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1768 | 13.1103 | 140_205 | <25mph | <15mph | HFTD - Distribution | 2017-10-23 21:24:00 | 1249 | 22.0037 | FALSE | <25mph | PG149 | 1.56 | 2019-02-13T18:50:00Z | 31.56 | 12 | 25-40mph | PG150 | 5.57 | 2019-02-13T19:00:00Z | 48 | 26 | 40-55mph | PG149 | 1.56 | 2019-02-13T19:20:00Z | 36.82 | 24 | 25-40mph | PG150 | 5.57 | 2019-02-13T19:00:00Z | 48 | 53 | 40-55mph
PG&E | 2015-03-14 02:30 | 2015-03-14 02:30 | 38.9038 | -122.7579 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 9210 Wildcat Road, Kelseyville |  | 12000 | Conductor | Overhead | Yes | 42077.1042 | 2015-03-14 02:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0274 | 2015 | 3 | 14 | 2 | 30 | 15-0019556 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2280 | 8.9688 | 124_289 | <25mph | <15mph | HFTD - Distribution | 2015-03-14 02:30:00 | 20 | 8.9688 | FALSE | <25mph | KELC1 | 2.83 | 2016-09-26T13:57:00Z | 11.01 | 1 | < 25mph | LKRC1 | 6.79 | 2016-09-26T14:05:00Z | 13 | 6 | < 25mph | KELC1 | 2.83 | 2016-09-26T14:57:00Z | 11.01 | 2 | < 25mph | LKRC1 | 6.79 | 2016-09-26T15:05:00Z | 14 | 12 | < 25mph
PG&E | 2017-09-08 | 17:21 | 38.6039 | -120.9275 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101379094 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42986 | 17:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1402 | 2017 | 9 | 8 | 17 | 21 | 17-0077122 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 8504 | 10.5347 | 203_272 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 17:21:00 | 1140 | 11.5767 | FALSE | <25mph | PG074 | 1.04 | 2018-10-31T06:40:00Z | 8.55 | 19 | < 25mph | PG103 | 5.52 | 2018-10-31T06:00:00Z | 9.22 | 94 | < 25mph | PG074 | 1.04 | 2018-10-31T06:40:00Z | 8.55 | 38 | < 25mph | PG103 | 5.52 | 2018-10-31T06:00:00Z | 9.22 | 187 | < 25mph
PG&E | 2016-06-03 | 2016-06-03 12:16 | 38.6435 | -120.6959 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | cal-fire and usfs | 103119737 |  | 21000 | Conductor | Overhead | Yes | 42524 | 2016-06-03 12:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0764 | 2016 | 6 | 3 | 12 | 16 | 16-0040808 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 101354 | 7.6436 | 213_274 | <25mph | <15mph | HFTD - Distribution | 2016-06-03 12:16:00 | 507 | 11.74 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6490 | 7.82 | 2016-08-14T02:49:00Z | 2.01 | 16 | < 25mph |  |  |  | 0 | 0 | No data | E6490 | 7.82 | 2016-08-14T02:49:00Z | 2.01 | 33 | < 25mph
PG&E | 2016-07-27 17:05 | 2016-07-27 17:05 | 38.5392 | -122.7656 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102029945 |  | 60000 | Conductor | Overhead | Yes | 42578.7118 | 2016-07-27 17:05 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0882 | 2016 | 7 | 27 | 17 | 5 | FU-2016-047 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 18.1446 | 123_269 | <25mph | <15mph | HFTD - Transmission | 2016-07-27 17:05:00 | 625 | 18.1446 | FALSE | <25mph | E6724 | 1.55 | 2015-09-29T16:40:00Z | 3 | 11 | < 25mph | RSAC1 | 5.1 | 2015-09-29T16:29:00Z | 8.99 | 60 | < 25mph | E6724 | 1.55 | 2015-09-29T17:50:00Z | 4 | 29 | < 25mph | RSAC1 | 5.1 | 2015-09-29T16:29:00Z | 8.99 | 126 | < 25mph
PG&E | 2018-07-14 | 11:34 | 38.4026 | -122.5489 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103141862 | Verizon | 12000 | Conductor | Overhead | Yes | 43295 | 11:34 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1745 | 2018 | 7 | 14 | 11 | 34 | 18-0059821 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 6426 | 11.4725 | 133_262 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 11:34:00 | 1485 | 15.7933 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1582 | 5.93 | 2015-09-15T08:23:00Z | 4 | 10 | < 25mph |  |  |  | 0 | 0 | No data | E1582 | 5.93 | 2015-09-15T08:23:00Z | 4 | 20 | < 25mph
PG&E | 2018-07-17 | 19:40 | 40.5927 | -122.4886 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101477082 | AT&T | 12000 | Conductor | Overhead | Yes | 43298 | 19:40 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1760 | 2018 | 7 | 17 | 19 | 40 | 18-0060840 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 30162 | 14.3022 | 137_382 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 19:40:00 | 1500 | 21.6282 | FALSE | <25mph | MMOC1 | 1.8 | 2016-05-10T11:00:00Z | 12.01 | 5 | < 25mph | MMOC1 | 1.8 | 2016-05-10T11:00:00Z | 12.01 | 10 | < 25mph | MMOC1 | 1.8 | 2016-05-10T12:00:00Z | 15.99 | 10 | < 25mph | MMOC1 | 1.8 | 2016-05-10T12:00:00Z | 15.99 | 20 | < 25mph
PG&E | 2017-08-15 19:29 | 19:28 | 39.5037 | -121.2783 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 100396172 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42962.8116 | 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1335 | 2017 | 8 | 15 | 19 | 28 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.8405 | 188_322 | <25mph | <15mph | HFTD - Distribution | 2017-08-15 19:28:00 | 1073 | 9.7276 | FALSE | <25mph | PG080 | 2.17 | 2019-04-18T05:20:00Z | 5.7 | 2 | < 25mph | PKCC1 | 4.51 | 2019-04-18T05:10:00Z | 13 | 3 | < 25mph | PG080 | 2.17 | 2019-04-18T06:00:00Z | 6.13 | 8 | < 25mph | PKCC1 | 4.51 | 2019-04-18T06:10:00Z | 14.99 | 10 | < 25mph
PG&E | 2018-07-29 | 11:39 | 39.0968 | -123.5018 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102177329 | Unknown | 12000 | Conductor | Overhead | Yes | 43310 | 11:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1796 | 2018 | 7 | 29 | 11 | 39 | 18-0064779 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4329 | 14.6452 | 92_301 | <25mph | <15mph | HFTD - Distribution | 2018-07-29 11:39:00 | 1536 | 18.4465 | FALSE | <25mph | E1763 | 2 | 2016-02-28T22:04:00Z | 4 | 4 | < 25mph | E1763 | 2 | 2016-02-28T22:04:00Z | 4 | 4 | < 25mph | E1763 | 2 | 2016-02-28T22:49:00Z | 4 | 8 | < 25mph | E1763 | 2 | 2016-02-28T22:49:00Z | 4 | 8 | < 25mph
PG&E | 2019-08-12 | 20:06 | 39.0952 | -123.4937 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 102177212 |  | 12000 | Conductor | Overhead | Yes | 43689 | 20:06 | Vegetation |  | Veg. contact |  |  |  | Fell into (No defect) | 2019-400 | 2019 | 8 | 12 | 20 | 6 | 19-0087090 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2508 | 13.5331 | 93_301 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 20:06:00 | 1970 | 19.4805 | FALSE | <25mph | PG256 | 1.12 | 2019-08-20T10:50:00Z | 3.29 | 10 | < 25mph | PG248 | 4.67 | 2019-08-20T11:00:00Z | 5.48 | 16 | < 25mph | PG256 | 1.12 | 2019-08-20T11:10:00Z | 4.38 | 21 | < 25mph | PG248 | 4.67 | 2019-08-20T11:20:00Z | 6.35 | 33 | < 25mph
PG&E | 2016-09-12 | 12:38 | 38.7832 | -120.6006 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101421708 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42625 | 12:38 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0974 | 2016 | 9 | 12 | 12 | 38 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 15.5165 | 217_282 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 12:38:00 | 716 | 15.5342 | FALSE | <25mph | AR807 | 2.03 | 2015-05-24T11:15:00Z | 0 | 1 | < 25mph | E3165 | 7.91 | 2015-05-24T11:45:00Z | 4 | 7 | < 25mph | AR807 | 2.03 | 2015-05-24T12:35:00Z | 0 | 3 | < 25mph | E3165 | 7.91 | 2015-05-24T12:05:00Z | 5.99 | 15 | < 25mph
PG&E | 2018-08-31 | 13:02 | 40.4775 | -122.4847 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103918932 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 13:02 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1872 | 2018 | 8 | 31 | 13 | 2 | 18-0075616 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18300 | 0.9461 | 137_376 | <25mph | <15mph | HFTD - Distribution | 2018-08-31 13:02:00 | 1611 | 11.7486 | FALSE | <25mph | E6886 | 2.55 | 2015-04-19T00:30:00Z | 8.01 | 5 | < 25mph | E6886 | 2.55 | 2015-04-19T00:30:00Z | 8.01 | 16 | < 25mph | E6886 | 2.55 | 2015-04-19T01:00:00Z | 8.99 | 9 | < 25mph | E6886 | 2.55 | 2015-04-19T01:00:00Z | 8.99 | 30 | < 25mph
PG&E | 2016-05-31 04:02 | 2016-05-31 04:02 | 35.7984 | -120.9743 | Vegetation | RURAL | < 0.25 Acres | Utility: PG&E | N.A. | 101863413 |  | 12000 | Conductor | Overhead | Yes | 42521.1681 | 2016-05-31 04:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0754 | 2016 | 5 | 31 | 4 | 2 | 16-0039748 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 51888 | 1.5922 | 201_118 | <25mph | <15mph | HFTD - Distribution | 2016-05-31 04:02:00 | 497 | 16.9662 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG171 | 4.38 | 2019-09-29T17:10:00Z | 7.67 | 25 | < 25mph |  |  |  | 0 | 0 | No data | PG171 | 4.38 | 2019-09-29T17:50:00Z | 10.58 | 47 | < 25mph
PG&E | 2017-10-08 | 22:58 | 39.3642 | -121.1131 | Vegetation | Rural | < 3 Meters | Fire Agency | INCIDENT NUMBER 26268 | 100068104 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43016 | 22:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Fell into (No defect) | 1471 | 2017 | 10 | 8 | 22 | 58 | 17-0085355 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 198802 | 15.5554 | 195_314 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 22:58:00 | 1211 | 22.0344 | FALSE | <25mph | E3651 | 3.94 | 2016-10-08T20:05:00Z | 8.99 | 12 | < 25mph | E3651 | 3.94 | 2016-10-08T20:05:00Z | 8.99 | 19 | < 25mph | E3651 | 3.94 | 2016-10-08T20:10:00Z | 8.99 | 24 | < 25mph | RRRC1 | 4.2 | 2016-10-08T20:13:00Z | 11.01 | 38 | < 25mph
PG&E | 2018-06-19 | 0:27 | 38.7604 | -120.8224 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101388356 | Unknown | 12000 | Conductor | Overhead | Yes | 43270 | 0:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1675 | 2018 | 6 | 19 | 0 | 27 | 18-0052111 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 141652 | 7.2853 | 207_281 | <25mph | <15mph | HFTD - Distribution | 2018-06-19 00:27:00 | 1417 | 13.5304 | FALSE | <25mph | E5691 | 1.82 | 2015-11-12T11:46:00Z | 4 | 12 | < 25mph | E5691 | 1.82 | 2015-11-12T11:46:00Z | 4 | 41 | < 25mph | E5691 | 1.82 | 2015-11-12T12:11:00Z | 4 | 24 | < 25mph | E3165 | 5.03 | 2015-11-12T12:35:00Z | 5.99 | 81 | < 25mph
PG&E | 2015-04-11 17:16 | 2015-04-11 17:16 | 40.5462 | -122.2343 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101491414 |  | 12000 | Conductor | Overhead | Yes | 42105.7194 | 2015-04-11 17:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0286 | 2015 | 4 | 11 | 17 | 16 | 15-0026023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 11914 | 19.429 | 148_380 | <25mph | <15mph | HFTD - Distribution | 2015-04-11 17:16:00 | 32 | 19.429 | FALSE | <25mph | RRAC1 | 3.7 | 2018-09-10T16:24:00Z | 3 | 1 | < 25mph | C5599 | 6.52 | 2018-09-10T17:11:00Z | 3 | 15 | < 25mph | RRAC1 | 3.7 | 2018-09-10T17:24:00Z | 4.99 | 2 | < 25mph | C5599 | 6.52 | 2018-09-10T18:11:00Z | 8.01 | 30 | < 25mph
PG&E | 2015-07-04 01:14 | 2015-07-04 01:14 | 38.9566 | -121.0434 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100037226 |  | 12000 | Other | Overhead | Yes | 42189.0514 | 2015-07-04 01:14 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0441 | 2015 | 7 | 4 | 1 | 14 | 15-0045440 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 53865 | 7.3476 | 198_292 | <25mph | <15mph | HFTD - Distribution | 2015-07-04 01:14:00 | 186 | 12.3228 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C0713 | 4.12 | 2015-04-28T22:25:00Z | 10.98 | 24 | < 25mph |  |  |  | 0 | 0 | No data | C0713 | 4.12 | 2015-04-28T22:25:00Z | 10.98 | 43 | < 25mph
PG&E | 2015-12-31 19:12 | 2015-12-31 19:12 | 37.1568 | -121.9868 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LOS GATOS MONTE SERENO SARATOGA | 100518215 | Verizon | 21000 | Conductor | Overhead | Yes | 42369.8 | 2015-12-31 19:12 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0689 | 2015 | 12 | 31 | 19 | 12 | 15-0087962 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7979 | 7.4149 | 156_193 | <25mph | <15mph | HFTD - Distribution | 2015-12-31 19:12:00 | 433 | 10.9251 | FALSE | <25mph | LSGC1 | 3.83 | 2019-01-19T08:32:00Z | 8.01 | 25 | < 25mph | SJS04 | 5.6 | 2019-01-19T08:10:00Z | 10.29 | 208 | < 25mph | LSGC1 | 3.83 | 2019-01-19T08:32:00Z | 8.01 | 54 | < 25mph | SJS04 | 5.6 | 2019-01-19T09:40:00Z | 10.51 | 417 | < 25mph
PG&E | 2016-10-11 23:17 | 23:16 | 39.0201 | -120.8294 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire.foresthill fire | 100025501 |  | 60000 | Conductor | Overhead | Yes | 42654.9701 | 23:16 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error |  | no-match | 1028 | 2016 | 10 | 11 | 23 | 16 | INT-08640 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 0 | 7.6312 | 207_295 | <25mph | <15mph | HFTD - Transmission | 2016-10-11 23:16:00 | 769 | 11.1078 | FALSE | <25mph |  |  |  | 0 | 0 | No data | FSHC1 | 7.19 | 2015-07-16T06:33:00Z | 3 | 7 | < 25mph |  |  |  | 0 | 0 | No data | FSHC1 | 7.19 | 2015-07-16T07:33:00Z | 3 | 14 | < 25mph
PG&E | 2018-08-07 | 21:03 | 38.2129 | -120.9184 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102042811 | Unknown | 12000 | Conductor | Overhead | Yes | 43319 | 21:03 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1828 | 2018 | 8 | 7 | 21 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2018-08-07 21:03:00 | NA | 0 | FALSE | <25mph | CMAC1 | 2.92 | 2019-05-28T20:59:00Z | 13 | 7 | < 25mph | PG375 | 5.2 | 2019-05-28T21:10:00Z | 15.35 | 25 | < 25mph | CMAC1 | 2.92 | 2019-05-28T20:59:00Z | 13 | 14 | < 25mph | PG375 | 5.2 | 2019-05-28T22:10:00Z | 16.44 | 50 | < 25mph
PG&E | 2017-06-27 09:28 | 9:23 | 37.9559 | -122.6176 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | marin county fire | 102260068 | UNFILED | 12000 | Conductor | Overhead | Yes | 42913.3944 | 9:23 | Other | N.A. | N.A. | N.A. | Unknown |  | Fell into (slight defect) | 1203 | 2017 | 6 | 27 | 9 | 23 | 17-0058882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 3920 | 16.1278 | 129_237 | <25mph | <15mph | HFTD - Distribution | 2017-06-27 09:23:00 | 942 | 18.7182 | FALSE | <25mph | MDEC1 | 2.55 | 2016-04-30T13:36:00Z | 32.99 | 15 | 25-40mph | MDEC1 | 2.55 | 2016-04-30T13:36:00Z | 32.99 | 21 | 25-40mph | MDEC1 | 2.55 | 2016-04-30T14:36:00Z | 32.99 | 29 | 25-40mph | MDEC1 | 2.55 | 2016-04-30T14:36:00Z | 32.99 | 41 | 25-40mph
PG&E | 2015-09-28 09:42 | 2015-09-28 09:42 | 37.9623 | -122.1765 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100458692 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42275.4042 | 2015-09-28 09:42 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0619 | 2015 | 9 | 28 | 9 | 42 | 15-0066062 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 2125 | 9.6053 | 148_237 | <25mph | <15mph | HFTD - Distribution | 2015-09-28 09:42:00 | 364 | 19.5931 | FALSE | <25mph | PG188 | 1.17 | 2019-08-28T18:10:00Z | 21.92 | 37 | < 25mph | UPBC1 | 6.07 | 2019-08-28T18:48:00Z | 25.99 | 211 | 25-40mph | PG188 | 1.17 | 2019-08-28T18:10:00Z | 21.92 | 74 | < 25mph | UPBC1 | 6.07 | 2019-08-28T19:36:00Z | 25.99 | 424 | 25-40mph
PG&E | 2016-09-23 05:23 | 15:23 | 39.3784 | -121.0922 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100091491 | None | 12000 | Conductor | Overhead | Yes | 42636.2243 | 15:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0999 | 2016 | 9 | 23 | 15 | 23 | 16-0067089 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 80185 | 10.9717 | 195_315 | <25mph | <15mph | HFTD - Distribution | 2016-09-23 15:23:00 | 741 | 11.3047 | FALSE | <25mph | E3651 | 3.67 | 2017-02-03T05:40:00Z | 10 | 9 | < 25mph | RRRC1 | 5.34 | 2017-02-03T05:13:00Z | 11.01 | 10 | < 25mph | E3651 | 3.67 | 2017-02-03T05:40:00Z | 10 | 21 | < 25mph | RRRC1 | 5.34 | 2017-02-03T06:13:00Z | 13 | 23 | < 25mph
PG&E | 2018-08-07 | 0.65694 | 40.4465 | -122.446 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464611 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43319 | 0.65694 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1826 | 2018 | 8 | 7 | 15 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 7.2812 | 139_374 | <25mph | <15mph | HFTD - Distribution | 2018-08-07 15:46:00 | 1566 | 14.3471 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D1852 | 7.52 | 2015-01-27T08:14:00Z | 0 | 6 | < 25mph |  |  |  | 0 | 0 | No data | D1852 | 7.52 | 2015-01-27T09:18:00Z | 0 | 12 | < 25mph
PG&E | 2019-07-27 | 8:22 | 40.3789 | -122.1873 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Self Extinguished |  | 103461102 |  | 12000 | Conductor | Overhead | Yes | 43673 | 8:22 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-382 | 2019 | 7 | 27 | 8 | 22 | 19-0081756 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 456 | 4.4493 | 149_370 | <25mph | <15mph | HFTD - Distribution | 2019-07-27 08:22:00 | 1935 | 12.5056 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AP525 | 5.17 | 2015-12-29T19:10:00Z | 7 | 6 | < 25mph |  |  |  | 0 | 0 | No data | AP525 | 5.17 | 2015-12-29T19:40:00Z | 8.01 | 12 | < 25mph
3. Redwood Valley (Mendocino Lake Complex) | 2017-10-08 | 23:36 | 39.2487 | -123.1663 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1989 | 2017 | 10 | 8 | 23 | 36 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 24.7673 | 107_309 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 23:36:00 | 1212 | 30.3049 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E7513 | 5.24 | 2017-05-16T09:03:00Z | 3 | 10 | < 25mph |  |  |  | 0 | 0 | No data | E7513 | 5.24 | 2017-05-16T09:03:00Z | 3 | 22 | < 25mph
PG&E | 2019-09-11 | 21:03 | 38.3132 | -120.9809 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 163341103 |  | 12000 | Conductor | Overhead | Yes | 43719 | 21:03 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-370 | 2019 | 9 | 11 | 21 | 3 | 19-0098003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25994 | 11.7888 | 200_256 | <25mph | <15mph | HFTD - Distribution | 2019-09-11 21:03:00 | 2035 | 13.1911 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 5.36 | 2019-04-06T03:05:00Z | 5.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 5.36 | 2019-04-06T04:05:00Z | 5.99 | 2 | < 25mph
PG&E | 2018-03-06 | 17:57 | 38.2811 | -120.8965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-647-5220 | 101238429 | AT&T | 12000 | Conductor | Overhead | Yes | 43165 | 17:57 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1566 | 2018 | 3 | 6 | 17 | 57 | 18-0020396 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 142000 | 3.9357 | 204_254 | <25mph | <15mph | HFTD - Distribution | 2018-03-06 17:57:00 | 1308 | 12.1612 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.07 | 2017-06-03T04:05:00Z | 12.01 | 2 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.07 | 2017-06-03T04:05:00Z | 12.01 | 4 | < 25mph
PG&E | 2015-07-15 09:00 | 2015-07-15 09:00 | 36.997 | -121.7381 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101795728 |  | 21000 | Conductor | Overhead | Yes | 42200.375 | 2015-07-15 09:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0463 | 2015 | 7 | 15 | 9 | 0 | 15-0047650 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3800 | 8.5113 | 167_184 | <25mph | <15mph | HFTD - Distribution | 2015-07-15 09:00:00 | 208 | 13.379 | FALSE | <25mph | CTOC1 | 3.71 | 2015-03-22T05:27:00Z | 8.01 | 1 | < 25mph | CTOC1 | 3.71 | 2015-03-22T05:27:00Z | 8.01 | 35 | < 25mph | CTOC1 | 3.71 | 2015-03-22T05:27:00Z | 8.01 | 2 | < 25mph | CTOC1 | 3.71 | 2015-03-22T05:27:00Z | 8.01 | 68 | < 25mph
PG&E | 2016-04-13 19:28 | 2016-04-13 19:28 | 40.4954 | -124.1219 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103659313 |  | 12000 | Conductor | Overhead | Yes | 42473.8111 | 2016-04-13 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0706 | 2016 | 4 | 13 | 19 | 28 | 16-0028421 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 688 | 19.0823 | 68_379 | <25mph | <15mph | HFTD - Distribution | 2016-04-13 19:28:00 | 450 | 22.9769 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AT493 | 5.02 | 2017-09-08T20:13:00Z | 8.01 | 21 | < 25mph |  |  |  | 0 | 0 | No data | KFOT | 4.03 | 2017-09-08T21:35:00Z | 18.41 | 43 | < 25mph
PG&E | 2015-05-09 21:37 | 2015-05-09 21:37 | 39.2848 | -121.0219 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100004095 | Pacific Bell | 12000 | Fuse | Overhead | Yes | 42133.9007 | 2015-05-09 21:37 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0312 | 2015 | 5 | 9 | 21 | 37 | 15-0033109 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 11 | 9.2188 | 198_310 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 21:37:00 | 58 | 15.4234 | FALSE | <25mph | E5439 | 3.42 | 2015-04-10T15:20:00Z | 3 | 28 | < 25mph | RRRC1 | 5.26 | 2015-04-10T15:13:00Z | 7 | 65 | < 25mph | E5439 | 3.42 | 2015-04-10T16:20:00Z | 4 | 56 | < 25mph | RRRC1 | 5.26 | 2015-04-10T16:13:00Z | 7 | 130 | < 25mph
PG&E | 2018-08-24 | 5:03 | 39.1184 | -121.0154 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JIM SMITH BATT CHIEF 3 | 100097647 | Unknown | 12000 | Conductor | Overhead | Yes | 43336 | 5:03 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1858 | 2018 | 8 | 24 | 5 | 3 | 18-0073024 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 4048 | 6.5682 | 199_301 | <25mph | <15mph | HFTD - Distribution | 2018-08-24 05:03:00 | 1597 | 12.3049 | FALSE | <25mph | AT999 | 2.07 | 2017-03-28T10:20:00Z | 4.99 | 22 | < 25mph | E1789 | 6.59 | 2017-03-28T10:42:00Z | 13 | 70 | < 25mph | AT999 | 2.07 | 2017-03-28T10:20:00Z | 4.99 | 43 | < 25mph | E1789 | 6.59 | 2017-03-28T10:42:00Z | 13 | 139 | < 25mph
PG&E | 2015-02-07 18:38 | 2015-02-07 18:38 | 40.4674 | -123.6545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | mile marker 36.61, hwy 36, bridgeville |  | 12000 | Conductor | Overhead | Yes | 42042.7764 | 2015-02-07 18:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0262 | 2015 | 2 | 7 | 18 | 38 | 15-0011390 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 7691 | 20.9308 | 88_377 | <25mph | <15mph | HFTD - Distribution | 2015-02-07 18:38:00 | 9 | 24.639 | FALSE | <25mph | E8593 | 2.58 | 2016-07-29T22:35:00Z | 10 | 11 | < 25mph | MDDC1 | 6.88 | 2016-07-29T21:53:00Z | 13 | 12 | < 25mph | E8593 | 2.58 | 2016-07-29T23:25:00Z | 12.01 | 20 | < 25mph | MDDC1 | 6.88 | 2016-07-29T21:53:00Z | 13 | 22 | < 25mph
PG&E | 2016-06-12 | 2016-06-12 13:14 | 37.5096 | -120.0462 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101083986 |  | 0 – 750 | Conductor | Overhead | Yes | 42533 | 2016-06-12 13:14 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0795 | 2016 | 6 | 12 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.8806 | 241_212 | <25mph | <15mph | HFTD - Distribution | 2016-06-12 13:14:00 | 539 | 13.4596 | FALSE | <25mph | PG457 | 2.02 | 2019-09-18T05:30:00Z | 7.96 | 15 | < 25mph | PG189 | 6.87 | 2019-09-18T05:10:00Z | 9.73 | 50 | < 25mph | PG457 | 2.02 | 2019-09-18T05:30:00Z | 7.96 | 28 | < 25mph | PG518 | 7.69 | 2019-09-18T07:10:00Z | 10.74 | 93 | < 25mph
PG&E | 2015-09-28 09:42 | 2015-09-28 09:42 | 37.9623 | -122.1765 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100458692 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42275.4042 | 2015-09-28 09:42 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0619 | 2015 | 9 | 28 | 9 | 42 | 15-0066062 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 2125 | 9.6053 | 148_237 | <25mph | <15mph | HFTD - Distribution | 2015-09-28 09:42:00 | 364 | 19.5931 | FALSE | <25mph | PLEC1 | 3.75 | 2017-09-09T02:28:00Z | 14.99 | 8 | < 25mph | D6785 | 7.72 | 2017-09-09T02:23:00Z | 18.01 | 165 | < 25mph | PLEC1 | 3.75 | 2017-09-09T03:28:00Z | 14.99 | 15 | < 25mph | DPXC1 | 7.94 | 2017-09-09T03:36:00Z | 18.99 | 337 | < 25mph
PG&E | 2017-05-25 15:05 | 15:05 | 36.5217 | -121.8473 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Buddy Bloxham 831-236-5659 | 101778611 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42880.6288 | 15:05 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1113 | 2017 | 5 | 25 | 15 | 5 | 17-0050761 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 13965 | 25.8899 | 162_158 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-05-25 15:05:00 | 853 | 26.2648 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E8505 | 7.82 | 2019-05-28T05:02:00Z | 20 | 63 | < 25mph |  |  |  | 0 | 0 | No data | E8505 | 7.82 | 2019-05-28T06:02:00Z | 22.01 | 124 | < 25mph
PG&E | 2018-06-05 | 10:13 | 40.6183 | -122.3173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JASON COLLINS 530-225-4628 | 101467801 | None | 12000 | Conductor | Overhead | Yes | 43256 | 10:13 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1631 | 2018 | 6 | 5 | 10 | 13 | 18-0047539 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 277 | 7.1547 | 144_384 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 10:13:00 | 1373 | 12.6046 | FALSE | <25mph | C5599 | 1.27 | 2018-09-01T09:31:00Z | 2.01 | 11 | < 25mph | RRAC1 | 7.21 | 2018-09-01T09:24:00Z | 8.01 | 12 | < 25mph | C5599 | 1.27 | 2018-09-01T09:31:00Z | 2.01 | 19 | < 25mph | RRAC1 | 7.21 | 2018-09-01T09:24:00Z | 8.01 | 21 | < 25mph
PG&E | 2015-10-16 09:43 | 2015-10-16 09:43 | 39.187 | -123.2015 | Vegetation | Rural | < 3 meters | Unknown |  | 102196855 |  | 12000 | Conductor | Overhead | Yes | 42293.4049 | 2015-10-16 09:43 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0653 | 2015 | 10 | 16 | 9 | 43 | 15-0070948 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 65228 | 2.2696 | 105_305 | <25mph | <15mph | HFTD - Distribution | 2015-10-16 09:43:00 | 397 | 16.8813 | FALSE | <25mph | E7513 | 1.34 | 2016-07-01T13:28:00Z | 1.01 | 12 | < 25mph | E7513 | 1.34 | 2016-07-01T13:28:00Z | 1.01 | 24 | < 25mph | E7513 | 1.34 | 2016-07-01T14:23:00Z | 2.01 | 24 | < 25mph | E7513 | 1.34 | 2016-07-01T14:23:00Z | 2.01 | 48 | < 25mph
PG&E | 2018-08-07 | 17:15 | 37.1181 | -122.1093 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101670606 | AT&T | 12000 | Conductor | Overhead | Yes | 43319 | 17:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1827 | 2018 | 8 | 7 | 17 | 15 | 18-0067641 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1988 | 17.3453 | 151_191 | <25mph | <15mph | HFTD - Distribution | 2018-08-07 17:15:00 | 1567 | 17.3453 | FALSE | <25mph | C1844 | 1.77 | 2017-08-06T02:00:00Z | 8.99 | 31 | < 25mph | C1844 | 1.77 | 2017-08-06T02:00:00Z | 8.99 | 63 | < 25mph | C1844 | 1.77 | 2017-08-06T02:00:00Z | 8.99 | 59 | < 25mph | C1844 | 1.77 | 2017-08-06T02:00:00Z | 8.99 | 121 | < 25mph
PG&E | 2019-07-19 | 11:59 | 37.9162 | -120.349 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 163351703 |  | 17000 | Conductor | Overhead | Yes | 43665 | 11:59 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-376 | 2019 | 7 | 19 | 11 | 59 | 19-0079030 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24042 | 10.7946 | 228_234 | <25mph | <15mph | HFTD - Distribution | 2019-07-19 11:59:00 | 1915 | 10.8841 | FALSE | <25mph | C3161 | 3.6 | 2017-04-17T15:15:00Z | 5.99 | 4 | < 25mph | C3161 | 3.6 | 2017-04-17T15:15:00Z | 5.99 | 4 | < 25mph | C3161 | 3.6 | 2017-04-17T15:15:00Z | 5.99 | 8 | < 25mph | C3161 | 3.6 | 2017-04-17T15:15:00Z | 5.99 | 8 | < 25mph
PG&E | 2016-07-28 08:12 | 2016-07-28 08:12 | 37.8207 | -120.1388 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101037043 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0884 | 2016 | 7 | 28 | 8 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 1.7128 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 08:12:00 | 627 | 11.4062 | FALSE | <25mph | SEWC1 | 2.5 | 2015-01-24T12:16:00Z | 11.01 | 5 | < 25mph | SEWC1 | 2.5 | 2015-01-24T12:16:00Z | 11.01 | 11 | < 25mph | SEWC1 | 2.5 | 2015-01-24T13:16:00Z | 13 | 10 | < 25mph | SEWC1 | 2.5 | 2015-01-24T13:16:00Z | 13 | 22 | < 25mph
PG&E | 2018-07-14 | 12:40 | 38.5793 | -122.878 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103122744 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 12:40 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1746 | 2018 | 7 | 14 | 12 | 40 | 18-0059799 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20804 | 12.0574 | 118_272 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 12:40:00 | 1486 | 14.4502 | FALSE | <25mph | D2144 | 3.55 | 2016-07-31T21:47:00Z | 8.99 | 15 | < 25mph | KHES | 5.2 | 2016-07-31T21:55:00Z | 18.41 | 29 | < 25mph | D2144 | 3.55 | 2016-07-31T23:02:00Z | 8.99 | 30 | < 25mph | KHES | 5.2 | 2016-07-31T22:55:00Z | 18.41 | 57 | < 25mph
PG&E | 2017-07-01 | 12:02 | 39.8209 | -121.6418 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 003/039 | Unknown | 60000 | Conductor | Overhead | Yes | 42917 | 12:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1212 | 2017 | 7 | 1 | 12 | 2 | INT-09792 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.6345 | 172_339 | <25mph | <15mph | HFTD - Transmission | 2017-07-01 12:02:00 | 954 | 9.664 | FALSE | <25mph | C8878 | 3.55 | 2015-06-22T17:48:00Z | 5.99 | 21 | < 25mph | CSTC1 | 7.61 | 2015-06-22T17:51:00Z | 10 | 31 | < 25mph | C8878 | 3.55 | 2015-06-22T18:48:00Z | 7 | 44 | < 25mph | CSTC1 | 7.61 | 2015-06-22T17:51:00Z | 10 | 64 | < 25mph
PG&E | 2016-06-12 | 2016-06-12 13:14 | 37.5096 | -120.0462 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101083986 |  | 0 – 750 | Conductor | Overhead | Yes | 42533 | 2016-06-12 13:14 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0795 | 2016 | 6 | 12 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.8806 | 241_212 | <25mph | <15mph | HFTD - Distribution | 2016-06-12 13:14:00 | 539 | 13.4596 | FALSE | <25mph | MPOC1 | 3.28 | 2018-03-07T07:07:00Z | 8.01 | 1 | < 25mph | MPOC1 | 3.28 | 2018-03-07T07:07:00Z | 8.01 | 1 | < 25mph | MPOC1 | 3.28 | 2018-03-07T08:07:00Z | 8.01 | 2 | < 25mph | MPOC1 | 3.28 | 2018-03-07T08:07:00Z | 8.01 | 2 | < 25mph
PG&E | 2019-07-25 | 0:15 | 39.0662 | -120.9754 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Placer Hills FD | 152491101 |  | 12000 | Conductor | Overhead | Yes | 43671 | 0:15 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-379 | 2019 | 7 | 25 | 0 | 15 | 19-0080924 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7845 | 8.7511 | 200_298 | <25mph | <15mph | HFTD - Distribution | 2019-07-25 00:15:00 | 1927 | 11.2312 | FALSE | <25mph | C5488 | 2.88 | 2015-01-08T20:01:00Z | 4.99 | 22 | < 25mph | C5488 | 2.88 | 2015-01-08T20:01:00Z | 4.99 | 38 | < 25mph | C5488 | 2.88 | 2015-01-08T20:01:00Z | 4.99 | 42 | < 25mph | C5488 | 2.88 | 2015-01-08T20:01:00Z | 4.99 | 74 | < 25mph
PG&E | 2015-05-09 21:37 | 2015-05-09 21:37 | 39.2848 | -121.0219 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100004095 | Pacific Bell | 12000 | Fuse | Overhead | Yes | 42133.9007 | 2015-05-09 21:37 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0312 | 2015 | 5 | 9 | 21 | 37 | 15-0033109 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 11 | 9.2188 | 198_310 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 21:37:00 | 58 | 15.4234 | FALSE | <25mph | E3651 | 3.92 | 2016-04-28T19:40:00Z | 13 | 28 | < 25mph | KGOO | 4.32 | 2016-04-28T20:00:00Z | 17.27 | 73 | < 25mph | E3651 | 3.92 | 2016-04-28T21:00:00Z | 13 | 56 | < 25mph | KGOO | 4.32 | 2016-04-28T20:20:00Z | 19.57 | 147 | < 25mph
PG&E | 2017-09-01 | 17:48 | 36.6518 | -121.7249 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MCFD | 103155761 | Unknown | 12000 | Conductor | Overhead | Yes | 42979 | 17:48 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1382 | 2017 | 9 | 1 | 17 | 48 | 17-0074898 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 8152 | 14.5474 | 167_165 | <25mph | <15mph | HFTD - Distribution | 2017-09-01 17:48:00 | 1120 | 19.9505 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E8875 | 7.26 | 2016-11-10T21:51:00Z | 14.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E8875 | 7.26 | 2016-11-10T21:51:00Z | 14.99 | 8 | < 25mph
PG&E | 2018-08-08 | 16:02 | 36.4703 | -121.7143 | Vegetation | Rural | < 3 meters | Customer | N.A. | 103910535 | None | 12000 | Conductor | Overhead | Yes | 43320 | 16:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1830 | 2018 | 8 | 8 | 16 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 14.7322 | 168_155 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:02:00 | 1569 | 15.5625 | FALSE | <25mph | PG206 | 1.48 | 2019-01-28T15:00:00Z | 10.74 | 6 | < 25mph | PG206 | 1.48 | 2019-01-28T15:00:00Z | 10.74 | 16 | < 25mph | PG206 | 1.48 | 2019-01-28T15:00:00Z | 10.74 | 12 | < 25mph | PG206 | 1.48 | 2019-01-28T15:00:00Z | 10.74 | 32 | < 25mph
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 9:36 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 14.8685 | 222_261 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 09:36:00 | 925 | 23.4839 | FALSE | <25mph | AT450 | 2.61 | 2015-02-02T11:45:00Z | 0 | 12 | < 25mph | C9148 | 7.6 | 2015-02-02T11:04:00Z | 8.01 | 23 | < 25mph | AT450 | 2.61 | 2015-02-02T12:45:00Z | 0 | 24 | < 25mph | C9148 | 7.6 | 2015-02-02T12:34:00Z | 8.99 | 46 | < 25mph
PG&E | 2017-08-28 | 10:07 | 39.0472 | -120.7859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | FORESTHILL | 100019525 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 10:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1357 | 2017 | 8 | 28 | 10 | 7 | 17-0073379 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 10077 | 5.9792 | 209_297 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 10:07:00 | 1095 | 13.4783 | FALSE | <25mph | AU268 | 3.78 | 2015-04-13T22:30:00Z | 4.99 | 4 | < 25mph | FSHC1 | 4.22 | 2015-04-13T22:33:00Z | 17 | 5 | < 25mph | AU268 | 3.78 | 2015-04-13T23:15:00Z | 7 | 8 | < 25mph | FSHC1 | 4.22 | 2015-04-13T22:33:00Z | 17 | 10 | < 25mph
PG&E | 2019-09-13 | 6:30 | 37.3348 | -121.7716 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 83392110 |  | 21000 | Splice/Clamp/Connector | Overhead | Yes | 43721 | 6:30 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-444 | 2019 | 9 | 13 | 6 | 30 | 19-0098560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 35534 | 3.3882 | 166_202 | <25mph | <15mph | HFTD - Distribution | 2019-09-13 06:30:00 | 2037 | 14.1926 | FALSE | <25mph | E8563 | 3.34 | 2019-01-05T21:10:00Z | 34 | 24 | 25-40mph | MIPC1 | 7.48 | 2019-01-05T21:19:00Z | 38.01 | 83 | 25-40mph | E8563 | 3.34 | 2019-01-05T21:10:00Z | 34 | 48 | 25-40mph | MIPC1 | 7.48 | 2019-01-05T21:19:00Z | 38.01 | 166 | 25-40mph
PG&E | 2016-06-21 | 20:49 | 35.5352 | -120.8457 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101900832 |  | 12000 | Conductor | Overhead | Yes | 42542 | 20:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0812 | 2016 | 6 | 21 | 20 | 49 | 16-0044904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7806 | 8.2716 | 207_103 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 20:49:00 | 558 | 17.6234 | FALSE | <25mph | PG175 | 3.43 | 2019-02-21T21:50:00Z | 31.54 | 7 | 25-40mph | PG175 | 3.43 | 2019-02-21T21:50:00Z | 31.54 | 25 | 25-40mph | PG175 | 3.43 | 2019-02-21T21:50:00Z | 31.54 | 13 | 25-40mph | PG175 | 3.43 | 2019-02-21T21:50:00Z | 31.54 | 47 | 25-40mph
PG&E | 2016-08-25 | 2016-08-25 12:04 | 36.9726 | -119.3816 | Vegetation | RURAL | < 3 meters | Utility: PG&E | N.A. | 100651318 | PONDEROSA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0945 | 2016 | 8 | 25 | 12 | 4 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.3948 | 271_183 | <25mph | <15mph | HFTD - Distribution | 2016-08-25 12:04:00 | 689 | 15.1668 | FALSE | <25mph | PG227 | 3.17 | 2019-10-21T03:30:00Z | 6.44 | 24 | < 25mph | PG198 | 5.53 | 2019-10-21T02:40:00Z | 7.61 | 72 | < 25mph | PG227 | 3.17 | 2019-10-21T03:30:00Z | 6.44 | 48 | < 25mph | PG198 | 5.53 | 2019-10-21T02:40:00Z | 7.61 | 144 | < 25mph
PG&E | 2018-06-30 | 22:18 | 40.6043 | -122.24 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101469808 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43281 | 22:18 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1716 | 2018 | 6 | 30 | 22 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 10.6263 | 147_383 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 22:18:00 | 1457 | 24.79 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C5599 | 4.85 | 2019-04-24T08:46:00Z | 8.01 | 13 | < 25mph |  |  |  | 0 | 0 | No data | C5599 | 4.85 | 2019-04-24T09:01:00Z | 8.99 | 22 | < 25mph
PG&E | 2018-02-12 | 20:20 | 39.9395 | -121.6494 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430947 | Unknown | 12000 | Conductor | Overhead | Yes | 43143 | 20:20 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1561 | 2018 | 2 | 12 | 20 | 20 | 18-0013604 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 149212 | 10.1876 | 172_346 | <25mph | <15mph | HFTD - Distribution | 2018-02-12 20:20:00 | 1303 | 14.6044 | FALSE | <25mph | PG134 | 2.86 | 2019-11-21T17:10:00Z | 4.45 | 6 | < 25mph | PG506 | 6.92 | 2019-11-21T17:20:00Z | 6.58 | 49 | < 25mph | PG134 | 2.86 | 2019-11-21T18:20:00Z | 8.32 | 12 | < 25mph | PG506 | 6.92 | 2019-11-21T17:50:00Z | 8.77 | 97 | < 25mph
PG&E | 2017-09-17 | 17:38 | 38.9946 | -121.0261 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100029537 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42995 | 17:38 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Branch (OverHanging) | 1417 | 2017 | 9 | 17 | 17 | 38 | 17-0079585 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 28509 | 11.5169 | 198_294 | <25mph | <15mph | HFTD - Distribution | 2017-09-17 17:38:00 | 1155 | 15.8476 | FALSE | <25mph | C0713 | 1.74 | 2017-05-30T09:04:00Z | 0 | 11 | < 25mph | AT999 | 7.97 | 2017-05-30T09:01:00Z | 3 | 19 | < 25mph | C0713 | 1.74 | 2017-05-30T10:10:00Z | 0 | 22 | < 25mph | AT999 | 7.97 | 2017-05-30T10:01:00Z | 3 | 40 | < 25mph
PG&E | 2015-07-24 14:30 | 2015-07-24 14:30 | 36.6913 | -119.0312 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46970 DUNLAP RD | YES | 0 – 750 | Transformer | Overhead | Yes | 42209.6042 | 2015-07-24 14:30 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0482 | 2015 | 7 | 24 | 14 | 30 | 15-0050401 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 281 | 12.3885 | 287_168 | <25mph | <15mph | HFTD - Distribution | 2015-07-24 14:30:00 | 227 | 13.0893 | FALSE | <25mph | PHRC1 | 0.81 | 2018-11-03T16:58:00Z | 4 | 1 | < 25mph | PRGC1 | 5.41 | 2018-11-03T17:00:00Z | 4.99 | 13 | < 25mph | PHRC1 | 0.81 | 2018-11-03T17:58:00Z | 8.99 | 2 | < 25mph | PHRC1 | 0.81 | 2018-11-03T17:58:00Z | 8.99 | 26 | < 25mph
PG&E | 2016-05-18 | 18:24 | 39.7381 | -123.1587 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42508 | 18:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0735 | 2016 | 5 | 18 | 18 | 24 | 16-0036911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1482 | 13.4862 | 108_336 | <25mph | <15mph | HFTD - Distribution | 2016-05-18 18:24:00 | 480 | 21.4181 | FALSE | <25mph | C3111 | 2.79 | 2018-07-26T13:31:00Z | 0 | 2 | < 25mph | EELC1 | 7.26 | 2018-07-26T13:45:00Z | 8.99 | 3 | < 25mph | C3111 | 2.79 | 2018-07-26T14:31:00Z | 0 | 4 | < 25mph | EELC1 | 7.26 | 2018-07-26T14:45:00Z | 8.99 | 6 | < 25mph
PG&E | 2019-08-14 | 10:16 | 35.379 | -120.4232 | Vegetation | Hardwood Woodland | < 1 meter | Cal Fire |  | 512769069280 |  | 21000 | Conductor | Overhead | Yes | 43691 | 10:16 | Vegetation | [5 empty] | no-match |  | 2019 | 8 | 14 | 10 | 16 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.0314 | 226_94 | <25mph | <15mph | HFTD - Distribution | 2019-08-14 10:16:00 | 1976 | 14.3934 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-09-10 | 20:37 | 38.0188 | -122.7225 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 102252760 | Unknown | 12000 | Conductor | Overhead | Yes | 43353 | 20:37 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1889 | 2018 | 9 | 10 | 20 | 37 | 18-0078359 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 219903 | 12.2581 | 125_241 | <25mph | <15mph | HFTD - Distribution | 2018-09-10 20:37:00 | 1628 | 18.8462 | FALSE | <25mph | BBEC1 | 1.27 | 2019-02-05T12:11:00Z | 11.01 | 7 | < 25mph | PG123 | 7.3 | 2019-02-05T12:20:00Z | 17.76 | 57 | < 25mph | BBEC1 | 1.27 | 2019-02-05T12:11:00Z | 11.01 | 14 | < 25mph | PG123 | 7.3 | 2019-02-05T13:30:00Z | 18.63 | 113 | < 25mph
PG&E | 2017-10-02 | 14:56 | 38.9102 | -120.9185 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100110800 | None | 21000 | Other | Overhead | Yes | 43010 | 14:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1447 | 2017 | 10 | 2 | 14 | 56 | 17-0083516 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 160 | 17.2967 | 203_289 | <25mph | <15mph | HFTD - Distribution | 2017-10-02 14:56:00 | 1185 | 22.7009 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.3 | 2017-04-06T13:56:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.3 | 2017-04-06T14:56:00Z | 8.99 | 2 | < 25mph
PG&E | 2015-09-19 09:51 | 2015-09-19 09:51 | 38.4755 | -122.9069 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FORESTVILLE | 103334444 |  | 12000 | Conductor | Overhead | Yes | 42266.4104 | 2015-09-19 09:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0603 | 2015 | 9 | 19 | 9 | 51 | 15-0062267 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 488 | 1.1332 | 117_266 | <25mph | <15mph | HFTD - Distribution | 2015-09-19 09:51:00 | 348 | 13.7107 | FALSE | <25mph | D4623 | 2.94 | 2019-03-27T01:31:00Z | 8.01 | 10 | < 25mph | E9070 | 4.38 | 2019-03-27T01:45:00Z | 8.01 | 107 | < 25mph | D4623 | 2.94 | 2019-03-27T01:31:00Z | 8.01 | 26 | < 25mph | AR323 | 7.96 | 2019-03-27T03:08:00Z | 8.99 | 216 | < 25mph
PG&E | 2017-10-28 | 15:26 | 39.4516 | -123.3838 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102209084 | Unknown | 12000 | Conductor | Overhead | Yes | 43036 | 15:26 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | no-match | 1510 | 2017 | 10 | 28 | 15 | 26 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 10.3107 | 98_320 | <25mph | <15mph | HFTD - Distribution | 2017-10-28 15:26:00 | 1252 | 11.7696 | FALSE | <25mph | PG118 | 1.44 | 2018-12-01T16:40:00Z | 13.15 | 24 | < 25mph | PG135 | 6.81 | 2018-12-01T16:20:00Z | 24.99 | 36 | < 25mph | PG120 | 3.17 | 2018-12-01T17:40:00Z | 16.89 | 48 | < 25mph | PG135 | 6.81 | 2018-12-01T16:20:00Z | 24.99 | 72 | < 25mph
PG&E | 2018-06-15 | 10:05 | 38.6238 | -121.0221 | Vegetation | Rural | < 3 meters | Customer | N.A. | 101376538 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43266 | 10:05 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1661 | 2018 | 6 | 15 | 10 | 5 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 10.3423 | 199_273 | <25mph | <15mph | HFTD - Distribution | 2018-06-15 10:05:00 | 1403 | 17.1425 | FALSE | <25mph | E8856 | 3.9 | 2017-08-06T16:35:00Z | 7 | 12 | < 25mph | FSLC1 | 7.47 | 2017-08-06T16:05:00Z | 14.63 | 57 | < 25mph | E8856 | 3.9 | 2017-08-06T17:25:00Z | 8.99 | 24 | < 25mph | FSLC1 | 7.47 | 2017-08-06T17:20:00Z | 15.01 | 109 | < 25mph
PG&E | 2015-02-23 13:25 | 2015-02-23 13:25 | 38.5046 | -122.7408 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RINCON VALLEY | BEHIND 4870 CARRIAGE LN SANTA ROSA |  | 12000 | Conductor | Overhead | Yes | 42058.559 | 2015-02-23 13:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0268 | 2015 | 2 | 23 | 13 | 25 | 15-0015168 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 85762 | 20.3218 | 124_267 | <25mph | <15mph | HFTD - Distribution | 2015-02-23 13:25:00 | 15 | 32.6885 | FALSE | 25-40mph | RSAC1 | 2.39 | 2019-03-04T00:29:00Z | 18.01 | 1 | < 25mph | RSAC1 | 2.39 | 2019-03-04T00:29:00Z | 18.01 | 61 | < 25mph | RSAC1 | 2.39 | 2019-03-04T00:29:00Z | 18.01 | 2 | < 25mph | RSAC1 | 2.39 | 2019-03-04T00:29:00Z | 18.01 | 122 | < 25mph
PG&E | 2019-07-27 | 4:51 | 37.9486 | -120.4656 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 163781705 |  | 17000 | Conductor | Overhead | Yes | 43673 | 4:51 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-385 | 2019 | 7 | 27 | 4 | 51 | 19-0081744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 1364 | 13.5826 | 223_236 | <25mph | <15mph | HFTD - Distribution | 2019-07-27 04:51:00 | 1934 | 16.9934 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F0305 | 5.84 | 2018-01-22T04:40:00Z | 2.01 | 13 | < 25mph |  |  |  | 0 | 0 | No data | F0305 | 5.84 | 2018-01-22T04:40:00Z | 2.01 | 25 | < 25mph
PG&E | 2018-09-03 | 18:29 | 39.4547 | -121.4955 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100395672 | Unknown | 12000 | Conductor | Overhead | Yes | 43346 | 18:29 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1880 | 2018 | 9 | 3 | 18 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 6.2719 | 178_319 | <25mph | <15mph | HFTD - Distribution | 2018-09-03 18:29:00 | 1619 | 14.7897 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TT309 | 4.73 | 2016-06-11T04:45:00Z | 8.01 | 2 | < 25mph |  |  |  | 0 | 0 | No data | TT309 | 4.73 | 2016-06-11T05:45:00Z | 8.99 | 4 | < 25mph
PG&E | 2015-04-30 00:26 | 2015-04-30 00:26 | 37.2401 | -122.2472 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 1145 VERDE R |  | 12000 | Conductor | Overhead | Yes | 42124.0181 | 2015-04-30 00:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0304 | 2015 | 4 | 30 | 0 | 26 | 15-0030607 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1256 | 5.7566 | 145_197 | <25mph | <15mph | HFTD - Distribution | 2015-04-30 00:26:00 | 50 | 15.5915 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG003 | 6.97 | 2018-08-22T08:00:00Z | 16.44 | 29 | < 25mph |  |  |  | 0 | 0 | No data | PG003 | 6.97 | 2018-08-22T08:00:00Z | 16.44 | 58 | < 25mph
PG&E | 2018-09-21 | 21:10 | 39.0273 | -122.6627 | Vegetation | Rural | < 3 meters | Customer | N.A. | 102147414 | Unknown | 12000 | Conductor | Overhead | Yes | 43364 | 21:10 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1908 | 2018 | 9 | 21 | 21 | 10 | 18-0082278 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 281055 | 11.7868 | 128_296 | <25mph | <15mph | HFTD - Distribution | 2018-09-21 21:10:00 | 1647 | 15.5314 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG128 | 4.07 | 2019-02-04T14:40:00Z | 18.86 | 18 | < 25mph |  |  |  | 0 | 0 | No data | PG128 | 4.07 | 2019-02-04T16:30:00Z | 24.34 | 36 | < 25mph
PG&E | 2017-05-05 15:52 | 15:52 | 40.3776 | -123.0019 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101501566 | None | 12000 | Conductor | Overhead | Yes | 42860.6614 | 15:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1084 | 2017 | 5 | 5 | 15 | 52 | 17-0045707 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 56893 | 24.5621 | 115_371 | <25mph | <15mph | HFTD - Distribution | 2017-05-05 15:52:00 | 824 | 35.0644 | FALSE | 25-40mph | TT100 | 2.89 | 2019-04-12T01:27:00Z | 22.01 | 1 | < 25mph | TT100 | 2.89 | 2019-04-12T01:27:00Z | 22.01 | 2 | < 25mph | TT100 | 2.89 | 2019-04-12T01:27:00Z | 22.01 | 2 | < 25mph | TT100 | 2.89 | 2019-04-12T01:27:00Z | 22.01 | 4 | < 25mph
PG&E | 2018-02-12 | 20:20 | 39.9395 | -121.6494 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430947 | Unknown | 12000 | Conductor | Overhead | Yes | 43143 | 20:20 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1561 | 2018 | 2 | 12 | 20 | 20 | 18-0013604 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 149212 | 10.1876 | 172_346 | <25mph | <15mph | HFTD - Distribution | 2018-02-12 20:20:00 | 1303 | 14.6044 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CSTC1 | 7.88 | 2015-07-22T10:51:00Z | 12.01 | 16 | < 25mph |  |  |  | 0 | 0 | No data | CSTC1 | 7.88 | 2015-07-22T10:51:00Z | 12.01 | 31 | < 25mph
PG&E | 2018-07-14 | 14:44 | 38.9524 | -121.2467 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100035452 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 14:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1748 | 2018 | 7 | 14 | 14 | 44 | 18-0059847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2430 | 9.5304 | 189_291 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 14:44:00 | 1488 | 13.6375 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LICC1 | 5.05 | 2016-04-02T15:13:00Z | 7 | 5 | < 25mph |  |  |  | 0 | 0 | No data | LICC1 | 5.05 | 2016-04-02T15:13:00Z | 7 | 10 | < 25mph
PG&E | 2019-07-18 | 19:57 | 37.081 | -119.4865 |  | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | No |  |  | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-09 | 2019 | 7 | 18 | 19 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.8761 | 266_189 | <25mph | <15mph | HFTD - Distribution | 2019-07-18 19:57:00 | 1914 | 14.7588 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTQC1 | 6.58 | 2017-10-15T04:52:00Z | 7 | 2 | < 25mph |  |  |  | 0 | 0 | No data | MTQC1 | 6.58 | 2017-10-15T05:52:00Z | 8.01 | 4 | < 25mph
PG&E | 2017-06-24 15:06 | 14:51 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 42910.6292 | 14:51 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1194 | 2017 | 6 | 24 | 14 | 51 | 17-0058332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 21296 | 10.4286 | 210_259 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 14:51:00 | 933 | 10.7263 | FALSE | <25mph | ANUC1 | 1.37 | 2016-10-12T04:53:00Z | 2.01 | 8 | < 25mph | MTZC1 | 6.33 | 2016-10-12T03:56:00Z | 4.99 | 9 | < 25mph | ANUC1 | 1.37 | 2016-10-12T05:53:00Z | 2.01 | 17 | < 25mph | MTZC1 | 6.33 | 2016-10-12T04:56:00Z | 5.99 | 19 | < 25mph
PG&E | 2015-08-16 07:35 | 2015-08-16 07:35 | 35.4572 | -120.6567 | Vegetation | Rural | < 3 meters | Utility: PG&E |  | 8932 SAN GABRIEL RD. SW C/O OF LOT, Atascadero | None | 0 – 750 | Conductor | Overhead | Yes | 42232.316 | 2015-08-16 07:35 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0534 | 2015 | 8 | 16 | 7 | 35 | 15-0055284 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.0129 | 215_99 | <25mph | <15mph | HFTD - Distribution | 2015-08-16 07:35:00 | 278 | 16.9932 | FALSE | <25mph | PG210 | 3.26 | 2019-05-02T22:10:00Z | 21.7 | 29 | < 25mph | PG191 | 6.6 | 2019-05-02T22:10:00Z | 24.11 | 82 | < 25mph | PG210 | 3.26 | 2019-05-02T23:20:00Z | 27.63 | 58 | 25-40mph | PG210 | 3.26 | 2019-05-02T23:20:00Z | 27.63 | 164 | 25-40mph
PG&E | 2017-10-28 | 15:26 | 39.4516 | -123.3838 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102209084 | Unknown | 12000 | Conductor | Overhead | Yes | 43036 | 15:26 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | no-match | 1510 | 2017 | 10 | 28 | 15 | 26 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 10.3107 | 98_320 | <25mph | <15mph | HFTD - Distribution | 2017-10-28 15:26:00 | 1252 | 11.7696 | FALSE | <25mph | E4027 | 3.28 | 2018-06-11T04:13:00Z | 5.99 | 12 | < 25mph | E4027 | 3.28 | 2018-06-11T04:13:00Z | 5.99 | 12 | < 25mph | E4027 | 3.28 | 2018-06-11T04:13:00Z | 5.99 | 24 | < 25mph | E4027 | 3.28 | 2018-06-11T04:13:00Z | 5.99 | 24 | < 25mph
PG&E | 2017-12-19 | 19:45 | 40.7271 | -122.3263 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101457738 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43088 | 19:45 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1545 | 2017 | 12 | 19 | 19 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 12.0712 | 144_390 | <25mph | <15mph | HFTD - Distribution | 2017-12-19 19:45:00 | 1287 | 14.9625 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2019-08-16 | 10:31 | 39.3714 | -121.3221 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103191101 |  | 12000 | Conductor | Overhead | Yes | 43693 | 10:31 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-397 | 2019 | 8 | 16 | 10 | 31 | 19-0088805 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4580 | 6.4736 | 186_315 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 10:31:00 | 1984 | 15.7456 | FALSE | <25mph | BNGC1 | 3.48 | 2015-07-24T13:51:00Z | 4 | 1 | < 25mph | BNGC1 | 3.48 | 2015-07-24T13:51:00Z | 4 | 1 | < 25mph | BNGC1 | 3.48 | 2015-07-24T14:51:00Z | 4 | 2 | < 25mph | BNGC1 | 3.48 | 2015-07-24T14:51:00Z | 4 | 2 | < 25mph
PG&E | 2018-07-27 | 23:12 | 37.18 | -122.029 | Vegetation | Rural | < 3 meters | Fire Agency | Jeremy Wise 408-378-4010 Incident # C182080066 | 100518365 | Unknown | 12000 | Conductor | Overhead | Yes | 43308 | 23:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1793 | 2018 | 7 | 27 | 23 | 12 | 18-0064525 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 30475 | 3.2895 | 154_194 | <25mph | <15mph | HFTD - Distribution | 2018-07-27 23:12:00 | 1533 | 9.1823 | FALSE | <25mph | PG050 | 2.33 | 2018-09-25T21:30:00Z | 8.99 | 16 | < 25mph | C1844 | 6.06 | 2018-09-25T21:39:00Z | 13 | 147 | < 25mph | PG050 | 2.33 | 2018-09-25T23:10:00Z | 10.51 | 32 | < 25mph | C1844 | 6.06 | 2018-09-25T21:39:00Z | 13 | 290 | < 25mph
PG&E | 2017-05-15 | 3:05 | 35.6261 | -120.8962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101873299 | Unknown | 21000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1097 | 2017 | 5 | 15 | 3 | 5 | 17-0047837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 337188 | 4.016 | 204_108 | <25mph | <15mph | HFTD - Distribution | 2017-05-15 03:05:00 | 837 | 18.5139 | FALSE | <25mph | TABC1 | 2.62 | 2018-06-14T15:07:00Z | 3 | 1 | < 25mph | TABC1 | 2.62 | 2018-06-14T15:07:00Z | 3 | 1 | < 25mph | TABC1 | 2.62 | 2018-06-14T16:07:00Z | 4 | 2 | < 25mph | TABC1 | 2.62 | 2018-06-14T16:07:00Z | 4 | 2 | < 25mph
PG&E | 2018-12-14 | 10:32 | 40.4379 | -123.7834 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101009136 | Unknown | 12000 | Conductor | Overhead | Yes | 43448 | 10:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1985 | 2018 | 12 | 14 | 10 | 32 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 36.1442 | 82_375 | 25-40mph | 30-45mph | HFTD - Distribution | 2018-12-14 10:32:00 | 1725 | 36.1442 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PG204 | 5.47 | 2019-04-18T12:30:00Z | 1.52 | 6 | < 25mph |  |  |  | 0 | 0 | No data | E8593 | 4.88 | 2019-04-18T13:35:00Z | 13 | 20 | < 25mph
PG&E | 2016-06-11 | 2016-06-11 19:45 | 39.3265 | -121.3921 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101292512 |  | 0 – 750 | Transformer | Overhead | Yes | 42532 | 2016-06-11 19:45 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0790 | 2016 | 6 | 11 | 19 | 45 | 16-0042611 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 642 | 8.1809 | 183_312 | <25mph | <15mph | HFTD - Distribution | 2016-06-11 19:45:00 | 533 | 16.0839 | FALSE | <25mph | BNGC1 | 3.76 | 2018-11-05T13:51:00Z | 3 | 1 | < 25mph | BNGC1 | 3.76 | 2018-11-05T13:51:00Z | 3 | 1 | < 25mph | BNGC1 | 3.76 | 2018-11-05T14:51:00Z | 3 | 2 | < 25mph | BNGC1 | 3.76 | 2018-11-05T14:51:00Z | 3 | 2 | < 25mph
PG&E | 2019-07-27 | 4:51 | 37.9486 | -120.4656 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 163781705 |  | 17000 | Conductor | Overhead | Yes | 43673 | 4:51 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-385 | 2019 | 7 | 27 | 4 | 51 | 19-0081744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 1364 | 13.5826 | 223_236 | <25mph | <15mph | HFTD - Distribution | 2019-07-27 04:51:00 | 1934 | 16.9934 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KO22 | 6.15 | 2017-02-20T19:15:00Z | 18.41 | 15 | < 25mph |  |  |  | 0 | 0 | No data | KO22 | 6.15 | 2017-02-20T20:55:00Z | 21.85 | 30 | < 25mph
PG&E | 2018-07-29 | 11:39 | 39.0968 | -123.5018 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102177329 | Unknown | 12000 | Conductor | Overhead | Yes | 43310 | 11:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1796 | 2018 | 7 | 29 | 11 | 39 | 18-0064779 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4329 | 14.6452 | 92_301 | <25mph | <15mph | HFTD - Distribution | 2018-07-29 11:39:00 | 1536 | 18.4465 | FALSE | <25mph | E1763 | 2 | 2015-10-08T21:17:00Z | 8.99 | 4 | < 25mph | E1763 | 2 | 2015-10-08T21:17:00Z | 8.99 | 8 | < 25mph | E1763 | 2 | 2015-10-08T22:47:00Z | 10 | 8 | < 25mph | E1763 | 2 | 2015-10-08T22:47:00Z | 10 | 16 | < 25mph
PG&E | 2019-06-03 | 14:31 | 40.6822 | -122.2806 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 101466598 |  | 12000 | Transformer | Overhead | Yes | 43619 | 14:31 | Equipment - Overloaded | Transformer |  |  |  |  | no-match | 2019-161 | 2019 | 6 | 3 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 6.522 | 146_387 | <25mph | <15mph | HFTD - Distribution | 2019-06-03 14:31:00 | 1798 | 12.4331 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C5599 | 6.05 | 2015-11-06T23:31:00Z | 13 | 4 | < 25mph |  |  |  | 0 | 0 | No data | C5599 | 6.05 | 2015-11-06T23:31:00Z | 13 | 6 | < 25mph
PG&E | 2016-07-29 01:31 | 2016-07-29 01:31 | 41.0396 | -123.674 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Hoopa FD | 100962351 |  | 12000 | Conductor | Overhead | Yes | 42580.0632 | 2016-07-29 01:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0891 | 2016 | 7 | 29 | 1 | 31 | 16-0053478 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1418 | 4.1421 | 88_408 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 01:31:00 | 633 | 13.6696 | FALSE | <25mph | HOAC1 | 0.58 | 2016-06-04T07:40:00Z | 4 | 1 | < 25mph | HOAC1 | 0.58 | 2016-06-04T07:40:00Z | 4 | 1 | < 25mph | HOAC1 | 0.58 | 2016-06-04T08:40:00Z | 4.99 | 2 | < 25mph | HOAC1 | 0.58 | 2016-06-04T08:40:00Z | 4.99 | 2 | < 25mph
PG&E | 2017-05-15 16:14 | 16:00 | 37.1766 | -119.8189 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SHAUN FAIRBANKS 559-683-4823 | 101108423 | SIERRA | 21000 | Conductor | Overhead | Yes | 42870.6767 | 16:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1099 | 2017 | 5 | 15 | 16 | 0 | 17-0048096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20007 | 15.7465 | 251_194 | <25mph | <15mph | HFTD - Distribution | 2017-05-15 16:00:00 | 839 | 20.7849 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5766 | 4.44 | 2018-04-29T08:56:00Z | 0 | 13 | < 25mph |  |  |  | 0 | 0 | No data | E5766 | 4.44 | 2018-04-29T09:56:00Z | 2.01 | 25 | < 25mph
PG&E | 2016-06-19 | 2016-06-19 17:19 | 38.4508 | -122.3546 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire--napa fire | 102256859 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 17:19 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0808 | 2016 | 6 | 19 | 17 | 19 | 16-0044337 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 672 | 13.296 | 141_264 | <25mph | <15mph | HFTD - Distribution | 2016-06-19 17:19:00 | 552 | 13.7776 | FALSE | <25mph | PG019 | 3.41 | 2019-06-04T23:30:00Z | 11.18 | 7 | < 25mph | ATLC1 | 5.13 | 2019-06-04T23:29:00Z | 18.01 | 50 | < 25mph | PG019 | 3.41 | 2019-06-05T00:10:00Z | 12.06 | 13 | < 25mph | ATLC1 | 5.13 | 2019-06-05T00:29:00Z | 18.01 | 93 | < 25mph
PG&E | 2018-10-14 | 20:08 | 38.8935 | -120.8497 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103674516 | Unknown | 21000 | Conductor | Overhead | Yes | 43387 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1940 | 2018 | 10 | 14 | 20 | 8 | 18-0090299 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 48095 | 8.663 | 206_288 | <25mph | <15mph | HFTD - Distribution | 2018-10-14 20:08:00 | 1679 | 24.0259 | FALSE | <25mph | C6662 | 3.02 | 2015-07-23T10:23:00Z | 4.99 | 13 | < 25mph | BDMC1 | 7.81 | 2015-07-23T10:36:00Z | 10 | 14 | < 25mph | C6662 | 3.02 | 2015-07-23T10:23:00Z | 4.99 | 25 | < 25mph | BDMC1 | 7.81 | 2015-07-23T10:36:00Z | 10 | 27 | < 25mph
PG&E | 2017-08-26 | 20:53 | 38.7066 | -121.0193 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101382231 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42973 | 20:53 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1350 | 2017 | 8 | 26 | 20 | 53 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.4442 | 199_278 | <25mph | <15mph | HFTD - Distribution | 2017-08-26 20:53:00 | 1088 | 14.1326 | FALSE | <25mph | E4740 | 2.39 | 2018-03-10T10:50:00Z | 2.01 | 34 | < 25mph | FSLC1 | 6.06 | 2018-03-10T10:55:00Z | 8.12 | 58 | < 25mph | E4740 | 2.39 | 2018-03-10T12:20:00Z | 2.01 | 66 | < 25mph | FSLC1 | 6.06 | 2018-03-10T10:55:00Z | 8.12 | 110 | < 25mph
PG&E | 2016-10-08 15:05 | 15:04 | 38.6686 | -120.9091 | Vegetation | RURAL | < 0.25 Acres | Customer | N.A. | 101380856 |  | 0 – 750 | Capacitor Bank | Overhead | Yes | 42651.6284 | 15:04 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1021 | 2016 | 10 | 8 | 15 | 4 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 10.4532 | 203_276 | <25mph | <15mph | HFTD - Distribution | 2016-10-08 15:04:00 | 762 | 14.8776 | FALSE | <25mph | PG181 | 3.7 | 2019-05-07T04:00:00Z | 12.06 | 42 | < 25mph | PG181 | 3.7 | 2019-05-07T04:00:00Z | 12.06 | 134 | < 25mph | PG181 | 3.7 | 2019-05-07T04:00:00Z | 12.06 | 84 | < 25mph | PG181 | 3.7 | 2019-05-07T04:00:00Z | 12.06 | 269 | < 25mph
PG&E | 2019-07-30 | 15:15 | 39.1207 | -121.072 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 152691104 |  | 12000 | Conductor | Overhead | Yes | 43676 | 15:15 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-386 | 2019 | 7 | 30 | 15 | 15 | 19-0082713 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 31302 | 12.2921 | 196_301 | <25mph | <15mph | HFTD - Distribution | 2019-07-30 15:15:00 | 1942 | 13.0851 | FALSE | <25mph | E1789 | 3.69 | 2016-04-13T16:06:00Z | 11.01 | 11 | < 25mph | C5488 | 4.01 | 2016-04-13T15:26:00Z | 13 | 65 | < 25mph | E1789 | 3.69 | 2016-04-13T16:24:00Z | 12.01 | 21 | < 25mph | C5488 | 4.01 | 2016-04-13T15:26:00Z | 13 | 127 | < 25mph
PG&E | 2018-08-05 | 13:56 | 37.4005 | -119.7532 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | JIM FORGA 209-966-3621 | 101017235 | Unknown | 12000 | Conductor | Overhead | Yes | 43317 | 13:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1821 | 2018 | 8 | 5 | 13 | 56 | 18-0066905 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 7325 | 10.7759 | 254_206 | <25mph | <15mph | HFTD - Distribution | 2018-08-05 13:56:00 | 1561 | 13.3386 | FALSE | <25mph | MIAC1 | 1.36 | 2016-03-13T20:59:00Z | 18.01 | 2 | < 25mph | MIAC1 | 1.36 | 2016-03-13T20:59:00Z | 18.01 | 34 | < 25mph | MIAC1 | 1.36 | 2016-03-13T20:59:00Z | 18.01 | 4 | < 25mph | MIAC1 | 1.36 | 2016-03-13T20:59:00Z | 18.01 | 66 | < 25mph
PG&E | 2015-02-23 02:05 | 2015-02-23 02:05 | 39.3027 | -121.0175 | Vegetation | Rural | < 3 meters | Fire Agency | NEVADA CITY FIRE | 100086316 |  | 12000 | Conductor | Overhead | Yes | 42058.0868 | 2015-02-23 02:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0267 | 2015 | 2 | 23 | 2 | 5 | 15-0014910 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 93279 | 24.5459 | 199_311 | <25mph | <15mph | HFTD - Distribution | 2015-02-23 02:05:00 | 14 | 25.6662 | FALSE | 25-40mph | E3651 | 2.92 | 2015-03-22T11:15:00Z | 2.01 | 13 | < 25mph | E5439 | 4.63 | 2015-03-22T11:15:00Z | 8.01 | 63 | < 25mph | E3651 | 2.92 | 2015-03-22T12:25:00Z | 4 | 25 | < 25mph | E5439 | 4.63 | 2015-03-22T12:20:00Z | 8.01 | 122 | < 25mph
PG&E | 2016-07-29 01:31 | 42580.0632 | 41.0396 | -123.674 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Hoopa FD | 100962351 |  | 12000 | Conductor | Overhead | Yes | 42580.0632 | 42580.0632 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0891 | 2016 | 7 | 29 | 1 | 31 | 16-0053478 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1418 | 4.1421 | 88_408 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 01:31:00 | 633 | 13.6696 | FALSE | <25mph | HOAC1 | 0.58 | 2019-07-29T05:40:00Z | 8.01 | 1 | < 25mph | HOAC1 | 0.58 | 2019-07-29T05:40:00Z | 8.01 | 8 | < 25mph | HOAC1 | 0.58 | 2019-07-29T05:40:00Z | 8.01 | 2 | < 25mph | HOAC1 | 0.58 | 2019-07-29T05:40:00Z | 8.01 | 16 | < 25mph
PG&E | 2016-09-26 | 10:40 | 38.0157 | -122.6889 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | marin county fire | 102252082 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42639 | 10:40 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1005 | 2016 | 9 | 26 | 10 | 40 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 4.5159 | 126_240 | <25mph | <15mph | HFTD - Distribution | 2016-09-26 10:40:00 | 747 | 11.2091 | FALSE | <25mph | BBEC1 | 1.12 | 2017-09-27T00:11:00Z | 14.99 | 2 | < 25mph | BBEC1 | 1.12 | 2017-09-27T00:11:00Z | 14.99 | 19 | < 25mph | BBEC1 | 1.12 | 2017-09-27T01:11:00Z | 15.99 | 4 | < 25mph | BBEC1 | 1.12 | 2017-09-27T01:11:00Z | 15.99 | 37 | < 25mph
PG&E | 2018-07-24 | 13:47 | 39.0606 | -123.4456 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102212216 | Unknown | 12000 | Conductor | Overhead | Yes | 43305 | 13:47 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1786 | 2018 | 7 | 24 | 13 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 16.5971 | 95_299 | <25mph | <15mph | HFTD - Distribution | 2018-07-24 13:47:00 | 1526 | 19.7448 | FALSE | <25mph | E1763 | 3.79 | 2015-08-20T23:02:00Z | 11.01 | 4 | < 25mph | BNVC1 | 7.27 | 2015-08-20T22:50:00Z | 15.99 | 7 | < 25mph | E1763 | 3.79 | 2015-08-20T23:02:00Z | 11.01 | 8 | < 25mph | BNVC1 | 7.27 | 2015-08-20T23:50:00Z | 20 | 14 | < 25mph
PG&E | 2019-09-13 | 6:30 | 37.3348 | -121.7716 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 83392110 |  | 21000 | Splice/Clamp/Connector | Overhead | Yes | 43721 | 6:30 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-444 | 2019 | 9 | 13 | 6 | 30 | 19-0098560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 35534 | 3.3882 | 166_202 | <25mph | <15mph | HFTD - Distribution | 2019-09-13 06:30:00 | 2037 | 14.1926 | FALSE | <25mph | UCBO | 3.77 | 2017-02-28T00:20:00Z | 19.39 | 24 | < 25mph | SJS01 | 6.07 | 2017-02-28T00:25:00Z | 23.24 | 101 | < 25mph | UCBO | 3.77 | 2017-02-28T00:20:00Z | 19.39 | 48 | < 25mph | SJS01 | 6.07 | 2017-02-28T00:25:00Z | 23.24 | 203 | < 25mph
PG&E | 2017-08-31 | 6:42 | 35.616 | -120.8577 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Derrick | 101860075 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 6:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1372 | 2017 | 8 | 31 | 6 | 42 | 17-0074386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1620 | 12.088 | 206_107 | <25mph | <15mph | HFTD - Distribution | 2017-08-31 06:42:00 | 1110 | 13.8216 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TABC1 | 4.66 | 2018-07-03T16:07:00Z | 8.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | TABC1 | 4.66 | 2018-07-03T17:07:00Z | 13 | 2 | < 25mph
PG&E | 2016-10-14 04:33 | 4:32 | 40.5228 | -121.6813 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101513661 |  | 12000 | Conductor | Overhead | Yes | 42657.1893 | 4:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1032 | 2016 | 10 | 14 | 4 | 32 | 16-0071897 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 38950 | 28.7152 | 171_378 | 25-40mph | 15-30mph | HFTD - Distribution | 2016-10-14 04:32:00 | 773 | 31.1927 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | VIOC1 | 5.45 | 2015-03-17T13:52:00Z | 3 | 1 | < 25mph |  |  |  | 0 | 0 | No data | VIOC1 | 5.45 | 2015-03-17T13:52:00Z | 3 | 2 | < 25mph
PG&E | 2016-07-28 08:12 | 2016-07-28 08:12 | 37.8207 | -120.1388 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101037043 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0884 | 2016 | 7 | 28 | 8 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 1.7128 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 08:12:00 | 627 | 11.4062 | FALSE | <25mph | SEWC1 | 2.5 | 2017-05-06T12:16:00Z | 4.99 | 4 | < 25mph | SEWC1 | 2.5 | 2017-05-06T12:16:00Z | 4.99 | 4 | < 25mph | SEWC1 | 2.5 | 2017-05-06T12:16:00Z | 4.99 | 9 | < 25mph | SEWC1 | 2.5 | 2017-05-06T12:16:00Z | 4.99 | 9 | < 25mph
PG&E | 2015-12-01 12:03 | 2015-12-01 12:03 | 35.6744 | -120.9932 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal FIRE | 101860660 |  | 21000 | Conductor | Overhead | Yes | 42339.5021 | 2015-12-01 12:03 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0680 | 2015 | 12 | 1 | 12 | 3 | 15-0081983 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 42427 | 6.9865 | 200_111 | <25mph | <15mph | HFTD - Distribution | 2015-12-01 12:03:00 | 424 | 12.3916 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TABC1 | 4.07 | 2019-06-06T22:07:00Z | 10 | 14 | < 25mph |  |  |  | 0 | 0 | No data | TABC1 | 4.07 | 2019-06-06T23:07:00Z | 11.01 | 27 | < 25mph
PG&E | 2019-05-17 | 15:12 | 38.4797 | -123.1486 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 42811111 |  | 12000 | Conductor | Overhead | Yes | 43602 | 15:12 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-200 | 2019 | 5 | 17 | 15 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 19.5511 | 107_266 | <25mph | <15mph | HFTD - Distribution | 2019-05-17 15:12:00 | 1775 | 20.334 | FALSE | <25mph | E8483 | 3.61 | 2017-08-03T16:40:00Z | 3 | 3 | < 25mph | E8483 | 3.61 | 2017-08-03T16:40:00Z | 3 | 8 | < 25mph | E8483 | 3.61 | 2017-08-03T17:10:00Z | 4 | 7 | < 25mph | E8483 | 3.61 | 2017-08-03T17:10:00Z | 4 | 16 | < 25mph
PG&E | 2015-09-04 07:49 | 2015-09-04 07:49 | 40.2318 | -122.3643 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | E/O FRONTIER RD & N/O WAGON WAY |  | 12000 | Conductor | Overhead | Yes | 42251.3257 | 2015-09-04 07:49 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0577 | 2015 | 9 | 4 | 7 | 49 | 15-0059323 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 9563 | 2.343 | 142_362 | <25mph | <15mph | HFTD - Distribution | 2015-09-04 07:49:00 | 321 | 17.9748 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 5.07 | 2016-07-12T09:26:00Z | 3 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 5.07 | 2016-07-12T10:26:00Z | 4 | 8 | < 25mph
PG&E | 2015-09-19 09:51 | 2015-09-19 09:51 | 38.4755 | -122.9069 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FORESTVILLE | 103334444 |  | 12000 | Conductor | Overhead | Yes | 42266.4104 | 2015-09-19 09:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0603 | 2015 | 9 | 19 | 9 | 51 | 15-0062267 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 488 | 1.1332 | 117_266 | <25mph | <15mph | HFTD - Distribution | 2015-09-19 09:51:00 | 348 | 13.7107 | FALSE | <25mph | D4623 | 2.94 | 2015-06-19T16:15:00Z | 4.99 | 6 | < 25mph | E5234 | 7.03 | 2015-06-19T16:18:00Z | 8.01 | 83 | < 25mph | D4623 | 2.94 | 2015-06-19T17:15:00Z | 5.99 | 13 | < 25mph | E5234 | 7.03 | 2015-06-19T17:18:00Z | 8.01 | 165 | < 25mph
PG&E | 2018-07-01 | 0:23 | 40.2697 | -124.2386 | Vegetation | Rural | < 3 meters | Fire Agency | fire chief | 100986962 | Unknown | 12000 | Conductor | Overhead | Yes | 43282 | 0:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1718 | 2018 | 7 | 1 | 0 | 23 | 18-0056043 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 22872 | 20.9894 | 63_366 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 00:23:00 | 1459 | 27.5371 | FALSE | 25-40mph | PTEC1 | 1.7 | 2017-08-03T21:08:00Z | 22.01 | 1 | < 25mph | PTEC1 | 1.7 | 2017-08-03T21:08:00Z | 22.01 | 1 | < 25mph | PTEC1 | 1.7 | 2017-08-03T22:08:00Z | 24 | 2 | < 25mph | PTEC1 | 1.7 | 2017-08-03T22:08:00Z | 24 | 2 | < 25mph
PG&E | 2018-11-16 | 17:02 | 38.7574 | -120.9012 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101409894 | AT&T | 21000 | Conductor | Overhead | Yes | 43420 | 17:02 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1976 | 2018 | 11 | 16 | 17 | 2 | 18-0100490 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 119860 | 5.5125 | 204_281 | <25mph | <15mph | HFTD - Distribution | 2018-11-16 17:02:00 | 1716 | 12.5682 | FALSE | <25mph | D2736 | 3.3 | 2018-05-18T14:01:00Z | 0 | 12 | < 25mph | D7401 | 7.89 | 2018-05-18T13:29:00Z | 4 | 61 | < 25mph | D2736 | 3.3 | 2018-05-18T14:41:00Z | 7 | 24 | < 25mph | D2736 | 3.3 | 2018-05-18T14:41:00Z | 7 | 122 | < 25mph
PG&E | 2018-11-16 | 17:02 | 38.7574 | -120.9012 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101409894 | AT&T | 21000 | Conductor | Overhead | Yes | 43420 | 17:02 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1976 | 2018 | 11 | 16 | 17 | 2 | 18-0100490 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 119860 | 5.5125 | 204_281 | <25mph | <15mph | HFTD - Distribution | 2018-11-16 17:02:00 | 1716 | 12.5682 | FALSE | <25mph | PG106 | 3.02 | 2019-11-08T14:40:00Z | 8.19 | 18 | < 25mph | PG068 | 7.29 | 2019-11-08T15:30:00Z | 8.9 | 122 | < 25mph | PG106 | 3.02 | 2019-11-08T14:40:00Z | 8.19 | 36 | < 25mph | PG073 | 6.48 | 2019-11-08T16:20:00Z | 9.35 | 244 | < 25mph
PG&E | 2017-07-16 11:59 | 11:59 | 36.6669 | -121.7515 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101761892 | None | 21000 | Fuse | Overhead | Yes | 42932.4994 | 11:59 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1259 | 2017 | 7 | 16 | 11 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 22.4318 | 166_166 | <25mph | <15mph | HFTD - Distribution | 2017-07-16 11:59:00 | 998 | 30.0095 | FALSE | 25-40mph | E6666 | 1.85 | 2018-04-24T04:35:00Z | 8.01 | 12 | < 25mph | E6666 | 1.85 | 2018-04-24T04:35:00Z | 8.01 | 20 | < 25mph | E6666 | 1.85 | 2018-04-24T04:35:00Z | 8.01 | 24 | < 25mph | E8875 | 6.38 | 2018-04-24T05:16:00Z | 8.01 | 40 | < 25mph
PG&E | 2018-07-25 | 0:42 | 39.7791 | -121.6173 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100327443 | Unknown | 12000 | Conductor | Overhead | Yes | 43306 | 0:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1788 | 2018 | 7 | 25 | 0 | 42 | 18-0063320 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6742 | 1.3279 | 173_337 | <25mph | <15mph | HFTD - Distribution | 2018-07-25 00:42:00 | 1528 | 11.7229 | FALSE | <25mph | PDEC1 | 1.8 | 2017-05-20T13:00:00Z | 2.01 | 1 | < 25mph | JBGC1 | 7.44 | 2017-05-20T13:13:00Z | 31 | 19 | 25-40mph | PDEC1 | 1.8 | 2017-05-20T14:00:00Z | 2.01 | 4 | < 25mph | JBGC1 | 7.44 | 2017-05-20T14:13:00Z | 31 | 39 | 25-40mph
PG&E | 2015-05-09 21:37 | 2015-05-09 21:37 | 39.2848 | -121.0219 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100004095 | Pacific Bell | 12000 | Fuse | Overhead | Yes | 42133.9007 | 2015-05-09 21:37 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0312 | 2015 | 5 | 9 | 21 | 37 | 15-0033109 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 11 | 9.2188 | 198_310 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 21:37:00 | 58 | 15.4234 | FALSE | <25mph | PG030 | 0.52 | 2019-05-11T02:30:00Z | 5.7 | 43 | < 25mph | AV504 | 4.21 | 2019-05-11T02:00:00Z | 14.99 | 92 | < 25mph | E5439 | 3.42 | 2019-05-11T02:58:00Z | 7 | 86 | < 25mph | AV504 | 4.21 | 2019-05-11T02:00:00Z | 14.99 | 184 | < 25mph
PG&E | 2018-08-12 | 14:46 | 38.6443 | -120.9211 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101410516 | Unknown | 21000 | Conductor | Overhead | Yes | 43324 | 14:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1838 | 2018 | 8 | 12 | 14 | 46 | 18-0069084 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4032 | 11.2318 | 203_274 | <25mph | <15mph | HFTD - Distribution | 2018-08-12 14:46:00 | 1577 | 12.412 | FALSE | <25mph | PG074 | 3.85 | 2019-08-04T00:10:00Z | 14.47 | 35 | < 25mph | C6129 | 5.26 | 2019-08-03T23:29:00Z | 17 | 135 | < 25mph | PG074 | 3.85 | 2019-08-04T00:30:00Z | 15.35 | 70 | < 25mph | C6129 | 5.26 | 2019-08-04T00:44:00Z | 24 | 268 | < 25mph
PG&E | 2019-08-16 | 8:19 | 40.1235 | -123.8758 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Self Extinguished |  | 192221102-2101118022{5563} |  | 12000 | Conductor | Overhead | Yes | 43693 | 8:19 | Vegetation | [5 empty] | Other/Unknown |  | 2019 | 8 | 16 | 8 | 19 | 19-0088744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 2979 | 5.7689 | 78_358 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 08:19:00 | 1983 | 18.468 | FALSE | <25mph | ERCC1 | 2.93 | 2016-11-05T18:28:00Z | 4 | 1 | < 25mph | ERCC1 | 2.93 | 2016-11-05T18:28:00Z | 4 | 5 | < 25mph | ERCC1 | 2.93 | 2016-11-05T19:28:00Z | 4 | 2 | < 25mph | ERCC1 | 2.93 | 2016-11-05T19:28:00Z | 4 | 8 | < 25mph
PG&E | 2016-05-19 01:42 | 2016-05-19 01:42 | 34.6645 | -120.4 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Santa Barbara County FD | 101916587 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42509.0708 | 2016-05-19 01:42 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | no-match | 0738 | 2016 | 5 | 19 | 1 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 6.9523 | 227_55 | <25mph | <15mph | HFTD - Distribution | 2016-05-19 01:42:00 | 482 | 22.8605 | FALSE | <25mph | E7619 | 2.88 | 2015-08-13T13:40:00Z | 8.01 | 6 | < 25mph | E2332 | 6.59 | 2015-08-13T13:35:00Z | 18.01 | 14 | < 25mph | E7619 | 2.88 | 2015-08-13T15:00:00Z | 10 | 12 | < 25mph | E2332 | 6.59 | 2015-08-13T15:27:00Z | 25.99 | 30 | 25-40mph
PG&E | 2015-04-30 00:26 | 2015-04-30 00:26 | 37.2401 | -122.2472 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 1145 VERDE R |  | 12000 | Conductor | Overhead | Yes | 42124.0181 | 2015-04-30 00:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0304 | 2015 | 4 | 30 | 0 | 26 | 15-0030607 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1256 | 5.7566 | 145_197 | <25mph | <15mph | HFTD - Distribution | 2015-04-30 00:26:00 | 50 | 15.5915 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.52 | 2016-05-27T11:07:00Z | 4.99 | 5 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.52 | 2016-05-27T11:07:00Z | 4.99 | 10 | < 25mph
PG&E | 2019-05-29 | 16:54 | 37.0371 | -119.5209 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 100680674 |  | 12000 | Pole | Overhead | Yes | 43614 | 16:54 | Vegetation |  | Veg. contact | Pole |  |  | Dead | 2019-202 | 2019 | 5 | 29 | 16 | 54 | 19-0059237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 6780 | 6.6167 | 265_186 | <25mph | <15mph | HFTD - Distribution | 2019-05-29 16:54:00 | 1787 | 9.3593 | FALSE | <25mph | PRHC1 | 3 | 2018-08-10T17:27:00Z | 5.99 | 1 | < 25mph | PRHC1 | 3 | 2018-08-10T17:27:00Z | 5.99 | 1 | < 25mph | PRHC1 | 3 | 2018-08-10T18:27:00Z | 8.99 | 2 | < 25mph | PRHC1 | 3 | 2018-08-10T18:27:00Z | 8.99 | 2 | < 25mph
PG&E | 2018-02-07 | 9:16 | 38.0369 | -120.2096 | Vegetation | Rural | < 3 meters | Fire Agency | Jason Podesta 209-586-3362 | 101038120 | AT&T | 17000 | Conductor | Overhead | Yes | 43138 | 9:16 | Contact From Object | N.A. | Other | Electric Facility | Human Error | third-party caused | Other/Unknown | 1559 | 2018 | 2 | 7 | 9 | 16 | 18-0012146 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 78738 | 9.6764 | 234_241 | <25mph | <15mph | HFTD - Distribution | 2018-02-07 09:16:00 | 1301 | 13.44 | FALSE | <25mph | MOUC1 | 2.73 | 2018-03-04T12:02:00Z | 0 | 1 | < 25mph | MOUC1 | 2.73 | 2018-03-04T12:02:00Z | 0 | 1 | < 25mph | MOUC1 | 2.73 | 2018-03-04T13:02:00Z | 0 | 2 | < 25mph | MOUC1 | 2.73 | 2018-03-04T13:02:00Z | 0 | 2 | < 25mph
PG&E | 2017-09-06 | 20:08 | 37.2925 | -122.294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100256917 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1400 | 2017 | 9 | 6 | 20 | 8 | 17-0076502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4914 | 6.7999 | 143_200 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 20:08:00 | 1138 | 13.6021 | FALSE | <25mph | LAHC1 | 2.3 | 2019-06-08T11:07:00Z | 22.01 | 5 | < 25mph | PG149 | 7.67 | 2019-06-08T10:30:00Z | 31.79 | 36 | 25-40mph | LAHC1 | 2.3 | 2019-06-08T11:07:00Z | 22.01 | 10 | < 25mph | PG149 | 7.67 | 2019-06-08T12:10:00Z | 32.01 | 72 | 25-40mph
PG&E | 2016-07-21 21:45 | 2016-07-21 21:45 | 40.8566 | -122.3387 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101455670 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0870 | 2016 | 7 | 21 | 21 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.7351 | 143_397 | <25mph | <15mph | HFTD - Distribution | 2016-07-21 21:45:00 | 613 | 15.1303 | FALSE | <25mph | CTANT | 1.58 | 2019-04-08T08:30:00Z | 4.97 | 4 | < 25mph | PG138 | 6.77 | 2019-04-08T08:00:00Z | 19.06 | 15 | < 25mph | CTANT | 1.58 | 2019-04-08T08:30:00Z | 4.97 | 8 | < 25mph | PG138 | 6.77 | 2019-04-08T08:00:00Z | 19.06 | 30 | < 25mph
PG&E | 2019-05-30 | 8:18 | 35.7005 | -120.8104 | Vehicle | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 101871463 |  | 12000 | Pole | Overhead | Yes | 43615 | 8:18 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-274 | 2019 | 5 | 30 | 8 | 18 | 19-0059906 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 171603 | 10.8019 | 208_112 | <25mph | <15mph | HFTD - Distribution | 2019-05-30 08:18:00 | 1791 | 17.2262 | FALSE | <25mph | PG537 | 0.11 | 2019-09-07T10:40:00Z | 10.22 | 6 | < 25mph | PG537 | 0.11 | 2019-09-07T10:40:00Z | 10.22 | 17 | < 25mph | PG537 | 0.11 | 2019-09-07T11:10:00Z | 10.89 | 12 | < 25mph | PG537 | 0.11 | 2019-09-07T11:10:00Z | 10.89 | 34 | < 25mph
PG&E | 2018-06-05 | 10:13 | 40.6183 | -122.3173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JASON COLLINS 530-225-4628 | 101467801 | None | 12000 | Conductor | Overhead | Yes | 43256 | 10:13 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1631 | 2018 | 6 | 5 | 10 | 13 | 18-0047539 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 277 | 7.1547 | 144_384 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 10:13:00 | 1373 | 12.6046 | FALSE | <25mph | C5599 | 1.27 | 2017-10-26T05:46:00Z | 11.01 | 4 | < 25mph | C5599 | 1.27 | 2017-10-26T05:46:00Z | 11.01 | 5 | < 25mph | C5599 | 1.27 | 2017-10-26T06:01:00Z | 14 | 8 | < 25mph | C5599 | 1.27 | 2017-10-26T06:01:00Z | 14 | 10 | < 25mph
PG&E | 2016-09-15 | 15:56 | 37.1102 | -121.9509 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100520198 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42628 | 15:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0982 | 2016 | 9 | 15 | 15 | 56 | 16-0065001 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 28900 | 4.729 | 158_190 | <25mph | <15mph | HFTD - Distribution | 2016-09-15 15:56:00 | 724 | 12.2674 | FALSE | <25mph | E6085 | 3.16 | 2015-05-14T06:07:00Z | 4 | 66 | < 25mph | LSGC1 | 6.49 | 2015-05-14T06:32:00Z | 10 | 107 | < 25mph | E6085 | 3.16 | 2015-05-14T06:07:00Z | 4 | 130 | < 25mph | LSGC1 | 6.49 | 2015-05-14T06:32:00Z | 10 | 209 | < 25mph
PG&E | 2017-06-30 23:55 | 23:54 | 38.5794 | -122.8835 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 101958804 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42916.9965 | 23:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1211 | 2017 | 6 | 30 | 23 | 54 | 17-0059922 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2025 | 14.1552 | 118_272 | <25mph | <15mph | HFTD - Distribution | 2017-06-30 23:54:00 | 950 | 23.4555 | FALSE | <25mph | AU487 | 3.93 | 2015-07-09T06:35:00Z | 4 | 16 | < 25mph | E6724 | 5.41 | 2015-07-09T06:30:00Z | 5.99 | 44 | < 25mph | AU487 | 3.93 | 2015-07-09T07:30:00Z | 4 | 31 | < 25mph | E6724 | 5.41 | 2015-07-09T06:30:00Z | 5.99 | 86 | < 25mph
PG&E | 2016-09-20 | 8:25 | 40.0044 | -123.7871 | Vegetation | RURAL | < 3 meters | Self Extinguished | N.A. | 100992643 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42633 | 8:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0990 | 2016 | 9 | 20 | 8 | 25 | 16-0065910 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 798 | 11.2567 | 82_351 | <25mph | <15mph | HFTD - Distribution | 2016-09-20 08:25:00 | 732 | 20.9022 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AV037 | 4.73 | 2018-12-11T10:23:00Z | 5.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | AV037 | 4.73 | 2018-12-11T10:23:00Z | 5.99 | 7 | < 25mph
PG&E | 2018-02-07 | 5:44 | 40.6543 | -122.5198 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 103922730 | Unknown | 12000 | Conductor | Overhead | Yes | 43138 | 5:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1558 | 2018 | 2 | 7 | 5 | 44 | 18-0012073 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 9610 | 17.8768 | 136_386 | <25mph | <15mph | HFTD - Distribution | 2018-02-07 05:44:00 | 1300 | 25.5948 | FALSE | 25-40mph | OBRC1 | 3.05 | 2016-09-28T00:00:00Z | 8.99 | 4 | < 25mph | MMOC1 | 5.95 | 2016-09-28T00:00:00Z | 13 | 6 | < 25mph | OBRC1 | 3.05 | 2016-09-28T01:00:00Z | 8.99 | 8 | < 25mph | MMOC1 | 5.95 | 2016-09-28T00:00:00Z | 13 | 12 | < 25mph
PG&E | 2016-09-28 | 14:00 | 35.2145 | -118.5625 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire |  |  | 0 – 750 | Conductor | Overhead | Yes | 42641 | 14:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1008 | 2016 | 9 | 28 | 14 | 0 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.8467 | 310_87 | <25mph | <15mph | HFTD - Distribution | 2016-09-28 14:00:00 | 750 | 26.957 | FALSE | 25-40mph | HFLC1 | 3.31 | 2017-09-28T22:13:00Z | 20 | 4 | < 25mph | HFLC1 | 3.31 | 2017-09-28T22:13:00Z | 20 | 31 | < 25mph | HFLC1 | 3.31 | 2017-09-28T23:13:00Z | 20 | 6 | < 25mph | HFLC1 | 3.31 | 2017-09-28T23:13:00Z | 20 | 64 | < 25mph
PG&E | 2019-07-18 | 19:57 | 37.081 | -119.4865 |  | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | No |  |  | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-09 | 2019 | 7 | 18 | 19 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.8761 | 266_189 | <25mph | <15mph | HFTD - Distribution | 2019-07-18 19:57:00 | 1914 | 14.7588 | FALSE | <25mph | PG218 | 2.5 | 2019-10-06T04:00:00Z | 5.91 | 42 | < 25mph | SE370 | 7.06 | 2019-10-06T03:50:00Z | 8.25 | 110 | < 25mph | PG389 | 1.62 | 2019-10-06T05:40:00Z | 8.61 | 84 | < 25mph | PG389 | 1.62 | 2019-10-06T05:40:00Z | 8.61 | 220 | < 25mph
PG&E | 2018-06-22 | 17:44 | 37.2485 | -119.5625 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Madera County | 101117749 | None | 0 – 750 | Conductor | Overhead | Yes | 43273 | 17:44 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1686 | 2018 | 6 | 22 | 17 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 10.123 | 263_198 | <25mph | <15mph | HFTD - Distribution | 2018-06-22 17:44:00 | 1428 | 12.3323 | FALSE | <25mph | NFRC1 | 3.29 | 2019-10-03T04:55:00Z | 5.99 | 1 | < 25mph | PG467 | 7.23 | 2019-10-03T05:30:00Z | 10.89 | 58 | < 25mph | C6459 | 2.53 | 2019-10-03T05:40:00Z | 7 | 3 | < 25mph | PG467 | 7.23 | 2019-10-03T05:40:00Z | 11.77 | 118 | < 25mph
PG&E | 2018-10-16 | 16:30 | 38.7754 | -122.8976 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MARK GRADEK (707) 889-4303 | 101962692 | AT&T | 12000 | Conductor | Overhead | Yes | 43389 | 16:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1943 | 2018 | 10 | 16 | 16 | 30 | 18-0091127 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 744 | 10.3513 | 118_282 | <25mph | <15mph | HFTD - Distribution | 2018-10-16 16:30:00 | 1682 | 19.9126 | FALSE | <25mph |  |  |  | 0 | 0 | No data | HWKC1 | 4.29 | 2015-05-18T00:56:00Z | 18.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | HWKC1 | 4.29 | 2015-05-18T00:56:00Z | 18.01 | 2 | < 25mph
PG&E | 2017-12-07 12:26 | 12:25 | 34.7115 | -120.1772 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 015/220 | Unknown | 115000 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1534 | 2017 | 12 | 7 | 12 | 25 | 17-0097211 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 4.373 | 237_58 | <25mph | <15mph | HFTD - Transmission | 2017-12-07 12:25:00 | 1276 | 13.3077 | FALSE | <25mph | TT480 | 2.15 | 2019-11-07T08:20:00Z | 10 | 1 | < 25mph | TT480 | 2.15 | 2019-11-07T08:20:00Z | 10 | 39 | < 25mph | TT480 | 2.15 | 2019-11-07T08:20:00Z | 10 | 2 | < 25mph | TT480 | 2.15 | 2019-11-07T08:20:00Z | 10 | 78 | < 25mph
PG&E | 2019-07-17 | 7:49 | 34.5066 | -120.2247 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Santa Barbara County FD | 4Bx0717190747 |  | 12000 | Other | Overhead | Yes | 43663 | 7:49 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-425 | 2019 | 7 | 17 | 7 | 49 | 19-0078239 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 19608 | 17.3045 | 235_46 | <25mph | <15mph | HFTD - Distribution | 2019-07-17 07:49:00 | 1908 | 28.4942 | FALSE | 25-40mph | UP481 | 2.43 | 2015-08-24T04:00:00Z | 28.99 | 11 | 25-40mph | UP481 | 2.43 | 2015-08-24T04:00:00Z | 28.99 | 11 | 25-40mph | UP481 | 2.43 | 2015-08-24T05:00:00Z | 30.04 | 21 | 25-40mph | UP481 | 2.43 | 2015-08-24T05:00:00Z | 30.04 | 21 | 25-40mph
PG&E | 2018-07-14 | 11:34 | 38.4026 | -122.5489 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103141862 | Verizon | 12000 | Conductor | Overhead | Yes | 43295 | 11:34 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1745 | 2018 | 7 | 14 | 11 | 34 | 18-0059821 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 6426 | 11.4725 | 133_262 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 11:34:00 | 1485 | 15.7933 | FALSE | <25mph | E9543 | 1.57 | 2016-09-28T11:03:00Z | 3 | 4 | < 25mph | E9543 | 1.57 | 2016-09-28T11:03:00Z | 3 | 14 | < 25mph | E9543 | 1.57 | 2016-09-28T11:03:00Z | 3 | 8 | < 25mph | E9543 | 1.57 | 2016-09-28T11:03:00Z | 3 | 28 | < 25mph
PG&E | 2017-04-28 16:21 | 15:49 | 38.7679 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chris paper fire investigator, 530/677-1868. incident #caaeuo11821 | 101409833 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42853.6815 | 15:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1077 | 2017 | 4 | 28 | 15 | 49 | 17-0043771 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 82614 | 19.7837 | 201_281 | <25mph | <15mph | HFTD - Distribution | 2017-04-28 15:49:00 | 817 | 25.4223 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | C6129 | 7.91 | 2018-03-03T08:59:00Z | 12.01 | 58 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 5.08 | 2018-03-03T09:56:00Z | 13 | 115 | < 25mph
PG&E | 2015-10-30 17:13 | 2015-10-30 17:13 | 38.3166 | -120.7226 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 7600 HWY 49, Jackson | None | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0662 | 2015 | 10 | 30 | 17 | 13 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 8.0122 | 211_256 | <25mph | <15mph | HFTD - Distribution | 2015-10-30 17:13:00 | 406 | 12.822 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KJAQ | 5.68 | 2015-03-28T20:15:00Z | 16.11 | 2 | < 25mph |  |  |  | 0 | 0 | No data | KJAQ | 5.68 | 2015-03-28T20:40:00Z | 16.11 | 6 | < 25mph
PG&E | 2018-08-26 | 15:29 | 39.3599 | -121.1209 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100107472 | Unknown | 12000 | Conductor | Overhead | Yes | 43338 | 15:29 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1860 | 2018 | 8 | 26 | 15 | 29 | 18-0073601 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 36162 | 13.8191 | 194_314 | <25mph | <15mph | HFTD - Distribution | 2018-08-26 15:29:00 | 1599 | 13.8191 | FALSE | <25mph | RRRC1 | 3.9 | 2019-11-21T13:13:00Z | 4 | 7 | < 25mph | PG348 | 7.58 | 2019-11-21T13:10:00Z | 4.9 | 61 | < 25mph | RRRC1 | 3.9 | 2019-11-21T14:13:00Z | 4 | 14 | < 25mph | PG348 | 7.58 | 2019-11-21T14:40:00Z | 5.1 | 122 | < 25mph
PG&E | 2017-10-08 | 22:19 | 39.7371 | -121.6464 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 103319605 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43016 | 22:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1468 | 2017 | 10 | 8 | 22 | 19 | 17-0085504 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 42839 | 9.4272 | 172_335 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 22:19:00 | 1208 | 31.7535 | FALSE | 25-40mph | PDEC1 | 1.62 | 2018-09-02T02:00:00Z | 4 | 1 | < 25mph | PDEC1 | 1.62 | 2018-09-02T02:00:00Z | 4 | 7 | < 25mph | PDEC1 | 1.62 | 2018-09-02T03:00:00Z | 4 | 2 | < 25mph | PDEC1 | 1.62 | 2018-09-02T03:00:00Z | 4 | 14 | < 25mph
PG&E | 2016-09-28 | 14:00 | 35.2145 | -118.5625 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire |  |  | 0 – 750 | Conductor | Overhead | Yes | 42641 | 14:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1008 | 2016 | 9 | 28 | 14 | 0 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.8467 | 310_87 | <25mph | <15mph | HFTD - Distribution | 2016-09-28 14:00:00 | 750 | 26.957 | FALSE | 25-40mph | HFLC1 | 3.31 | 2015-09-29T21:13:00Z | 17 | 10 | < 25mph | C1020 | 5.93 | 2015-09-29T21:53:00Z | 20 | 37 | < 25mph | HFLC1 | 3.31 | 2015-09-29T22:13:00Z | 20 | 17 | < 25mph | C1020 | 5.93 | 2015-09-29T22:17:00Z | 21 | 71 | < 25mph
PG&E | 2016-07-29 01:31 | 2016-07-29 01:31 | 41.0396 | -123.674 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Hoopa FD | 100962351 |  | 12000 | Conductor | Overhead | Yes | 42580.0632 | 2016-07-29 01:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0891 | 2016 | 7 | 29 | 1 | 31 | 16-0053478 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1418 | 4.1421 | 88_408 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 01:31:00 | 633 | 13.6696 | FALSE | <25mph | HOAC1 | 0.58 | 2019-06-13T15:40:00Z | 4 | 1 | < 25mph | BIIC1 | 4.46 | 2019-06-13T15:40:00Z | 5.99 | 8 | < 25mph | HOAC1 | 0.58 | 2019-06-13T16:40:00Z | 4.99 | 2 | < 25mph | BIIC1 | 4.46 | 2019-06-13T16:40:00Z | 8.01 | 16 | < 25mph
PG&E | 2015-09-25 17:28 | 2015-09-25 17:28 | 38.7169 | -120.7693 | Vegetation | Rural | < 0.25 Acres | Fire Agency | el dorado F D | 101405928 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42272.7278 | 2015-09-25 17:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0616 | 2015 | 9 | 25 | 17 | 28 | 15-0063666 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 111180 | 8.3925 | 209_279 | <25mph | <15mph | HFTD - Distribution | 2015-09-25 17:28:00 | 361 | 11.4196 | FALSE | <25mph | E6490 | 3.78 | 2016-10-09T18:24:00Z | 4.99 | 33 | < 25mph | C6129 | 4.54 | 2016-10-09T18:09:00Z | 8.01 | 58 | < 25mph | E5691 | 2.8 | 2016-10-09T19:16:00Z | 8.99 | 63 | < 25mph | E5691 | 2.8 | 2016-10-09T19:16:00Z | 8.99 | 112 | < 25mph
PG&E | 2017-10-10 | 13:36 | 38.931 | -123.3023 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 102214553 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43018 | 13:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1481 | 2017 | 10 | 10 | 13 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.7263 | 101_291 | <25mph | <15mph | HFTD - Distribution | 2017-10-10 13:36:00 | 1224 | 17.0479 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BNVC1 | 4.62 | 2016-01-25T03:50:00Z | 5.99 | 9 | < 25mph |  |  |  | 0 | 0 | No data | BNVC1 | 4.62 | 2016-01-25T04:50:00Z | 8.99 | 17 | < 25mph
PG&E | 2017-08-29 | 12:49 | 37.4507 | -119.6454 | Vegetation | Rural | > 5000 Acres | Fire Agency | USFS | 101017368 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-29 | 12:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1366 | 2017 | 8 | 29 | 12 | 49 | 17-0073823 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | 3rd Party | 3rd Party - Unknown | 5894785 | 7.4398 | 259_209 | <25mph | <15mph | HFTD - Distribution | 2017-08-29 12:49:00 | 1104 | 13.5545 | FALSE | <25mph | TR172 | 0.9 | 2017-08-26T23:45:00Z | 14 | 5 | < 25mph | MIAC1 | 5.9 | 2017-08-26T23:59:00Z | 14 | 27 | < 25mph | TR172 | 0.9 | 2017-08-27T00:45:00Z | 17 | 10 | < 25mph | TR172 | 0.9 | 2017-08-27T00:45:00Z | 17 | 57 | < 25mph
PG&E | 2016-10-13 23:23 | 23:14 | 40.4901 | -122.3729 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | SHASTA COUNTY FIRE | 101502366 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42656.9745 | 23:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1029 | 2016 | 10 | 13 | 23 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 30.3025 | 142_377 | 25-40mph | 30-45mph | HFTD - Distribution | 2016-10-13 23:14:00 | 770 | 30.3025 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | RRAC1 | 4.59 | 2019-07-02T00:24:00Z | 18.01 | 32 | < 25mph |  |  |  | 0 | 0 | No data | KRDD | 4.3 | 2019-07-02T00:53:00Z | 18.41 | 64 | < 25mph
PG&E | 2016-08-01 | 2016-08-01 18:29 | 38.6956 | -120.9283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412720 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0898 | 2016 | 8 | 1 | 18 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2359 | 203_277 | <25mph | <15mph | HFTD - Distribution | 2016-08-01 18:29:00 | 641 | 12.0255 | FALSE | <25mph | D2736 | 1.29 | 2016-08-12T04:55:00Z | 0 | 12 | < 25mph | BENC1 | 7.25 | 2016-08-12T04:59:00Z | 4.99 | 68 | < 25mph | D2736 | 1.29 | 2016-08-12T05:55:00Z | 0 | 24 | < 25mph | BENC1 | 7.25 | 2016-08-12T05:59:00Z | 5.99 | 128 | < 25mph
PG&E | 2015-07-16 19:11 | 2015-07-16 19:11 | 37.1989 | -119.7712 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 20334 ROAD 400 |  | 12000 | Conductor | Overhead | Yes | 42201.7993 | 2015-07-16 19:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0465 | 2015 | 7 | 16 | 19 | 11 | 15-0048064 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 8.6422 | 254_195 | <25mph | <15mph | HFTD - Distribution | 2015-07-16 19:11:00 | 210 | 13.1745 | FALSE | <25mph | E5766 | 3.27 | 2015-11-05T21:17:00Z | 8.01 | 18 | < 25mph | E5766 | 3.27 | 2015-11-05T21:17:00Z | 8.01 | 18 | < 25mph | E5766 | 3.27 | 2015-11-05T21:17:00Z | 8.01 | 36 | < 25mph | E5766 | 3.27 | 2015-11-05T21:17:00Z | 8.01 | 36 | < 25mph
PG&E | 2019-08-12 | 20:06 | 39.0952 | -123.4937 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 102177212 |  | 12000 | Conductor | Overhead | Yes | 43689 | 20:06 | Vegetation |  | Veg. contact |  |  |  | Fell into (No defect) | 2019-400 | 2019 | 8 | 12 | 20 | 6 | 19-0087090 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2508 | 13.5331 | 93_301 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 20:06:00 | 1970 | 19.4805 | FALSE | <25mph | E1763 | 1.72 | 2018-10-15T08:16:00Z | 0 | 4 | < 25mph | E1763 | 1.72 | 2018-10-15T08:16:00Z | 0 | 4 | < 25mph | E1763 | 1.72 | 2018-10-15T09:30:00Z | 0 | 9 | < 25mph | E1763 | 1.72 | 2018-10-15T09:30:00Z | 0 | 9 | < 25mph
PG&E | 2015-08-22 20:38 | 2015-08-22 20:38 | 38.7748 | -120.8564 | Vegetation | Rural | < 3 meters | Self Extinguished |  | at base of co pole 21721 - 720 Woodridge Rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42238.8597 | 2015-08-22 20:38 | Contact From Object | N.A. | Vegetation | Communication Facility | Unknown | tree hit phone lines | Fell into (Moderate-Severe defect) | 0549 | 2015 | 8 | 22 | 20 | 38 | 15-0056766 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26513 | 9.2929 | 206_282 | <25mph | <15mph | HFTD - Distribution | 2015-08-22 20:38:00 | 293 | 10.7008 | FALSE | <25mph | E5691 | 3.87 | 2018-03-21T19:16:00Z | 12.01 | 12 | < 25mph | KPVF | 6.56 | 2018-03-21T19:15:00Z | 23.02 | 69 | < 25mph | E5691 | 3.87 | 2018-03-21T20:16:00Z | 14.99 | 24 | < 25mph | KPVF | 6.56 | 2018-03-21T19:35:00Z | 28.77 | 139 | 25-40mph
PG&E | 2019-09-12 | 14:25 | 37.3144 | -122.1865 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 024131103 |  | 12000 | Conductor | Overhead | Yes | 43720 | 14:25 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-217 | 2019 | 9 | 12 | 14 | 25 | 19-0098386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 89097 | 5.2412 | 147_201 | <25mph | <15mph | HFTD - Distribution | 2019-09-12 14:25:00 | 2036 | 15.0249 | FALSE | <25mph | LAHC1 | 3.83 | 2016-06-10T17:07:00Z | 11.01 | 21 | < 25mph | E7138 | 7.92 | 2016-06-10T17:17:00Z | 12.01 | 92 | < 25mph | LAHC1 | 3.83 | 2016-06-10T17:07:00Z | 11.01 | 41 | < 25mph | E7138 | 7.92 | 2016-06-10T17:48:00Z | 14.99 | 178 | < 25mph
PG&E | 2018-07-01 | 0:45 | 38.8842 | -120.847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Brian Mackwood (530)708-2711 | 100109003 | None | 21000 | Conductor | Overhead | Yes | 43282 | 0:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1719 | 2018 | 7 | 1 | 0 | 45 | 18-0056045 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5760 | 9.2878 | 206_288 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 00:45:00 | 1460 | 12.1055 | FALSE | <25mph | PG180 | 3.22 | 2019-12-11T04:10:00Z | 9.06 | 25 | < 25mph | BDMC1 | 7.75 | 2019-12-11T04:36:00Z | 18.01 | 44 | < 25mph | PG180 | 3.22 | 2019-12-11T04:10:00Z | 9.06 | 49 | < 25mph | BDMC1 | 7.75 | 2019-12-11T04:36:00Z | 18.01 | 87 | < 25mph
PG&E | 2019-09-01 | 16:50 | 35.908 | -121.011 |  | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 103477437 |  | 12000 | Pole | Overhead | Yes | 43709 | 16:50 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-17 | 2019 | 9 | 1 | 16 | 50 | 19-0094475 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45432 | 5.8888 | 199_124 | <25mph | <15mph | HFTD - Distribution | 2019-09-01 16:50:00 | 2009 | 25.5842 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2015-09-18 17:05 | 2015-09-18 17:05 | 37.8992 | -120.4551 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101019893 |  | 17000 | Conductor | Overhead | Yes | 42265.7118 | 2015-09-18 17:05 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0602 | 2015 | 9 | 18 | 17 | 5 | 15-0062207 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 35222 | 9.055 | 223_234 | <25mph | <15mph | HFTD - Distribution | 2015-09-18 17:05:00 | 347 | 11.0018 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.2 | 2018-08-09T06:03:00Z | 3 | 1 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.2 | 2018-08-09T07:03:00Z | 4.99 | 2 | < 25mph
PG&E | 2017-06-15 08:08 | 7:39 | 39.2276 | -121.2348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE CHIEF | 103676075 | Unknown | 21000 | Conductor | Overhead | Yes | 42901.3391 | 7:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1147 | 2017 | 6 | 15 | 7 | 39 | 17-0055387 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 740 | 10.5195 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 07:39:00 | 886 | 12.4202 | FALSE | <25mph | E2572 | 2.6 | 2016-04-03T00:58:00Z | 4 | 12 | < 25mph | E1789 | 7.9 | 2016-04-03T00:48:00Z | 5.99 | 28 | < 25mph | E2572 | 2.6 | 2016-04-03T00:58:00Z | 4 | 23 | < 25mph | E1789 | 7.9 | 2016-04-03T00:48:00Z | 5.99 | 55 | < 25mph
PG&E | 2016-06-10 15:51 | 2016-06-10 15:51 | 39.9934 | -123.7883 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100992291 |  | 12000 | Conductor | Overhead | Yes | 42531.6604 | 2016-06-10 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0788 | 2016 | 6 | 10 | 15 | 51 | 16-0042501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | N.A. | 22.4156 | 82_351 | <25mph | <15mph | HFTD - Distribution | 2016-06-10 15:51:00 | 531 | 22.7996 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AV037 | 5.5 | 2016-05-23T15:23:00Z | 3 | 4 | < 25mph |  |  |  | 0 | 0 | No data | AV037 | 5.5 | 2016-05-23T16:53:00Z | 4 | 7 | < 25mph
PG&E | 2018-06-09 | 0:46 | 35.0745 | -120.5167 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101927520 | Unknown | 12000 | Conductor | Overhead | Yes | 43260 | 0:46 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1645 | 2018 | 6 | 9 | 0 | 46 | 18-0049171 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 16825 | 5.84 | 221_78 | <25mph | <15mph | HFTD - Distribution | 2018-06-09 00:46:00 | 1387 | 22.9582 | FALSE | <25mph | F0412 | 2.71 | 2017-03-06T19:35:00Z | 10 | 15 | < 25mph | AU609 | 7.04 | 2017-03-06T19:45:00Z | 15.99 | 23 | < 25mph | F0412 | 2.71 | 2017-03-06T20:45:00Z | 13 | 32 | < 25mph | AU609 | 7.04 | 2017-03-06T19:45:00Z | 15.99 | 48 | < 25mph
PG&E | 2015-06-04 13:17 | 2015-06-04 13:17 | 39.2694 | -123.7841 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42159.5535 | 2015-06-04 13:17 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0344 | 2015 | 6 | 4 | 13 | 17 | 15-0038501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20525 | 22.1312 | 81_311 | <25mph | <15mph | HFTD - Distribution | 2015-06-04 13:17:00 | 90 | 22.6218 | FALSE | <25mph | E6025 | 1.61 | 2016-12-26T19:45:00Z | 5.99 | 4 | < 25mph | E6025 | 1.61 | 2016-12-26T19:45:00Z | 5.99 | 4 | < 25mph | E6025 | 1.61 | 2016-12-26T20:00:00Z | 5.99 | 8 | < 25mph | E6025 | 1.61 | 2016-12-26T20:00:00Z | 5.99 | 8 | < 25mph
PG&E | 2019-09-10 | 7:13 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 82841102 |  | 12000 | Conductor | Overhead | Yes | 43718 | 7:13 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-369 | 2019 | 9 | 10 | 7 | 13 | 19-0097264 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 23500 | 14.6244 | 147_193 | <25mph | <15mph | HFTD - Distribution | 2019-09-10 07:13:00 | 2029 | 17.7422 | FALSE | <25mph | PG055 | 1.57 | 2018-07-01T11:00:00Z | 4.16 | 7 | < 25mph | E6800 | 5.35 | 2018-07-01T11:00:00Z | 8.01 | 41 | < 25mph | PG055 | 1.57 | 2018-07-01T12:00:00Z | 8.12 | 14 | < 25mph | PG055 | 1.57 | 2018-07-01T12:00:00Z | 8.12 | 84 | < 25mph
PG&E | 2015-10-16 09:43 | 2015-10-16 09:43 | 39.187 | -123.2015 | Vegetation | Rural | < 3 meters | Unknown |  | 102196855 |  | 12000 | Conductor | Overhead | Yes | 42293.4049 | 2015-10-16 09:43 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0653 | 2015 | 10 | 16 | 9 | 43 | 15-0070948 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 65228 | 2.2696 | 105_305 | <25mph | <15mph | HFTD - Distribution | 2015-10-16 09:43:00 | 397 | 16.8813 | FALSE | <25mph | E7513 | 1.34 | 2017-02-27T22:28:00Z | 7 | 12 | < 25mph | E7513 | 1.34 | 2017-02-27T22:28:00Z | 7 | 12 | < 25mph | E7513 | 1.34 | 2017-02-27T23:23:00Z | 12.01 | 24 | < 25mph | E7513 | 1.34 | 2017-02-27T23:23:00Z | 12.01 | 24 | < 25mph
PG&E | 2017-06-15 15:04 | 15:01 | 39.3913 | -123.3054 | Vegetation | Rural | < 0.25 Acres | Fire Agency | STEPHEN | 103838176 | YES | 12000 | Conductor | Overhead | Yes | 42901.6279 | 15:01 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1148 | 2017 | 6 | 15 | 15 | 1 | 17-0055557 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 180469 | 19.6681 | 101_317 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 15:01:00 | 887 | 19.7788 | FALSE | <25mph | PG120 | 3.9 | 2019-02-21T21:10:00Z | 29.8 | 26 | 25-40mph | PG089 | 7.4 | 2019-02-21T22:00:00Z | 35.52 | 50 | 25-40mph | PG120 | 3.9 | 2019-02-21T21:10:00Z | 29.8 | 55 | 25-40mph | PG089 | 7.4 | 2019-02-21T22:00:00Z | 35.52 | 103 | 25-40mph
PG&E | 2015-08-08 07:42 | 42224.3208 | 39.2007 | -121.2137 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100076217 | Pacific Bell | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0519 | 2015 | 8 | 8 | 7 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 14.1661 | 190_305 | <25mph | <15mph | HFTD - Distribution | 2015-08-08 07:42:00 | 263 | 14.9803 | FALSE | <25mph | PG448 | 4 | 2019-07-19T20:50:00Z | 12.28 | 12 | < 25mph | PG348 | 4.61 | 2019-07-19T20:50:00Z | 12.48 | 52 | < 25mph | PG448 | 4 | 2019-07-19T20:50:00Z | 12.28 | 24 | < 25mph | PG348 | 4.61 | 2019-07-19T20:50:00Z | 12.48 | 99 | < 25mph
PG&E | 2017-06-13 | 14:30 | 37.8526 | -122.1853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Tower 005/035c | Unknown | 115000 | Conductor | Overhead | Yes | 42899 | 14:30 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1143 | 2017 | 6 | 13 | 14 | 30 | INT-09744 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | Balloons | 0 | 10.6352 | 148_231 | <25mph | <15mph | HFTD - Transmission | 2017-06-13 14:30:00 | 882 | 14.5193 | FALSE | <25mph | E5555 | 2.22 | 2015-03-29T21:55:00Z | 13 | 53 | < 25mph | LTRC1 | 6.59 | 2015-03-29T22:28:00Z | 14.99 | 123 | < 25mph | E5555 | 2.22 | 2015-03-29T21:55:00Z | 13 | 103 | < 25mph | LTRC1 | 6.59 | 2015-03-29T23:28:00Z | 14.99 | 244 | < 25mph
PG&E | 2019-05-08 | 10:23 | 39.3851 | -122.557 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | Colusa FD | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-312 | 2019 | 5 | 8 | 10 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 11.1721 | 133_316 | <25mph | <15mph | HFTD - Distribution | 2019-05-08 10:23:00 | 1764 | 11.4886 | FALSE | <25mph | SYWC1 | 1.49 | 2016-04-15T23:26:00Z | 15.99 | 1 | < 25mph | TS378 | 6.32 | 2016-04-15T23:28:00Z | 15.99 | 2 | < 25mph | SYWC1 | 1.49 | 2016-04-16T00:26:00Z | 17 | 2 | < 25mph | SYWC1 | 1.49 | 2016-04-16T00:26:00Z | 17 | 4 | < 25mph
PG&E | 2018-11-17 | 17:20 | 38.7082 | -120.6927 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101421319 | Unknown | 12000 | Conductor | Overhead | Yes | 43421 | 17:20 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1977 | 2018 | 11 | 17 | 17 | 20 | 18-0100697 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 35749 | 6.6792 | 213_278 | <25mph | <15mph | HFTD - Distribution | 2018-11-17 17:20:00 | 1717 | 12.841 | FALSE | <25mph | PG077 | 1.14 | 2019-11-14T22:00:00Z | 12.8 | 16 | < 25mph | PG604 | 7.88 | 2019-11-14T22:20:00Z | 15.35 | 95 | < 25mph | PG077 | 1.14 | 2019-11-14T22:00:00Z | 12.8 | 32 | < 25mph | PG604 | 7.88 | 2019-11-14T22:20:00Z | 15.35 | 189 | < 25mph
PG&E | 2016-08-05 | 2016-08-05 14:46 | 40.4797 | -123.7803 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103572261 |  | 12000 | Conductor | Overhead | Yes | 42587 | 2016-08-05 14:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0907 | 2016 | 8 | 5 | 14 | 46 | 16-0055425 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 7019 | 13.7408 | 83_377 | <25mph | <15mph | HFTD - Distribution | 2016-08-05 14:46:00 | 650 | 14.7579 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E8593 | 4.09 | 2016-05-21T17:30:00Z | 4 | 12 | < 25mph |  |  |  | 0 | 0 | No data | E8593 | 4.09 | 2016-05-21T18:25:00Z | 7 | 24 | < 25mph
PG&E | 2018-07-19 | 0:08 | 36.9372 | -119.4557 | Vegetation | Rural | < 0.25 Acres | Fire Agency | incident # 10559 | 100677019 | AT&T | 12000 | Conductor | Overhead | Yes | 43300 | 0:08 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1766 | 2018 | 7 | 19 | 0 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 10.281 | 268_181 | <25mph | <15mph | HFTD - Distribution | 2018-07-19 00:08:00 | 1506 | 18.2382 | FALSE | <25mph | FCHC1 | 3.86 | 2017-05-03T15:00:00Z | 7 | 1 | < 25mph | FCHC1 | 3.86 | 2017-05-03T15:00:00Z | 7 | 1 | < 25mph | FCHC1 | 3.86 | 2017-05-03T16:00:00Z | 8.01 | 2 | < 25mph | FCHC1 | 3.86 | 2017-05-03T16:00:00Z | 8.01 | 2 | < 25mph
PG&E | 2019-04-09 | 14:07 | 34.6311 | -119.9813 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Fire Dept | Santa Barbra County FD | 101863014 |  | 12000 | Conductor | Overhead | Yes | 43564 | 14:07 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-263 | 2019 | 4 | 9 | 14 | 7 | 19-0040969 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 70756 | 38.5369 | 246_53 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-09 14:07:00 | 1737 | 43.1384 | FALSE | 40-55mph |  |  |  | 0 | 0 | No data | SXWC1 | 5.08 | 2019-10-30T10:09:00Z | 10 | 16 | < 25mph |  |  |  | 0 | 0 | No data | SXWC1 | 5.08 | 2019-10-30T10:09:00Z | 10 | 32 | < 25mph
PG&E | 2018-07-17 | 16:53 | 38.3955 | -122.9212 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101978449 | AT&T | 12000 | Conductor | Overhead | Yes | 43298 | 16:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1759 | 2018 | 7 | 17 | 16 | 53 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 13.5832 | 116_262 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 16:53:00 | 1499 | 13.5832 | FALSE | <25mph | D3838 | 2.28 | 2016-04-25T13:34:00Z | 10 | 27 | < 25mph | E9070 | 4.36 | 2016-04-25T13:55:00Z | 28.99 | 67 | 25-40mph | D4623 | 2.87 | 2016-04-25T15:32:00Z | 12.01 | 52 | < 25mph | E9070 | 4.36 | 2016-04-25T15:10:00Z | 41 | 132 | 40-55mph
PG&E | 2016-07-25 15:32 | 2016-07-25 15:32 | 38.3522 | -120.7107 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42576.6472 | 2016-07-25 15:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0878 | 2016 | 7 | 25 | 15 | 32 | 16-0052398 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 19951 | 10.4912 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-25 15:32:00 | 621 | 14.4675 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2018-05-22T11:56:00Z | 11.01 | 7 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2018-05-22T11:56:00Z | 11.01 | 11 | < 25mph
PG&E | 2019-07-19 | 11:59 | 37.9162 | -120.349 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 163351703 |  | 17000 | Conductor | Overhead | Yes | 43665 | 11:59 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-376 | 2019 | 7 | 19 | 11 | 59 | 19-0079030 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24042 | 10.7946 | 228_234 | <25mph | <15mph | HFTD - Distribution | 2019-07-19 11:59:00 | 1915 | 10.8841 | FALSE | <25mph | C3161 | 3.6 | 2016-12-31T09:28:00Z | 4.99 | 5 | < 25mph | C3161 | 3.6 | 2016-12-31T09:28:00Z | 4.99 | 5 | < 25mph | C3161 | 3.6 | 2016-12-31T09:28:00Z | 4.99 | 9 | < 25mph | C3161 | 3.6 | 2016-12-31T09:28:00Z | 4.99 | 9 | < 25mph
PG&E | 2017-07-01 | 12:02 | 39.8209 | -121.6418 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 003/039 | Unknown | 60000 | Conductor | Overhead | Yes | 42917 | 12:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1212 | 2017 | 7 | 1 | 12 | 2 | INT-09792 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.6345 | 172_339 | <25mph | <15mph | HFTD - Transmission | 2017-07-01 12:02:00 | 954 | 9.664 | FALSE | <25mph | PG075 | 3.12 | 2018-12-26T18:20:00Z | 3.51 | 22 | < 25mph | PG134 | 5.37 | 2018-12-26T18:10:00Z | 6.35 | 30 | < 25mph | PG075 | 3.12 | 2018-12-26T19:20:00Z | 5.03 | 44 | < 25mph | PG134 | 5.37 | 2018-12-26T19:00:00Z | 6.8 | 60 | < 25mph
PG&E | 2018-08-07 | 15:46 | 40.4465 | -122.446 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464611 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43319 | 15:46 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1826 | 2018 | 8 | 7 | 15 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 7.2812 | 139_374 | <25mph | <15mph | HFTD - Distribution | 2018-08-07 15:46:00 | 1566 | 14.3471 | FALSE | <25mph | PG174 | 1.54 | 2019-10-26T12:50:00Z | 5.55 | 6 | < 25mph | PG139 | 6.95 | 2019-10-26T13:00:00Z | 14.38 | 30 | < 25mph | PG174 | 1.54 | 2019-10-26T14:10:00Z | 9.73 | 12 | < 25mph | PG139 | 6.95 | 2019-10-26T13:00:00Z | 14.38 | 60 | < 25mph
PG&E | 2016-10-14 19:45 | 19:44 | 39.6245 | -121.5382 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100435570 |  | 0 – 750 | Conductor | Overhead | Yes | 42657.8228 | 19:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1036 | 2016 | 10 | 14 | 19 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.5623 | 177_329 | <25mph | <15mph | HFTD - Distribution | 2016-10-14 19:44:00 | 777 | 22.2526 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CICC1 | 5.69 | 2015-08-03T17:54:00Z | 11.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CICC1 | 5.69 | 2015-08-03T18:54:00Z | 17 | 2 | < 25mph
PG&E | 2019-09-26 | 14:12 | 36.9517 | -121.8278 | Vegetation | Shrub | 1 meter - < 3 meters | Cal Fire |  | 2287 |  | 21000 | Conductor | Overhead | Yes | 43734 | 14:12 | Vegetation |  | Veg. contact |  |  |  | Branch (OverHanging) | 2019-352 | 2019 | 9 | 26 | 14 | 12 | 19-0104163 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 2856 | 23.4173 | 163_181 | <25mph | <15mph | HFTD - Distribution | 2019-09-26 14:12:00 | 2060 | 23.8621 | FALSE | <25mph | E8014 | 2.22 | 2016-01-06T14:08:00Z | 18.01 | 29 | < 25mph | E5038 | 7.49 | 2016-01-06T14:11:00Z | 20 | 56 | < 25mph | E8014 | 2.22 | 2016-01-06T14:08:00Z | 18.01 | 56 | < 25mph | E5038 | 7.49 | 2016-01-06T14:11:00Z | 20 | 108 | < 25mph
PG&E | 2019-09-22 | 11:56 | 37.5168 | -119.9159 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103967994 |  | 21000 | Pole | Overhead | Yes | 43730 | 11:56 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-452 | 2019 | 9 | 22 | 11 | 56 | 19-0102232 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 133232 | 11.5782 | 247_213 | <25mph | <15mph | HFTD - Distribution | 2019-09-22 11:56:00 | 2051 | 13.905 | FALSE | <25mph | MPOC1 | 3.98 | 2015-10-14T03:07:00Z | 8.01 | 1 | < 25mph | MPOC1 | 3.98 | 2015-10-14T03:07:00Z | 8.01 | 4 | < 25mph | MPOC1 | 3.98 | 2015-10-14T03:07:00Z | 8.01 | 2 | < 25mph | MPOC1 | 3.98 | 2015-10-14T03:07:00Z | 8.01 | 7 | < 25mph
PG&E | 2017-07-18 | 11:30 | 38.0484 | -120.5565 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 012/071 | Unknown | 115000 | Conductor | Overhead | Yes | 42934 | 11:30 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1265 | 2017 | 7 | 18 | 11 | 30 | INT-09873 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 55499 | 7.0574 | 219_242 | <25mph | <15mph | HFTD - Transmission | 2017-07-18 11:30:00 | 1005 | 15.7901 | FALSE | <25mph | PG266 | 3.34 | 2019-05-22T00:10:00Z | 10.51 | 6 | < 25mph | PG334 | 7.56 | 2019-05-22T00:50:00Z | 25.43 | 37 | 25-40mph | PG266 | 3.34 | 2019-05-22T00:10:00Z | 10.51 | 12 | < 25mph | PG334 | 7.56 | 2019-05-22T00:50:00Z | 25.43 | 73 | 25-40mph
PG&E | 2015-06-30 18:18 | 2015-06-30 18:18 | 36.2199 | -121.7534 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | loadside of 88973 | unknown | 12000 | Conductor | Overhead | Yes | 42185.7625 | 2015-06-30 18:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0432 | 2015 | 6 | 30 | 18 | 18 | 15-0044405 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 158 | 5.7006 | 166_141 | <25mph | <15mph | HFTD - Distribution | 2015-06-30 18:18:00 | 177 | 8.2628 | FALSE | <25mph | PPSC1 | 2.3 | 2017-10-08T20:04:00Z | 8.01 | 1 | < 25mph | TR419 | 7.53 | 2017-10-08T20:15:00Z | 18.01 | 2 | < 25mph | PPSC1 | 2.3 | 2017-10-08T20:04:00Z | 8.01 | 2 | < 25mph | TR419 | 7.53 | 2017-10-08T21:15:00Z | 21 | 4 | < 25mph
PG&E | 2015-10-07 15:04 | 2015-10-07 15:04 | 35.3079 | -120.8328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101924901 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42284.6277 | 2015-10-07 15:04 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0640 | 2015 | 10 | 7 | 15 | 3 | 15-0068730 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 77896 | 15.4357 | 207_90 | <25mph | <15mph | HFTD - Distribution | 2015-10-07 15:03:00 | 384 | 16.4418 | FALSE | <25mph | E6113 | 0.7 | 2017-08-07T09:27:00Z | 8.01 | 8 | < 25mph | E6113 | 0.7 | 2017-08-07T09:27:00Z | 8.01 | 9 | < 25mph | E6113 | 0.7 | 2017-08-07T10:12:00Z | 10 | 16 | < 25mph | E6113 | 0.7 | 2017-08-07T10:12:00Z | 10 | 19 | < 25mph
PG&E | 2017-07-12 15:09 | 15:09 | 37.1491 | -122.0037 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 103565794 | Unknown | 21000 | Conductor | Overhead | Yes | 42928.6313 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1248 | 2017 | 7 | 12 | 15 | 9 | 17-0062439 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24690 | 9.5326 | 155_192 | <25mph | <15mph | HFTD - Distribution | 2017-07-12 15:09:00 | 986 | 9.5326 | FALSE | <25mph | D8979 | 3.17 | 2017-11-12T22:28:00Z | 7 | 27 | < 25mph | E6085 | 6.59 | 2017-11-12T23:10:00Z | 8.99 | 128 | < 25mph | D8979 | 3.17 | 2017-11-12T22:28:00Z | 7 | 53 | < 25mph | E6085 | 6.59 | 2017-11-12T23:10:00Z | 8.99 | 253 | < 25mph
PG&E | 2019-04-20 | 6:57 | 37.8686 | -121.6843 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | East County FD | Unknown |  | 17000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-321 | 2019 | 4 | 20 | 6 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 39.0116 | 170_232 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-20 06:57:00 | 1744 | 39.0116 | FALSE | 25-40mph | D3588 | 2.98 | 2018-05-08T15:37:00Z | 4 | 5 | < 25mph | VAQC1 | 6.19 | 2018-05-08T15:45:00Z | 23 | 83 | < 25mph | D3588 | 2.98 | 2018-05-08T16:08:00Z | 5.99 | 11 | < 25mph | VAQC1 | 6.19 | 2018-05-08T16:45:00Z | 28.01 | 166 | 25-40mph
PG&E | 2019-07-01 | 2:15 | 38.2955 | -120.8335 |  | Shrub | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-252 | 2019 | 7 | 1 | 2 | 15 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.9479 | 207_255 | <25mph | <15mph | HFTD - Distribution | 2019-07-01 02:15:00 | 1878 | 14.184 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.85 | 2018-03-10T10:05:00Z | 5.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.85 | 2018-03-10T11:05:00Z | 7 | 8 | < 25mph
PG&E | 2015-03-04 18:44 | 2015-03-04 18:44 | 38.9995 | -122.7545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kelseyville FD | 102156367 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42067.7806 | 2015-03-04 18:44 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0271 | 2015 | 3 | 4 | 18 | 44 | 15-0017374 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29532 | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2015-03-04 18:44:00 | NA | 0 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.58 | 2016-03-10T02:57:00Z | 25.99 | 5 | 25-40mph |  |  |  | 0 | 0 | No data | KELC1 | 6.58 | 2016-03-10T02:57:00Z | 25.99 | 10 | 25-40mph
PG&E | 2019-03-13 | 16:08 | 39.8831 | -122.5498 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 6Fn0313191607 |  | 12000 | Conductor | Overhead | Yes | 43537 | 16:08 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-194 | 2019 | 3 | 13 | 16 | 8 | 19-0033617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 21012 | 20.7105 | 134_343 | <25mph | <15mph | HFTD - Distribution | 2019-03-13 16:08:00 | 1734 | 26.4067 | FALSE | 25-40mph | TCKC1 | 3.76 | 2016-09-14T21:28:00Z | 12.01 | 1 | < 25mph | EPKC1 | 5.75 | 2016-09-14T21:03:00Z | 17 | 2 | < 25mph | TCKC1 | 3.76 | 2016-09-14T21:28:00Z | 12.01 | 2 | < 25mph | EPKC1 | 5.75 | 2016-09-14T21:03:00Z | 17 | 4 | < 25mph
PG&E | 2015-06-03 09:33 | 2015-06-03 09:33 | 39.6896 | -121.6216 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42158.3979 | 2015-06-03 09:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0341 | 2015 | 6 | 3 | 9 | 33 | 15-0038091 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 28146 | 6.3564 | 173_332 | <25mph | <15mph | HFTD - Distribution | 2015-06-03 09:33:00 | 87 | 12.6567 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CICC1 | 6.93 | 2018-10-24T21:54:00Z | 8.99 | 21 | < 25mph |  |  |  | 0 | 0 | No data | CICC1 | 6.93 | 2018-10-24T21:54:00Z | 8.99 | 35 | < 25mph
PG&E | 2015-09-10 05:42 | 42257.2375 | 37.4609 | -121.8434 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100619766 | None | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0588 | 2015 | 9 | 10 | 5 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 1.7354 | 163_209 | <25mph | <15mph | HFTD - Distribution | 2015-09-10 05:42:00 | 333 | 13.8129 | FALSE | <25mph | E3968 | 2.89 | 2018-05-25T08:20:00Z | 5.99 | 4 | < 25mph | RSPC1 | 6.56 | 2018-05-25T07:28:00Z | 18.01 | 26 | < 25mph | E3968 | 2.89 | 2018-05-25T08:50:00Z | 5.99 | 8 | < 25mph | RSPC1 | 6.56 | 2018-05-25T08:28:00Z | 20 | 52 | < 25mph
PG&E | 2017-07-20 13:46 | 13:45 | 35.0804 | -120.5538 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | PAUL LEE 805 903-3416 INC # 8291 | 101941116 | Unknown | 12000 | Conductor | Overhead | Yes | 42936.5736 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1275 | 2017 | 7 | 20 | 13 | 45 | 17-0064321 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 45999 | 13.843 | 220_78 | <25mph | <15mph | HFTD - Distribution | 2017-07-20 13:45:00 | 1013 | 14.6968 | FALSE | <25mph | PG168 | 3.82 | 2019-01-31T16:40:00Z | 6.58 | 14 | < 25mph | PG168 | 3.82 | 2019-01-31T16:40:00Z | 6.58 | 45 | < 25mph | PG168 | 3.82 | 2019-01-31T18:00:00Z | 16.67 | 28 | < 25mph | PG168 | 3.82 | 2019-01-31T18:00:00Z | 16.67 | 89 | < 25mph
PG&E | 2017-08-17 | 15:15 | 39.3703 | -121.0484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | PHIL MICHAEL 265-2894 INCIENT # CA NEV 21642 | 100083029 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42964 | 15:15 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1338 | 2017 | 8 | 17 | 15 | 15 | 17-0071121 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 32850 | 10.6037 | 197_315 | <25mph | <15mph | HFTD - Distribution | 2017-08-17 15:15:00 | 1076 | 10.6037 | FALSE | <25mph | PG363 | 2.02 | 2019-11-17T13:30:00Z | 1.25 | 24 | < 25mph | RRRC1 | 5.9 | 2019-11-17T14:13:00Z | 5.99 | 43 | < 25mph | PG363 | 2.02 | 2019-11-17T15:10:00Z | 2.71 | 48 | < 25mph | RRRC1 | 5.9 | 2019-11-17T15:13:00Z | 7 | 86 | < 25mph
PG&E | 2016-06-24 | 2016-06-24 14:38 | 40.22 | -122.283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101526647 | PACIFIC BELL | 0 – 750 | Unknown | Overhead | Yes | 42545 | 2016-06-24 14:38 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0821 | 2016 | 6 | 24 | 14 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 11.9685 | 145_362 | <25mph | <15mph | HFTD - Distribution | 2016-06-24 14:38:00 | 564 | 17.4582 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2017-07-05 12:11 | 11:58 | 39.2105 | -121.2266 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVE ROBERTSON 530 906 4892 | 100010286 | Unknown | 21000 | Conductor | Overhead | Yes | 42921.5077 | 11:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1223 | 2017 | 7 | 5 | 11 | 58 | 17-0060605 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 10231 | 9.71 | 190_306 | <25mph | <15mph | HFTD - Distribution | 2017-07-05 11:58:00 | 962 | 14.0848 | FALSE | <25mph | E2572 | 2.49 | 2016-03-03T07:49:00Z | 1.01 | 12 | < 25mph | E1789 | 6.76 | 2016-03-03T07:48:00Z | 3 | 28 | < 25mph | E2572 | 2.49 | 2016-03-03T09:29:00Z | 8.01 | 23 | < 25mph | E1789 | 6.76 | 2016-03-03T09:30:00Z | 11.01 | 55 | < 25mph
PG&E | 2017-06-10 07:38 | 07:37 | 35.4359 | -120.4957 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101890429 | Unknown | 21000 | Conductor | Overhead | Yes | 42896.3177 | 07:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1140 | 2017 | 6 | 10 | 7 | 37 | 17-0054182 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 34397 | 9.2577 | 222_98 | <25mph | <15mph | HFTD - Distribution | 2017-06-10 07:37:00 | 879 | 18.05 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2260 | 7.67 | 2016-02-28T21:39:00Z | 14 | 7 | < 25mph |  |  |  | 0 | 0 | No data | E2260 | 7.67 | 2016-02-28T21:39:00Z | 14 | 14 | < 25mph
PG&E | 2019-09-22 | 11:56 | 37.5168 | -119.9159 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103967994 |  | 21000 | Pole | Overhead | Yes | 43730 | 11:56 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-452 | 2019 | 9 | 22 | 11 | 56 | 19-0102232 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 133232 | 11.5782 | 247_213 | <25mph | <15mph | HFTD - Distribution | 2019-09-22 11:56:00 | 2051 | 13.905 | FALSE | <25mph | MPOC1 | 3.98 | 2018-09-19T14:07:00Z | 8.99 | 1 | < 25mph | MPOC1 | 3.98 | 2018-09-19T14:07:00Z | 8.99 | 6 | < 25mph | MPOC1 | 3.98 | 2018-09-19T14:07:00Z | 8.99 | 2 | < 25mph | MPOC1 | 3.98 | 2018-09-19T14:07:00Z | 8.99 | 12 | < 25mph
PG&E | 2016-05-18 | 18:24 | 39.7381 | -123.1587 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42508 | 18:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0735 | 2016 | 5 | 18 | 18 | 24 | 16-0036911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1482 | 13.4862 | 108_336 | <25mph | <15mph | HFTD - Distribution | 2016-05-18 18:24:00 | 480 | 21.4181 | FALSE | <25mph | C3111 | 2.79 | 2017-05-28T01:00:00Z | 10 | 2 | < 25mph | EELC1 | 7.26 | 2017-05-28T01:45:00Z | 11.01 | 3 | < 25mph | C3111 | 2.79 | 2017-05-28T01:00:00Z | 10 | 3 | < 25mph | EELC1 | 7.26 | 2017-05-28T01:45:00Z | 11.01 | 5 | < 25mph
PG&E | 2018-07-14 | 12:56 | 39.2093 | -121.197 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE DEPT LEFT BEFORE UPTAINING THAT INFO | 100086833 | None | 21000 | Conductor | Overhead | Yes | 43295 | 12:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1747 | 2018 | 7 | 14 | 12 | 56 | 18-0059841 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 3720 | 10.2359 | 191_306 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 12:56:00 | 1487 | 12.6903 | FALSE | <25mph | PG348 | 3.64 | 2019-06-18T10:10:00Z | 12.06 | 7 | < 25mph | PG348 | 3.64 | 2019-06-18T10:10:00Z | 12.06 | 48 | < 25mph | PG348 | 3.64 | 2019-06-18T11:10:00Z | 12.93 | 13 | < 25mph | PG348 | 3.64 | 2019-06-18T11:10:00Z | 12.93 | 93 | < 25mph
PG&E | 2018-08-13 | 15:33 | 38.708 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101377799 | Unknown | 21000 | Conductor | Overhead | Yes | 43325 | 15:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1840 | 2018 | 8 | 13 | 15 | 33 | 18-0069470 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1004 | 11.7134 | 201_278 | <25mph | <15mph | HFTD - Distribution | 2018-08-13 15:33:00 | 1579 | 13.7748 | FALSE | <25mph | D7401 | 3.18 | 2016-03-07T17:23:00Z | 4.99 | 32 | < 25mph | D7413 | 4.96 | 2016-03-07T17:21:00Z | 5.99 | 63 | < 25mph | D7401 | 3.18 | 2016-03-07T17:38:00Z | 5.99 | 64 | < 25mph | E4740 | 5.14 | 2016-03-07T17:50:00Z | 5.99 | 123 | < 25mph
PG&E | 2017-07-23 09:22 | 09:22 | 40.642 | -122.2302 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT? | 101459708 | FRONTIER COMMUNICATI | 12000 | Conductor | Overhead | Yes | 42939.3906 | 09:22 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1282 | 2017 | 7 | 23 | 9 | 22 | 17-0064801 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 184712 | 3.9314 | 148_385 | <25mph | <15mph | HFTD - Distribution | 2017-07-23 09:22:00 | 1021 | 13.6933 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C5599 | 5.97 | 2018-11-08T02:01:00Z | 13 | 10 | < 25mph |  |  |  | 0 | 0 | No data | C5599 | 5.97 | 2018-11-08T03:16:00Z | 14.99 | 19 | < 25mph
PG&E | 2015-06-12 13:07 | 2015-06-12 13:07 | 40.4077 | -122.4104 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS STREET FROM 4139 OLD HAPPY VALLEY RD |  | 12000 | Lightning Arrestor | Overhead | No |  |  | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | no-match | 0378 | 2015 | 6 | 12 | 13 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Lightning Arrestor | N.A. | 9.7698 | 140_372 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 13:07:00 | 124 | 24.3549 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6886 | 5.64 | 2015-04-01T01:02:00Z | 14.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6886 | 5.64 | 2015-04-01T01:02:00Z | 14.99 | 8 | < 25mph
PG&E | 2017-09-11 | 7:18 | 37.0008 | -121.6667 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100621936 | VERIZON CALIFORNIA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1407 | 2017 | 9 | 11 | 7 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.0313 | 170_184 | <25mph | <15mph | HFTD - Distribution | 2017-09-11 07:18:00 | 1145 | 32.6801 | FALSE | 25-40mph | AU710 | 3.82 | 2019-04-11T01:15:00Z | 13 | 4 | < 25mph | KE16 | 6.78 | 2019-04-11T01:10:00Z | 26.46 | 27 | 25-40mph | AU710 | 3.82 | 2019-04-11T02:00:00Z | 13 | 8 | < 25mph | KE16 | 6.78 | 2019-04-11T01:10:00Z | 26.46 | 53 | 25-40mph
PG&E | 2015-08-13 03:46 | 2015-08-13 03:46 | 37.2072 | -119.7343 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 44365 SAVAGE RD COARSEGOLD |  | 21000 | Conductor | Overhead | Yes | 42229.1569 | 2015-08-13 03:46 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0526 | 2015 | 8 | 13 | 3 | 46 | 15-0054655 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 7600 | 7.8941 | 255_196 | <25mph | <15mph | HFTD - Distribution | 2015-08-13 03:46:00 | 270 | 10.403 | FALSE | <25mph | D7022 | 2.54 | 2016-05-19T22:57:00Z | 12.01 | 6 | < 25mph | D7022 | 2.54 | 2016-05-19T22:57:00Z | 12.01 | 18 | < 25mph | D7022 | 2.54 | 2016-05-19T22:57:00Z | 12.01 | 12 | < 25mph | D7022 | 2.54 | 2016-05-19T22:57:00Z | 12.01 | 36 | < 25mph
PG&E | 2016-06-26 11:06 | 2016-06-26 11:06 | 40.4832 | -122.0466 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101483777 | FRONTIER | 12000 | Conductor | Overhead | Yes | 42547.4625 | 2016-06-26 11:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0826 | 2016 | 6 | 26 | 11 | 6 | 16-0045846 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 15520 | 6.1274 | 155_376 | <25mph | <15mph | HFTD - Distribution | 2016-06-26 11:06:00 | 566 | 14.8861 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2017-09-08 | 17:21 | 38.6039 | -120.9275 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101379094 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42986 | 17:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1402 | 2017 | 9 | 8 | 17 | 21 | 17-0077122 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 8504 | 10.5347 | 203_272 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 17:21:00 | 1140 | 11.5767 | FALSE | <25mph | BENC1 | 0.96 | 2018-08-21T04:59:00Z | 5.99 | 19 | < 25mph | BENC1 | 0.96 | 2018-08-21T04:59:00Z | 5.99 | 82 | < 25mph | BENC1 | 0.96 | 2018-08-21T04:59:00Z | 5.99 | 38 | < 25mph | PG106 | 7.71 | 2018-08-21T06:30:00Z | 8.12 | 162 | < 25mph
PG&E | 2015-08-22 20:38 | 2015-08-22 20:38 | 38.7748 | -120.8564 | Vegetation | Rural | < 3 meters | Self Extinguished |  | at base of co pole 21721 - 720 Woodridge Rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42238.8597 | 2015-08-22 20:38 | Contact From Object | N.A. | Vegetation | Communication Facility | Unknown | tree hit phone lines | Fell into (Moderate-Severe defect) | 0549 | 2015 | 8 | 22 | 20 | 38 | 15-0056766 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26513 | 9.2929 | 206_282 | <25mph | <15mph | HFTD - Distribution | 2015-08-22 20:38:00 | 293 | 10.7008 | FALSE | <25mph | PG027 | 3.87 | 2019-10-16T03:10:00Z | 3.29 | 20 | < 25mph | PG104 | 7.14 | 2019-10-16T03:30:00Z | 9.57 | 122 | < 25mph | PG027 | 3.87 | 2019-10-16T03:10:00Z | 3.29 | 37 | < 25mph | PG104 | 7.14 | 2019-10-16T03:50:00Z | 13.51 | 229 | < 25mph
PG&E | 2016-07-15 05:19 | 42566.2215 | 35.1839 | -120.5018 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101846594 |  | 12000 | Conductor | Overhead | Yes | 42566.2215 | 42566.2215 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0851 | 2016 | 7 | 15 | 5 | 19 | 16-0050086 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 62404 | 2.6454 | 222_84 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 05:19:00 | 594 | 14.1102 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C9687 | 4.56 | 2018-11-11T19:20:00Z | 4.99 | 31 | < 25mph |  |  |  | 0 | 0 | No data | C9687 | 4.56 | 2018-11-11T20:02:00Z | 8.99 | 63 | < 25mph
PG&E | 2019-03-19 | 12:52 | 37.9956 | -120.3244 | Tree - cutting, 3rd party | Hardwood Forest | 1 meter - < 3 meters | Self Extinguished |  | 101045032 |  | 17000 | Conductor | Overhead | Yes | 43543 | 12:52 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-187 | 2019 | 3 | 19 | 12 | 52 | 19-0035101 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 70602 | 12.9023 | 229_239 | <25mph | <15mph | HFTD - Distribution | 2019-03-19 12:52:00 | 1736 | 14.3226 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.27 | 2017-08-29T19:02:00Z | 18.01 | 16 | < 25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.27 | 2017-08-29T19:02:00Z | 18.01 | 31 | < 25mph
PG&E | 2018-08-08 | 16:02 | 36.4703 | -121.7143 | Vegetation | Rural | < 3 meters | Customer | N.A. | 103910535 | None | 12000 | Conductor | Overhead | Yes | 43320 | 16:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1830 | 2018 | 8 | 8 | 16 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 14.7322 | 168_155 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:02:00 | 1569 | 15.5625 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-08-08 | 10:03 | 40.7933 | -124.0242 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CHIEF | 100983089 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 10:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1829 | 2018 | 8 | 8 | 10 | 3 | 18-0067921 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 27379 | 3.1403 | 73_395 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 10:03:00 | 1568 | 7.3376 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.13 | 2016-02-09T04:55:00Z | 14 | 43 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.13 | 2016-02-09T05:55:00Z | 18.01 | 82 | < 25mph
PG&E | 2016-07-28 08:12 | 42579.3417 | 37.8207 | -120.1388 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101037043 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0884 | 2016 | 7 | 28 | 8 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 1.7128 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 08:12:00 | 627 | 11.4062 | FALSE | <25mph | SEWC1 | 2.5 | 2018-07-08T18:16:00Z | 8.99 | 4 | < 25mph | SEWC1 | 2.5 | 2018-07-08T18:16:00Z | 8.99 | 5 | < 25mph | SEWC1 | 2.5 | 2018-07-08T19:16:00Z | 13 | 9 | < 25mph | SEWC1 | 2.5 | 2018-07-08T19:16:00Z | 13 | 10 | < 25mph
PG&E | 2017-09-27 | 12:12 | 39.4845 | -121.3545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | bill lopez cell 530 521-8052 | 100429924 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 43005 | 12:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1436 | 2017 | 9 | 27 | 12 | 12 | 17-0082180 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 6370 | 7.6613 | 184_321 | <25mph | <15mph | HFTD - Distribution | 2017-09-27 12:12:00 | 1174 | 27.61 | FALSE | 25-40mph | TT309 | 3.08 | 2015-10-10T23:45:00Z | 8.99 | 1 | < 25mph | BNGC1 | 7.37 | 2015-10-10T23:51:00Z | 15.99 | 2 | < 25mph | TT309 | 3.08 | 2015-10-11T00:45:00Z | 11.01 | 2 | < 25mph | BNGC1 | 7.37 | 2015-10-10T23:51:00Z | 15.99 | 4 | < 25mph
PG&E | 2018-06-10 | 17:19 | 38.4157 | -122.9184 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101978419 | AT&T | 12000 | Conductor | Overhead | Yes | 43261 | 17:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1647 | 2018 | 6 | 10 | 17 | 19 | 18-0049445 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2386 | 19.6716 | 117_263 | <25mph | <15mph | HFTD - Distribution | 2018-06-10 17:19:00 | 1389 | 23.7271 | FALSE | <25mph | GRWWW | 1.77 | 2018-06-17T18:00:00Z | 7.9 | 44 | < 25mph | DENWW | 6.15 | 2018-06-17T18:00:00Z | 8.1 | 103 | < 25mph | E9071 | 3.68 | 2018-06-17T18:42:00Z | 10 | 85 | < 25mph | DENWW | 6.15 | 2018-06-17T19:00:00Z | 10.11 | 203 | < 25mph
PG&E | 2019-09-13 | 8:53 | 39.0754 | -121.1717 | Bird Found | Herbaceous | 0.25 - 10 Acres | Fire Dept | Consolidated FD | Etr0913190810 |  | 12000 | Other | Overhead | Yes | 43721 | 8:53 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-46 | 2019 | 9 | 13 | 8 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 10.4382 | 192_298 | <25mph | <15mph | HFTD - Distribution | 2019-09-13 08:53:00 | 2038 | 13.5808 | FALSE | <25mph | PG367 | 1.38 | 2019-10-07T15:00:00Z | 7.81 | 12 | < 25mph | PG367 | 1.38 | 2019-10-07T15:00:00Z | 7.81 | 45 | < 25mph | PG367 | 1.38 | 2019-10-07T15:00:00Z | 7.81 | 24 | < 25mph | PG429 | 6.51 | 2019-10-07T16:00:00Z | 7.9 | 89 | < 25mph
PG&E | 2017-10-08 | 19:44 | 39.7446 | -121.597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100330456 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 19:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1464 | 2017 | 10 | 8 | 19 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 33.2724 | 174_335 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-08 19:44:00 | 1202 | 34.7906 | FALSE | 25-40mph | PDEC1 | 1.6 | 2015-11-03T13:00:00Z | 3 | 1 | < 25mph | JBGC1 | 5.77 | 2015-11-03T12:13:00Z | 12.01 | 13 | < 25mph | PDEC1 | 1.6 | 2015-11-03T13:00:00Z | 3 | 2 | < 25mph | JBGC1 | 5.77 | 2015-11-03T13:13:00Z | 14.99 | 23 | < 25mph
PG&E | 2016-07-28 14:24 | 2016-07-28 14:24 | 37.8232 | -120.1356 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101037045 |  | 17000 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Guy/Span Wire | N.A. | N.A. | Unknown |  | no-match | 0888 | 2016 | 7 | 28 | 14 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Guy/Span Wire | N.A. | 10.9021 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 14:24:00 | 631 | 11.4062 | FALSE | <25mph | SEWC1 | 2.46 | 2016-01-10T06:16:00Z | 7 | 5 | < 25mph | SEWC1 | 2.46 | 2016-01-10T06:16:00Z | 7 | 10 | < 25mph | SEWC1 | 2.46 | 2016-01-10T06:16:00Z | 7 | 10 | < 25mph | SEWC1 | 2.46 | 2016-01-10T06:16:00Z | 7 | 20 | < 25mph
PG&E | 2019-07-22 | 8:11 | 38.7687 | -120.9633 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | El Dorado County FD | 6Ht0722190809 |  | 21000 | Other | Overhead | Yes | 43668 | 8:11 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-49 | 2019 | 7 | 22 | 8 | 11 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.6529 | 201_281 | <25mph | <15mph | HFTD - Distribution | 2019-07-22 08:11:00 | 1920 | 11.9774 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D4464 | 5.5 | 2015-02-04T09:26:00Z | 4.99 | 50 | < 25mph |  |  |  | 0 | 0 | No data | D4464 | 5.5 | 2015-02-04T09:26:00Z | 4.99 | 101 | < 25mph
PG&E | 2019-09-12 | 14:25 | 37.3144 | -122.1865 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 024131103 |  | 12000 | Conductor | Overhead | Yes | 43720 | 14:25 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-217 | 2019 | 9 | 12 | 14 | 25 | 19-0098386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 89097 | 5.2412 | 147_201 | <25mph | <15mph | HFTD - Distribution | 2019-09-12 14:25:00 | 2036 | 15.0249 | FALSE | <25mph | LAHC1 | 3.83 | 2018-10-25T19:07:00Z | 11.01 | 48 | < 25mph | LAHC1 | 3.83 | 2018-10-25T19:07:00Z | 11.01 | 133 | < 25mph | LAHC1 | 3.83 | 2018-10-25T20:07:00Z | 12.01 | 96 | < 25mph | LAHC1 | 3.83 | 2018-10-25T20:07:00Z | 12.01 | 260 | < 25mph
PG&E | 2017-10-08 | 22:19 | 39.7371 | -121.6464 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 103319605 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43016 | 22:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1468 | 2017 | 10 | 8 | 22 | 19 | 17-0085504 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 42839 | 9.4272 | 172_335 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 22:19:00 | 1208 | 31.7535 | FALSE | 25-40mph | PDEC1 | 1.62 | 2018-02-10T07:00:00Z | 2.01 | 1 | < 25mph | PDEC1 | 1.62 | 2018-02-10T07:00:00Z | 2.01 | 7 | < 25mph | PDEC1 | 1.62 | 2018-02-10T08:00:00Z | 2.01 | 2 | < 25mph | PDEC1 | 1.62 | 2018-02-10T08:00:00Z | 2.01 | 14 | < 25mph
PG&E | 2016-08-12 | 2016-08-12 10:08 | 38.8751 | -122.4223 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 102168360 |  | 12000 | Conductor | Overhead | Yes | 42594 | 2016-08-12 10:08 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0922 | 2016 | 8 | 12 | 10 | 8 | 16-0056982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 1368 | 5.1025 | 138_288 | <25mph | <15mph | HFTD - Distribution | 2016-08-12 10:08:00 | 665 | 17.0718 | FALSE | <25mph | KNXC1 | 0.95 | 2019-07-11T08:09:00Z | 4.99 | 7 | < 25mph | PG110 | 7.91 | 2019-07-11T08:20:00Z | 7 | 22 | < 25mph | KNXC1 | 0.95 | 2019-07-11T09:09:00Z | 4.99 | 14 | < 25mph | PG110 | 7.91 | 2019-07-11T08:20:00Z | 7 | 43 | < 25mph
PG&E | 2015-09-19 09:51 | 2015-09-19 09:51 | 38.4755 | -122.9069 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FORESTVILLE | 103334444 |  | 12000 | Conductor | Overhead | Yes | 42266.4104 | 2015-09-19 09:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0603 | 2015 | 9 | 19 | 9 | 51 | 15-0062267 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 488 | 1.1332 | 117_266 | <25mph | <15mph | HFTD - Distribution | 2015-09-19 09:51:00 | 348 | 13.7107 | FALSE | <25mph | D4623 | 2.94 | 2015-06-24T01:58:00Z | 5.99 | 7 | < 25mph | AR323 | 7.96 | 2015-06-24T01:31:00Z | 13 | 61 | < 25mph | D4623 | 2.94 | 2015-06-24T01:58:00Z | 5.99 | 15 | < 25mph | AR323 | 7.96 | 2015-06-24T01:31:00Z | 13 | 127 | < 25mph
PG&E | 2015-08-29 03:30 | 2015-08-29 03:30 | 38.6302 | -122.8327 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Dirt road across from 3204 Rio Lindo Rd, Healdsburg |  | 12000 | Conductor | Overhead | Yes | 42245.1458 | 2015-08-29 03:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0566 | 2015 | 8 | 29 | 3 | 30 | 15-0058127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4780 | 9.2134 | 120_274 | <25mph | <15mph | HFTD - Distribution | 2015-08-29 03:30:00 | 310 | 15.1029 | FALSE | <25mph | KHES | 3.89 | 2016-06-08T00:01:00Z | 18.41 | 9 | < 25mph | KHES | 3.89 | 2016-06-08T00:01:00Z | 18.41 | 29 | < 25mph | KHES | 3.89 | 2016-06-08T00:01:00Z | 18.41 | 18 | < 25mph | KHES | 3.89 | 2016-06-08T00:01:00Z | 18.41 | 57 | < 25mph
PG&E | 2016-06-12 01:45 | 1:45 | 37.4643 | -122.3459 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Unknown | 100265854 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42533.0729 | 1:45 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0796 | 2016 | 6 | 12 | 1 | 45 | 16-0042637 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 19836 | 11.0705 | 141_210 | <25mph | <15mph | HFTD - Distribution | 2016-06-12 01:45:00 | 534 | 17.9563 | FALSE | <25mph | PUGC1 | 2.7 | 2017-09-20T00:18:00Z | 20 | 7 | < 25mph | E4076 | 6.04 | 2017-09-20T00:25:00Z | 23 | 82 | < 25mph | PUGC1 | 2.7 | 2017-09-20T01:18:00Z | 21 | 14 | < 25mph | E4076 | 6.04 | 2017-09-20T01:05:00Z | 28.99 | 158 | 25-40mph
PG&E | 2017-07-23 09:22 | 09:22 | 40.642 | -122.2302 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT? | 101459708 | FRONTIER COMMUNICATI | 12000 | Conductor | Overhead | Yes | 42939.3906 | 09:22 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1282 | 2017 | 7 | 23 | 9 | 22 | 17-0064801 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 184712 | 3.9314 | 148_385 | <25mph | <15mph | HFTD - Distribution | 2017-07-23 09:22:00 | 1021 | 13.6933 | FALSE | <25mph | PG307 | 2.22 | 2019-08-20T05:00:00Z | 5.26 | 12 | < 25mph | PG316 | 7.5 | 2019-08-20T05:00:00Z | 8.77 | 40 | < 25mph | PG307 | 2.22 | 2019-08-20T05:00:00Z | 5.26 | 24 | < 25mph | PG316 | 7.5 | 2019-08-20T05:00:00Z | 8.77 | 80 | < 25mph
PG&E | 2019-04-20 | 6:57 | 37.8686 | -121.6843 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | East County FD | Unknown |  | 17000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-321 | 2019 | 4 | 20 | 6 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 39.0116 | 170_232 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-20 06:57:00 | 1744 | 39.0116 | FALSE | 25-40mph | D3588 | 2.98 | 2018-01-12T22:15:00Z | 8.01 | 6 | < 25mph | VAQC1 | 6.19 | 2018-01-12T21:45:00Z | 20 | 26 | < 25mph | D3588 | 2.98 | 2018-01-12T22:15:00Z | 8.01 | 12 | < 25mph | VAQC1 | 6.19 | 2018-01-12T21:45:00Z | 20 | 64 | < 25mph
PG&E | 2017-09-08 | 21:14 | 37.9604 | -120.3764 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | John Lite 209-984-5623 | 101042521 | Unknown | 17000 | Conductor | Overhead | Yes | 42986 | 21:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1403 | 2017 | 9 | 8 | 21 | 14 | 17-0077137 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49858 | 11.2644 | 227_237 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 21:14:00 | 1141 | 11.9927 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C3161 | 5.93 | 2016-10-15T13:35:00Z | 0 | 4 | < 25mph |  |  |  | 0 | 0 | No data | C3161 | 5.93 | 2016-10-15T14:35:00Z | 0 | 8 | < 25mph
PG&E | 2015-10-30 17:13 | 2015-10-30 17:13 | 38.3166 | -120.7226 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 7600 HWY 49, Jackson | None | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0662 | 2015 | 10 | 30 | 17 | 13 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 8.0122 | 211_256 | <25mph | <15mph | HFTD - Distribution | 2015-10-30 17:13:00 | 406 | 12.822 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.34 | 2015-09-19T18:56:00Z | 8.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.34 | 2015-09-19T19:56:00Z | 10 | 2 | < 25mph
PG&E | 2018-06-30 | 22:18 | 40.6043 | -122.24 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101469808 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43281 | 22:18 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1716 | 2018 | 6 | 30 | 22 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 10.6263 | 147_383 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 22:18:00 | 1457 | 24.79 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RRAC1 | 6.7 | 2017-01-31T16:24:00Z | 4.99 | 5 | < 25mph |  |  |  | 0 | 0 | No data | RRAC1 | 6.7 | 2017-01-31T16:24:00Z | 4.99 | 9 | < 25mph
PG&E | 2015-07-07 15:27 | 2015-07-07 15:27 | 35.155 | -120.5442 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 303corraltos cyn rd | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42192.6438 | 2015-07-07 15:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0449 | 2015 | 7 | 7 | 15 | 27 | 15-0046127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 98566 | 24.1391 | 220_82 | <25mph | <15mph | HFTD - Distribution | 2015-07-07 15:27:00 | 194 | 24.1391 | FALSE | <25mph | D6295 | 2.38 | 2019-02-07T23:58:00Z | 8.01 | 31 | < 25mph | PG168 | 5.8 | 2019-02-08T00:20:00Z | 11.18 | 41 | < 25mph | D6295 | 2.38 | 2019-02-07T23:58:00Z | 8.01 | 58 | < 25mph | PG168 | 5.8 | 2019-02-08T00:20:00Z | 11.18 | 78 | < 25mph
PG&E | 2015-09-12 09:51 | 2015-09-12 09:51 | 39.1164 | -121.0693 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | TOP OF AVALON PLACE, GRASS VALLEY TOWER NUMBER 19/152 40689729 |  | 115000 | Conductor | Overhead | Yes | 42259.4104 | 2015-09-12 09:51 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0594 | 2015 | 9 | 12 | 9 | 51 | VD-2015-079 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.5014 | 196_301 | <25mph | <15mph | HFTD - Transmission | 2015-09-12 09:51:00 | 339 | 14.0472 | FALSE | <25mph | E1789 | 3.95 | 2016-02-04T21:42:00Z | 8.99 | 16 | < 25mph | C0713 | 7.07 | 2016-02-04T22:34:00Z | 11.01 | 53 | < 25mph | E1789 | 3.95 | 2016-02-04T23:00:00Z | 11.01 | 31 | < 25mph | E1789 | 3.95 | 2016-02-04T23:00:00Z | 11.01 | 104 | < 25mph
PG&E | 2017-10-08 | 19:44 | 39.7446 | -121.597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100330456 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 19:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1464 | 2017 | 10 | 8 | 19 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 33.2724 | 174_335 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-08 19:44:00 | 1202 | 34.7906 | FALSE | 25-40mph | PDEC1 | 1.6 | 2017-01-23T06:00:00Z | 4.99 | 1 | < 25mph | JBGC1 | 5.77 | 2017-01-23T05:13:00Z | 8.01 | 8 | < 25mph | PDEC1 | 1.6 | 2017-01-23T07:00:00Z | 7 | 2 | < 25mph | JBGC1 | 5.77 | 2017-01-23T06:13:00Z | 8.01 | 16 | < 25mph
PG&E | 2018-06-04 | 9:25 | 35.4593 | -120.4921 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101895513 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43255 | 9:25 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1624 | 2018 | 6 | 4 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 12.0315 | 222_99 | <25mph | <15mph | HFTD - Distribution | 2018-06-04 09:25:00 | 1366 | 20.4837 | FALSE | <25mph | PG271 | 3.63 | 2019-10-24T17:20:00Z | 23.67 | 13 | < 25mph | PG271 | 3.63 | 2019-10-24T17:20:00Z | 23.67 | 53 | < 25mph | PG271 | 3.63 | 2019-10-24T18:40:00Z | 25.72 | 26 | 25-40mph | PG235 | 7.89 | 2019-10-24T18:40:00Z | 27.76 | 106 | 25-40mph
PG&E | 2018-08-01 | 17:58 | 38.9155 | -122.799 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102156435 | Unknown | 12000 | Conductor | Overhead | Yes | 43313 | 17:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1805 | 2018 | 8 | 1 | 17 | 58 | 18-0065921 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2744 | 14.8702 | 122_290 | <25mph | <15mph | HFTD - Distribution | 2018-08-01 17:58:00 | 1545 | 14.8702 | FALSE | <25mph | E4393 | 3.97 | 2019-10-18T22:45:00Z | 11.01 | 4 | < 25mph | KELC1 | 4.99 | 2019-10-18T21:57:00Z | 21 | 35 | < 25mph | E4393 | 3.97 | 2019-10-18T22:45:00Z | 11.01 | 8 | < 25mph | KELC1 | 4.99 | 2019-10-18T21:57:00Z | 21 | 70 | < 25mph
PG&E | 2018-07-14 | 11:34 | 38.4026 | -122.5489 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103141862 | Verizon | 12000 | Conductor | Overhead | Yes | 43295 | 11:34 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1745 | 2018 | 7 | 14 | 11 | 34 | 18-0059821 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 6426 | 11.4725 | 133_262 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 11:34:00 | 1485 | 15.7933 | FALSE | <25mph | E9543 | 1.57 | 2017-04-27T10:58:00Z | 5.99 | 3 | < 25mph | E9543 | 1.57 | 2017-04-27T10:58:00Z | 5.99 | 10 | < 25mph | E9543 | 1.57 | 2017-04-27T10:58:00Z | 5.99 | 4 | < 25mph | E9543 | 1.57 | 2017-04-27T10:58:00Z | 5.99 | 17 | < 25mph
PG&E | 2016-09-12 | 4:24 | 36.3999 | -121.902 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire Hwy 1 Carmel Hill | 101669614 |  | 12000 | Conductor | Overhead | Yes | 42625 | 4:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0973 | 2016 | 9 | 12 | 4 | 24 | 16-0063826 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 130604 | 5.4712 | 159_151 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 04:24:00 | 715 | 8.1881 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TR419 | 7.81 | 2015-12-03T16:15:00Z | 17 | 1 | < 25mph |  |  |  | 0 | 0 | No data | TR419 | 7.81 | 2015-12-03T17:15:00Z | 21 | 2 | < 25mph
PG&E | 2017-10-04 | 23:42 | 38.6554 | -120.9934 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101375442 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 43012 | 23:42 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1452 | 2017 | 10 | 4 | 23 | 42 | 17-0084323 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7553 | 12.9958 | 200_275 | <25mph | <15mph | HFTD - Distribution | 2017-10-04 23:42:00 | 1190 | 14.755 | FALSE | <25mph | D7401 | 2.11 | 2018-06-24T10:46:00Z | 4.99 | 20 | < 25mph | FSLC1 | 7.78 | 2018-06-24T09:55:00Z | 7.94 | 63 | < 25mph | D7401 | 2.11 | 2018-06-24T11:16:00Z | 5.99 | 40 | < 25mph | FSLC1 | 7.78 | 2018-06-24T09:55:00Z | 7.94 | 124 | < 25mph
PG&E | 2018-06-30 | 11:14 | 39.3621 | -121.0809 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ENGINEER YUREK | 100091354 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 11:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1713 | 2018 | 6 | 30 | 11 | 14 | 18-0055945 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5724 | 3.7745 | 196_314 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 11:14:00 | 1454 | 12.1468 | FALSE | <25mph | E3651 | 2.44 | 2015-01-08T01:20:00Z | 3 | 12 | < 25mph | E3651 | 2.44 | 2015-01-08T01:20:00Z | 3 | 19 | < 25mph | E3651 | 2.44 | 2015-01-08T01:40:00Z | 3 | 24 | < 25mph | RRRC1 | 4.49 | 2015-01-08T02:13:00Z | 8.01 | 35 | < 25mph
PG&E | 2015-11-09 05:55 | 2015-11-09 05:55 | 34.9984 | -120.3634 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42317.2465 | 2015-11-09 05:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0673 | 2015 | 11 | 9 | 5 | 55 | 15-0076534 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 205393 | 8.4294 | 228_73 | <25mph | <15mph | HFTD - Distribution | 2015-11-09 05:55:00 | 417 | 17.7768 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F0412 | 7.53 | 2018-06-26T10:50:00Z | 4 | 5 | < 25mph |  |  |  | 0 | 0 | No data | F0412 | 7.53 | 2018-06-26T10:50:00Z | 4 | 15 | < 25mph
PG&E | 2019-05-30 | 8:18 | 35.7005 | -120.8104 | Vehicle | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 101871463 |  | 12000 | Pole | Overhead | Yes | 43615 | 8:18 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-274 | 2019 | 5 | 30 | 8 | 18 | 19-0059906 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 171603 | 10.8019 | 208_112 | <25mph | <15mph | HFTD - Distribution | 2019-05-30 08:18:00 | 1791 | 17.2262 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG169 | 7 | 2019-04-08T22:00:00Z | 10.96 | 11 | < 25mph |  |  |  | 0 | 0 | No data | PG169 | 7 | 2019-04-08T23:20:00Z | 18.41 | 22 | < 25mph
PG&E | 2019-07-19 | 11:59 | 37.9162 | -120.349 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 163351703 |  | 17000 | Conductor | Overhead | Yes | 43665 | 11:59 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-376 | 2019 | 7 | 19 | 11 | 59 | 19-0079030 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24042 | 10.7946 | 228_234 | <25mph | <15mph | HFTD - Distribution | 2019-07-19 11:59:00 | 1915 | 10.8841 | FALSE | <25mph | PG167 | 3.32 | 2018-11-22T18:10:00Z | 20.4 | 32 | < 25mph | PG167 | 3.32 | 2018-11-22T18:10:00Z | 20.4 | 51 | < 25mph | PG167 | 3.32 | 2018-11-22T18:10:00Z | 20.4 | 60 | < 25mph | PG167 | 3.32 | 2018-11-22T18:10:00Z | 20.4 | 95 | < 25mph
PG&E | 2018-07-25 | 0:42 | 39.7791 | -121.6173 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100327443 | Unknown | 12000 | Conductor | Overhead | Yes | 43306 | 0:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1788 | 2018 | 7 | 25 | 0 | 42 | 18-0063320 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6742 | 1.3279 | 173_337 | <25mph | <15mph | HFTD - Distribution | 2018-07-25 00:42:00 | 1528 | 11.7229 | FALSE | <25mph | PDEC1 | 1.8 | 2016-08-31T13:00:00Z | 1.01 | 1 | < 25mph | JBGC1 | 7.44 | 2016-08-31T12:13:00Z | 14 | 15 | < 25mph | PDEC1 | 1.8 | 2016-08-31T14:00:00Z | 2.01 | 4 | < 25mph | JBGC1 | 7.44 | 2016-08-31T13:13:00Z | 14 | 32 | < 25mph
PG&E | 2017-06-15 15:04 | 15:01 | 39.3913 | -123.3054 | Vegetation | Rural | < 0.25 Acres | Fire Agency | STEPHEN | 103838176 | YES | 12000 | Conductor | Overhead | Yes | 42901.6279 | 15:01 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1148 | 2017 | 6 | 15 | 15 | 1 | 17-0055557 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 180469 | 19.6681 | 101_317 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 15:01:00 | 887 | 19.7788 | FALSE | <25mph | PG120 | 3.9 | 2019-07-30T13:20:00Z | 1.32 | 18 | < 25mph | PG232 | 5.02 | 2019-07-30T13:10:00Z | 9.64 | 56 | < 25mph | PG120 | 3.9 | 2019-07-30T15:00:00Z | 3.74 | 36 | < 25mph | PG232 | 5.02 | 2019-07-30T13:10:00Z | 9.64 | 111 | < 25mph
PG&E | 2019-08-12 | 20:06 | 39.0952 | -123.4937 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 102177212 |  | 12000 | Conductor | Overhead | Yes | 43689 | 20:06 | Vegetation |  | Veg. contact |  |  |  | Fell into (No defect) | 2019-400 | 2019 | 8 | 12 | 20 | 6 | 19-0087090 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2508 | 13.5331 | 93_301 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 20:06:00 | 1970 | 19.4805 | FALSE | <25mph | E1763 | 1.72 | 2018-07-08T07:24:00Z | 0 | 4 | < 25mph | E1763 | 1.72 | 2018-07-08T07:24:00Z | 0 | 4 | < 25mph | E1763 | 1.72 | 2018-07-08T08:24:00Z | 3 | 8 | < 25mph | E1763 | 1.72 | 2018-07-08T08:24:00Z | 3 | 8 | < 25mph
PG&E | 2018-07-14 | 11:34 | 38.4026 | -122.5489 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103141862 | Verizon | 12000 | Conductor | Overhead | Yes | 43295 | 11:34 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1745 | 2018 | 7 | 14 | 11 | 34 | 18-0059821 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 6426 | 11.4725 | 133_262 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 11:34:00 | 1485 | 15.7933 | FALSE | <25mph | PG251 | 3.78 | 2019-06-03T13:10:00Z | 1.1 | 10 | < 25mph | PG177 | 4.3 | 2019-06-03T13:10:00Z | 10.96 | 48 | < 25mph | PG251 | 3.78 | 2019-06-03T14:10:00Z | 3.06 | 20 | < 25mph | PG177 | 4.3 | 2019-06-03T14:30:00Z | 13.15 | 96 | < 25mph
PG&E | 2017-10-08 | 22:19 | 39.7371 | -121.6464 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 103319605 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43016 | 22:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1468 | 2017 | 10 | 8 | 22 | 19 | 17-0085504 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 42839 | 9.4272 | 172_335 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 22:19:00 | 1208 | 31.7535 | FALSE | 25-40mph | PDEC1 | 1.62 | 2015-05-07T10:00:00Z | 12.01 | 1 | < 25mph | E4833 | 5.29 | 2015-05-07T10:39:00Z | 14 | 11 | < 25mph | PDEC1 | 1.62 | 2015-05-07T10:00:00Z | 12.01 | 2 | < 25mph | E4833 | 5.29 | 2015-05-07T11:24:00Z | 17.98 | 21 | < 25mph
PG&E | 2017-07-23 09:22 | 09:22 | 40.642 | -122.2302 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT? | 101459708 | FRONTIER COMMUNICATI | 12000 | Conductor | Overhead | Yes | 42939.3906 | 09:22 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1282 | 2017 | 7 | 23 | 9 | 22 | 17-0064801 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 184712 | 3.9314 | 148_385 | <25mph | <15mph | HFTD - Distribution | 2017-07-23 09:22:00 | 1021 | 13.6933 | FALSE | <25mph | PG307 | 2.22 | 2019-09-21T12:50:00Z | 12.06 | 12 | < 25mph | PG307 | 2.22 | 2019-09-21T12:50:00Z | 12.06 | 40 | < 25mph | PG307 | 2.22 | 2019-09-21T13:00:00Z | 14.16 | 24 | < 25mph | PG526 | 4.23 | 2019-09-21T13:00:00Z | 16.06 | 80 | < 25mph
PG&E | 2017-07-31 14:42 | 14:41 | 38.7967 | -121.1329 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103782414 | Unknown | 12000 | Conductor | Overhead | Yes | 42947.6123 | 14:41 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1305 | 2017 | 7 | 31 | 14 | 41 | 17-0066797 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 210 | 10.6525 | 194_283 | <25mph | <15mph | HFTD - Distribution | 2017-07-31 14:41:00 | 1043 | 12.727 | FALSE | <25mph | D2336 | 3.3 | 2015-05-04T22:36:00Z | 3 | 2 | < 25mph | PLTC1 | 7.08 | 2015-05-04T22:56:00Z | 11.01 | 25 | < 25mph | D2336 | 3.3 | 2015-05-04T23:21:00Z | 4.99 | 8 | < 25mph | PLTC1 | 7.08 | 2015-05-04T22:56:00Z | 11.01 | 56 | < 25mph
PG&E | 2016-06-11 | 2016-06-11 19:45 | 39.3265 | -121.3921 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101292512 |  | 0 – 750 | Transformer | Overhead | Yes | 42532 | 2016-06-11 19:45 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0790 | 2016 | 6 | 11 | 19 | 45 | 16-0042611 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 642 | 8.1809 | 183_312 | <25mph | <15mph | HFTD - Distribution | 2016-06-11 19:45:00 | 533 | 16.0839 | FALSE | <25mph | BNGC1 | 3.76 | 2015-07-15T13:51:00Z | 2.01 | 1 | < 25mph | BNGC1 | 3.76 | 2015-07-15T13:51:00Z | 2.01 | 1 | < 25mph | BNGC1 | 3.76 | 2015-07-15T14:51:00Z | 4 | 2 | < 25mph | BNGC1 | 3.76 | 2015-07-15T14:51:00Z | 4 | 2 | < 25mph
PG&E | 2018-07-19 | 5:29 | 40.1918 | -123.5373 | Vegetation | Rural | < 0.25 Acres | Fire Agency | fire captain | 103909820 | Unknown | 12000 | Conductor | Overhead | Yes | 43300 | 5:29 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1767 | 2018 | 7 | 19 | 5 | 29 | 18-0061308 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 73380 | 5.6109 | 92_361 | <25mph | <15mph | HFTD - Distribution | 2018-07-19 05:29:00 | 1507 | 13.8917 | FALSE | <25mph | ALDC1 | 2.86 | 2019-03-09T06:51:00Z | 4.99 | 1 | < 25mph | ALDC1 | 2.86 | 2019-03-09T06:51:00Z | 4.99 | 1 | < 25mph | ALDC1 | 2.86 | 2019-03-09T06:51:00Z | 4.99 | 2 | < 25mph | ALDC1 | 2.86 | 2019-03-09T06:51:00Z | 4.99 | 2 | < 25mph
PG&E | 2015-07-04 01:14 | 2015-07-04 01:14 | 38.9566 | -121.0434 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100037226 |  | 12000 | Other | Overhead | Yes | 42189.0514 | 2015-07-04 01:14 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0441 | 2015 | 7 | 4 | 1 | 14 | 15-0045440 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 53865 | 7.3476 | 198_292 | <25mph | <15mph | HFTD - Distribution | 2015-07-04 01:14:00 | 186 | 12.3228 | FALSE | <25mph | KAUN | 2.31 | 2018-09-09T20:35:00Z | 11.5 | 1 | < 25mph | KAUN | 2.31 | 2018-09-09T20:35:00Z | 11.5 | 25 | < 25mph | KAUN | 2.31 | 2018-09-09T20:35:00Z | 11.5 | 1 | < 25mph | KAUN | 2.31 | 2018-09-09T20:35:00Z | 11.5 | 48 | < 25mph
PG&E | 2015-05-06 17:17 | 2015-05-06 17:17 | 37.4273 | -119.8803 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | BOOSTER 8179 INDIAN PEEK N/O MIWUK | None | 21000 | Other | Overhead | Yes | 42130.7201 | 2015-05-06 17:17 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0307 | 2015 | 5 | 6 | 17 | 17 | 15-0032311 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 81600 | 12.4413 | 249_208 | <25mph | <15mph | HFTD - Distribution | 2015-05-06 17:17:00 | 53 | 13.2212 | FALSE | <25mph | E9110 | 2.97 | 2016-11-07T05:25:00Z | 4.99 | 6 | < 25mph | MIAC1 | 7.42 | 2016-11-07T04:59:00Z | 10 | 9 | < 25mph | E9110 | 2.97 | 2016-11-07T05:25:00Z | 4.99 | 12 | < 25mph | MIAC1 | 7.42 | 2016-11-07T04:59:00Z | 10 | 18 | < 25mph
2. Cascade (Neu Wind Complex) | 2017-10-08 | 23:45 | 39.322 | -121.4021 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1988 | 2017 | 10 | 8 | 23 | 45 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Equip Failure | Conductor | 0 | 17.3686 | 182_312 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 23:45:00 | 1213 | 29.7104 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PG381 | 4.34 | 2019-06-15T05:00:00Z | 9.22 | 13 | < 25mph |  |  |  | 0 | 0 | No data | PG381 | 4.34 | 2019-06-15T05:00:00Z | 9.22 | 24 | < 25mph
PG&E | 2019-07-06 | 14:22 | 34.6388 | -119.9695 |  | Herbaceous | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | 182721104 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43652 | 14:22 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-153 | 2019 | 7 | 6 | 14 | 22 | 19-0074960 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 14213 | 21.2189 | 246_54 | <25mph | <15mph | HFTD - Distribution | 2019-07-06 14:22:00 | 1888 | 23.8361 | FALSE | <25mph |  |  |  | 0 | 0 | No data | FGMC1 | 6.93 | 2017-08-01T09:35:00Z | 14.99 | 13 | < 25mph |  |  |  | 0 | 0 | No data | FGMC1 | 6.93 | 2017-08-01T10:35:00Z | 14.99 | 22 | < 25mph
PG&E | 2015-02-07 18:38 | 2015-02-07 18:38 | 40.4674 | -123.6545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | mile marker 36.61, hwy 36, bridgeville |  | 12000 | Conductor | Overhead | Yes | 42042.7764 | 2015-02-07 18:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0262 | 2015 | 2 | 7 | 18 | 38 | 15-0011390 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 7691 | 20.9308 | 88_377 | <25mph | <15mph | HFTD - Distribution | 2015-02-07 18:38:00 | 9 | 24.639 | FALSE | <25mph | E8593 | 2.58 | 2016-12-09T23:10:00Z | 17 | 6 | < 25mph | E8593 | 2.58 | 2016-12-09T23:10:00Z | 17 | 7 | < 25mph | E8593 | 2.58 | 2016-12-09T23:40:00Z | 17 | 16 | < 25mph | E8593 | 2.58 | 2016-12-09T23:40:00Z | 17 | 18 | < 25mph
PG&E | 2017-09-06 | 20:08 | 37.2925 | -122.294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100256917 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1400 | 2017 | 9 | 6 | 20 | 8 | 17-0076502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4914 | 6.7999 | 143_200 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 20:08:00 | 1138 | 13.6021 | FALSE | <25mph | LAHC1 | 2.3 | 2016-05-25T03:07:00Z | 8.99 | 1 | < 25mph | LAHC1 | 2.3 | 2016-05-25T03:07:00Z | 8.99 | 1 | < 25mph | LAHC1 | 2.3 | 2016-05-25T03:07:00Z | 8.99 | 2 | < 25mph | LAHC1 | 2.3 | 2016-05-25T03:07:00Z | 8.99 | 2 | < 25mph
PG&E | 2016-11-09 | 9:06 | 37.4532 | -119.6413 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | US FOREST SERVICE | 101017062 |  | 12000 | Conductor | Overhead | Yes | 42683 | 9:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1046 | 2016 | 11 | 9 | 9 | 6 | 16-0078863 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1586 | 6.3162 | 259_209 | <25mph | <15mph | HFTD - Distribution | 2016-11-09 09:06:00 | 787 | 14.6769 | FALSE | <25mph | E7845 | 1.7 | 2017-07-04T14:01:00Z | 0 | 2 | < 25mph | MIAC1 | 6.17 | 2017-07-04T13:59:00Z | 10 | 27 | < 25mph | E7845 | 1.7 | 2017-07-04T15:01:00Z | 0 | 4 | < 25mph | MIAC1 | 6.17 | 2017-07-04T13:59:00Z | 10 | 52 | < 25mph
PG&E | 2019-07-30 | 15:15 | 39.1207 | -121.072 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 152691104 |  | 12000 | Conductor | Overhead | Yes | 43676 | 15:15 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-386 | 2019 | 7 | 30 | 15 | 15 | 19-0082713 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 31302 | 12.2921 | 196_301 | <25mph | <15mph | HFTD - Distribution | 2019-07-30 15:15:00 | 1942 | 13.0851 | FALSE | <25mph | E1789 | 3.69 | 2019-03-01T10:06:00Z | 4 | 11 | < 25mph | D9434 | 6.51 | 2019-03-01T10:00:00Z | 4.99 | 62 | < 25mph | E1789 | 3.69 | 2019-03-01T10:42:00Z | 4 | 21 | < 25mph | D9434 | 6.51 | 2019-03-01T10:00:00Z | 4.99 | 118 | < 25mph
PG&E | 2017-06-24 10:32 | 10:31 | 38.9438 | -121.0447 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100090318 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42910.439 | 10:31 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1193 | 2017 | 6 | 24 | 10 | 31 | 17-0058318 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 582 | 9.5424 | 198_291 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 10:31:00 | 932 | 10.7882 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8862 | 4.36 | 2018-12-04T13:30:00Z | 5.99 | 24 | < 25mph |  |  |  | 0 | 0 | No data | D8862 | 4.36 | 2018-12-04T14:46:00Z | 7 | 45 | < 25mph
PG&E | 2016-07-31 12:11 | 2016-07-31 12:11 | 38.7827 | -120.9168 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101417359 |  | 21000 | Conductor | Overhead | Yes | 42582.5076 | 2016-07-31 12:11 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0895 | 2016 | 7 | 31 | 12 | 11 | 16-0053949 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 10.9662 | 203_282 | <25mph | <15mph | HFTD - Distribution | 2016-07-31 12:11:00 | 638 | 14.1387 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5691 | 7.14 | 2015-01-17T15:37:00Z | 4.99 | 47 | < 25mph |  |  |  | 0 | 0 | No data | D4464 | 7.25 | 2015-01-17T16:18:00Z | 7 | 93 | < 25mph
PG&E | 2019-04-20 | 6:57 | 37.8686 | -121.6843 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | East County FD | Unknown |  | 17000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-321 | 2019 | 4 | 20 | 6 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 39.0116 | 170_232 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-20 06:57:00 | 1744 | 39.0116 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | VAQC1 | 6.19 | 2015-03-13T14:45:00Z | 5.99 | 6 | < 25mph |  |  |  | 0 | 0 | No data | LVMC1 | 6.26 | 2015-03-13T16:02:00Z | 12.01 | 15 | < 25mph
PG&E | 2016-08-30 | 2016-08-30 16:01 | 36.5941 | -121.9212 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Unknown | 101734977 |  | 21000 | Conductor | Overhead | Yes | 42612 | 2016-08-30 16:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0951 | 2016 | 8 | 30 | 16 | 1 | 16-0061130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 199327 | 14.6893 | 159_162 | <25mph | <15mph | HFTD - Distribution | 2016-08-30 16:01:00 | 694 | 14.6893 | FALSE | <25mph | E6019 | 2.96 | 2016-10-05T13:33:00Z | 5.99 | 50 | < 25mph | E6019 | 2.96 | 2016-10-05T13:33:00Z | 5.99 | 54 | < 25mph | E6019 | 2.96 | 2016-10-05T14:19:00Z | 8.01 | 96 | < 25mph | E6019 | 2.96 | 2016-10-05T14:19:00Z | 8.01 | 104 | < 25mph
PG&E | 2016-08-13 | 14:31 | 37.4642 | -119.8589 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire |  |  | 21000 | Conductor | Overhead | Yes | 42595 | 14:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0923 | 2016 | 8 | 13 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.5527 | 249_210 | <25mph | <15mph | HFTD - Distribution | 2016-08-13 14:31:00 | 667 | 11.4441 | FALSE | <25mph | C1522 | 2.94 | 2017-08-02T05:01:00Z | 4.99 | 6 | < 25mph | MIAC1 | 6.96 | 2017-08-02T04:59:00Z | 7 | 10 | < 25mph | E9110 | 3.11 | 2017-08-02T05:31:00Z | 5.99 | 11 | < 25mph | MPOC1 | 7.53 | 2017-08-02T06:07:00Z | 8.01 | 19 | < 25mph
PG&E | 2019-07-25 | 7:39 | 39.1735 | -123.5763 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Oj 2 P/Ss Of Cgc# 215532055340 |  | 12000 | Other | Overhead | Yes | 43671 | 7:39 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-380 | 2019 | 7 | 25 | 7 | 39 | 19-0080947 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 790 | 2.0398 | 89_305 | <25mph | <15mph | HFTD - Distribution | 2019-07-25 07:39:00 | 1928 | 13.3511 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG248 | 4.83 | 2019-07-08T01:00:00Z | 12.06 | 10 | < 25mph |  |  |  | 0 | 0 | No data | PG248 | 4.83 | 2019-07-08T02:10:00Z | 12.93 | 20 | < 25mph
PG&E | 2015-07-05 21:21 | 2015-07-05 21:21 | 38.6524 | -120.6278 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | one span east of c/o 1055 |  | 21000 | Conductor | Overhead | Yes | 42190.8896 | 2015-07-05 21:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0445 | 2015 | 7 | 5 | 21 | 21 | 15-0045605 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 22374 | 5.6191 | 215_275 | <25mph | <15mph | HFTD - Distribution | 2015-07-05 21:21:00 | 190 | 12.9317 | FALSE | <25mph | PG433 | 2.39 | 2019-07-22T15:40:00Z | 8.12 | 6 | < 25mph | PG433 | 2.39 | 2019-07-22T15:40:00Z | 8.12 | 39 | < 25mph | PG433 | 2.39 | 2019-07-22T17:10:00Z | 8.32 | 12 | < 25mph | GZFC1 | 5.69 | 2019-07-22T17:17:00Z | 13 | 78 | < 25mph
PG&E | 2017-07-24 14:02 | 14:01 | 37.2635 | -122.3364 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike klink 650-879-0121 | 100322130 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42940.5845 | 14:01 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1286 | 2017 | 7 | 24 | 14 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 18.4533 | 141_199 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 14:01:00 | 1025 | 18.6394 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 5.31 | 2015-06-24T02:07:00Z | 8.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 5.31 | 2015-06-24T02:07:00Z | 8.99 | 2 | < 25mph
PG&E | 2017-08-28 | 10:07 | 39.0472 | -120.7859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | FORESTHILL | 100019525 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 10:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1357 | 2017 | 8 | 28 | 10 | 7 | 17-0073379 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 10077 | 5.9792 | 209_297 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 10:07:00 | 1095 | 13.4783 | FALSE | <25mph | AU268 | 3.78 | 2015-06-25T11:55:00Z | 0 | 2 | < 25mph | FSHC1 | 4.22 | 2015-06-25T11:33:00Z | 2.01 | 3 | < 25mph | AU268 | 3.78 | 2015-06-25T12:58:00Z | 1.01 | 7 | < 25mph | FSHC1 | 4.22 | 2015-06-25T12:33:00Z | 2.01 | 9 | < 25mph
PG&E | 2015-08-16 07:35 | 2015-08-16 07:35 | 35.4572 | -120.6567 | Vegetation | Rural | < 3 meters | Utility: PG&E |  | 8932 SAN GABRIEL RD. SW C/O OF LOT, Atascadero | None | 0 – 750 | Conductor | Overhead | Yes | 42232.316 | 2015-08-16 07:35 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0534 | 2015 | 8 | 16 | 7 | 35 | 15-0055284 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.0129 | 215_99 | <25mph | <15mph | HFTD - Distribution | 2015-08-16 07:35:00 | 278 | 16.9932 | FALSE | <25mph | E1179 | 1.71 | 2017-11-12T13:12:00Z | 3 | 10 | < 25mph | TT469 | 6.73 | 2017-11-12T12:14:00Z | 4.99 | 16 | < 25mph | E2260 | 2.13 | 2017-11-12T14:00:00Z | 4 | 21 | < 25mph | TT469 | 6.73 | 2017-11-12T12:14:00Z | 4.99 | 32 | < 25mph
PG&E | 2019-07-18 | 19:57 | 37.081 | -119.4865 |  | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | No |  |  | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-09 | 2019 | 7 | 18 | 19 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.8761 | 266_189 | <25mph | <15mph | HFTD - Distribution | 2019-07-18 19:57:00 | 1914 | 14.7588 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PRHC1 | 6.39 | 2018-09-03T01:27:00Z | 8.99 | 2 | < 25mph |  |  |  | 0 | 0 | No data | PRHC1 | 6.39 | 2018-09-03T01:27:00Z | 8.99 | 4 | < 25mph
PG&E | 2017-06-16 22:30 | 22:30 | 38.0373 | -122.1847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101424286 | Unknown | 21000 | Conductor | Overhead | Yes | 42902.9378 | 22:30 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1156 | 2017 | 6 | 16 | 22 | 30 | 17-0055882 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 12000 | 25.2975 | 148_241 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-06-16 22:30:00 | 895 | 25.6656 | FALSE | 25-40mph | MZXC1 | 3.24 | 2018-09-28T00:48:00Z | 20 | 16 | < 25mph | KCCR | 7.88 | 2018-09-28T00:50:00Z | 24.16 | 86 | < 25mph | MZXC1 | 3.24 | 2018-09-28T00:48:00Z | 20 | 32 | < 25mph | KCCR | 7.88 | 2018-09-28T00:50:00Z | 24.16 | 166 | < 25mph
PG&E | 2017-09-03 | 17:52 | 37.4956 | -119.8367 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101086621 | Unknown | 21000 | Transformer | Overhead | Yes | 42981 | 17:52 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 1389 | 2017 | 9 | 3 | 17 | 52 | 17-0075617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 4512 | 13.9592 | 250_212 | <25mph | <15mph | HFTD - Distribution | 2017-09-03 17:52:00 | 1127 | 22.0754 | FALSE | <25mph | JSDC1 | 3.33 | 2016-02-25T01:47:00Z | 1.01 | 1 | < 25mph | MIAC1 | 7.27 | 2016-02-25T00:59:00Z | 11.01 | 6 | < 25mph | JSDC1 | 3.33 | 2016-02-25T02:47:00Z | 1.01 | 2 | < 25mph | MIAC1 | 7.27 | 2016-02-25T00:59:00Z | 11.01 | 13 | < 25mph
PG&E | 2015-03-15 22:47 | 2015-03-15 22:47 | 38.3346 | -120.5325 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 103106530 |  | 12000 | Conductor | Overhead | Yes | 42078.9493 | 2015-03-15 22:47 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0279 | 2015 | 3 | 15 | 22 | 47 | 15-0019709 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 14520 | 7.4897 | 220_257 | <25mph | <15mph | HFTD - Distribution | 2015-03-15 22:47:00 | 25 | 18.5478 | FALSE | <25mph | D9396 | 3.65 | 2018-12-06T10:45:00Z | 3 | 24 | < 25mph | MTZC1 | 7.54 | 2018-12-06T10:56:00Z | 8.01 | 54 | < 25mph | D9396 | 3.65 | 2018-12-06T10:45:00Z | 3 | 46 | < 25mph | MTZC1 | 7.54 | 2018-12-06T11:56:00Z | 10 | 106 | < 25mph
PG&E | 2017-05-15 16:14 | 16:00 | 37.1766 | -119.8189 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SHAUN FAIRBANKS 559-683-4823 | 101108423 | SIERRA | 21000 | Conductor | Overhead | Yes | 42870.6767 | 16:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1099 | 2017 | 5 | 15 | 16 | 0 | 17-0048096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20007 | 15.7465 | 251_194 | <25mph | <15mph | HFTD - Distribution | 2017-05-15 16:00:00 | 839 | 20.7849 | FALSE | <25mph | PG434 | 1.78 | 2019-11-25T05:20:00Z | 7.61 | 6 | < 25mph | PG434 | 1.78 | 2019-11-25T05:20:00Z | 7.61 | 42 | < 25mph | PG434 | 1.78 | 2019-11-25T05:20:00Z | 7.61 | 12 | < 25mph | PG434 | 1.78 | 2019-11-25T05:20:00Z | 7.61 | 84 | < 25mph
PG&E | 2015-11-21 10:36 | 2015-11-21 10:36 | 38.0679 | -120.1872 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101045952 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42329.4417 | 2015-11-21 10:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0677 | 2015 | 11 | 21 | 10 | 36 | 15-0079868 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18350 | 7.816 | 235_243 | <25mph | <15mph | HFTD - Distribution | 2015-11-21 10:36:00 | 421 | 16.6927 | FALSE | <25mph | MOUC1 | 3.29 | 2018-05-16T12:02:00Z | 7 | 1 | < 25mph | MOUC1 | 3.29 | 2018-05-16T12:02:00Z | 7 | 1 | < 25mph | MOUC1 | 3.29 | 2018-05-16T13:02:00Z | 8.99 | 2 | < 25mph | MOUC1 | 3.29 | 2018-05-16T13:02:00Z | 8.99 | 2 | < 25mph
PG&E | 2015-08-16 07:35 | 2015-08-16 07:35 | 35.4572 | -120.6567 | Vegetation | Rural | < 3 meters | Utility: PG&E |  | 8932 SAN GABRIEL RD. SW C/O OF LOT, Atascadero | None | 0 – 750 | Conductor | Overhead | Yes | 42232.316 | 2015-08-16 07:35 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0534 | 2015 | 8 | 16 | 7 | 35 | 15-0055284 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.0129 | 215_99 | <25mph | <15mph | HFTD - Distribution | 2015-08-16 07:35:00 | 278 | 16.9932 | FALSE | <25mph | E2260 | 2.13 | 2015-07-07T16:29:00Z | 8.99 | 5 | < 25mph | E2260 | 2.13 | 2015-07-07T16:29:00Z | 8.99 | 9 | < 25mph | E2260 | 2.13 | 2015-07-07T17:23:00Z | 10 | 10 | < 25mph | E6394 | 5.58 | 2015-07-07T18:16:00Z | 14 | 17 | < 25mph
PG&E | 2019-05-29 | 16:54 | 37.0371 | -119.5209 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 100680674 |  | 12000 | Pole | Overhead | Yes | 43614 | 16:54 | Vegetation |  | Veg. contact | Pole |  |  | Dead | 2019-202 | 2019 | 5 | 29 | 16 | 54 | 19-0059237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 6780 | 6.6167 | 265_186 | <25mph | <15mph | HFTD - Distribution | 2019-05-29 16:54:00 | 1787 | 9.3593 | FALSE | <25mph | PRHC1 | 3 | 2019-01-14T21:27:00Z | 8.01 | 1 | < 25mph | PG202 | 6.2 | 2019-01-14T21:30:00Z | 21.03 | 7 | < 25mph | PRHC1 | 3 | 2019-01-14T22:27:00Z | 8.99 | 2 | < 25mph | PG202 | 6.2 | 2019-01-14T22:40:00Z | 26.53 | 14 | 25-40mph
PG&E | 2016-06-19 | 42540.5049 | 39.3811 | -123.7737 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102187888 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42540 | 42540.5049 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0807 | 2016 | 6 | 19 | 12 | 7 | 16-0044317 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6100 | 11.4602 | 81_317 | <25mph | <15mph | HFTD - Distribution | 2016-06-19 12:07:00 | 550 | 15.3844 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6025 | 6.3 | 2017-10-22T05:15:00Z | 0 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6025 | 6.3 | 2017-10-22T06:15:00Z | 0 | 8 | < 25mph
PG&E | 2016-07-20 19:15 | 2016-07-20 19:15 | 37.7712 | -121.8104 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100898986 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42571.8021 | 2016-07-20 19:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0865 | 2016 | 7 | 20 | 19 | 15 | 16-0051308 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3013 | 17.1873 | 164_226 | <25mph | <15mph | HFTD - Distribution | 2016-07-20 19:15:00 | 608 | 18.9944 | FALSE | <25mph | LVMC1 | 3.62 | 2015-03-03T04:02:00Z | 7 | 1 | < 25mph | LVMC1 | 3.62 | 2015-03-03T04:02:00Z | 7 | 38 | < 25mph | LVMC1 | 3.62 | 2015-03-03T05:02:00Z | 8.01 | 2 | < 25mph | LVMC1 | 3.62 | 2015-03-03T05:02:00Z | 8.01 | 76 | < 25mph
PG&E | 2018-09-21 | 21:10 | 39.0273 | -122.6627 | Vegetation | Rural | < 3 meters | Customer | N.A. | 102147414 | Unknown | 12000 | Conductor | Overhead | Yes | 43364 | 21:10 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1908 | 2018 | 9 | 21 | 21 | 10 | 18-0082278 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 281055 | 11.7868 | 128_296 | <25mph | <15mph | HFTD - Distribution | 2018-09-21 21:10:00 | 1647 | 15.5314 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-02-07 | 9:16 | 38.0369 | -120.2096 | Vegetation | Rural | < 3 meters | Fire Agency | Jason Podesta 209-586-3362 | 101038120 | AT&T | 17000 | Conductor | Overhead | Yes | 43138 | 9:16 | Contact From Object | N.A. | Other | Electric Facility | Human Error | third-party caused | Other/Unknown | 1559 | 2018 | 2 | 7 | 9 | 16 | 18-0012146 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 78738 | 9.6764 | 234_241 | <25mph | <15mph | HFTD - Distribution | 2018-02-07 09:16:00 | 1301 | 13.44 | FALSE | <25mph | MOUC1 | 2.73 | 2017-12-25T06:02:00Z | 10 | 1 | < 25mph | MOUC1 | 2.73 | 2017-12-25T06:02:00Z | 10 | 1 | < 25mph | MOUC1 | 2.73 | 2017-12-25T07:02:00Z | 15.99 | 2 | < 25mph | MOUC1 | 2.73 | 2017-12-25T07:02:00Z | 15.99 | 2 | < 25mph
PG&E | 2018-06-10 | 17:19 | 38.4157 | -122.9184 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101978419 | AT&T | 12000 | Conductor | Overhead | Yes | 43261 | 17:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1647 | 2018 | 6 | 10 | 17 | 19 | 18-0049445 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2386 | 19.6716 | 117_263 | <25mph | <15mph | HFTD - Distribution | 2018-06-10 17:19:00 | 1389 | 23.7271 | FALSE | <25mph | DUTWW | 3.33 | 2017-11-26T03:00:00Z | 3.31 | 44 | < 25mph | RTVWW | 6.01 | 2017-11-26T03:00:00Z | 3.31 | 94 | < 25mph | E9071 | 3.68 | 2017-11-26T04:23:00Z | 4 | 89 | < 25mph | BTOWW | 5.73 | 2017-11-26T04:30:00Z | 4.61 | 190 | < 25mph
PG&E | 2015-06-15 15:35 | 2015-06-15 15:35 | 37.1852 | -121.7595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Jose city | 100618215 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42170.6493 | 2015-06-15 15:35 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0384 | 2015 | 6 | 15 | 15 | 35 | 15-0041178 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 345 | 20.7397 | 166_194 | <25mph | <15mph | HFTD - Distribution | 2015-06-15 15:35:00 | 130 | 21.599 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C0234 | 7.88 | 2018-10-28T20:15:00Z | 13 | 44 | < 25mph |  |  |  | 0 | 0 | No data | C0234 | 7.88 | 2018-10-28T20:15:00Z | 13 | 87 | < 25mph
PG&E | 2017-07-25 15:52 | 15:51 | 38.3779 | -122.5388 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102031447 | Unknown | 12000 | Conductor | Overhead | Yes | 42941.6609 | 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1290 | 2017 | 7 | 25 | 15 | 51 | 17-0065437 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 18584 | 12.338 | 133_260 | <25mph | <15mph | HFTD - Distribution | 2017-07-25 15:51:00 | 1029 | 16.6773 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1582 | 7.55 | 2016-04-01T22:03:00Z | 11.01 | 6 | < 25mph |  |  |  | 0 | 0 | No data | E1582 | 7.55 | 2016-04-01T22:33:00Z | 14 | 12 | < 25mph
PG&E | 2019-06-18 | 19:49 | 35.8876 | -120.9217 | Bird Found | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Pole | Overhead | Yes | 43634 | 19:49 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | no-match | 2019-55 | 2019 | 6 | 18 | 19 | 49 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 15.5935 | 203_122 | <25mph | <15mph | HFTD - Distribution | 2019-06-18 19:49:00 | 1852 | 21.7258 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RBYC1 | 6.84 | 2016-05-07T02:12:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | RBYC1 | 6.84 | 2016-05-07T02:12:00Z | 7 | 2 | < 25mph
PG&E | 2015-04-04 16:49 | 2015-04-04 16:49 | 38.8824 | -122.5914 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 20748 Jerusalem Grade Road, Middletown |  | 12000 | Other | Overhead | Yes | 42098.7007 | 2015-04-04 16:49 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0285 | 2015 | 4 | 4 | 16 | 49 | 15-0024208 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 20448 | 16.9925 | 131_288 | <25mph | <15mph | HFTD - Distribution | 2015-04-04 16:49:00 | 31 | 19.3597 | FALSE | <25mph | PG110 | 3.04 | 2019-06-02T14:50:00Z | 4.38 | 12 | < 25mph | PG096 | 7.7 | 2019-06-02T14:30:00Z | 14.47 | 49 | < 25mph | PG110 | 3.04 | 2019-06-02T15:50:00Z | 7.25 | 24 | < 25mph | PG096 | 7.7 | 2019-06-02T15:20:00Z | 15.77 | 96 | < 25mph
PG&E | 2017-07-12 15:09 | 15:09 | 37.1491 | -122.0037 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 103565794 | Unknown | 21000 | Conductor | Overhead | Yes | 42928.6313 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1248 | 2017 | 7 | 12 | 15 | 9 | 17-0062439 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24690 | 9.5326 | 155_192 | <25mph | <15mph | HFTD - Distribution | 2017-07-12 15:09:00 | 986 | 9.5326 | FALSE | <25mph | D9791 | 1 | 2018-07-21T15:10:00Z | 8.01 | 12 | < 25mph | PG050 | 4.58 | 2018-07-21T15:00:00Z | 19.28 | 133 | < 25mph | D9791 | 1 | 2018-07-21T16:10:00Z | 8.01 | 26 | < 25mph | PG050 | 4.58 | 2018-07-21T15:00:00Z | 19.28 | 264 | < 25mph
PG&E | 2018-10-20 | 14:31 | 40.5218 | -124.1137 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Str. 003/000 | None | 60000 | Conductor | Overhead | Yes | 43393 | 14:31 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1947 | 2018 | 10 | 20 | 14 | 31 | INT-11477 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 410982 | 9.6901 | 69_380 | <25mph | <15mph | HFTD - Transmission | 2018-10-20 14:31:00 | 1686 | 10.3412 | FALSE | <25mph | KFOT | 2.39 | 2015-03-15T21:55:00Z | 20.71 | 26 | < 25mph | KFOT | 2.39 | 2015-03-15T21:55:00Z | 20.71 | 26 | < 25mph | KFOT | 2.39 | 2015-03-15T21:55:00Z | 20.71 | 52 | < 25mph | KFOT | 2.39 | 2015-03-15T21:55:00Z | 20.71 | 52 | < 25mph
PG&E | 2016-08-10 | 2016-08-10 08:36 | 37.0575 | -121.9556 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 101680487 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0917 | 2016 | 8 | 10 | 8 | 36 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 6.3982 | 157_187 | <25mph | <15mph | HFTD - Distribution | 2016-08-10 08:36:00 | 659 | 9.833 | FALSE | <25mph | E9039 | 1.19 | 2018-04-10T08:38:00Z | 3 | 37 | < 25mph | D9791 | 7.03 | 2018-04-10T07:50:00Z | 5.99 | 158 | < 25mph | E9039 | 1.19 | 2018-04-10T09:08:00Z | 3 | 74 | < 25mph | C8539 | 7.1 | 2018-04-10T09:06:00Z | 7 | 314 | < 25mph
PG&E | 2019-08-12 | 20:06 | 39.0952 | -123.4937 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 102177212 |  | 12000 | Conductor | Overhead | Yes | 43689 | 20:06 | Vegetation |  | Veg. contact |  |  |  | Fell into (No defect) | 2019-400 | 2019 | 8 | 12 | 20 | 6 | 19-0087090 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2508 | 13.5331 | 93_301 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 20:06:00 | 1970 | 19.4805 | FALSE | <25mph | E1763 | 1.72 | 2018-10-21T16:15:00Z | 2.01 | 4 | < 25mph | E1763 | 1.72 | 2018-10-21T16:15:00Z | 2.01 | 4 | < 25mph | E1763 | 1.72 | 2018-10-21T17:15:00Z | 2.01 | 7 | < 25mph | E1763 | 1.72 | 2018-10-21T17:15:00Z | 2.01 | 7 | < 25mph
PG&E | 2017-05-14 | 11:59 | 38.0798 | -122.8665 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102247059 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42869 | 11:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1095 | 2017 | 5 | 14 | 11 | 59 | 17-0047802 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 377483 | 24.3878 | 118_244 | <25mph | <15mph | HFTD - Distribution | 2017-05-14 11:59:00 | 835 | 24.3878 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PTRCA | 4.65 | 2015-10-18T19:20:00Z | 18.7 | 7 | < 25mph |  |  |  | 0 | 0 | No data | PTRCA | 4.65 | 2015-10-18T20:10:00Z | 19.19 | 14 | < 25mph
PG&E | 2016-09-22 | 13:53 | 40.224 | -122.3417 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101539450 | None | 12000 | Conductor | Overhead | Yes | 42635 | 13:53 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0996 | 2016 | 9 | 22 | 13 | 53 | 16-0066692 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 14706 | 14.6017 | 143_362 | <25mph | <15mph | HFTD - Distribution | 2016-09-22 13:53:00 | 739 | 20.1469 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 6.08 | 2015-05-11T04:11:00Z | 4 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 6.08 | 2015-05-11T04:28:00Z | 7 | 8 | < 25mph
PG&E | 2019-09-22 | 11:56 | 37.5168 | -119.9159 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103967994 |  | 21000 | Pole | Overhead | Yes | 43730 | 11:56 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-452 | 2019 | 9 | 22 | 11 | 56 | 19-0102232 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 133232 | 11.5782 | 247_213 | <25mph | <15mph | HFTD - Distribution | 2019-09-22 11:56:00 | 2051 | 13.905 | FALSE | <25mph | MPOC1 | 3.98 | 2015-07-05T04:07:00Z | 11.01 | 1 | < 25mph | MPOC1 | 3.98 | 2015-07-05T04:07:00Z | 11.01 | 5 | < 25mph | MPOC1 | 3.98 | 2015-07-05T05:07:00Z | 11.01 | 2 | < 25mph | MPOC1 | 3.98 | 2015-07-05T05:07:00Z | 11.01 | 8 | < 25mph
PG&E | 2017-12-29 | 16:31 | 37.8517 | -122.1586 | Vegetation | Rural | < 3 Meters | Fire Agency | 925-933-1313 | 100488954 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1552 | 2017 | 12 | 29 | 16 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 4.4772 | 149_231 | <25mph | <15mph | HFTD - Distribution | 2017-12-29 16:31:00 | 1294 | 9.6531 | FALSE | <25mph | E5555 | 3.67 | 2017-12-27T16:57:00Z | 10 | 32 | < 25mph | E5555 | 3.67 | 2017-12-27T16:57:00Z | 10 | 129 | < 25mph | E5555 | 3.67 | 2017-12-27T17:28:00Z | 10 | 63 | < 25mph | E5555 | 3.67 | 2017-12-27T17:28:00Z | 10 | 257 | < 25mph
PG&E | 2019-09-10 | 7:13 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 82841102 |  | 12000 | Conductor | Overhead | Yes | 43718 | 7:13 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-369 | 2019 | 9 | 10 | 7 | 13 | 19-0097264 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 23500 | 14.6244 | 147_193 | <25mph | <15mph | HFTD - Distribution | 2019-09-10 07:13:00 | 2029 | 17.7422 | FALSE | <25mph | BNDC1 | 2.84 | 2018-04-05T19:50:00Z | 5.99 | 1 | < 25mph | C1844 | 4.46 | 2018-04-05T19:50:00Z | 5.99 | 21 | < 25mph | BNDC1 | 2.84 | 2018-04-05T20:50:00Z | 8.01 | 2 | < 25mph | BNDC1 | 2.84 | 2018-04-05T20:50:00Z | 8.01 | 45 | < 25mph
PG&E | 2016-06-19 | 2016-06-19 17:19 | 38.4508 | -122.3546 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire--napa fire | 102256859 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 17:19 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0808 | 2016 | 6 | 19 | 17 | 19 | 16-0044337 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 672 | 13.296 | 141_264 | <25mph | <15mph | HFTD - Distribution | 2016-06-19 17:19:00 | 552 | 13.7776 | FALSE | <25mph | PG019 | 3.41 | 2019-01-25T23:40:00Z | 5.26 | 6 | < 25mph | PG185 | 6.12 | 2019-01-26T00:00:00Z | 13.6 | 31 | < 25mph | PG019 | 3.41 | 2019-01-25T23:40:00Z | 5.26 | 12 | < 25mph | PG185 | 6.12 | 2019-01-26T00:00:00Z | 13.6 | 62 | < 25mph
PG&E | 2018-09-01 | 14:25 | 36.8088 | -121.5916 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Twr 35/222 | None | 115000 | Conductor | Overhead | Yes | 43344 | 14:25 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1875 | 2018 | 9 | 1 | 14 | 25 | INT-11331 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 702145 | 13.8683 | 173_173 | <25mph | <15mph | HFTD - Transmission | 2018-09-01 14:25:00 | 1614 | 16.3299 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AP200 | 7.05 | 2018-12-21T16:51:00Z | 0 | 6 | < 25mph |  |  |  | 0 | 0 | No data | AP200 | 7.05 | 2018-12-21T17:46:00Z | 0 | 11 | < 25mph
PG&E | 2015-10-25 05:50 | 2015-10-25 05:50 | 37.7843 | -121.7683 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | cutouts 9504 |  | 21000 | Conductor | Overhead | Yes | 42302.2431 | 2015-10-25 05:50 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0657 | 2015 | 10 | 25 | 5 | 50 | 15-0073203 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 10710 | 23.3456 | 166_227 | <25mph | <15mph | HFTD - Distribution | 2015-10-25 05:50:00 | 401 | 23.3456 | FALSE | <25mph | LVMC1 | 2.34 | 2016-01-10T08:02:00Z | 5.99 | 2 | < 25mph | LVMC1 | 2.34 | 2016-01-10T08:02:00Z | 5.99 | 6 | < 25mph | VAQC1 | 1.86 | 2016-01-10T08:45:00Z | 5.99 | 4 | < 25mph | VAQC1 | 1.86 | 2016-01-10T08:45:00Z | 5.99 | 12 | < 25mph
PG&E | 2018-08-24 | 5:03 | 39.1184 | -121.0154 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JIM SMITH BATT CHIEF 3 | 100097647 | Unknown | 12000 | Conductor | Overhead | Yes | 43336 | 5:03 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1858 | 2018 | 8 | 24 | 5 | 3 | 18-0073024 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 4048 | 6.5682 | 199_301 | <25mph | <15mph | HFTD - Distribution | 2018-08-24 05:03:00 | 1597 | 12.3049 | FALSE | <25mph | AT999 | 2.07 | 2015-09-01T06:58:00Z | 3 | 20 | < 25mph | E1789 | 6.59 | 2015-09-01T07:42:00Z | 7 | 66 | < 25mph | AT999 | 2.07 | 2015-09-01T08:24:00Z | 3 | 26 | < 25mph | E1789 | 6.59 | 2015-09-01T08:06:00Z | 7 | 124 | < 25mph
PG&E | 2018-08-28 | 12:50 | 40.2139 | -123.5966 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100994840 | Unknown | 12000 | Conductor | Overhead | Yes | 43340 | 12:50 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1866 | 2018 | 8 | 28 | 12 | 50 | 18-0074371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 82754 | 9.6027 | 90_363 | <25mph | <15mph | HFTD - Distribution | 2018-08-28 12:50:00 | 1605 | 19.5452 | FALSE | <25mph | ALDC1 | 1.95 | 2018-10-24T19:51:00Z | 4.99 | 1 | < 25mph | ALDC1 | 1.95 | 2018-10-24T19:51:00Z | 4.99 | 1 | < 25mph | ALDC1 | 1.95 | 2018-10-24T20:51:00Z | 4.99 | 2 | < 25mph | ALDC1 | 1.95 | 2018-10-24T20:51:00Z | 4.99 | 2 | < 25mph
PG&E | 2017-08-05 08:33 | 08:33 | 38.4583 | -120.8695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JEFF MICHEL- 530 409 2223 | 101236223 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42952.3565 | 08:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1317 | 2017 | 8 | 5 | 8 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 6.5905 | 205_264 | <25mph | <15mph | HFTD - Distribution | 2017-08-05 08:33:00 | 1055 | 14.6063 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 6.33 | 2015-10-09T21:05:00Z | 12.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 6.33 | 2015-10-09T22:05:00Z | 13 | 2 | < 25mph
PG&E | 2015-06-03 09:33 | 2015-06-03 09:33 | 39.6896 | -121.6216 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42158.3979 | 2015-06-03 09:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0341 | 2015 | 6 | 3 | 9 | 33 | 15-0038091 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 28146 | 6.3564 | 173_332 | <25mph | <15mph | HFTD - Distribution | 2015-06-03 09:33:00 | 87 | 12.6567 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JBGC1 | 7.74 | 2016-11-13T16:13:00Z | 21 | 9 | < 25mph |  |  |  | 0 | 0 | No data | JBGC1 | 7.74 | 2016-11-13T17:13:00Z | 21 | 19 | < 25mph
PG&E | 2019-05-15 | 21:31 | 38.5731 | -122.9603 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Unknown |  | 103931177 |  | 12000 | Conductor | Overhead | Yes | 43600 | 21:31 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-316 | 2019 | 5 | 15 | 21 | 31 | 19-0052480 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 27780 | 16.5892 | 115_271 | <25mph | <15mph | HFTD - Distribution | 2019-05-15 21:31:00 | 1774 | 23.8094 | FALSE | <25mph | D9841 | 3.34 | 2016-02-22T03:18:00Z | 0 | 4 | < 25mph | D2144 | 7.64 | 2016-02-22T03:08:00Z | 2.01 | 45 | < 25mph | D9841 | 3.34 | 2016-02-22T03:48:00Z | 1.01 | 8 | < 25mph | D2144 | 7.64 | 2016-02-22T03:08:00Z | 2.01 | 87 | < 25mph
PG&E | 2019-08-16 | 10:31 | 39.3714 | -121.3221 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103191101 |  | 12000 | Conductor | Overhead | Yes | 43693 | 10:31 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-397 | 2019 | 8 | 16 | 10 | 31 | 19-0088805 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4580 | 6.4736 | 186_315 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 10:31:00 | 1984 | 15.7456 | FALSE | <25mph | BNGC1 | 3.48 | 2018-02-18T15:51:00Z | 14.99 | 1 | < 25mph | BNGC1 | 3.48 | 2018-02-18T15:51:00Z | 14.99 | 1 | < 25mph | BNGC1 | 3.48 | 2018-02-18T16:51:00Z | 17 | 2 | < 25mph | BNGC1 | 3.48 | 2018-02-18T16:51:00Z | 17 | 2 | < 25mph
PG&E | 2017-06-08 15:19 | 15:08 | 34.6058 | -120.0214 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SHAWN STEINER | 101947678 | Unknown | 12000 | Conductor | Overhead | Yes | 42894.6382 | 15:08 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1136 | 2017 | 6 | 8 | 15 | 8 | 17-0053783 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 41311 | 18.6266 | 244_52 | <25mph | <15mph | HFTD - Distribution | 2017-06-08 15:08:00 | 875 | 20.2983 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RHWC1 | 6.88 | 2015-09-28T15:06:00Z | 3 | 15 | < 25mph |  |  |  | 0 | 0 | No data | RHWC1 | 6.88 | 2015-09-28T16:06:00Z | 4 | 33 | < 25mph
PG&E | 2018-08-08 | 16:03 | 37.2974 | -122.2651 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 100307515 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 16:03 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1831 | 2018 | 8 | 8 | 16 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.1654 | 144_201 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:03:00 | 1570 | 9.1654 | FALSE | <25mph | LAHC1 | 0.77 | 2016-01-10T04:07:00Z | 4.99 | 1 | < 25mph | AU836 | 7.23 | 2016-01-10T03:55:00Z | 8.99 | 48 | < 25mph | LAHC1 | 0.77 | 2016-01-10T05:07:00Z | 4.99 | 2 | < 25mph | AU836 | 7.23 | 2016-01-10T03:55:00Z | 8.99 | 96 | < 25mph
PG&E | 2017-08-26 | 20:53 | 38.7066 | -121.0193 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101382231 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42973 | 20:53 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1350 | 2017 | 8 | 26 | 20 | 53 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.4442 | 199_278 | <25mph | <15mph | HFTD - Distribution | 2017-08-26 20:53:00 | 1088 | 14.1326 | FALSE | <25mph | D4464 | 2.39 | 2015-02-23T04:52:00Z | 13 | 32 | < 25mph | D4464 | 2.39 | 2015-02-23T04:52:00Z | 13 | 44 | < 25mph | D4464 | 2.39 | 2015-02-23T06:07:00Z | 15.99 | 64 | < 25mph | D4464 | 2.39 | 2015-02-23T06:07:00Z | 15.99 | 88 | < 25mph
PG&E | 2017-09-03 | 17:52 | 37.4956 | -119.8367 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101086621 | Unknown | 21000 | Transformer | Overhead | Yes | 42981 | 17:52 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 1389 | 2017 | 9 | 3 | 17 | 52 | 17-0075617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 4512 | 13.9592 | 250_212 | <25mph | <15mph | HFTD - Distribution | 2017-09-03 17:52:00 | 1127 | 22.0754 | FALSE | <25mph | PG522 | 3.37 | 2019-12-19T20:50:00Z | 9.51 | 19 | < 25mph | MIAC1 | 7.27 | 2019-12-19T20:59:00Z | 14 | 44 | < 25mph | PG522 | 3.37 | 2019-12-19T20:50:00Z | 9.51 | 38 | < 25mph | MIAC1 | 7.27 | 2019-12-19T20:59:00Z | 14 | 83 | < 25mph
PG&E | 2015-07-05 21:21 | 2015-07-05 21:21 | 38.6524 | -120.6278 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | one span east of c/o 1055 |  | 21000 | Conductor | Overhead | Yes | 42190.8896 | 2015-07-05 21:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0445 | 2015 | 7 | 5 | 21 | 21 | 15-0045605 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 22374 | 5.6191 | 215_275 | <25mph | <15mph | HFTD - Distribution | 2015-07-05 21:21:00 | 190 | 12.9317 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GZFC1 | 5.69 | 2018-04-07T22:17:00Z | 14.99 | 2 | < 25mph |  |  |  | 0 | 0 | No data | GZFC1 | 5.69 | 2018-04-07T23:17:00Z | 17 | 5 | < 25mph
PG&E | 2019-06-26 | 13:14 | 40.0185 | -122.4107 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | Circuit Id 103331101 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43642 | 13:14 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-331 | 2019 | 6 | 26 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2684 | 140_351 | <25mph | <15mph | HFTD - Distribution | 2019-06-26 13:14:00 | 1870 | 19.4401 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-06-03 | 2016-06-03 12:16 | 38.6435 | -120.6959 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | cal-fire and usfs | 103119737 |  | 21000 | Conductor | Overhead | Yes | 42524 | 2016-06-03 12:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0764 | 2016 | 6 | 3 | 12 | 16 | 16-0040808 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 101354 | 7.6436 | 213_274 | <25mph | <15mph | HFTD - Distribution | 2016-06-03 12:16:00 | 507 | 11.74 | FALSE | <25mph | PG077 | 3.41 | 2019-04-10T09:20:00Z | 5.48 | 6 | < 25mph | PG077 | 3.41 | 2019-04-10T09:20:00Z | 5.48 | 30 | < 25mph | PG077 | 3.41 | 2019-04-10T09:20:00Z | 5.48 | 12 | < 25mph | PG068 | 7.91 | 2019-04-10T11:10:00Z | 6.8 | 60 | < 25mph
PG&E | 2017-05-05 15:52 | 15:52 | 40.3776 | -123.0019 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101501566 | None | 12000 | Conductor | Overhead | Yes | 42860.6614 | 15:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1084 | 2017 | 5 | 5 | 15 | 52 | 17-0045707 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 56893 | 24.5621 | 115_371 | <25mph | <15mph | HFTD - Distribution | 2017-05-05 15:52:00 | 824 | 35.0644 | FALSE | 25-40mph | TT100 | 2.89 | 2015-01-10T08:27:00Z | 0 | 1 | < 25mph | TT100 | 2.89 | 2015-01-10T08:27:00Z | 0 | 2 | < 25mph | TT100 | 2.89 | 2015-01-10T09:27:00Z | 1.01 | 2 | < 25mph | TT100 | 2.89 | 2015-01-10T09:27:00Z | 1.01 | 4 | < 25mph
PG&E | 2015-09-25 17:28 | 2015-09-25 17:28 | 38.7169 | -120.7693 | Vegetation | Rural | < 0.25 Acres | Fire Agency | el dorado F D | 101405928 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42272.7278 | 2015-09-25 17:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0616 | 2015 | 9 | 25 | 17 | 28 | 15-0063666 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 111180 | 8.3925 | 209_279 | <25mph | <15mph | HFTD - Distribution | 2015-09-25 17:28:00 | 361 | 11.4196 | FALSE | <25mph | AV185 | 1.68 | 2017-07-06T04:30:00Z | 0 | 29 | < 25mph | E3165 | 6.01 | 2017-07-06T04:26:00Z | 2.01 | 59 | < 25mph | AV185 | 1.68 | 2017-07-06T06:00:00Z | 1.01 | 53 | < 25mph | E3165 | 6.01 | 2017-07-06T05:36:00Z | 3 | 111 | < 25mph
PG&E | 2015-01-16 07:07 | 2015-01-16 07:07 | 38.7753 | -122.7004 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 102167494 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0257 | 2015 | 1 | 16 | 7 | 7 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 19.4177 | 126_282 | <25mph | <15mph | HFTD - Distribution | 2015-01-16 07:07:00 | 4 | 24.2776 | FALSE | <25mph | LKRC1 | 3.05 | 2017-04-20T16:05:00Z | 18.01 | 1 | < 25mph | LKRC1 | 3.05 | 2017-04-20T16:05:00Z | 18.01 | 2 | < 25mph | LKRC1 | 3.05 | 2017-04-20T16:05:00Z | 18.01 | 2 | < 25mph | HWKC1 | 7.87 | 2017-04-20T16:56:00Z | 18.99 | 4 | < 25mph
PG&E | 2017-08-05 18:13 | 18:08 | 39.0968 | -123.2147 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102196629 | Unknown | 12000 | Conductor | Overhead | Yes | 42952.7592 | 18:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1318 | 2017 | 8 | 5 | 18 | 8 | 17-0068200 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 134239 | 10.1139 | 105_301 | <25mph | <15mph | HFTD - Distribution | 2017-08-05 18:08:00 | 1056 | 16.2126 | FALSE | <25mph | E6035 | 3.84 | 2017-06-20T15:49:00Z | 2.01 | 11 | < 25mph | COWC1 | 7.84 | 2017-06-20T15:01:00Z | 7 | 22 | < 25mph | E6035 | 3.84 | 2017-06-20T16:54:00Z | 4 | 22 | < 25mph | COWC1 | 7.84 | 2017-06-20T16:01:00Z | 7 | 44 | < 25mph
PG&E | 2016-08-05 | 2016-08-05 14:46 | 40.4797 | -123.7803 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103572261 |  | 12000 | Conductor | Overhead | Yes | 42587 | 2016-08-05 14:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0907 | 2016 | 8 | 5 | 14 | 46 | 16-0055425 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 7019 | 13.7408 | 83_377 | <25mph | <15mph | HFTD - Distribution | 2016-08-05 14:46:00 | 650 | 14.7579 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2015-10-30 17:13 | 2015-10-30 17:13 | 38.3166 | -120.7226 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 7600 HWY 49, Jackson | None | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0662 | 2015 | 10 | 30 | 17 | 13 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 8.0122 | 211_256 | <25mph | <15mph | HFTD - Distribution | 2015-10-30 17:13:00 | 406 | 12.822 | FALSE | <25mph | PG372 | 2.84 | 2019-07-09T23:10:00Z | 13.8 | 12 | < 25mph | PG116 | 6.03 | 2019-07-09T22:40:00Z | 21.7 | 62 | < 25mph | PG372 | 2.84 | 2019-07-10T00:00:00Z | 15.99 | 24 | < 25mph | PG116 | 6.03 | 2019-07-09T22:40:00Z | 21.7 | 113 | < 25mph
PG&E | 2017-08-06 11:38 | 11:38 | 36.5857 | -121.7121 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101747125 | Unknown | 12000 | Conductor | Overhead | Yes | 42953.4849 | 11:38 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1321 | 2017 | 8 | 6 | 11 | 38 | 17-0068279 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 87172 | 7.0101 | 168_161 | <25mph | <15mph | HFTD - Distribution | 2017-08-06 11:38:00 | 1059 | 12.123 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E8875 | 7.87 | 2017-08-21T12:33:00Z | 4 | 17 | < 25mph |  |  |  | 0 | 0 | No data | E8875 | 7.87 | 2017-08-21T13:18:00Z | 4 | 33 | < 25mph
PG&E | 2018-09-21 | 23:02 | 38.6428 | -122.7453 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102218862 | Unknown | 12000 | Conductor | Overhead | Yes | 43364 | 23:02 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1909 | 2018 | 9 | 21 | 23 | 2 | 18-0082304 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 9470 | 7.2054 | 124_275 | <25mph | <15mph | HFTD - Distribution | 2018-09-21 23:02:00 | 1648 | 14.1592 | FALSE | <25mph | E3235 | 2.39 | 2017-09-26T01:13:00Z | 1.01 | 4 | < 25mph | R08WW | 7.94 | 2017-09-26T02:00:00Z | 8.21 | 25 | < 25mph | E3235 | 2.39 | 2017-09-26T02:57:00Z | 2.01 | 9 | < 25mph | R08WW | 7.94 | 2017-09-26T02:00:00Z | 8.21 | 51 | < 25mph
PG&E | 2019-05-17 | 15:12 | 38.4797 | -123.1486 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 42811111 |  | 12000 | Conductor | Overhead | Yes | 43602 | 15:12 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-200 | 2019 | 5 | 17 | 15 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 19.5511 | 107_266 | <25mph | <15mph | HFTD - Distribution | 2019-05-17 15:12:00 | 1775 | 20.334 | FALSE | <25mph | E8483 | 3.61 | 2017-09-25T03:13:00Z | 2.01 | 4 | < 25mph | E8483 | 3.61 | 2017-09-25T03:13:00Z | 2.01 | 10 | < 25mph | E8483 | 3.61 | 2017-09-25T04:25:00Z | 2.01 | 8 | < 25mph | E8483 | 3.61 | 2017-09-25T04:25:00Z | 2.01 | 19 | < 25mph
PG&E | 2018-06-04 | 9:25 | 35.4593 | -120.4921 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101895513 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43255 | 9:25 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1624 | 2018 | 6 | 4 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 12.0315 | 222_99 | <25mph | <15mph | HFTD - Distribution | 2018-06-04 09:25:00 | 1366 | 20.4837 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2017-09-27 | 12:12 | 39.4845 | -121.3545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | bill lopez cell 530 521-8052 | 100429924 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 43005 | 12:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1436 | 2017 | 9 | 27 | 12 | 12 | 17-0082180 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 6370 | 7.6613 | 184_321 | <25mph | <15mph | HFTD - Distribution | 2017-09-27 12:12:00 | 1174 | 27.61 | FALSE | 25-40mph | TT309 | 3.08 | 2015-06-12T17:45:00Z | 4 | 1 | < 25mph | BNGC1 | 7.37 | 2015-06-12T17:51:00Z | 8.99 | 2 | < 25mph | TT309 | 3.08 | 2015-06-12T18:45:00Z | 5.99 | 2 | < 25mph | BNGC1 | 7.37 | 2015-06-12T18:51:00Z | 10 | 4 | < 25mph
PG&E | 2019-09-30 | 14:29 | 34.6139 | -120.1799 | Contact with High Voltage, 3rd party | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 183041102 |  | 12000 | Conductor | Overhead | Yes | 43738 | 14:29 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-13 | 2019 | 9 | 30 | 14 | 29 | 19-0105582 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 4080 | 26.8876 | 237_52 | 25-40mph | 15-30mph | HFTD - Distribution | 2019-09-30 14:29:00 | 2072 | 27.9753 | FALSE | 25-40mph | C9206 | 2.6 | 2016-11-10T02:55:00Z | 1.01 | 6 | < 25mph | AP901 | 4.92 | 2016-11-10T02:50:00Z | 4.99 | 10 | < 25mph | C9206 | 2.6 | 2016-11-10T02:55:00Z | 1.01 | 9 | < 25mph | AP901 | 4.92 | 2016-11-10T02:50:00Z | 4.99 | 16 | < 25mph
PG&E | 2016-05-15 15:54 | 2016-05-15 15:54 | 36.7948 | -119.3966 | Vegetation | RURAL | 100 - 299 Acres | Fire Agency | Cal Fire | 100729685 | None | 12000 | Conductor | Overhead | Yes | 42505.6625 | 2016-05-15 15:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0730 | 2016 | 5 | 15 | 15 | 54 | 16-0036136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 180310 | 10.5903 | 270_173 | <25mph | <15mph | HFTD - Distribution | 2016-05-15 15:54:00 | 474 | 14.7659 | FALSE | <25mph |  |  |  | 0 | 0 | No data | FCHC1 | 7.54 | 2018-07-04T20:00:00Z | 14 | 1 | < 25mph |  |  |  | 0 | 0 | No data | FCHC1 | 7.54 | 2018-07-04T21:00:00Z | 15.99 | 2 | < 25mph
PG&E | 2016-09-16 20:56 | 2016-09-16 20:56 | 39.8387 | -121.7023 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 100441760 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42629.8722 | 2016-09-16 20:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0983 | 2016 | 9 | 16 | 20 | 56 | 16-0065273 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 314427 | 11.5178 | 170_340 | <25mph | <15mph | HFTD - Distribution | 2016-09-16 20:56:00 | 725 | 12.6422 | FALSE | <25mph | C8878 | 3.59 | 2015-09-18T17:28:00Z | 4.99 | 13 | < 25mph | C8878 | 3.59 | 2015-09-18T17:28:00Z | 4.99 | 20 | < 25mph | C8878 | 3.59 | 2015-09-18T17:28:00Z | 4.99 | 25 | < 25mph | CSTC1 | 4.21 | 2015-09-18T17:51:00Z | 8.01 | 45 | < 25mph
PG&E | 2019-05-10 | 14:52 | 40.704 | -122.8314 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Fire Dept | Lewiston FD | Keswick-Trinity 60Kv Line |  | 60000 | Conductor | Overhead | Yes | 43595 | 14:52 | Vegetation |  | Contact from Object - Other | Electric Facility |  |  | no-match | 2019-301 | 2019 | 5 | 10 | 14 | 52 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.0535 | 123_389 | <25mph | <15mph | HFTD - Transmission | 2019-05-10 14:52:00 | 1766 | 13.0849 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TCAC1 | 5.87 | 2017-01-16T07:28:00Z | 5.99 | 6 | < 25mph |  |  |  | 0 | 0 | No data | TCAC1 | 5.87 | 2017-01-16T08:28:00Z | 8.01 | 11 | < 25mph
PG&E | 2015-05-27 21:44 | 2015-05-27 21:44 | 39.169 | -120.9612 | Vegetation | Rural | < 0.25 Acres | Fire Agency | PEARDALE F.D. | 100077687 |  | 12000 | Conductor | Overhead | Yes | 42151.9056 | 2015-05-27 21:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0329 | 2015 | 5 | 27 | 21 | 44 | 15-0036850 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10828 | 3.691 | 201_303 | <25mph | <15mph | HFTD - Distribution | 2015-05-27 21:44:00 | 75 | 11.9096 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5439 | 7.11 | 2018-04-27T07:05:00Z | 8.99 | 74 | < 25mph |  |  |  | 0 | 0 | No data | E5439 | 7.11 | 2018-04-27T07:55:00Z | 12.01 | 144 | < 25mph
PG&E | 2018-06-30 | 11:14 | 39.3621 | -121.0809 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ENGINEER YUREK | 100091354 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 11:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1713 | 2018 | 6 | 30 | 11 | 14 | 18-0055945 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5724 | 3.7745 | 196_314 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 11:14:00 | 1454 | 12.1468 | FALSE | <25mph | E3651 | 2.44 | 2015-08-26T14:55:00Z | 2.01 | 9 | < 25mph | RRRC1 | 4.49 | 2015-08-26T15:13:00Z | 8.01 | 16 | < 25mph | E3651 | 2.44 | 2015-08-26T16:45:00Z | 4 | 13 | < 25mph | RRRC1 | 4.49 | 2015-08-26T16:13:00Z | 8.01 | 27 | < 25mph
PG&E | 2015-04-02 09:44 | 2015-04-02 09:44 | 39.6772 | -121.492 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100338726 |  | 12000 | Conductor | Overhead | Yes | 42096.4056 | 2015-04-02 09:44 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0284 | 2015 | 4 | 2 | 9 | 44 | 15-0023747 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 100204 | 15.7458 | 178_332 | <25mph | <15mph | HFTD - Distribution | 2015-04-02 09:44:00 | 30 | 15.7458 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JBGC1 | 4.06 | 2017-11-03T11:13:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | JBGC1 | 4.06 | 2017-11-03T12:13:00Z | 8.01 | 2 | < 25mph
PG&E | 2017-09-06 | 19:26 | 40.8392 | -122.3635 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103643183 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 19:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1399 | 2017 | 9 | 6 | 19 | 26 | 17-0076501 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 23830 | 6.5088 | 142_396 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 19:26:00 | 1137 | 12.365 | FALSE | <25mph | CTANT | 1.93 | 2016-05-09T17:30:00Z | 9.93 | 4 | < 25mph | CTANT | 1.93 | 2016-05-09T17:30:00Z | 9.93 | 9 | < 25mph | CTANT | 1.93 | 2016-05-09T18:30:00Z | 11.81 | 8 | < 25mph | SLFC1 | 6.48 | 2016-05-09T18:19:00Z | 12.01 | 18 | < 25mph
PG&E | 2017-12-16 | 11:51 | 38.8171 | -122.7041 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Shawn Ohare | 102167231 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43085 | 11:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1540 | 2017 | 12 | 16 | 11 | 51 | 17-0102101 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26120 | 34.3488 | 126_285 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-12-16 11:51:00 | 1282 | 35.345 | FALSE | 25-40mph | LKRC1 | 2.09 | 2018-04-10T00:05:00Z | 5.99 | 1 | < 25mph | KELC1 | 6.55 | 2018-04-10T00:57:00Z | 13 | 3 | < 25mph | LKRC1 | 2.09 | 2018-04-10T01:05:00Z | 5.99 | 2 | < 25mph | KELC1 | 6.55 | 2018-04-10T01:57:00Z | 13 | 5 | < 25mph
PG&E | 2017-10-09 | 1:02 | 38.7037 | -120.6725 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101408485 | Unknown | 21000 | Other | Overhead | Yes | 43017 | 1:02 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1473 | 2017 | 10 | 9 | 1 | 2 | 17-0085324 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 419843 | 26.702 | 214_278 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-10-09 01:02:00 | 1216 | 29.779 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E5691 | 7.21 | 2015-08-14T22:04:00Z | 14 | 25 | < 25mph |  |  |  | 0 | 0 | No data | E5691 | 7.21 | 2015-08-14T22:04:00Z | 14 | 49 | < 25mph
PG&E | 2017-06-16 22:30 | 22:30 | 38.0373 | -122.1847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101424286 | Unknown | 21000 | Conductor | Overhead | Yes | 42902.9378 | 22:30 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1156 | 2017 | 6 | 16 | 22 | 30 | 17-0055882 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 12000 | 25.2975 | 148_241 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-06-16 22:30:00 | 895 | 25.6656 | FALSE | 25-40mph | PG049 | 3.65 | 2018-10-20T19:30:00Z | 8.32 | 6 | < 25mph | PG042 | 5.72 | 2018-10-20T19:40:00Z | 12.06 | 86 | < 25mph | PG049 | 3.65 | 2018-10-20T20:50:00Z | 8.77 | 12 | < 25mph | PG042 | 5.72 | 2018-10-20T19:40:00Z | 12.06 | 174 | < 25mph
PG&E | 2017-07-24 19:31 | 19:31 | 38.3519 | -120.7103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.8134 | 19:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1288 | 2017 | 7 | 24 | 19 | 31 | 17-0065145 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14281 | 10.3402 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 19:31:00 | 1027 | 12.2366 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ANUC1 | 4.14 | 2016-05-09T02:53:00Z | 4.99 | 2 | < 25mph |  |  |  | 0 | 0 | No data | ANUC1 | 4.14 | 2016-05-09T02:53:00Z | 4.99 | 4 | < 25mph
PG&E | 2016-09-28 | 14:00 | 35.2145 | -118.5625 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire |  |  | 0 – 750 | Conductor | Overhead | Yes | 42641 | 14:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1008 | 2016 | 9 | 28 | 14 | 0 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.8467 | 310_87 | <25mph | <15mph | HFTD - Distribution | 2016-09-28 14:00:00 | 750 | 26.957 | FALSE | 25-40mph | SE060 | 3.82 | 2019-09-12T11:00:00Z | 22.64 | 9 | < 25mph | SE060 | 3.82 | 2019-09-12T11:00:00Z | 22.64 | 69 | < 25mph | SE060 | 3.82 | 2019-09-12T11:00:00Z | 22.64 | 17 | < 25mph | SE060 | 3.82 | 2019-09-12T11:00:00Z | 22.64 | 134 | < 25mph
PG&E | 2019-04-09 | 15:27 | 37.7341 | -120.0776 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 101076921 |  | 21000 | Pole | Overhead | Yes | 43564 | 15:27 | Vegetation |  | Veg. contact | Pole |  |  | Branch (Not overhanging, > 12ft) | 2019-313 | 2019 | 4 | 9 | 15 | 27 | 19-0041008 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 179862 | 22.8983 | 240_225 | <25mph | <15mph | HFTD - Distribution | 2019-04-09 15:27:00 | 1738 | 29.8749 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | SEWC1 | 4.76 | 2018-09-15T01:16:00Z | 8.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | SEWC1 | 4.76 | 2018-09-15T02:16:00Z | 10 | 2 | < 25mph
PG&E | 2019-03-13 | 16:08 | 39.8831 | -122.5498 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 6Fn0313191607 |  | 12000 | Conductor | Overhead | Yes | 43537 | 16:08 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-194 | 2019 | 3 | 13 | 16 | 8 | 19-0033617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 21012 | 20.7105 | 134_343 | <25mph | <15mph | HFTD - Distribution | 2019-03-13 16:08:00 | 1734 | 26.4067 | FALSE | 25-40mph | TCKC1 | 3.76 | 2016-08-24T19:28:00Z | 14 | 2 | < 25mph | EPKC1 | 5.75 | 2016-08-24T20:03:00Z | 15.99 | 3 | < 25mph | TCKC1 | 3.76 | 2016-08-24T19:28:00Z | 14 | 3 | < 25mph | EPKC1 | 5.75 | 2016-08-24T20:03:00Z | 15.99 | 5 | < 25mph
PG&E | 2016-06-26 | 2016-06-26 16:38 | 39.5042 | -121.4475 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100375810 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42547 | 2016-06-26 16:38 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0823 | 2016 | 6 | 26 | 16 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 9.04 | 180_322 | <25mph | <15mph | HFTD - Distribution | 2016-06-26 16:38:00 | 567 | 14.524 | FALSE | <25mph | TT309 | 3.14 | 2017-07-13T20:45:00Z | 12.01 | 1 | < 25mph | TT309 | 3.14 | 2017-07-13T20:45:00Z | 12.01 | 1 | < 25mph | TT309 | 3.14 | 2017-07-13T21:45:00Z | 13 | 2 | < 25mph | TT309 | 3.14 | 2017-07-13T21:45:00Z | 13 | 2 | < 25mph
PG&E | 2017-07-02 | 13:28 | 39.8605 | -121.6274 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 000/017c | Unknown | 60000 | Conductor | Overhead | Yes | 42918 | 13:28 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1216 | 2017 | 7 | 2 | 13 | 28 | INT-09794 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 10.1141 | 173_342 | <25mph | <15mph | HFTD - Transmission | 2017-07-02 13:28:00 | 956 | 11.4462 | FALSE | <25mph | C8878 | 1.44 | 2015-01-24T11:48:00Z | 4.99 | 24 | < 25mph | CSTC1 | 7.55 | 2015-01-24T11:51:00Z | 8.01 | 32 | < 25mph | C8878 | 1.44 | 2015-01-24T11:48:00Z | 4.99 | 47 | < 25mph | CSTC1 | 7.55 | 2015-01-24T11:51:00Z | 8.01 | 63 | < 25mph
PG&E | 2019-09-30 | 14:29 | 34.6139 | -120.1799 | Contact with High Voltage, 3rd party | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 183041102 |  | 12000 | Conductor | Overhead | Yes | 43738 | 14:29 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-13 | 2019 | 9 | 30 | 14 | 29 | 19-0105582 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 4080 | 26.8876 | 237_52 | 25-40mph | 15-30mph | HFTD - Distribution | 2019-09-30 14:29:00 | 2072 | 27.9753 | FALSE | 25-40mph | C9206 | 2.6 | 2015-11-06T18:01:00Z | 2.01 | 5 | < 25mph | AP901 | 4.92 | 2015-11-06T17:50:00Z | 5.99 | 9 | < 25mph | C9206 | 2.6 | 2015-11-06T19:06:00Z | 4 | 12 | < 25mph | AP901 | 4.92 | 2015-11-06T17:50:00Z | 5.99 | 18 | < 25mph
PG&E | 2019-10-08 | 17:59 | 35.2979 | -120.4868 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 182541103 |  | 12000 | Conductor | Overhead | Yes | 43746 | 17:59 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-207 | 2019 | 10 | 8 | 17 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.8254 | 223_90 | <25mph | <15mph | HFTD - Distribution | 2019-10-08 17:59:00 | 2082 | 10.8694 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-07-21 | 14:51 | 35.6846 | -120.9427 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101943190 | Unknown | 21000 | Conductor | Overhead | Yes | 43302 | 14:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1775 | 2018 | 7 | 21 | 14 | 51 | 18-0062364 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 110814 | 14.9597 | 202_111 | <25mph | <15mph | HFTD - Distribution | 2018-07-21 14:51:00 | 1515 | 21.9627 | FALSE | <25mph | TABC1 | 2.21 | 2016-10-27T16:07:00Z | 4 | 1 | < 25mph | D4060 | 5.73 | 2016-10-27T16:21:00Z | 4.99 | 17 | < 25mph | TABC1 | 2.21 | 2016-10-27T17:07:00Z | 4 | 2 | < 25mph | D4060 | 5.73 | 2016-10-27T16:36:00Z | 4.99 | 34 | < 25mph
PG&E | 2019-06-27 | 2:23 | 36.8198 | -119.3334 | Bird Found | Hardwood Woodland | 0.25 - 10 Acres | Self Extinguished |  | Kings River-Sanger-Reedley 115Kv At 16/089 |  | 115000 | Insulator | Overhead | Yes | 43643 | 2:23 | Equipment - PG&E | Insulator |  |  |  |  | no-match | 2019-104 | 2019 | 6 | 27 | 2 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | N.A. | 13.572 | 273_175 | <25mph | <15mph | HFTD - Transmission | 2019-06-27 02:23:00 | 1872 | 13.572 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2888 | 7.11 | 2019-02-24T21:56:00Z | 10 | 7 | < 25mph |  |  |  | 0 | 0 | No data | E2888 | 7.11 | 2019-02-24T21:56:00Z | 10 | 14 | < 25mph
PG&E | 2017-07-22 12:26 | 12:25 | 40.8795 | -123.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Josh , comander chief of forest service. | 100980577 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.518 | 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1279 | 2017 | 7 | 22 | 12 | 25 | 17-0064721 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 23227 | 10.7493 | 84_399 | <25mph | <15mph | HFTD - Distribution | 2017-07-22 12:25:00 | 1018 | 13.5476 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BHTC1 | 5.5 | 2019-12-18T01:46:00Z | 30 | 7 | 25-40mph |  |  |  | 0 | 0 | No data | BHTC1 | 5.5 | 2019-12-18T01:46:00Z | 30 | 14 | 25-40mph
PG&E | 2015-12-31 19:12 | 2015-12-31 19:12 | 37.1568 | -121.9868 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LOS GATOS MONTE SERENO SARATOGA | 100518215 | Verizon | 21000 | Conductor | Overhead | Yes | 42369.8 | 2015-12-31 19:12 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0689 | 2015 | 12 | 31 | 19 | 12 | 15-0087962 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7979 | 7.4149 | 156_193 | <25mph | <15mph | HFTD - Distribution | 2015-12-31 19:12:00 | 433 | 10.9251 | FALSE | <25mph | LSGC1 | 3.83 | 2019-08-22T13:32:00Z | 8.01 | 30 | < 25mph | AV151 | 5.33 | 2019-08-22T12:40:00Z | 13 | 208 | < 25mph | LSGC1 | 3.83 | 2019-08-22T13:32:00Z | 8.01 | 59 | < 25mph | AV151 | 5.33 | 2019-08-22T12:40:00Z | 13 | 404 | < 25mph
PG&E | 2016-07-15 05:19 | 42566.2215 | 35.1839 | -120.5018 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101846594 |  | 12000 | Conductor | Overhead | Yes | 42566.2215 | 42566.2215 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0851 | 2016 | 7 | 15 | 5 | 19 | 16-0050086 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 62404 | 2.6454 | 222_84 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 05:19:00 | 594 | 14.1102 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C9687 | 4.56 | 2017-01-06T11:58:00Z | 8.99 | 9 | < 25mph |  |  |  | 0 | 0 | No data | C9687 | 4.56 | 2017-01-06T12:58:00Z | 12.01 | 21 | < 25mph
PG&E | 2018-10-24 | 7:08 | 37.9475 | -120.2671 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SCOTT PITTMAN 209-768-8182 TCU INCIDENT# 012528 | 101047865 | Unknown | 17000 | Conductor | Overhead | Yes | 43397 | 7:08 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1949 | 2018 | 10 | 24 | 7 | 8 | 18-0093599 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 13433 | 8.6394 | 231_236 | <25mph | <15mph | HFTD - Distribution | 2018-10-24 07:08:00 | 1688 | 12.0171 | FALSE | <25mph | C3161 | 2.32 | 2017-10-16T19:00:00Z | 7 | 4 | < 25mph | C3161 | 2.32 | 2017-10-16T19:00:00Z | 7 | 4 | < 25mph | C3161 | 2.32 | 2017-10-16T19:45:00Z | 10 | 8 | < 25mph | C3161 | 2.32 | 2017-10-16T19:45:00Z | 10 | 8 | < 25mph
PG&E | 2015-07-01 09:17 | 2015-07-01 09:17 | 38.5715 | -122.5443 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42186.3868 | 2015-07-01 09:17 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0433 | 2015 | 7 | 1 | 9 | 17 | 15-0044529 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 85168 | 0.56943 | 133_271 | <25mph | <15mph | HFTD - Distribution | 2015-07-01 09:17:00 | 178 | 20.9979 | FALSE | <25mph | E2050 | 3.6 | 2016-03-20T04:47:00Z | 3 | 4 | < 25mph | AT925 | 5.49 | 2016-03-20T03:49:00Z | 4 | 33 | < 25mph | E2050 | 3.6 | 2016-03-20T05:17:00Z | 4 | 7 | < 25mph | AT925 | 5.49 | 2016-03-20T05:39:00Z | 8.01 | 64 | < 25mph
PG&E | 2016-07-15 14:09 | 2016-07-15 14:09 | 38.6965 | -120.8598 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412774 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.5896 | 2016-07-15 14:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0852 | 2016 | 7 | 15 | 14 | 9 | 16-0050274 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 11253 | 10.7453 | 205_277 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 14:09:00 | 595 | 14.2057 | FALSE | <25mph | PG027 | 3.79 | 2019-08-30T11:30:00Z | 3.74 | 19 | < 25mph | PG181 | 5.82 | 2019-08-30T11:20:00Z | 5.26 | 78 | < 25mph | PG027 | 3.79 | 2019-08-30T11:50:00Z | 4.38 | 37 | < 25mph | PG181 | 5.82 | 2019-08-30T11:20:00Z | 5.26 | 156 | < 25mph
PG&E | 2018-09-01 | 14:25 | 36.8088 | -121.5916 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Twr 35/222 | None | 115000 | Conductor | Overhead | Yes | 43344 | 14:25 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1875 | 2018 | 9 | 1 | 14 | 25 | INT-11331 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 702145 | 13.8683 | 173_173 | <25mph | <15mph | HFTD - Transmission | 2018-09-01 14:25:00 | 1614 | 16.3299 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2019-04-20 | 6:57 | 37.8686 | -121.6843 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | East County FD | Unknown |  | 17000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-321 | 2019 | 4 | 20 | 6 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 39.0116 | 170_232 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-20 06:57:00 | 1744 | 39.0116 | FALSE | 25-40mph | D3588 | 2.98 | 2019-06-14T01:57:00Z | 13 | 1 | < 25mph | KC83 | 4.32 | 2019-06-14T01:40:00Z | 28.77 | 103 | 25-40mph | D3588 | 2.98 | 2019-06-14T02:57:00Z | 14 | 2 | < 25mph | KC83 | 4.32 | 2019-06-14T02:40:00Z | 32.21 | 204 | 25-40mph
PG&E | 2015-04-02 09:44 | 2015-04-02 09:44 | 39.6772 | -121.492 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100338726 |  | 12000 | Conductor | Overhead | Yes | 42096.4056 | 2015-04-02 09:44 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0284 | 2015 | 4 | 2 | 9 | 44 | 15-0023747 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 100204 | 15.7458 | 178_332 | <25mph | <15mph | HFTD - Distribution | 2015-04-02 09:44:00 | 30 | 15.7458 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JBGC1 | 4.06 | 2015-12-12T13:13:00Z | 17 | 1 | < 25mph |  |  |  | 0 | 0 | No data | JBGC1 | 4.06 | 2015-12-12T13:13:00Z | 17 | 2 | < 25mph
PG&E | 2017-07-01 04:43 | 3:12 | 38.1952 | -122.9197 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103855493 | Unknown | 12000 | Conductor | Overhead | Yes | 42917.1963 | 3:12 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1214 | 2017 | 7 | 1 | 3 | 12 | 17-0059935 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 41370 | 14.0388 | 116_251 | <25mph | <15mph | HFTD - Distribution | 2017-07-01 03:12:00 | 951 | 27.9197 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PTRCA | 7.17 | 2015-02-07T08:20:00Z | 36.31 | 7 | 25-40mph |  |  |  | 0 | 0 | No data | PTRCA | 7.17 | 2015-02-07T08:40:00Z | 36.89 | 14 | 25-40mph
PG&E | 2019-07-15 | 7:51 | 38.3266 | -122.568 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 42721104 |  | 12000 | Conductor | Overhead | Yes | 43661 | 7:51 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-343 | 2019 | 7 | 15 | 7 | 51 | 19-0077351 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2348 | 31.0114 | 132_257 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-07-15 07:51:00 | 1903 | 35.3209 | FALSE | 25-40mph | PG562 | 2.12 | 2019-12-04T10:50:00Z | 13.15 | 24 | < 25mph | PG562 | 2.12 | 2019-12-04T10:50:00Z | 13.15 | 106 | < 25mph | PG177 | 1.33 | 2019-12-04T11:50:00Z | 14.03 | 48 | < 25mph | PG177 | 1.33 | 2019-12-04T11:50:00Z | 14.03 | 212 | < 25mph
PG&E | 2017-10-16 | 12:10 | 36.5831 | -121.9368 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101781248 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43024 | 12:10 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | Other/Unknown | 1493 | 2017 | 10 | 16 | 12 | 10 | 17-0087767 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 6313 | 5.0415 | 158_161 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:10:00 | 1236 | 13.6905 | FALSE | <25mph | E8505 | 1.61 | 2016-05-01T20:09:00Z | 30 | 56 | 25-40mph | E8505 | 1.61 | 2016-05-01T20:09:00Z | 30 | 60 | 25-40mph | E8505 | 1.61 | 2016-05-01T20:39:00Z | 38.99 | 107 | 25-40mph | E8505 | 1.61 | 2016-05-01T20:39:00Z | 38.99 | 116 | 25-40mph
PG&E | 2015-09-24 13:56 | 2015-09-24 13:56 | 39.3508 | -121.2454 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 9692 Rices-Texas Hill rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42271.5806 | 2015-09-24 13:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0614 | 2015 | 9 | 24 | 13 | 56 | 15-0063159 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 51917 | 10.3419 | 189_313 | <25mph | <15mph | HFTD - Distribution | 2015-09-24 13:56:00 | 359 | 13.3743 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BNGC1 | 7.8 | 2016-05-09T17:51:00Z | 8.99 | 2 | < 25mph |  |  |  | 0 | 0 | No data | BNGC1 | 7.8 | 2016-05-09T18:51:00Z | 11.01 | 4 | < 25mph
PG&E | 2018-06-23 | 9:31 | 40.8632 | -122.3962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | RYAN MEANS 530-238-2416 | 101472252 | AT&T | 12000 | Conductor | Overhead | Yes | 43274 | 9:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1688 | 2018 | 6 | 23 | 9 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2018-06-23 09:31:00 | NA | 0 | FALSE | <25mph | CTANT | 1.62 | 2019-12-10T19:15:00Z | 5.37 | 10 | < 25mph | CTVOL | 5.6 | 2019-12-10T19:13:00Z | 6.26 | 22 | < 25mph | CTANT | 1.62 | 2019-12-10T19:15:00Z | 5.37 | 20 | < 25mph | CTVOL | 5.6 | 2019-12-10T20:58:00Z | 9.17 | 43 | < 25mph
PG&E | 2019-06-19 | 11:44 | 39.8612 | -121.6907 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100400933 |  | 12000 | Conductor | Overhead | Yes | 43635 | 11:44 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-224 | 2019 | 6 | 19 | 11 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.9144 | 170_342 | <25mph | <15mph | HFTD - Distribution | 2019-06-19 11:44:00 | 1855 | 12.1329 | FALSE | <25mph | C8878 | 2.27 | 2016-09-29T05:33:00Z | 0 | 13 | < 25mph | CSTC1 | 4.21 | 2016-09-29T04:51:00Z | 13 | 14 | < 25mph | C8878 | 2.27 | 2016-09-29T06:33:00Z | 0 | 25 | < 25mph | CSTC1 | 4.21 | 2016-09-29T05:51:00Z | 13 | 27 | < 25mph
PG&E | 2018-09-24 | 0:35 | 39.8152 | -121.6438 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Pole 3/42B | None | 60000 | Conductor | Overhead | Yes | 43367 | 0:35 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1913 | 2018 | 9 | 24 | 0 | 35 | INT-11388 | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 2407691 | 10.8571 | 172_339 | <25mph | <15mph | HFTD - Transmission | 2018-09-24 00:35:00 | 1652 | 11.6135 | FALSE | <25mph | E4833 | 2.09 | 2016-04-11T13:40:00Z | 0 | 24 | < 25mph | CSTC1 | 7.71 | 2016-04-11T12:51:00Z | 4.99 | 32 | < 25mph | E4833 | 2.09 | 2016-04-11T14:43:00Z | 0 | 47 | < 25mph | CSTC1 | 7.71 | 2016-04-11T12:51:00Z | 4.99 | 67 | < 25mph
PG&E | 2018-09-14 | 15:08 | 35.328 | -120.6982 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Sean Hernandez Cell # 805 903 3423 | 103400199 | Unknown | 12000 | Conductor | Overhead | Yes | 43357 | 15:08 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1898 | 2018 | 9 | 14 | 15 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 24.1105 | 213_92 | <25mph | <15mph | HFTD - Distribution | 2018-09-14 15:08:00 | 1637 | 24.1304 | FALSE | <25mph | ARGC1 | 2.05 | 2015-06-10T15:54:00Z | 7 | 1 | < 25mph | E6113 | 7.29 | 2015-06-10T15:17:00Z | 13 | 5 | < 25mph | ARGC1 | 2.05 | 2015-06-10T16:54:00Z | 8.99 | 2 | < 25mph | E6113 | 7.29 | 2015-06-10T15:17:00Z | 13 | 9 | < 25mph
PG&E | 2017-10-23 | 21:24 | 37.3713 | -122.348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100270421 | Unknown | 12000 | Conductor | Overhead | Yes | 43031 | 21:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1507 | 2017 | 10 | 23 | 21 | 24 | 17-0089820 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1768 | 13.1103 | 140_205 | <25mph | <15mph | HFTD - Distribution | 2017-10-23 21:24:00 | 1249 | 22.0037 | FALSE | <25mph | E4551 | 1.61 | 2015-06-30T07:32:00Z | 1.01 | 6 | < 25mph | PUGC1 | 7.55 | 2015-06-30T07:18:00Z | 5.99 | 20 | < 25mph | E4551 | 1.61 | 2015-06-30T08:02:00Z | 1.01 | 11 | < 25mph | PUGC1 | 7.55 | 2015-06-30T07:18:00Z | 5.99 | 38 | < 25mph
PG&E | 2017-08-28 | 14:06 | 38.634 | -122.4194 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102253236 | Unknown | 21000 | Conductor | Overhead | Yes | 42975 | 14:06 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1359 | 2017 | 8 | 28 | 14 | 6 | 17-0073526 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 1896 | 12.4455 | 138_274 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 14:06:00 | 1097 | 13.1602 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AT925 | 4.29 | 2016-05-25T11:34:00Z | 1.01 | 9 | < 25mph |  |  |  | 0 | 0 | No data | AT925 | 4.29 | 2016-05-25T12:19:00Z | 1.01 | 19 | < 25mph
PG&E | 2019-06-18 | 19:49 | 35.8876 | -120.9217 | Bird Found | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Pole | Overhead | Yes | 43634 | 19:49 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | no-match | 2019-55 | 2019 | 6 | 18 | 19 | 49 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 15.5935 | 203_122 | <25mph | <15mph | HFTD - Distribution | 2019-06-18 19:49:00 | 1852 | 21.7258 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RBYC1 | 6.84 | 2017-08-15T19:12:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | RBYC1 | 6.84 | 2017-08-15T20:12:00Z | 8.99 | 2 | < 25mph
PG&E | 2016-06-21 | 2016-06-21 16:53 | 38.4233 | -122.5448 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | KENWOOD FIRE XST | 102036904 | Yes | 0 – 750 | Conductor | Overhead | Yes | 42542 | 2016-06-21 16:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0814 | 2016 | 6 | 21 | 16 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 14.0146 | 133_263 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 16:53:00 | 556 | 14.0381 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG091 | 4.97 | 2018-10-22T23:10:00Z | 12.06 | 21 | < 25mph |  |  |  | 0 | 0 | No data | PG091 | 4.97 | 2018-10-22T23:10:00Z | 12.06 | 41 | < 25mph
PG&E | 2015-06-06 15:38 | 2015-06-06 15:38 | 39.0409 | -123.4019 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 11480 ANDERSON VALLEY WAY @ BRIDGE |  | 12000 | Conductor | Overhead | Yes | 42161.6514 | 2015-06-06 15:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0355 | 2015 | 6 | 6 | 15 | 38 | 15-0039056 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 1748 | 19.2204 | 97_298 | <25mph | <15mph | HFTD - Distribution | 2015-06-06 15:38:00 | 101 | 19.2204 | FALSE | <25mph | PG252 | 2.47 | 2019-09-06T13:20:00Z | 5.7 | 9 | < 25mph | BNVC1 | 4.68 | 2019-09-06T12:50:00Z | 11.01 | 24 | < 25mph | PG252 | 2.47 | 2019-09-06T14:30:00Z | 7.96 | 18 | < 25mph | BNVC1 | 4.68 | 2019-09-06T12:50:00Z | 11.01 | 48 | < 25mph
PG&E | 2018-07-28 | 6:51 | 38.7473 | -120.7866 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101418155 | AT&T | 21000 | Conductor | Overhead | Yes | 43309 | 6:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1794 | 2018 | 7 | 28 | 6 | 51 | 18-0064545 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 15429 | 14.6813 | 209_280 | <25mph | <15mph | HFTD - Distribution | 2018-07-28 06:51:00 | 1534 | 14.6813 | FALSE | <25mph | AV185 | 2.88 | 2018-01-14T05:30:00Z | 0 | 5 | < 25mph | E3165 | 4.37 | 2018-01-14T06:26:00Z | 4.99 | 95 | < 25mph | AV185 | 2.88 | 2018-01-14T06:30:00Z | 0 | 10 | < 25mph | E3165 | 4.37 | 2018-01-14T06:36:00Z | 4.99 | 191 | < 25mph
PG&E | 2018-06-19 | 0:27 | 38.7604 | -120.8224 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101388356 | Unknown | 12000 | Conductor | Overhead | Yes | 43270 | 0:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1675 | 2018 | 6 | 19 | 0 | 27 | 18-0052111 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 141652 | 7.2853 | 207_281 | <25mph | <15mph | HFTD - Distribution | 2018-06-19 00:27:00 | 1417 | 13.5304 | FALSE | <25mph | E5691 | 1.82 | 2015-12-31T04:41:00Z | 0 | 13 | < 25mph | C5121 | 4.69 | 2015-12-31T04:13:00Z | 3 | 55 | < 25mph | E5691 | 1.82 | 2015-12-31T05:36:00Z | 3 | 25 | < 25mph | E5691 | 1.82 | 2015-12-31T05:36:00Z | 3 | 107 | < 25mph
PG&E | 2017-09-20 | 2:06 | 37.2597 | -122.3222 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100322388 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42998 | 2:06 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1424 | 2017 | 9 | 20 | 2 | 6 | 17-0080179 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 36593 | 8.989 | 141_198 | <25mph | <15mph | HFTD - Distribution | 2017-09-20 02:06:00 | 1162 | 20.1127 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.84 | 2017-10-12T11:07:00Z | 11.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.84 | 2017-10-12T11:07:00Z | 11.01 | 2 | < 25mph
PG&E | 2018-07-01 | 8:13 | 39.4154 | -121.5122 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430344 | AT&T | 12000 | Conductor | Overhead | Yes | 43282 | 8:13 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1720 | 2018 | 7 | 1 | 8 | 13 | 18-0056061 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 7848 | 6.5616 | 178_317 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 08:13:00 | 1461 | 14.6967 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BNGC1 | 7.14 | 2017-11-29T07:51:00Z | 3 | 2 | < 25mph |  |  |  | 0 | 0 | No data | BNGC1 | 7.14 | 2017-11-29T08:51:00Z | 4 | 4 | < 25mph
PG&E | 2015-02-23 13:25 | 2015-02-23 13:25 | 38.5046 | -122.7408 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RINCON VALLEY | BEHIND 4870 CARRIAGE LN SANTA ROSA |  | 12000 | Conductor | Overhead | Yes | 42058.559 | 2015-02-23 13:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0268 | 2015 | 2 | 23 | 13 | 25 | 15-0015168 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 85762 | 20.3218 | 124_267 | <25mph | <15mph | HFTD - Distribution | 2015-02-23 13:25:00 | 15 | 32.6885 | FALSE | 25-40mph | RSAC1 | 2.39 | 2015-12-28T13:29:00Z | 4.99 | 13 | < 25mph | E1582 | 6.75 | 2015-12-28T12:53:00Z | 5.99 | 95 | < 25mph | RSAC1 | 2.39 | 2015-12-28T14:29:00Z | 4.99 | 26 | < 25mph | E1582 | 6.75 | 2015-12-28T12:53:00Z | 5.99 | 188 | < 25mph
PG&E | 2019-06-08 | 18:51 | 38.6105 | -122.9732 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 42751113 |  | 12000 | Conductor | Overhead | Yes | 43624 | 18:51 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-355 | 2019 | 6 | 8 | 18 | 51 | 19-0064689 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 44664 | 14.8219 | 114_273 | <25mph | <15mph | HFTD - Distribution | 2019-06-08 18:51:00 | 1812 | 19.8533 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GYWWW | 6.75 | 2018-09-18T18:00:00Z | 7.29 | 23 | < 25mph |  |  |  | 0 | 0 | No data | GYWWW | 6.75 | 2018-09-18T19:00:00Z | 7.61 | 46 | < 25mph
PG&E | 2018-06-11 | 17:49 | 34.7329 | -120.0861 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103015183 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43262 | 17:49 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1649 | 2018 | 6 | 11 | 17 | 49 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 16.7571 | 241_59 | <25mph | <15mph | HFTD - Distribution | 2018-06-11 17:49:00 | 1391 | 18.839 | FALSE | <25mph | PG214 | 2.52 | 2019-11-11T00:40:00Z | 13.87 | 19 | < 25mph | TT480 | 7.53 | 2019-11-11T00:20:00Z | 14 | 28 | < 25mph | PG214 | 2.52 | 2019-11-11T00:40:00Z | 13.87 | 38 | < 25mph | TT480 | 7.53 | 2019-11-11T00:20:00Z | 14 | 56 | < 25mph
PG&E | 2016-06-15 | 2016-06-15 13:09 | 38.4433 | -120.7568 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103169620 |  | 12000 | Conductor | Overhead | Yes | 42536 | 2016-06-15 13:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0801 | 2016 | 6 | 15 | 13 | 9 | 16-0043476 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 23963 | 15.7348 | 210_263 | <25mph | <15mph | HFTD - Distribution | 2016-06-15 13:09:00 | 543 | 16.8625 | FALSE | <25mph | PG116 | 2.93 | 2018-10-30T21:50:00Z | 13.8 | 7 | < 25mph | KJAQ | 5.02 | 2018-10-30T21:55:00Z | 16.11 | 22 | < 25mph | PG116 | 2.93 | 2018-10-30T21:50:00Z | 13.8 | 18 | < 25mph | MTZC1 | 6.74 | 2018-10-30T22:56:00Z | 18.01 | 49 | < 25mph
PG&E | 2018-07-14 | 12:40 | 38.5793 | -122.878 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103122744 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 12:40 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1746 | 2018 | 7 | 14 | 12 | 40 | 18-0059799 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20804 | 12.0574 | 118_272 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 12:40:00 | 1486 | 14.4502 | FALSE | <25mph | F39WW | 2.3 | 2019-09-08T05:15:00Z | 14.5 | 19 | < 25mph | PG549 | 6.76 | 2019-09-08T05:20:00Z | 26.15 | 116 | 25-40mph | F39WW | 2.3 | 2019-09-08T05:15:00Z | 14.5 | 37 | < 25mph | PG549 | 6.76 | 2019-09-08T05:20:00Z | 26.15 | 229 | 25-40mph
PG&E | 2017-12-07 12:26 | 12:25 | 34.7115 | -120.1772 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 015/220 | Unknown | 115000 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1534 | 2017 | 12 | 7 | 12 | 25 | 17-0097211 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 4.373 | 237_58 | <25mph | <15mph | HFTD - Transmission | 2017-12-07 12:25:00 | 1276 | 13.3077 | FALSE | <25mph |  |  |  | 0 | 0 | No data | UCSE | 7.79 | 2015-06-30T09:00:00Z | 4.7 | 13 | < 25mph |  |  |  | 0 | 0 | No data | UCSE | 7.79 | 2015-06-30T09:40:00Z | 5.21 | 26 | < 25mph
PG&E | 2019-07-23 | 16:55 | 37.2128 | -119.505 | Gun Shot | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | 252521103 |  | 12000 | Conductor | Overhead | Yes | 43669 | 16:55 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-434 | 2019 | 7 | 23 | 16 | 55 | 19-0080383 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 513358 | 13.6168 | 265_196 | <25mph | <15mph | HFTD - Distribution | 2019-07-23 16:55:00 | 1923 | 13.6168 | FALSE | <25mph | NFRC1 | 1.4 | 2019-07-03T07:55:00Z | 8.01 | 2 | < 25mph | PG389 | 7.63 | 2019-07-03T07:00:00Z | 12.28 | 9 | < 25mph | NFRC1 | 1.4 | 2019-07-03T08:55:00Z | 8.01 | 4 | < 25mph | PG389 | 7.63 | 2019-07-03T07:00:00Z | 12.28 | 17 | < 25mph
PG&E | 2019-05-24 | 15:03 | 35.1696 | -120.5103 |  | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 40589503 |  | 500000 | Pole | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-100 | 2019 | 5 | 24 | 15 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 14.866 | 222_83 | <25mph | <15mph | HFTD - Transmission | 2019-05-24 15:03:00 | 1780 | 15.7146 | FALSE | <25mph | C9687 | 3.56 | 2018-01-20T14:29:00Z | 4 | 4 | < 25mph | F0194 | 5.22 | 2018-01-20T14:34:00Z | 8.99 | 27 | < 25mph | C9687 | 3.56 | 2018-01-20T15:44:00Z | 5.99 | 8 | < 25mph | F0194 | 5.22 | 2018-01-20T14:34:00Z | 8.99 | 56 | < 25mph
PG&E | 2018-02-12 | 20:20 | 39.9395 | -121.6494 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430947 | Unknown | 12000 | Conductor | Overhead | Yes | 43143 | 20:20 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1561 | 2018 | 2 | 12 | 20 | 20 | 18-0013604 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 149212 | 10.1876 | 172_346 | <25mph | <15mph | HFTD - Distribution | 2018-02-12 20:20:00 | 1303 | 14.6044 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CSTC1 | 7.88 | 2018-06-10T04:51:00Z | 21 | 20 | < 25mph |  |  |  | 0 | 0 | No data | CSTC1 | 7.88 | 2018-06-10T04:51:00Z | 21 | 39 | < 25mph
PG&E | 2017-07-07 | 15:09 | 40.9054 | -122.3806 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101455950 | Unknown | 12000 | Conductor | Overhead | Yes | 42923 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1229 | 2017 | 7 | 7 | 15 | 9 | 17-0061903 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.0906 | 142_400 | <25mph | <15mph | HFTD - Distribution | 2017-07-07 15:09:00 | 969 | 11.4161 | FALSE | <25mph | CTANT | 2.76 | 2015-07-13T07:00:00Z | 11.18 | 9 | < 25mph | CTANT | 2.76 | 2015-07-13T07:00:00Z | 11.18 | 9 | < 25mph | CTANT | 2.76 | 2015-07-13T07:45:00Z | 11.18 | 16 | < 25mph | CTANT | 2.76 | 2015-07-13T07:45:00Z | 11.18 | 16 | < 25mph
PG&E | 2015-07-26 12:25 | 2015-07-26 12:25 | 39.1586 | -121.0634 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 15499 ALLISON RANCH RD |  | 12000 | Conductor | Overhead | Yes | 42211.5174 | 2015-07-26 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0485 | 2015 | 7 | 26 | 12 | 25 | 15-0050558 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2224 | 13.0644 | 197_303 | <25mph | <15mph | HFTD - Distribution | 2015-07-26 12:25:00 | 230 | 13.6917 | FALSE | <25mph | E1789 | 3.9 | 2019-10-09T17:00:00Z | 5.99 | 10 | < 25mph | PG429 | 7.31 | 2019-10-09T16:30:00Z | 6.8 | 37 | < 25mph | E1789 | 3.9 | 2019-10-09T17:36:00Z | 10 | 20 | < 25mph | E1789 | 3.9 | 2019-10-09T17:36:00Z | 10 | 77 | < 25mph
PG&E | 2016-07-20 19:15 | 2016-07-20 19:15 | 37.7712 | -121.8104 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100898986 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42571.8021 | 2016-07-20 19:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0865 | 2016 | 7 | 20 | 19 | 15 | 16-0051308 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3013 | 17.1873 | 164_226 | <25mph | <15mph | HFTD - Distribution | 2016-07-20 19:15:00 | 608 | 18.9944 | FALSE | <25mph | LVMC1 | 3.62 | 2016-08-12T17:02:00Z | 7 | 1 | < 25mph | VAQC1 | 4.3 | 2016-08-12T17:45:00Z | 17 | 48 | < 25mph | LVMC1 | 3.62 | 2016-08-12T18:02:00Z | 8.01 | 2 | < 25mph | VAQC1 | 4.3 | 2016-08-12T17:45:00Z | 17 | 94 | < 25mph
PG&E | 2018-08-21 | 10:13 | 38.6972 | -120.889 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101385436 | Unknown | 12000 | Conductor | Overhead | Yes | 43333 | 10:13 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1852 | 2018 | 8 | 21 | 10 | 13 | 18-0072055 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4572 | 5.9109 | 204_277 | <25mph | <15mph | HFTD - Distribution | 2018-08-21 10:13:00 | 1591 | 12.0437 | FALSE | <25mph | C6129 | 2.16 | 2016-08-03T19:49:00Z | 17 | 26 | < 25mph | C6129 | 2.16 | 2016-08-03T19:49:00Z | 17 | 72 | < 25mph | C6129 | 2.16 | 2016-08-03T19:49:00Z | 17 | 54 | < 25mph | C6129 | 2.16 | 2016-08-03T19:49:00Z | 17 | 145 | < 25mph
PG&E | 2016-08-30 | 2016-08-30 16:01 | 36.5941 | -121.9212 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Unknown | 101734977 |  | 21000 | Conductor | Overhead | Yes | 42612 | 2016-08-30 16:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0951 | 2016 | 8 | 30 | 16 | 1 | 16-0061130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 199327 | 14.6893 | 159_162 | <25mph | <15mph | HFTD - Distribution | 2016-08-30 16:01:00 | 694 | 14.6893 | FALSE | <25mph | D4637 | 3.09 | 2019-04-30T06:02:00Z | 18.01 | 32 | < 25mph | D4637 | 3.09 | 2019-04-30T06:02:00Z | 18.01 | 36 | < 25mph | D4637 | 3.09 | 2019-04-30T07:30:00Z | 18.99 | 61 | < 25mph | D4637 | 3.09 | 2019-04-30T07:30:00Z | 18.99 | 69 | < 25mph
PG&E | 2019-05-31 | 15:25 | 40.4431 | -121.8211 |  | Hardwood Woodland | 1 meter - < 3 meters | Self Extinguished |  | 101556319 |  | 12000 | Conductor | Overhead | Yes | 43616 | 15:25 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-88 | 2019 | 5 | 31 | 15 | 25 | 19-0060901 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 55546 | 8.5736 | 165_374 | <25mph | <15mph | HFTD - Distribution | 2019-05-31 15:25:00 | 1795 | 18.5418 | FALSE | <25mph | PG130 | 1.76 | 2019-03-08T04:40:00Z | 6.13 | 6 | < 25mph | PG193 | 6.12 | 2019-03-08T05:00:00Z | 8.12 | 18 | < 25mph | PG130 | 1.76 | 2019-03-08T06:10:00Z | 8.12 | 12 | < 25mph | PG193 | 6.12 | 2019-03-08T05:30:00Z | 12.93 | 36 | < 25mph
PG&E | 2018-08-20 | 9:34 | 39.8014 | -121.5813 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100400441 | Unknown | 12000 | Conductor | Overhead | Yes | 43332 | 9:34 | Contact From Object | N.A. | Other | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1849 | 2018 | 8 | 20 | 9 | 34 | 18-0071596 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 394259 | 5.4464 | 175_338 | <25mph | <15mph | HFTD - Distribution | 2018-08-20 09:34:00 | 1588 | 11.8754 | FALSE | <25mph | C4565 | 3.06 | 2017-10-26T08:03:00Z | 2.01 | 6 | < 25mph | JBGC1 | 6.67 | 2017-10-26T07:13:00Z | 20 | 20 | < 25mph | C4565 | 3.06 | 2017-10-26T09:03:00Z | 2.01 | 12 | < 25mph | JBGC1 | 6.67 | 2017-10-26T08:13:00Z | 27 | 40 | 25-40mph
PG&E | 2017-10-10 | 13:36 | 38.931 | -123.3023 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 102214553 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43018 | 13:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1481 | 2017 | 10 | 10 | 13 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.7263 | 101_291 | <25mph | <15mph | HFTD - Distribution | 2017-10-10 13:36:00 | 1224 | 17.0479 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BNVC1 | 4.62 | 2017-04-19T08:50:00Z | 8.99 | 7 | < 25mph |  |  |  | 0 | 0 | No data | BNVC1 | 4.62 | 2017-04-19T09:50:00Z | 10 | 13 | < 25mph
PG&E | 2017-08-28 | 9:14 | 38.7443 | -122.6491 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 103781085 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42975 | 9:14 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1356 | 2017 | 8 | 28 | 9 | 14 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 4.693 | 128_281 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 09:14:00 | 1094 | 16.6198 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E0674 | 6.69 | 2015-04-08T12:49:00Z | 0 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E0674 | 6.69 | 2015-04-08T13:49:00Z | 0 | 8 | < 25mph
PG&E | 2016-09-22 | 13:53 | 40.224 | -122.3417 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101539450 | None | 12000 | Conductor | Overhead | Yes | 42635 | 13:53 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0996 | 2016 | 9 | 22 | 13 | 53 | 16-0066692 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 14706 | 14.6017 | 143_362 | <25mph | <15mph | HFTD - Distribution | 2016-09-22 13:53:00 | 739 | 20.1469 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-12-12 | 12:09 | 38.727 | -120.7947 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 101404403 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43446 | 12:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1984 | 2018 | 12 | 12 | 12 | 9 | No ILIS or TOTL available | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.1462 | 208_279 | <25mph | <15mph | HFTD - Distribution | 2018-12-12 12:09:00 | 1724 | 13.5134 | FALSE | <25mph | E6490 | 3.26 | 2017-06-20T01:41:00Z | 7 | 35 | < 25mph | E6490 | 3.26 | 2017-06-20T01:41:00Z | 7 | 53 | < 25mph | E6490 | 3.26 | 2017-06-20T01:41:00Z | 7 | 70 | < 25mph | E6490 | 3.26 | 2017-06-20T01:41:00Z | 7 | 106 | < 25mph
PG&E | 2016-09-28 | 14:00 | 35.2145 | -118.5625 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire |  |  | 0 – 750 | Conductor | Overhead | Yes | 42641 | 14:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1008 | 2016 | 9 | 28 | 14 | 0 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.8467 | 310_87 | <25mph | <15mph | HFTD - Distribution | 2016-09-28 14:00:00 | 750 | 26.957 | FALSE | 25-40mph | UP691 | 1.1 | 2017-07-30T12:35:00Z | 8.05 | 3 | < 25mph | C8288 | 6.96 | 2017-07-30T13:08:00Z | 10 | 32 | < 25mph | UP691 | 1.1 | 2017-07-30T12:35:00Z | 8.05 | 6 | < 25mph | C8288 | 6.96 | 2017-07-30T13:08:00Z | 10 | 58 | < 25mph
PG&E | 2018-05-28 | 6:30 | 40.4382 | -122.3001 | Building | Rural | Structure Only | Unknown | N.A. | 101495757 | Unknown | 0 – 750 | conductor | Overhead | Yes | 43248 | 6:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1610 | 2018 | 5 | 28 | 6 | 30 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 17.501 | 145_374 | <25mph | <15mph | HFTD - Distribution | 2018-05-28 06:30:00 | 1352 | 26.4092 | FALSE | 25-40mph | AP525 | 2.99 | 2016-04-14T18:45:00Z | 10 | 6 | < 25mph | E6886 | 7.97 | 2016-04-14T18:39:00Z | 15.99 | 11 | < 25mph | AP525 | 2.99 | 2016-04-14T19:25:00Z | 14 | 12 | < 25mph | E6886 | 7.97 | 2016-04-14T18:39:00Z | 15.99 | 22 | < 25mph
PG&E | 2018-09-10 | 20:37 | 38.0188 | -122.7225 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 102252760 | Unknown | 12000 | Conductor | Overhead | Yes | 43353 | 20:37 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1889 | 2018 | 9 | 10 | 20 | 37 | 18-0078359 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 219903 | 12.2581 | 125_241 | <25mph | <15mph | HFTD - Distribution | 2018-09-10 20:37:00 | 1628 | 18.8462 | FALSE | <25mph | BBEC1 | 1.27 | 2016-09-26T16:11:00Z | 7 | 1 | < 25mph | WDAC1 | 4.66 | 2016-09-26T16:51:00Z | 12.01 | 14 | < 25mph | BBEC1 | 1.27 | 2016-09-26T17:11:00Z | 11.01 | 2 | < 25mph | WDAC1 | 4.66 | 2016-09-26T17:51:00Z | 12.01 | 28 | < 25mph
PG&E | 2017-09-03 | 12:52 | 37.2162 | -119.4807 | Vegetation | Rural | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103345573 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-09-03 | 12:52 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1388 | 2017 | 9 | 3 | 12 | 52 | 17-0075546 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 2362 | 10.0918 | 266_196 | <25mph | <15mph | HFTD - Distribution | 2017-09-03 12:52:00 | 1126 | 25.526 | FALSE | 25-40mph | NFRC1 | 1.81 | 2019-01-06T23:55:00Z | 8.01 | 1 | < 25mph | NFRC1 | 1.81 | 2019-01-06T23:55:00Z | 8.01 | 1 | < 25mph | NFRC1 | 1.81 | 2019-01-06T23:55:00Z | 8.01 | 3 | < 25mph | NFRC1 | 1.81 | 2019-01-06T23:55:00Z | 8.01 | 3 | < 25mph
PG&E | 2015-03-14 02:30 | 2015-03-14 02:30 | 38.9038 | -122.7579 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 9210 Wildcat Road, Kelseyville |  | 12000 | Conductor | Overhead | Yes | 42077.1042 | 2015-03-14 02:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0274 | 2015 | 3 | 14 | 2 | 30 | 15-0019556 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2280 | 8.9688 | 124_289 | <25mph | <15mph | HFTD - Distribution | 2015-03-14 02:30:00 | 20 | 8.9688 | FALSE | <25mph | KELC1 | 2.83 | 2016-03-13T18:57:00Z | 34.99 | 1 | 25-40mph | KELC1 | 2.83 | 2016-03-13T18:57:00Z | 34.99 | 6 | 25-40mph | KELC1 | 2.83 | 2016-03-13T18:57:00Z | 34.99 | 2 | 25-40mph | LKRC1 | 6.79 | 2016-03-13T20:05:00Z | 35.99 | 12 | 25-40mph
PG&E | 2017-10-16 | 12:26 | 36.6641 | -121.0995 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Nick Shawkey E4462 209-402-1645 Cover Engine from Tuolumne Calaveras Unit | 101689865 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43024 | 12:26 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1495 | 2017 | 10 | 16 | 12 | 26 | 17-0087754 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 519 | 1.3904 | 195_165 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:26:00 | 1238 | 14.8173 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1697 | 6.85 | 2018-07-09T06:22:00Z | 4.99 | 5 | < 25mph |  |  |  | 0 | 0 | No data | E1697 | 6.85 | 2018-07-09T06:22:00Z | 4.99 | 9 | < 25mph
PG&E | 2016-07-31 12:11 | 2016-07-31 12:11 | 38.7827 | -120.9168 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101417359 |  | 21000 | Conductor | Overhead | Yes | 42582.5076 | 2016-07-31 12:11 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0895 | 2016 | 7 | 31 | 12 | 11 | 16-0053949 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 10.9662 | 203_282 | <25mph | <15mph | HFTD - Distribution | 2016-07-31 12:11:00 | 638 | 14.1387 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 6.02 | 2017-02-25T17:56:00Z | 7 | 53 | < 25mph |  |  |  | 0 | 0 | No data | C6129 | 7.06 | 2017-02-25T19:24:00Z | 8.99 | 106 | < 25mph
PG&E | 2015-06-27 12:48 | 2015-06-27 12:48 | 37.9474 | -120.4274 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101034512 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.5333 | 2015-06-27 12:48 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0414 | 2015 | 6 | 27 | 12 | 48 | 15-0043755 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 150075 | 11.0891 | 224_236 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 12:48:00 | 159 | 19.6587 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2017-10-11 | 11:57 | 38.5015 | -123.0237 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101974930 | Unknown | 12000 | Conductor | Overhead | Yes | 43019 | 11:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1484 | 2017 | 10 | 11 | 11 | 57 | 17-0086350 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 226925 | 16.5068 | 112_268 | <25mph | <15mph | HFTD - Distribution | 2017-10-11 11:57:00 | 1227 | 19.0479 | FALSE | <25mph | D9841 | 2.93 | 2019-03-25T06:45:00Z | 1.01 | 19 | < 25mph | E8483 | 5.87 | 2019-03-25T06:16:00Z | 15.99 | 23 | < 25mph | D9841 | 2.93 | 2019-03-25T07:45:00Z | 1.01 | 38 | < 25mph | E8483 | 5.87 | 2019-03-25T06:16:00Z | 15.99 | 46 | < 25mph
PG&E | 2018-10-15 | 3:23 | 38.2897 | -120.5803 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103378003 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43388 | 3:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1941 | 2018 | 10 | 15 | 3 | 23 | 18-0090342 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1464 | 26.0611 | 218_255 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-15 03:23:00 | 1680 | 26.2858 | FALSE | 25-40mph | AT317 | 3.74 | 2019-04-20T21:44:00Z | 14 | 12 | < 25mph | PG148 | 5.31 | 2019-04-20T22:00:00Z | 19.06 | 46 | < 25mph | AT317 | 3.74 | 2019-04-20T22:54:00Z | 14 | 24 | < 25mph | ESPC1 | 4.93 | 2019-04-20T22:13:00Z | 20 | 92 | < 25mph
PG&E | 2016-08-02 | 2016-08-02 16:15 | 37.0312 | -119.4395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Fresno County FD | 100675986 |  | 12000 | Conductor | Overhead | Yes | 42584 | 2016-08-02 16:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0900 | 2016 | 8 | 2 | 16 | 15 | 16-0054552 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 265566 | 14.0604 | 268_186 | <25mph | <15mph | HFTD - Distribution | 2016-08-02 16:15:00 | 643 | 14.6638 | FALSE | <25mph | PG410 | 3.56 | 2019-09-22T22:30:00Z | 14.03 | 54 | < 25mph | PG586 | 6.38 | 2019-09-22T23:20:00Z | 17.83 | 102 | < 25mph | PG410 | 3.56 | 2019-09-22T22:30:00Z | 14.03 | 108 | < 25mph | PG586 | 6.38 | 2019-09-22T23:20:00Z | 17.83 | 204 | < 25mph
PG&E | 2016-08-03 | 2016-08-03 12:41 | 39.3269 | -120.6033 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100001032 |  | 12000 | Conductor | Overhead | Yes | 42585 | 2016-08-03 12:41 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0902 | 2016 | 8 | 3 | 12 | 41 | 16-0054769 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 20554 | 9.0542 | 216_312 | <25mph | <15mph | HFTD - Distribution | 2016-08-03 12:41:00 | 645 | 12.3394 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CF043 | 6.13 | 2017-03-10T02:21:00Z | 0 | 4 | < 25mph |  |  |  | 0 | 0 | No data | CF043 | 6.13 | 2017-03-10T03:21:00Z | 0 | 8 | < 25mph
PG&E | 2017-12-16 | 11:51 | 38.8171 | -122.7041 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Shawn Ohare | 102167231 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43085 | 11:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1540 | 2017 | 12 | 16 | 11 | 51 | 17-0102101 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26120 | 34.3488 | 126_285 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-12-16 11:51:00 | 1282 | 35.345 | FALSE | 25-40mph | LKRC1 | 2.09 | 2016-07-29T17:05:00Z | 4.99 | 1 | < 25mph | KELC1 | 6.55 | 2016-07-29T16:57:00Z | 11.01 | 2 | < 25mph | LKRC1 | 2.09 | 2016-07-29T18:05:00Z | 7 | 2 | < 25mph | KELC1 | 6.55 | 2016-07-29T17:57:00Z | 11.01 | 4 | < 25mph
PG&E | 2017-07-24 19:31 | 19:31 | 38.3519 | -120.7103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.8134 | 19:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1288 | 2017 | 7 | 24 | 19 | 31 | 17-0065145 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14281 | 10.3402 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 19:31:00 | 1027 | 12.2366 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2016-01-09T16:56:00Z | 14 | 3 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2016-01-09T16:56:00Z | 14 | 6 | < 25mph
PG&E | 2019-09-28 | 13:16 | 37.2553 | -119.5057 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 252531103 |  | 12000 | Conductor | Overhead | Yes | 43736 | 13:16 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-36 | 2019 | 9 | 28 | 13 | 16 | 19-0104972 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 1296 | 12.1111 | 265_198 | <25mph | <15mph | HFTD - Distribution | 2019-09-28 13:16:00 | 2064 | 13.545 | FALSE | <25mph | C6459 | 1.57 | 2016-12-23T17:20:00Z | 14 | 4 | < 25mph | D7778 | 7.57 | 2016-12-23T17:13:00Z | 20 | 29 | < 25mph | NFRC1 | 1.54 | 2016-12-23T17:55:00Z | 18.99 | 8 | < 25mph | D7778 | 7.57 | 2016-12-23T17:13:00Z | 20 | 71 | < 25mph
PG&E | 2017-07-05 12:11 | 11:58 | 39.2105 | -121.2266 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVE ROBERTSON 530 906 4892 | 100010286 | Unknown | 21000 | Conductor | Overhead | Yes | 42921.5077 | 11:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1223 | 2017 | 7 | 5 | 11 | 58 | 17-0060605 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 10231 | 9.71 | 190_306 | <25mph | <15mph | HFTD - Distribution | 2017-07-05 11:58:00 | 962 | 14.0848 | FALSE | <25mph | E2572 | 2.49 | 2016-10-19T11:03:00Z | 2.01 | 13 | < 25mph | E1789 | 6.76 | 2016-10-19T11:30:00Z | 4 | 30 | < 25mph | E2572 | 2.49 | 2016-10-19T11:03:00Z | 2.01 | 25 | < 25mph | E1789 | 6.76 | 2016-10-19T11:30:00Z | 4 | 58 | < 25mph
PG&E | 2015-04-02 09:44 | 2015-04-02 09:44 | 39.6772 | -121.492 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100338726 |  | 12000 | Conductor | Overhead | Yes | 42096.4056 | 2015-04-02 09:44 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0284 | 2015 | 4 | 2 | 9 | 44 | 15-0023747 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 100204 | 15.7458 | 178_332 | <25mph | <15mph | HFTD - Distribution | 2015-04-02 09:44:00 | 30 | 15.7458 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JBGC1 | 4.06 | 2015-10-20T17:13:00Z | 22.01 | 11 | < 25mph |  |  |  | 0 | 0 | No data | JBGC1 | 4.06 | 2015-10-20T18:13:00Z | 22.01 | 22 | < 25mph
PG&E | 2017-10-16 | 12:26 | 36.6641 | -121.0995 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Nick Shawkey E4462 209-402-1645 Cover Engine from Tuolumne Calaveras Unit | 101689865 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43024 | 12:26 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1495 | 2017 | 10 | 16 | 12 | 26 | 17-0087754 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 519 | 1.3904 | 195_165 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:26:00 | 1238 | 14.8173 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1697 | 6.85 | 2015-06-28T17:55:00Z | 8.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E1697 | 6.85 | 2015-06-28T18:40:00Z | 8.99 | 8 | < 25mph
PG&E | 2019-09-11 | 21:03 | 38.3132 | -120.9809 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 163341103 |  | 12000 | Conductor | Overhead | Yes | 43719 | 21:03 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-370 | 2019 | 9 | 11 | 21 | 3 | 19-0098003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25994 | 11.7888 | 200_256 | <25mph | <15mph | HFTD - Distribution | 2019-09-11 21:03:00 | 2035 | 13.1911 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 5.36 | 2016-06-07T19:05:00Z | 10 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 5.36 | 2016-06-07T20:05:00Z | 11.01 | 2 | < 25mph
PG&E | 2016-09-23 05:23 | 15:23 | 39.3784 | -121.0922 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100091491 | None | 12000 | Conductor | Overhead | Yes | 42636.2243 | 15:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0999 | 2016 | 9 | 23 | 15 | 23 | 16-0067089 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 80185 | 10.9717 | 195_315 | <25mph | <15mph | HFTD - Distribution | 2016-09-23 15:23:00 | 741 | 11.3047 | FALSE | <25mph | E3651 | 3.67 | 2018-01-08T22:55:00Z | 2.01 | 12 | < 25mph | RRRC1 | 5.34 | 2018-01-08T23:13:00Z | 4.99 | 13 | < 25mph | E3651 | 3.67 | 2018-01-08T22:55:00Z | 2.01 | 24 | < 25mph | RRRC1 | 5.34 | 2018-01-09T00:13:00Z | 5.99 | 26 | < 25mph
PG&E | 2018-09-14 | 15:08 | 35.328 | -120.6982 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Sean Hernandez Cell # 805 903 3423 | 103400199 | Unknown | 12000 | Conductor | Overhead | Yes | 43357 | 15:08 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1898 | 2018 | 9 | 14 | 15 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 24.1105 | 213_92 | <25mph | <15mph | HFTD - Distribution | 2018-09-14 15:08:00 | 1637 | 24.1304 | FALSE | <25mph | PG119 | 3.27 | 2019-06-06T10:40:00Z | 7.25 | 7 | < 25mph | PG223 | 4.41 | 2019-06-06T09:50:00Z | 9.22 | 33 | < 25mph | PG119 | 3.27 | 2019-06-06T11:20:00Z | 10.29 | 14 | < 25mph | PG223 | 4.41 | 2019-06-06T11:40:00Z | 11.83 | 65 | < 25mph
PG&E | 2015-06-27 21:15 | 2015-06-27 21:15 | 39.2699 | -121.0403 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 16151 INDAIN FLAT RD |  | 12000 | Conductor | Overhead | Yes | 42182.8854 | 2015-06-27 21:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0416 | 2015 | 6 | 27 | 21 | 15 | 15-0043789 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4210 | 5.8168 | 198_309 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 21:15:00 | 161 | 11.6482 | FALSE | <25mph | E6355 | 3.61 | 2015-10-30T00:59:00Z | 8.99 | 47 | < 25mph | RRRC1 | 4.73 | 2015-10-30T01:13:00Z | 12.01 | 73 | < 25mph | E6355 | 3.61 | 2015-10-30T00:59:00Z | 8.99 | 93 | < 25mph | RRRC1 | 4.73 | 2015-10-30T01:13:00Z | 12.01 | 144 | < 25mph
PG&E | 2015-08-14 17:44 | 2015-08-14 17:44 | 37.8894 | -120.4933 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | ENTRANCE TO 14650 HWY 108, JAMESTOWN |  | 17000 | Conductor | Overhead | Yes | 42230.7389 | 2015-08-14 17:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0531 | 2015 | 8 | 14 | 17 | 44 | 15-0055160 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 1726 | 11.4655 | 222_233 | <25mph | <15mph | HFTD - Distribution | 2015-08-14 17:44:00 | 275 | 13.236 | FALSE | <25mph | GNSC1 | 3.85 | 2018-01-08T11:03:00Z | 5.99 | 1 | < 25mph | GNSC1 | 3.85 | 2018-01-08T11:03:00Z | 5.99 | 8 | < 25mph | GNSC1 | 3.85 | 2018-01-08T12:03:00Z | 7 | 2 | < 25mph | GNSC1 | 3.85 | 2018-01-08T12:03:00Z | 7 | 16 | < 25mph
PG&E | 2015-10-07 15:04 | 2015-10-07 15:04 | 35.3079 | -120.8328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101924901 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42284.6277 | 2015-10-07 15:04 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0640 | 2015 | 10 | 7 | 15 | 3 | 15-0068730 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 77896 | 15.4357 | 207_90 | <25mph | <15mph | HFTD - Distribution | 2015-10-07 15:03:00 | 384 | 16.4418 | FALSE | <25mph | E6113 | 0.7 | 2015-01-11T00:59:00Z | 4.99 | 8 | < 25mph | E6113 | 0.7 | 2015-01-11T00:59:00Z | 4.99 | 8 | < 25mph | E6113 | 0.7 | 2015-01-11T00:59:00Z | 4.99 | 16 | < 25mph | E6113 | 0.7 | 2015-01-11T00:59:00Z | 4.99 | 16 | < 25mph
PG&E | 2018-11-01 | 20:45 | 38.372 | -123.0507 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103852431 | AT&T | 12000 | Conductor | Overhead | Yes | 43405 | 20:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1958 | 2018 | 11 | 1 | 20 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.9426 | 111_260 | <25mph | <15mph | HFTD - Distribution | 2018-11-01 20:45:00 | 1697 | 13.8199 | FALSE | <25mph | BBYC1 | 3.77 | 2015-11-17T12:10:00Z | 6.6 | 3 | < 25mph | UCBM | 4.05 | 2015-11-17T12:40:00Z | 11.79 | 34 | < 25mph | BBYC1 | 3.77 | 2015-11-17T12:10:00Z | 6.6 | 4 | < 25mph | UCBM | 4.05 | 2015-11-17T13:00:00Z | 13.49 | 67 | < 25mph
PG&E | 2015-11-21 10:36 | 2015-11-21 10:36 | 38.0679 | -120.1872 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101045952 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42329.4417 | 2015-11-21 10:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0677 | 2015 | 11 | 21 | 10 | 36 | 15-0079868 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18350 | 7.816 | 235_243 | <25mph | <15mph | HFTD - Distribution | 2015-11-21 10:36:00 | 421 | 16.6927 | FALSE | <25mph | MOUC1 | 3.29 | 2018-10-05T13:02:00Z | 8.01 | 1 | < 25mph | MOUC1 | 3.29 | 2018-10-05T13:02:00Z | 8.01 | 19 | < 25mph | MOUC1 | 3.29 | 2018-10-05T13:02:00Z | 8.01 | 2 | < 25mph | MOUC1 | 3.29 | 2018-10-05T13:02:00Z | 8.01 | 38 | < 25mph
PG&E | 2019-08-12 | 17:42 | 38.6618 | -120.7451 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 101415488, 101404439 |  | 12000 | Pole | Overhead | Yes | 43689 | 17:42 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (slight defect) | 2019-241 | 2019 | 8 | 12 | 17 | 42 | 19-0087080 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 54604 | 8.3029 | 210_275 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 17:42:00 | 1968 | 11.2889 | FALSE | <25mph | E4543 | 3.82 | 2015-03-09T06:58:00Z | 0 | 4 | < 25mph | E6490 | 4.88 | 2015-03-09T07:01:00Z | 16.98 | 28 | < 25mph | E4543 | 3.82 | 2015-03-09T07:58:00Z | 0 | 8 | < 25mph | E6490 | 4.88 | 2015-03-09T07:01:00Z | 16.98 | 56 | < 25mph
PG&E | 2015-02-23 02:05 | 2015-02-23 02:05 | 39.3027 | -121.0175 | Vegetation | Rural | < 3 meters | Fire Agency | NEVADA CITY FIRE | 100086316 |  | 12000 | Conductor | Overhead | Yes | 42058.0868 | 2015-02-23 02:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0267 | 2015 | 2 | 23 | 2 | 5 | 15-0014910 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 93279 | 24.5459 | 199_311 | <25mph | <15mph | HFTD - Distribution | 2015-02-23 02:05:00 | 14 | 25.6662 | FALSE | 25-40mph | E3651 | 2.92 | 2018-01-11T19:50:00Z | 3 | 13 | < 25mph | E5439 | 4.63 | 2018-01-11T19:50:00Z | 7 | 72 | < 25mph | E3651 | 2.92 | 2018-01-11T20:50:00Z | 4 | 25 | < 25mph | AS856 | 6.41 | 2018-01-11T20:45:00Z | 10 | 141 | < 25mph
PG&E | 2019-08-31 | 10:20 | 40.661 | -122.356 | Vehicle | Barren/Other | 3 meters - 0.25 Acres | Fire Dept | Shasta Lake FD | 103571671 | Yes | 12000 | Fuse | Overbuild | Yes | 43708 | 10:20 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-421 | 2019 | 8 | 31 | 10 | 20 | 19-0094332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3050 | 3.1396 | 143_386 | <25mph | <15mph | HFTD - Distribution | 2019-08-31 10:20:00 | 2007 | 12.9011 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AU138 | 7.86 | 2017-03-17T15:05:00Z | 5.99 | 7 | < 25mph |  |  |  | 0 | 0 | No data | AU138 | 7.86 | 2017-03-17T15:05:00Z | 5.99 | 14 | < 25mph
PG&E | 2017-08-28 | 9:14 | 38.7443 | -122.6491 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 103781085 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42975 | 9:14 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1356 | 2017 | 8 | 28 | 9 | 14 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 4.693 | 128_281 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 09:14:00 | 1094 | 16.6198 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E0674 | 6.69 | 2015-06-05T11:12:00Z | 2.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E0674 | 6.69 | 2015-06-05T11:12:00Z | 2.01 | 8 | < 25mph
PG&E | 2015-07-15 09:00 | 2015-07-15 09:00 | 36.997 | -121.7381 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101795728 |  | 21000 | Conductor | Overhead | Yes | 42200.375 | 2015-07-15 09:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0463 | 2015 | 7 | 15 | 9 | 0 | 15-0047650 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3800 | 8.5113 | 167_184 | <25mph | <15mph | HFTD - Distribution | 2015-07-15 09:00:00 | 208 | 13.379 | FALSE | <25mph | CTOC1 | 3.71 | 2019-01-28T11:27:00Z | 4 | 1 | < 25mph | CTOC1 | 3.71 | 2019-01-28T11:27:00Z | 4 | 16 | < 25mph | CTOC1 | 3.71 | 2019-01-28T12:27:00Z | 4 | 2 | < 25mph | CTOC1 | 3.71 | 2019-01-28T12:27:00Z | 4 | 33 | < 25mph
PG&E | 2019-08-20 | 9:03 | 41.1088 | -121.5034 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-297 | 2019 | 8 | 20 | 9 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 2.4258 | 178_411 | <25mph | <15mph | HFTD - Distribution | 2019-08-20 09:03:00 | 1990 | 15.6046 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2015-06-12 13:07 | 2015-06-12 13:07 | 40.4077 | -122.4104 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS STREET FROM 4139 OLD HAPPY VALLEY RD |  | 12000 | Lightning Arrestor | Overhead | No |  |  | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | no-match | 0378 | 2015 | 6 | 12 | 13 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Lightning Arrestor | N.A. | 9.7698 | 140_372 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 13:07:00 | 124 | 24.3549 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 7.46 | 2018-06-11T06:52:00Z | 4 | 8 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 7.46 | 2018-06-11T07:07:00Z | 4 | 16 | < 25mph
PG&E | 2017-08-31 | 6:42 | 35.616 | -120.8577 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Derrick | 101860075 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 6:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1372 | 2017 | 8 | 31 | 6 | 42 | 17-0074386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1620 | 12.088 | 206_107 | <25mph | <15mph | HFTD - Distribution | 2017-08-31 06:42:00 | 1110 | 13.8216 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TABC1 | 4.66 | 2017-11-22T18:07:00Z | 2.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | TABC1 | 4.66 | 2017-11-22T19:07:00Z | 3 | 2 | < 25mph
PG&E | 2018-07-17 | 11:11 | 35.6986 | -120.9777 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | dennis byrnes 8055434244 inc # = 18ca-slu-007640 | 103886652 | Unknown | 21000 | Conductor | Overhead | Yes | 43298 | 11:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1755 | 2018 | 7 | 17 | 11 | 11 | 18-0060637 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 9121 | 4.768 | 201_112 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 11:11:00 | 1495 | 12.6145 | FALSE | <25mph | E9175 | 3.58 | 2017-01-04T06:20:00Z | 10 | 13 | < 25mph | TABC1 | 4.19 | 2017-01-04T06:07:00Z | 14.99 | 18 | < 25mph | E9175 | 3.58 | 2017-01-04T06:20:00Z | 10 | 25 | < 25mph | TABC1 | 4.19 | 2017-01-04T07:07:00Z | 18.99 | 35 | < 25mph
PG&E | 2019-07-27 | 4:51 | 37.9486 | -120.4656 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 163781705 |  | 17000 | Conductor | Overhead | Yes | 43673 | 4:51 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-385 | 2019 | 7 | 27 | 4 | 51 | 19-0081744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 1364 | 13.5826 | 223_236 | <25mph | <15mph | HFTD - Distribution | 2019-07-27 04:51:00 | 1934 | 16.9934 | FALSE | <25mph | PG167 | 3.88 | 2019-06-20T07:50:00Z | 5.48 | 12 | < 25mph | PG167 | 3.88 | 2019-06-20T07:50:00Z | 5.48 | 24 | < 25mph | PG167 | 3.88 | 2019-06-20T09:10:00Z | 5.48 | 24 | < 25mph | PG167 | 3.88 | 2019-06-20T09:10:00Z | 5.48 | 48 | < 25mph
PG&E | 2017-09-01 | 17:48 | 36.6518 | -121.7249 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MCFD | 103155761 | Unknown | 12000 | Conductor | Overhead | Yes | 42979 | 17:48 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1382 | 2017 | 9 | 1 | 17 | 48 | 17-0074898 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 8152 | 14.5474 | 167_165 | <25mph | <15mph | HFTD - Distribution | 2017-09-01 17:48:00 | 1120 | 19.9505 | FALSE | <25mph | E6666 | 3.59 | 2015-04-22T05:10:00Z | 10 | 12 | < 25mph | E6666 | 3.59 | 2015-04-22T05:10:00Z | 10 | 25 | < 25mph | E6666 | 3.59 | 2015-04-22T05:40:00Z | 11.99 | 24 | < 25mph | E6666 | 3.59 | 2015-04-22T05:40:00Z | 11.99 | 48 | < 25mph
PG&E | 2017-05-24 16:25 | 16:24 | 38.834 | -121.1197 | Vegetation | Rural | < 3 Meters | Fire Agency | Fire Capt | 103838109 | None | 12000 | Conductor | Overhead | Yes | 42879.6837 | 16:24 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | no-match | 1111 | 2017 | 5 | 24 | 16 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 20.975 | 194_285 | <25mph | <15mph | HFTD - Distribution | 2017-05-24 16:24:00 | 851 | 20.975 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D7393 | 4.05 | 2017-12-03T15:23:00Z | 4.99 | 15 | < 25mph |  |  |  | 0 | 0 | No data | D8862 | 4.36 | 2017-12-03T16:57:00Z | 5.99 | 31 | < 25mph
PG&E | 2016-09-25 | 19:19 | 37.0993 | -122.1155 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire ben lomond fire | 101670837 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42638 | 19:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1003 | 2016 | 9 | 25 | 19 | 19 | 16-0067346 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1497 | 2.1111 | 150_190 | <25mph | <15mph | HFTD - Distribution | 2016-09-25 19:19:00 | 746 | 9.8702 | FALSE | <25mph | BNDC1 | 3.83 | 2017-12-17T02:50:00Z | 28.01 | 28 | 25-40mph | BNDC1 | 3.83 | 2017-12-17T02:50:00Z | 28.01 | 55 | 25-40mph | BNDC1 | 3.83 | 2017-12-17T02:50:00Z | 28.01 | 58 | 25-40mph | BNDC1 | 3.83 | 2017-12-17T02:50:00Z | 28.01 | 115 | 25-40mph
PG&E | 2017-08-12 09:09 | 09:08 | 34.6689 | -120.0286 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103391912 | Unknown | 12000 | Conductor | Overhead | Yes | 42959.3812 | 09:08 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | wire cut | Other/Unknown | 1330 | 2017 | 8 | 12 | 9 | 8 | 17-0069829 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 26070 | 3.5662 | 244_55 | <25mph | <15mph | HFTD - Distribution | 2017-08-12 09:08:00 | 1068 | 23.4799 | FALSE | <25mph | UCSE | 1.88 | 2016-01-28T13:20:00Z | 6.91 | 6 | < 25mph | TR154 | 5.6 | 2016-01-28T13:33:00Z | 27 | 19 | 25-40mph | UCSE | 1.88 | 2016-01-28T13:20:00Z | 6.91 | 12 | < 25mph | TR154 | 5.6 | 2016-01-28T13:33:00Z | 27 | 36 | 25-40mph
PG&E | 2019-05-17 | 15:12 | 38.4797 | -123.1486 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 42811111 |  | 12000 | Conductor | Overhead | Yes | 43602 | 15:12 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-200 | 2019 | 5 | 17 | 15 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 19.5511 | 107_266 | <25mph | <15mph | HFTD - Distribution | 2019-05-17 15:12:00 | 1775 | 20.334 | FALSE | <25mph | E8483 | 3.61 | 2018-03-29T07:31:00Z | 1.01 | 4 | < 25mph | E8483 | 3.61 | 2018-03-29T07:31:00Z | 1.01 | 6 | < 25mph | E8483 | 3.61 | 2018-03-29T08:16:00Z | 2.01 | 8 | < 25mph | E8483 | 3.61 | 2018-03-29T08:16:00Z | 2.01 | 12 | < 25mph
PG&E | 2017-05-15 16:14 | 16:00 | 37.1766 | -119.8189 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SHAUN FAIRBANKS 559-683-4823 | 101108423 | SIERRA | 21000 | Conductor | Overhead | Yes | 42870.6767 | 16:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1099 | 2017 | 5 | 15 | 16 | 0 | 17-0048096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20007 | 15.7465 | 251_194 | <25mph | <15mph | HFTD - Distribution | 2017-05-15 16:00:00 | 839 | 20.7849 | FALSE | <25mph | D7022 | 2.93 | 2018-12-30T14:40:00Z | 0 | 6 | < 25mph | E5766 | 4.44 | 2018-12-30T14:44:00Z | 0 | 17 | < 25mph | D7022 | 2.93 | 2018-12-30T15:40:00Z | 0 | 12 | < 25mph | E5766 | 4.44 | 2018-12-30T15:44:00Z | 0 | 35 | < 25mph
PG&E | 2019-07-21 | 10:14 | 38.9716 | -120.9991 |  | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire | Placer Hill FD | 152241102 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43667 | 10:14 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-127 | 2019 | 7 | 21 | 10 | 14 | 19-0079578 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 32850 | 6.8026 | 199_293 | <25mph | <15mph | HFTD - Distribution | 2019-07-21 10:14:00 | 1916 | 10.8012 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG349 | 6.34 | 2019-10-22T00:40:00Z | 13.09 | 41 | < 25mph |  |  |  | 0 | 0 | No data | PG349 | 6.34 | 2019-10-22T00:40:00Z | 13.09 | 83 | < 25mph
PG&E | 2017-06-15 04:31 | 2:58 | 40.299 | -122.4318 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101511631 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42901.1885 | 2:58 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | Other/Unknown | 1145 | 2017 | 6 | 15 | 2 | 58 | 17-0055359 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1762 | 9.755 | 139_366 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 02:58:00 | 884 | 19.4408 | FALSE | <25mph | E7114 | 1.68 | 2018-02-04T08:59:00Z | 8.01 | 4 | < 25mph | E7114 | 1.68 | 2018-02-04T08:59:00Z | 8.01 | 4 | < 25mph | E7114 | 1.68 | 2018-02-04T09:44:00Z | 10 | 8 | < 25mph | E7114 | 1.68 | 2018-02-04T09:44:00Z | 10 | 8 | < 25mph
PG&E | 2015-07-12 17:04 | 2015-07-12 17:04 | 37.4713 | -122.4256 | Vegetation | Rural | < 0.25 Acres | Fire Agency | COUNTY FIRE | 1 s w c509 |  | 12000 | Conductor | Overhead | Yes | 42197.7111 | 2015-07-12 17:04 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown | Jumper | Other/Unknown | 0456 | 2015 | 7 | 12 | 17 | 4 | 15-0047023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 117853 | 14.8289 | 137_210 | <25mph | <15mph | HFTD - Distribution | 2015-07-12 17:04:00 | 201 | 14.9925 | FALSE | <25mph | D9259 | 3.49 | 2016-09-08T14:14:00Z | 7 | 4 | < 25mph | HSPC1 | 6.33 | 2016-09-08T13:18:00Z | 25.99 | 57 | 25-40mph | D9259 | 3.49 | 2016-09-08T14:44:00Z | 10 | 8 | < 25mph | HSPC1 | 6.33 | 2016-09-08T13:18:00Z | 25.99 | 112 | 25-40mph
PG&E | 2019-09-22 | 11:56 | 37.5168 | -119.9159 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103967994 |  | 21000 | Pole | Overhead | Yes | 43730 | 11:56 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-452 | 2019 | 9 | 22 | 11 | 56 | 19-0102232 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 133232 | 11.5782 | 247_213 | <25mph | <15mph | HFTD - Distribution | 2019-09-22 11:56:00 | 2051 | 13.905 | FALSE | <25mph | MPOC1 | 3.98 | 2019-05-12T11:07:00Z | 7 | 8 | < 25mph | MPOC1 | 3.98 | 2019-05-12T11:07:00Z | 7 | 18 | < 25mph | MPOC1 | 3.98 | 2019-05-12T12:07:00Z | 8.01 | 15 | < 25mph | MPOC1 | 3.98 | 2019-05-12T12:07:00Z | 8.01 | 33 | < 25mph
PG&E | 2017-06-24 15:06 | 14:51 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 42910.6292 | 14:51 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1194 | 2017 | 6 | 24 | 14 | 51 | 17-0058332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 21296 | 10.4286 | 210_259 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 14:51:00 | 933 | 10.7263 | FALSE | <25mph | PG116 | 2.81 | 2018-11-17T23:50:00Z | 5.7 | 19 | < 25mph | MTZC1 | 6.33 | 2018-11-17T23:56:00Z | 5.99 | 20 | < 25mph | PG116 | 2.81 | 2018-11-17T23:50:00Z | 5.7 | 29 | < 25mph | MTZC1 | 6.33 | 2018-11-17T23:56:00Z | 5.99 | 31 | < 25mph
PG&E | 2018-08-01 | 17:58 | 38.9155 | -122.799 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102156435 | Unknown | 12000 | Conductor | Overhead | Yes | 43313 | 17:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1805 | 2018 | 8 | 1 | 17 | 58 | 18-0065921 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2744 | 14.8702 | 122_290 | <25mph | <15mph | HFTD - Distribution | 2018-08-01 17:58:00 | 1545 | 14.8702 | FALSE | <25mph | E4393 | 3.97 | 2017-07-20T14:47:00Z | 4.99 | 4 | < 25mph | KELC1 | 4.99 | 2017-07-20T13:57:00Z | 14.99 | 5 | < 25mph | E4393 | 3.97 | 2017-07-20T14:47:00Z | 4.99 | 8 | < 25mph | KELC1 | 4.99 | 2017-07-20T13:57:00Z | 14.99 | 10 | < 25mph
PG&E | 2016-05-29 14:19 | 2016-05-29 14:19 | 40.5795 | -122.4694 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103156596 | Yes | 12000 | Conductor | Overhead | Yes | 42519.5965 | 2016-05-29 14:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0751 | 2016 | 5 | 29 | 14 | 19 | 16-0039619 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3860 | 1.6611 | 138_382 | <25mph | <15mph | HFTD - Distribution | 2016-05-29 14:19:00 | 494 | 20.6013 | FALSE | <25mph | MMOC1 | 1.91 | 2018-02-25T07:00:00Z | 18.01 | 5 | < 25mph | MMOC1 | 1.91 | 2018-02-25T07:00:00Z | 18.01 | 12 | < 25mph | MMOC1 | 1.91 | 2018-02-25T07:00:00Z | 18.01 | 10 | < 25mph | MMOC1 | 1.91 | 2018-02-25T07:00:00Z | 18.01 | 25 | < 25mph
PG&E | 2017-06-15 15:04 | 15:01 | 39.3913 | -123.3054 | Vegetation | Rural | < 0.25 Acres | Fire Agency | STEPHEN | 103838176 | YES | 12000 | Conductor | Overhead | Yes | 42901.6279 | 15:01 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1148 | 2017 | 6 | 15 | 15 | 1 | 17-0055557 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 180469 | 19.6681 | 101_317 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 15:01:00 | 887 | 19.7788 | FALSE | <25mph | E4027 | 2.73 | 2015-11-28T09:33:00Z | 3 | 24 | < 25mph | E4027 | 2.73 | 2015-11-28T09:33:00Z | 3 | 24 | < 25mph | E4027 | 2.73 | 2015-11-28T09:33:00Z | 3 | 48 | < 25mph | E4027 | 2.73 | 2015-11-28T09:33:00Z | 3 | 48 | < 25mph
PG&E | 2017-07-23 18:25 | 18:25 | 39.6723 | -123.5336 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103823226 | Unknown | 12000 | Conductor | Overhead | Yes | 42939.7676 | 18:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1284 | 2017 | 7 | 23 | 18 | 25 | 17-0064854 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 12864 | 11.8402 | 92_333 | <25mph | <15mph | HFTD - Distribution | 2017-07-23 18:25:00 | 1023 | 16.2282 | FALSE | <25mph | LAYC1 | 3.32 | 2018-09-27T16:29:00Z | 2.01 | 1 | < 25mph | LAYC1 | 3.32 | 2018-09-27T16:29:00Z | 2.01 | 7 | < 25mph | LAYC1 | 3.32 | 2018-09-27T16:29:00Z | 2.01 | 2 | < 25mph | LAYC1 | 3.32 | 2018-09-27T16:29:00Z | 2.01 | 14 | < 25mph
PG&E | 2017-07-16 11:59 | 11:59 | 36.6669 | -121.7515 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101761892 | None | 21000 | Fuse | Overhead | Yes | 42932.4994 | 11:59 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1259 | 2017 | 7 | 16 | 11 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 22.4318 | 166_166 | <25mph | <15mph | HFTD - Distribution | 2017-07-16 11:59:00 | 998 | 30.0095 | FALSE | 25-40mph | E4669 | 2.51 | 2016-09-22T23:02:00Z | 11.01 | 6 | < 25mph | KMRY | 7.55 | 2016-09-22T22:36:00Z | 29.93 | 17 | 25-40mph | E4669 | 2.51 | 2016-09-22T23:52:00Z | 13 | 12 | < 25mph | KMRY | 7.55 | 2016-09-22T22:36:00Z | 29.93 | 28 | 25-40mph
PG&E | 2018-08-08 | 16:02 | 36.4703 | -121.7143 | Vegetation | Rural | < 3 meters | Customer | N.A. | 103910535 | None | 12000 | Conductor | Overhead | Yes | 43320 | 16:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1830 | 2018 | 8 | 8 | 16 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 14.7322 | 168_155 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:02:00 | 1569 | 15.5625 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-05-11 | 17:43 | 38.8218 | -120.9295 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Douglas Ferro. cell-530-708-2715. office-530-677-6192 | 101388939 | AT&T | 21000 | Conductor | Overhead | Yes | 43231 | 17:43 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1588 | 2018 | 5 | 11 | 17 | 43 | 18-0040415 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 53784 | 23.6414 | 202_284 | <25mph | <15mph | HFTD - Distribution | 2018-05-11 17:43:00 | 1330 | 24.2639 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 4.34 | 2017-09-04T19:56:00Z | 12.01 | 18 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 4.34 | 2017-09-04T20:56:00Z | 17 | 37 | < 25mph
PG&E | 2016-06-21 | 20:49 | 35.5352 | -120.8457 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101900832 |  | 12000 | Conductor | Overhead | Yes | 42542 | 20:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0812 | 2016 | 6 | 21 | 20 | 49 | 16-0044904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7806 | 8.2716 | 207_103 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 20:49:00 | 558 | 17.6234 | FALSE | <25mph | PG175 | 3.43 | 2019-08-12T03:20:00Z | 10.09 | 6 | < 25mph | PG191 | 5.32 | 2019-08-12T04:00:00Z | 11.41 | 22 | < 25mph | PG175 | 3.43 | 2019-08-12T05:10:00Z | 24.34 | 12 | < 25mph | PG175 | 3.43 | 2019-08-12T05:10:00Z | 24.34 | 44 | < 25mph
PG&E | 2017-09-05 | 6:58 | 39.6727 | -123.5128 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 102194697 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 42983 | 6:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1395 | 2017 | 9 | 5 | 6 | 58 | 17-0075976 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10528 | 9.1824 | 93_333 | <25mph | <15mph | HFTD - Distribution | 2017-09-05 06:58:00 | 1133 | 14.0364 | FALSE | <25mph | LAYC1 | 2.53 | 2016-08-03T14:29:00Z | 2.01 | 1 | < 25mph | LAYC1 | 2.53 | 2016-08-03T14:29:00Z | 2.01 | 1 | < 25mph | LAYC1 | 2.53 | 2016-08-03T15:29:00Z | 2.01 | 2 | < 25mph | LAYC1 | 2.53 | 2016-08-03T15:29:00Z | 2.01 | 2 | < 25mph
PG&E | 2017-07-16 11:59 | 11:59 | 36.6669 | -121.7515 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101761892 | None | 21000 | Fuse | Overhead | Yes | 42932.4994 | 11:59 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1259 | 2017 | 7 | 16 | 11 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 22.4318 | 166_166 | <25mph | <15mph | HFTD - Distribution | 2017-07-16 11:59:00 | 998 | 30.0095 | FALSE | 25-40mph | E6666 | 1.85 | 2015-02-07T22:30:00Z | 13 | 9 | < 25mph | E6666 | 1.85 | 2015-02-07T22:30:00Z | 13 | 9 | < 25mph | E6666 | 1.85 | 2015-02-07T23:30:00Z | 13 | 17 | < 25mph | E6666 | 1.85 | 2015-02-07T23:30:00Z | 13 | 17 | < 25mph
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 9:36 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 14.8685 | 222_261 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 09:36:00 | 925 | 23.4839 | FALSE | <25mph | AT450 | 2.61 | 2017-01-27T03:13:00Z | 8.99 | 8 | < 25mph | C9148 | 7.6 | 2017-01-27T03:33:00Z | 10 | 18 | < 25mph | AT450 | 2.61 | 2017-01-27T03:13:00Z | 8.99 | 17 | < 25mph | ULBC1 | 6.95 | 2017-01-27T04:33:00Z | 34 | 39 | 25-40mph
PG&E | 2019-07-22 | 21:39 | 38.8618 | -121.1044 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 152561103 |  | 12000 | Conductor | Overhead | Yes | 43668 | 21:39 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-336 | 2019 | 7 | 22 | 21 | 39 | 19-0080025 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 9842 | 9.5984 | 195_286 | <25mph | <15mph | HFTD - Distribution | 2019-07-22 21:39:00 | 1921 | 13.5446 | FALSE | <25mph | D8862 | 2.4 | 2019-10-31T20:31:00Z | 4 | 4 | < 25mph | PG366 | 4.9 | 2019-10-31T20:20:00Z | 12.06 | 31 | < 25mph | D8862 | 2.4 | 2019-10-31T21:00:00Z | 5.99 | 8 | < 25mph | PLTC1 | 5.53 | 2019-10-31T20:56:00Z | 14 | 61 | < 25mph
PG&E | 2018-07-14 | 14:44 | 38.9524 | -121.2467 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100035452 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 14:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1748 | 2018 | 7 | 14 | 14 | 44 | 18-0059847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2430 | 9.5304 | 189_291 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 14:44:00 | 1488 | 13.6375 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LICC1 | 5.05 | 2015-10-18T15:13:00Z | 8.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | LICC1 | 5.05 | 2015-10-18T15:13:00Z | 8.01 | 9 | < 25mph
PG&E | 2018-10-16 | 16:30 | 38.7754 | -122.8976 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MARK GRADEK (707) 889-4303 | 101962692 | AT&T | 12000 | Conductor | Overhead | Yes | 43389 | 16:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1943 | 2018 | 10 | 16 | 16 | 30 | 18-0091127 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 744 | 10.3513 | 118_282 | <25mph | <15mph | HFTD - Distribution | 2018-10-16 16:30:00 | 1682 | 19.9126 | FALSE | <25mph |  |  |  | 0 | 0 | No data | HWKC1 | 4.29 | 2016-06-10T06:56:00Z | 12.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | HWKC1 | 4.29 | 2016-06-10T07:56:00Z | 13 | 2 | < 25mph
PG&E | 2015-06-27 22:28 | 2015-06-27 22:28 | 38.1194 | -120.6218 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 101281699 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.9361 | 2015-06-27 22:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0417 | 2015 | 6 | 27 | 22 | 28 | 15-0043798 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 517 | 14.2862 | 216_246 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 22:28:00 | 162 | 15.5829 | FALSE | <25mph | C9085 | 3.92 | 2018-05-22T19:16:00Z | 10 | 6 | < 25mph | C9085 | 3.92 | 2018-05-22T19:16:00Z | 10 | 6 | < 25mph | C9085 | 3.92 | 2018-05-22T20:07:00Z | 13 | 12 | < 25mph | C9085 | 3.92 | 2018-05-22T20:07:00Z | 13 | 12 | < 25mph
PG&E | 2017-08-26 | 20:53 | 38.7066 | -121.0193 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101382231 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42973 | 20:53 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1350 | 2017 | 8 | 26 | 20 | 53 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.4442 | 199_278 | <25mph | <15mph | HFTD - Distribution | 2017-08-26 20:53:00 | 1088 | 14.1326 | FALSE | <25mph | PG111 | 2.52 | 2019-04-18T07:20:00Z | 7 | 62 | < 25mph | PG027 | 6.31 | 2019-04-18T07:20:00Z | 8.55 | 109 | < 25mph | PG111 | 2.52 | 2019-04-18T07:20:00Z | 7 | 124 | < 25mph | PG027 | 6.31 | 2019-04-18T07:20:00Z | 8.55 | 216 | < 25mph
PG&E | 2016-06-04 | 22:15 | 38.5117 | -122.9373 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42525 | 22:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0768 | 2016 | 6 | 4 | 22 | 15 | 16-0041119 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7220 | 6.1483 | 116_268 | <25mph | <15mph | HFTD - Distribution | 2016-06-04 22:15:00 | 514 | 16.4728 | FALSE | <25mph | AR798 | 3.33 | 2019-05-18T19:54:00Z | 2.01 | 36 | < 25mph | E9070 | 7.35 | 2019-05-18T20:15:00Z | 8.99 | 62 | < 25mph | AR798 | 3.33 | 2019-05-18T20:57:00Z | 5.99 | 72 | < 25mph | E9070 | 7.35 | 2019-05-18T21:15:00Z | 12.01 | 127 | < 25mph
PG&E | 2017-06-10 07:38 | 07:37 | 35.4359 | -120.4957 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101890429 | Unknown | 21000 | Conductor | Overhead | Yes | 42896.3177 | 07:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1140 | 2017 | 6 | 10 | 7 | 37 | 17-0054182 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 34397 | 9.2577 | 222_98 | <25mph | <15mph | HFTD - Distribution | 2017-06-10 07:37:00 | 879 | 18.05 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2260 | 7.67 | 2016-06-13T20:04:00Z | 17 | 7 | < 25mph |  |  |  | 0 | 0 | No data | E2260 | 7.67 | 2016-06-13T20:22:00Z | 18.99 | 14 | < 25mph
PG&E | 2016-06-03 | 2016-06-03 12:16 | 38.6435 | -120.6959 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | cal-fire and usfs | 103119737 |  | 21000 | Conductor | Overhead | Yes | 42524 | 2016-06-03 12:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0764 | 2016 | 6 | 3 | 12 | 16 | 16-0040808 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 101354 | 7.6436 | 213_274 | <25mph | <15mph | HFTD - Distribution | 2016-06-03 12:16:00 | 507 | 11.74 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6490 | 7.82 | 2016-05-21T10:06:00Z | 4.99 | 16 | < 25mph |  |  |  | 0 | 0 | No data | E6490 | 7.82 | 2016-05-21T11:12:00Z | 4.99 | 32 | < 25mph
PG&E | 2019-07-15 | 7:51 | 38.3266 | -122.568 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 42721104 |  | 12000 | Conductor | Overhead | Yes | 43661 | 7:51 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-343 | 2019 | 7 | 15 | 7 | 51 | 19-0077351 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2348 | 31.0114 | 132_257 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-07-15 07:51:00 | 1903 | 35.3209 | FALSE | 25-40mph | F11WW | 3.53 | 2017-10-09T13:00:00Z | 24.49 | 1 | < 25mph | KENWW | 5.78 | 2017-10-09T13:00:00Z | 27.81 | 26 | 25-40mph | F11WW | 3.53 | 2017-10-09T14:00:00Z | 26.19 | 2 | 25-40mph | KENWW | 5.78 | 2017-10-09T13:00:00Z | 27.81 | 51 | 25-40mph
PG&E | 2016-09-15 | 15:56 | 37.1102 | -121.9509 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100520198 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42628 | 15:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0982 | 2016 | 9 | 15 | 15 | 56 | 16-0065001 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 28900 | 4.729 | 158_190 | <25mph | <15mph | HFTD - Distribution | 2016-09-15 15:56:00 | 724 | 12.2674 | FALSE | <25mph | PG062 | 2.51 | 2019-09-30T19:10:00Z | 12.64 | 50 | < 25mph | F5763 | 7.38 | 2019-09-30T18:50:00Z | 14.99 | 162 | < 25mph | D8700 | 3.83 | 2019-09-30T20:01:00Z | 15.99 | 98 | < 25mph | F5763 | 7.38 | 2019-09-30T19:31:00Z | 15.99 | 319 | < 25mph
PG&E | 2017-10-20 | 6:18 | 39.2922 | -121.0157 | Vegetation | Rural | < 3 Meters | Fire Agency | PHILLIP NUNNINK INCIDENT # 27272 | 100087647 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43028 | 6:18 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1499 | 2017 | 10 | 20 | 6 | 18 | 17-0088957 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 102410 | 6.1464 | 199_310 | <25mph | <15mph | HFTD - Distribution | 2017-10-20 06:18:00 | 1242 | 23.0997 | FALSE | <25mph | E3651 | 3.59 | 2016-10-06T01:40:00Z | 3 | 16 | < 25mph | RRRC1 | 5.48 | 2016-10-06T02:13:00Z | 11.01 | 72 | < 25mph | E3651 | 3.59 | 2016-10-06T01:40:00Z | 3 | 32 | < 25mph | RRRC1 | 5.48 | 2016-10-06T02:13:00Z | 11.01 | 143 | < 25mph
PG&E | 2018-11-15 | 6:09 | 38.3599 | -122.3682 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102241814 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43419 | 6:09 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1974 | 2018 | 11 | 15 | 6 | 9 | 18-0099862 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 441 | 10.2454 | 140_259 | <25mph | <15mph | HFTD - Distribution | 2018-11-15 06:09:00 | 1714 | 12.9788 | FALSE | <25mph | AS725 | 3.41 | 2016-06-18T13:18:00Z | 2.01 | 8 | < 25mph | E6860 | 7.62 | 2016-06-18T12:30:00Z | 4.99 | 13 | < 25mph | AS725 | 3.41 | 2016-06-18T14:19:00Z | 4 | 16 | < 25mph | E6860 | 7.62 | 2016-06-18T12:30:00Z | 4.99 | 26 | < 25mph
PG&E | 2016-08-03 | 2016-08-03 12:41 | 39.3269 | -120.6033 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100001032 |  | 12000 | Conductor | Overhead | Yes | 42585 | 2016-08-03 12:41 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0902 | 2016 | 8 | 3 | 12 | 41 | 16-0054769 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 20554 | 9.0542 | 216_312 | <25mph | <15mph | HFTD - Distribution | 2016-08-03 12:41:00 | 645 | 12.3394 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2015-07-03 03:23 | 2015-07-03 03:23 | 35.6785 | -120.9567 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 1 soan 1 conducter 1 span loade side transformer formtr 1008493290 |  | 21000 | Conductor | Overhead | Yes | 42188.141 | 2015-07-03 03:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0438 | 2015 | 7 | 3 | 3 | 23 | 15-0045239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 978 | 7.7054 | 202_111 | <25mph | <15mph | HFTD - Distribution | 2015-07-03 03:23:00 | 183 | 16.8894 | FALSE | <25mph | TABC1 | 2.38 | 2019-02-23T13:07:00Z | 2.01 | 1 | < 25mph | PG169 | 7.59 | 2019-02-23T12:50:00Z | 2.42 | 23 | < 25mph | TABC1 | 2.38 | 2019-02-23T13:07:00Z | 2.01 | 2 | < 25mph | PG169 | 7.59 | 2019-02-23T14:00:00Z | 2.86 | 46 | < 25mph
PG&E | 2019-08-31 | 10:20 | 40.661 | -122.356 | Vehicle | Barren/Other | 3 meters - 0.25 Acres | Fire Dept | Shasta Lake FD | 103571671 | Yes | 12000 | Fuse | Overbuild | Yes | 43708 | 10:20 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-421 | 2019 | 8 | 31 | 10 | 20 | 19-0094332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3050 | 3.1396 | 143_386 | <25mph | <15mph | HFTD - Distribution | 2019-08-31 10:20:00 | 2007 | 12.9011 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG302 | 6.41 | 2019-05-10T02:00:00Z | 15.77 | 24 | < 25mph |  |  |  | 0 | 0 | No data | PG302 | 6.41 | 2019-05-10T02:00:00Z | 15.77 | 51 | < 25mph
PG&E | 2017-10-09 | 1:45 | 38.8576 | -122.7221 | Vegetation | Rural | < 0.25 Acres | Fire Agency | wink | 103570679 | Unknown | 12000 | Conductor | Overhead | Yes | 43017 | 1:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Other/Unknown | 1477 | 2017 | 10 | 9 | 1 | 45 | 17-0085344 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 219653 | 32.3097 | 125_287 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-09 01:45:00 | 1220 | 32.3097 | FALSE | 25-40mph | LKRC1 | 3.67 | 2016-10-19T20:05:00Z | 8.01 | 2 | < 25mph | LKRC1 | 3.67 | 2016-10-19T20:05:00Z | 8.01 | 2 | < 25mph | KELC1 | 3.85 | 2016-10-19T21:57:00Z | 8.99 | 4 | < 25mph | KELC1 | 3.85 | 2016-10-19T21:57:00Z | 8.99 | 4 | < 25mph
PG&E | 2017-04-29 15:29 | 15:07 | 37.0349 | -119.5242 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100678661 | Unknown | 12000 | Conductor | Overhead | Yes | 42854.6453 | 15:07 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1078 | 2017 | 4 | 29 | 15 | 7 | 17-0043911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 7.6275 | 265_186 | <25mph | <15mph | HFTD - Distribution | 2017-04-29 15:07:00 | 818 | 19.1329 | FALSE | <25mph | PRHC1 | 2.76 | 2018-01-06T02:27:00Z | 2.01 | 1 | < 25mph | PRHC1 | 2.76 | 2018-01-06T02:27:00Z | 2.01 | 1 | < 25mph | PRHC1 | 2.76 | 2018-01-06T03:27:00Z | 2.01 | 2 | < 25mph | PRHC1 | 2.76 | 2018-01-06T03:27:00Z | 2.01 | 2 | < 25mph
PG&E | 2016-11-09 | 9:06 | 37.4532 | -119.6413 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | US FOREST SERVICE | 101017062 |  | 12000 | Conductor | Overhead | Yes | 42683 | 9:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1046 | 2016 | 11 | 9 | 9 | 6 | 16-0078863 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1586 | 6.3162 | 259_209 | <25mph | <15mph | HFTD - Distribution | 2016-11-09 09:06:00 | 787 | 14.6769 | FALSE | <25mph | TR172 | 1.09 | 2017-08-17T09:45:00Z | 8.01 | 6 | < 25mph | TR172 | 1.09 | 2017-08-17T09:45:00Z | 8.01 | 34 | < 25mph | TR172 | 1.09 | 2017-08-17T10:45:00Z | 8.99 | 11 | < 25mph | TR172 | 1.09 | 2017-08-17T10:45:00Z | 8.99 | 61 | < 25mph
PG&E | 2015-06-09 15:24 | 2015-06-09 15:24 | 38.3651 | -122.2541 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | load side 2987 | Yes | 21000 | Conductor | Overhead | Yes | 42164.6417 | 2015-06-09 15:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0368 | 2015 | 6 | 9 | 15 | 24 | 15-0039825 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 651298 | 15.2247 | 145_259 | <25mph | <15mph | HFTD - Distribution | 2015-06-09 15:24:00 | 114 | 15.4726 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ATLC1 | 7.61 | 2015-03-24T13:29:00Z | 15.99 | 9 | < 25mph |  |  |  | 0 | 0 | No data | ATLC1 | 7.61 | 2015-03-24T14:29:00Z | 17 | 18 | < 25mph
PG&E | 2015-07-01 12:57 | 2015-07-01 12:57 | 39.4146 | -121.379 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42186.5396 | 2015-07-01 12:57 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0434 | 2015 | 7 | 1 | 12 | 57 | 15-0044609 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 12.6482 | 183_317 | <25mph | <15mph | HFTD - Distribution | 2015-07-01 12:57:00 | 179 | 18.7031 | FALSE | <25mph | BNGC1 | 2.37 | 2016-06-10T14:51:00Z | 5.99 | 1 | < 25mph | TT309 | 4.14 | 2016-06-10T14:45:00Z | 10 | 2 | < 25mph | BNGC1 | 2.37 | 2016-06-10T15:51:00Z | 8.01 | 2 | < 25mph | TT309 | 4.14 | 2016-06-10T15:45:00Z | 13 | 4 | < 25mph
PG&E | 2015-06-12 13:07 | 2015-06-12 13:07 | 40.4077 | -122.4104 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS STREET FROM 4139 OLD HAPPY VALLEY RD |  | 12000 | Lightning Arrestor | Overhead | No |  |  | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | no-match | 0378 | 2015 | 6 | 12 | 13 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Lightning Arrestor | N.A. | 9.7698 | 140_372 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 13:07:00 | 124 | 24.3549 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 7.46 | 2017-06-12T20:40:00Z | 28.99 | 8 | 25-40mph |  |  |  | 0 | 0 | No data | E7114 | 7.46 | 2017-06-12T21:25:00Z | 32.99 | 16 | 25-40mph
PG&E | 2017-05-25 15:05 | 15:05 | 36.5217 | -121.8473 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Buddy Bloxham 831-236-5659 | 101778611 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42880.6288 | 15:05 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1113 | 2017 | 5 | 25 | 15 | 5 | 17-0050761 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 13965 | 25.8899 | 162_158 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-05-25 15:05:00 | 853 | 26.2648 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E6407 | 7.69 | 2018-03-31T08:56:00Z | 4 | 44 | < 25mph |  |  |  | 0 | 0 | No data | D4637 | 7.45 | 2018-03-31T10:03:00Z | 5.99 | 86 | < 25mph
PG&E | 2017-08-08 20:35 | 20:35 | 37.2637 | -119.7103 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TROY CHEEK1-209-966-3621 | 103793352 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42955.8578 | 20:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1327 | 2017 | 8 | 8 | 20 | 35 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.9357 | 256_199 | <25mph | <15mph | HFTD - Distribution | 2017-08-08 20:35:00 | 1065 | 11.9714 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D7778 | 4.64 | 2018-02-22T16:19:00Z | 4.99 | 52 | < 25mph |  |  |  | 0 | 0 | No data | D7778 | 4.64 | 2018-02-22T17:22:00Z | 8.01 | 102 | < 25mph
PG&E | 2017-09-06 | 19:26 | 40.8392 | -122.3635 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103643183 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 19:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1399 | 2017 | 9 | 6 | 19 | 26 | 17-0076501 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 23830 | 6.5088 | 142_396 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 19:26:00 | 1137 | 12.365 | FALSE | <25mph | CTANT | 1.93 | 2017-08-28T02:45:00Z | 1.86 | 3 | < 25mph | SLFC1 | 6.48 | 2017-08-28T02:19:00Z | 4.99 | 8 | < 25mph | CTANT | 1.93 | 2017-08-28T03:30:00Z | 2.48 | 7 | < 25mph | SLFC1 | 6.48 | 2017-08-28T02:19:00Z | 4.99 | 17 | < 25mph
PG&E | 2015-08-28 12:02 | 2015-08-28 12:02 | 37.9047 | -122.2058 | Vegetation | Rural | < 0.25 Acres | Fire Agency | EB MUD | 103623279 |  | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0563 | 2015 | 8 | 28 | 12 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 10.0355 | 147_234 | <25mph | <15mph | HFTD - Distribution | 2015-08-28 12:02:00 | 307 | 16.9223 | FALSE | <25mph | ONOC1 | 2.86 | 2016-03-06T22:33:00Z | 23 | 31 | < 25mph | ONOC1 | 2.86 | 2016-03-06T22:33:00Z | 23 | 135 | < 25mph | ONOC1 | 2.86 | 2016-03-06T23:33:00Z | 25.99 | 62 | 25-40mph | ONOC1 | 2.86 | 2016-03-06T23:33:00Z | 25.99 | 270 | 25-40mph
PG&E | 2019-06-08 | 18:51 | 38.6105 | -122.9732 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 42751113 |  | 12000 | Conductor | Overhead | Yes | 43624 | 18:51 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-355 | 2019 | 6 | 8 | 18 | 51 | 19-0064689 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 44664 | 14.8219 | 114_273 | <25mph | <15mph | HFTD - Distribution | 2019-06-08 18:51:00 | 1812 | 19.8533 | FALSE | <25mph |  |  |  | 0 | 0 | No data | DRYWW | 4.17 | 2017-07-16T23:00:00Z | 16.28 | 24 | < 25mph |  |  |  | 0 | 0 | No data | KHES | 4.97 | 2017-07-17T00:00:00Z | 17.25 | 54 | < 25mph
PG&E | 2016-07-28 08:12 | 2016-07-28 08:12 | 37.8207 | -120.1388 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101037043 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0884 | 2016 | 7 | 28 | 8 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 1.7128 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 08:12:00 | 627 | 11.4062 | FALSE | <25mph | SEWC1 | 2.5 | 2015-05-29T11:16:00Z | 10 | 5 | < 25mph | SEWC1 | 2.5 | 2015-05-29T11:16:00Z | 10 | 11 | < 25mph | SEWC1 | 2.5 | 2015-05-29T12:16:00Z | 11.01 | 10 | < 25mph | SEWC1 | 2.5 | 2015-05-29T12:16:00Z | 11.01 | 22 | < 25mph
PG&E | 2019-05-08 | 10:23 | 39.3851 | -122.557 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | Colusa FD | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-312 | 2019 | 5 | 8 | 10 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 11.1721 | 133_316 | <25mph | <15mph | HFTD - Distribution | 2019-05-08 10:23:00 | 1764 | 11.4886 | FALSE | <25mph | SYWC1 | 1.49 | 2017-09-22T05:26:00Z | 7 | 1 | < 25mph | TS378 | 6.32 | 2017-09-22T04:28:00Z | 11.01 | 2 | < 25mph | SYWC1 | 1.49 | 2017-09-22T06:26:00Z | 8.99 | 2 | < 25mph | TS378 | 6.32 | 2017-09-22T04:28:00Z | 11.01 | 4 | < 25mph
PG&E | 2018-09-21 | 23:02 | 38.6428 | -122.7453 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102218862 | Unknown | 12000 | Conductor | Overhead | Yes | 43364 | 23:02 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1909 | 2018 | 9 | 21 | 23 | 2 | 18-0082304 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 9470 | 7.2054 | 124_275 | <25mph | <15mph | HFTD - Distribution | 2018-09-21 23:02:00 | 1648 | 14.1592 | FALSE | <25mph | PG553 | 0.88 | 2019-09-26T12:10:00Z | 4.23 | 18 | < 25mph | PG132 | 6.33 | 2019-09-26T12:30:00Z | 27.56 | 100 | 25-40mph | PG553 | 0.88 | 2019-09-26T12:40:00Z | 6.13 | 35 | < 25mph | PG132 | 6.33 | 2019-09-26T12:30:00Z | 27.56 | 199 | 25-40mph
PG&E | 2015-07-07 10:42 | 2015-07-07 10:42 | 39.1138 | -121.0655 | Vegetation | Rural | < 0.25 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42192.4458 | 2015-07-07 10:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0448 | 2015 | 7 | 7 | 10 | 42 | 15-0045985 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 46738 | 10.1548 | 197_300 | <25mph | <15mph | HFTD - Distribution | 2015-07-07 10:42:00 | 193 | 12.5396 | FALSE | <25mph | AV369 | 3.22 | 2018-07-13T03:02:00Z | 3 | 10 | < 25mph | E1789 | 4.22 | 2018-07-13T02:42:00Z | 7 | 64 | < 25mph | AV369 | 3.22 | 2018-07-13T03:02:00Z | 3 | 20 | < 25mph | E1789 | 4.22 | 2018-07-13T02:42:00Z | 7 | 124 | < 25mph
PG&E | 2019-06-10 | 13:29 | 38.8137 | -120.9433 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Other | Customer | 153652109 |  | 21000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-243 | 2019 | 6 | 10 | 13 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.2437 | 202_284 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 13:29:00 | 1823 | 9.9566 | FALSE | <25mph | PLTC1 | 3.76 | 2018-02-01T10:56:00Z | 2.01 | 1 | < 25mph | PLTC1 | 3.76 | 2018-02-01T10:56:00Z | 2.01 | 80 | < 25mph | PLTC1 | 3.76 | 2018-02-01T11:56:00Z | 3 | 2 | < 25mph | PLTC1 | 3.76 | 2018-02-01T11:56:00Z | 3 | 159 | < 25mph
PG&E | 2017-09-03 | 17:52 | 37.4956 | -119.8367 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101086621 | Unknown | 21000 | Transformer | Overhead | Yes | 42981 | 17:52 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 1389 | 2017 | 9 | 3 | 17 | 52 | 17-0075617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 4512 | 13.9592 | 250_212 | <25mph | <15mph | HFTD - Distribution | 2017-09-03 17:52:00 | 1127 | 22.0754 | FALSE | <25mph | JSDC1 | 3.33 | 2018-06-12T06:47:00Z | 4 | 1 | < 25mph | MIAC1 | 7.27 | 2018-06-12T06:59:00Z | 10 | 10 | < 25mph | JSDC1 | 3.33 | 2018-06-12T07:47:00Z | 4 | 2 | < 25mph | MIAC1 | 7.27 | 2018-06-12T06:59:00Z | 10 | 20 | < 25mph
PG&E | 2016-06-30 | 0:03 | 39.8157 | -121.5994 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42551 | 0:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0832 | 2016 | 6 | 30 | 0 | 3 | 16-0046763 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 299100 | 7.8781 | 174_339 | <25mph | <15mph | HFTD - Distribution | 2016-06-30 00:03:00 | 575 | 11.8323 | FALSE | <25mph | C4565 | 1.82 | 2019-02-14T05:20:00Z | 11.01 | 10 | < 25mph | PG134 | 6.37 | 2019-02-14T06:10:00Z | 21.7 | 35 | < 25mph | C4565 | 1.82 | 2019-02-14T05:20:00Z | 11.01 | 20 | < 25mph | PG134 | 6.37 | 2019-02-14T06:10:00Z | 21.7 | 70 | < 25mph
PG&E | 2015-04-02 09:44 | 2015-04-02 09:44 | 39.6772 | -121.492 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100338726 |  | 12000 | Conductor | Overhead | Yes | 42096.4056 | 2015-04-02 09:44 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0284 | 2015 | 4 | 2 | 9 | 44 | 15-0023747 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 100204 | 15.7458 | 178_332 | <25mph | <15mph | HFTD - Distribution | 2015-04-02 09:44:00 | 30 | 15.7458 | FALSE | <25mph | PG246 | 3.9 | 2019-11-18T15:00:00Z | 14.47 | 18 | < 25mph | JBGC1 | 4.06 | 2019-11-18T15:13:00Z | 27 | 61 | 25-40mph | PG246 | 3.9 | 2019-11-18T15:40:00Z | 14.92 | 36 | < 25mph | JBGC1 | 4.06 | 2019-11-18T15:13:00Z | 27 | 122 | 25-40mph
PG&E | 2016-09-26 | 10:40 | 38.0157 | -122.6889 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | marin county fire | 102252082 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42639 | 10:40 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1005 | 2016 | 9 | 26 | 10 | 40 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 4.5159 | 126_240 | <25mph | <15mph | HFTD - Distribution | 2016-09-26 10:40:00 | 747 | 11.2091 | FALSE | <25mph | BBEC1 | 1.12 | 2017-03-13T09:11:00Z | 8.99 | 2 | < 25mph | NBRC1 | 6.67 | 2017-03-13T08:33:00Z | 24 | 27 | < 25mph | BBEC1 | 1.12 | 2017-03-13T09:11:00Z | 8.99 | 4 | < 25mph | NBRC1 | 6.67 | 2017-03-13T08:33:00Z | 24 | 54 | < 25mph
PG&E | 2018-08-26 | 15:29 | 39.3599 | -121.1209 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100107472 | Unknown | 12000 | Conductor | Overhead | Yes | 43338 | 15:29 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1860 | 2018 | 8 | 26 | 15 | 29 | 18-0073601 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 36162 | 13.8191 | 194_314 | <25mph | <15mph | HFTD - Distribution | 2018-08-26 15:29:00 | 1599 | 13.8191 | FALSE | <25mph | RRRC1 | 3.9 | 2015-08-05T06:13:00Z | 3 | 1 | < 25mph | RRRC1 | 3.9 | 2015-08-05T06:13:00Z | 3 | 7 | < 25mph | RRRC1 | 3.9 | 2015-08-05T07:13:00Z | 4 | 2 | < 25mph | RRRC1 | 3.9 | 2015-08-05T07:13:00Z | 4 | 14 | < 25mph
PG&E | 2017-10-20 | 13:45 | 34.5532 | -120.5303 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 101921492 | Unknown | 12000 | Conductor | Overhead | Yes | 43028 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1502 | 2017 | 10 | 20 | 13 | 45 | 17-0089249 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 173 | 31.847 | 221_49 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-20 13:45:00 | 1245 | 35.5655 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E2332 | 4.19 | 2019-02-25T03:39:00Z | 20 | 10 | < 25mph |  |  |  | 0 | 0 | No data | PTGC1 | 6.9 | 2019-02-25T05:00:00Z | 23.02 | 21 | < 25mph
PG&E | 2019-09-12 | 14:25 | 37.3144 | -122.1865 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 024131103 |  | 12000 | Conductor | Overhead | Yes | 43720 | 14:25 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-217 | 2019 | 9 | 12 | 14 | 25 | 19-0098386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 89097 | 5.2412 | 147_201 | <25mph | <15mph | HFTD - Distribution | 2019-09-12 14:25:00 | 2036 | 15.0249 | FALSE | <25mph | AU836 | 3.83 | 2017-02-06T00:15:00Z | 37 | 19 | 25-40mph | AU836 | 3.83 | 2017-02-06T00:15:00Z | 37 | 88 | 25-40mph | AU836 | 3.83 | 2017-02-06T01:10:00Z | 48 | 36 | 40-55mph | AU836 | 3.83 | 2017-02-06T01:10:00Z | 48 | 166 | 40-55mph
PG&E | 2019-09-27 | 10:30 | 36.5336 | -121.1464 | Vegetation | Barren/Other | 0.25 - 10 Acres | Cal Fire |  | 182492105 |  | 21000 | Conductor | Overhead | Yes | 43735 | 10:30 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-359 | 2019 | 9 | 27 | 10 | 30 | 19-0104536 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20631 | 5.3593 | 193_158 | <25mph | <15mph | HFTD - Distribution | 2019-09-27 10:30:00 | 2062 | 16.3021 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.34 | 2015-11-16T00:37:00Z | 27 | 1 | 25-40mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.34 | 2015-11-16T01:37:00Z | 31 | 2 | 25-40mph
PG&E | 2016-10-02 16:41 | 16:41 | 39.8888 | -121.6648 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103358082 |  | 12000 | Other | Overhead | Yes | 42645.6954 | 16:41 | Other | N.A. | N.A. | N.A. | Weather | lightning strike | Other/Unknown | 1013 | 2016 | 10 | 2 | 16 | 41 | 16-0069050 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 339550 | 8.5152 | 171_343 | <25mph | <15mph | HFTD - Distribution | 2016-10-02 16:41:00 | 755 | 17.2989 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CSTC1 | 5.65 | 2015-12-25T05:51:00Z | 8.01 | 10 | < 25mph |  |  |  | 0 | 0 | No data | CSTC1 | 5.65 | 2015-12-25T05:51:00Z | 8.01 | 20 | < 25mph
PG&E | 2017-08-30 | 22:37 | 38.9993 | -120.9887 | Vegetation | Rural | < 3 Meters | Fire Agency | Andy 530-889-0111 | 100026238 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42977 | 22:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1370 | 2017 | 8 | 30 | 22 | 37 | 17-0074333 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 3750 | 7.3126 | 200_294 | <25mph | <15mph | HFTD - Distribution | 2017-08-30 22:37:00 | 1108 | 12.9461 | FALSE | <25mph | C0713 | 3.13 | 2015-08-12T00:43:00Z | 7 | 8 | < 25mph | C5488 | 5.56 | 2015-08-12T00:55:00Z | 10 | 34 | < 25mph | C0713 | 3.13 | 2015-08-12T01:43:00Z | 8.99 | 16 | < 25mph | C5488 | 5.56 | 2015-08-12T00:55:00Z | 10 | 68 | < 25mph
PG&E | 2019-09-22 | 11:56 | 37.5168 | -119.9159 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103967994 |  | 21000 | Pole | Overhead | Yes | 43730 | 11:56 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-452 | 2019 | 9 | 22 | 11 | 56 | 19-0102232 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 133232 | 11.5782 | 247_213 | <25mph | <15mph | HFTD - Distribution | 2019-09-22 11:56:00 | 2051 | 13.905 | FALSE | <25mph | MPOC1 | 3.98 | 2018-03-22T11:07:00Z | 21 | 1 | < 25mph | MPOC1 | 3.98 | 2018-03-22T11:07:00Z | 21 | 6 | < 25mph | MPOC1 | 3.98 | 2018-03-22T11:07:00Z | 21 | 2 | < 25mph | MPOC1 | 3.98 | 2018-03-22T11:07:00Z | 21 | 10 | < 25mph
PG&E | 2016-08-31 | 2016-08-31 14:52 | 35.1918 | -120.4697 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101942860 |  | 12000 | Conductor | Overhead | Yes | 42613 | 2016-08-31 14:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0955 | 2016 | 8 | 31 | 14 | 52 | 16-0061423 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 156294 | 16.7717 | 224_84 | <25mph | <15mph | HFTD - Distribution | 2016-08-31 14:52:00 | 697 | 16.7717 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG168 | 7.41 | 2019-04-30T12:00:00Z | 5.48 | 39 | < 25mph |  |  |  | 0 | 0 | No data | D6295 | 6.77 | 2019-04-30T13:09:00Z | 5.99 | 78 | < 25mph
PG&E | 2015-06-30 18:18 | 2015-06-30 18:18 | 36.2199 | -121.7534 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | loadside of 88973 | unknown | 12000 | Conductor | Overhead | Yes | 42185.7625 | 2015-06-30 18:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0432 | 2015 | 6 | 30 | 18 | 18 | 15-0044405 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 158 | 5.7006 | 166_141 | <25mph | <15mph | HFTD - Distribution | 2015-06-30 18:18:00 | 177 | 8.2628 | FALSE | <25mph | PPSC1 | 2.3 | 2015-08-15T23:04:00Z | 7 | 1 | < 25mph | E4662 | 6.7 | 2015-08-15T22:30:00Z | 7 | 5 | < 25mph | PPSC1 | 2.3 | 2015-08-16T00:04:00Z | 8.01 | 2 | < 25mph | PPSC1 | 2.3 | 2015-08-16T00:04:00Z | 8.01 | 10 | < 25mph
PG&E | 2017-06-15 08:08 | 7:39 | 39.2276 | -121.2348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE CHIEF | 103676075 | Unknown | 21000 | Conductor | Overhead | Yes | 42901.3391 | 7:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1147 | 2017 | 6 | 15 | 7 | 39 | 17-0055387 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 740 | 10.5195 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 07:39:00 | 886 | 12.4202 | FALSE | <25mph | E2572 | 2.6 | 2017-01-11T11:03:00Z | 11.01 | 12 | < 25mph | E6355 | 7.24 | 2017-01-11T10:24:00Z | 23 | 34 | < 25mph | E2572 | 2.6 | 2017-01-11T11:03:00Z | 11.01 | 24 | < 25mph | E6355 | 7.24 | 2017-01-11T10:24:00Z | 23 | 68 | < 25mph
PG&E | 2017-10-23 | 21:24 | 37.3713 | -122.348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100270421 | Unknown | 12000 | Conductor | Overhead | Yes | 43031 | 21:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1507 | 2017 | 10 | 23 | 21 | 24 | 17-0089820 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1768 | 13.1103 | 140_205 | <25mph | <15mph | HFTD - Distribution | 2017-10-23 21:24:00 | 1249 | 22.0037 | FALSE | <25mph | PG149 | 1.56 | 2019-05-15T00:30:00Z | 7.9 | 13 | < 25mph | PG056 | 7.33 | 2019-05-14T23:50:00Z | 14.03 | 33 | < 25mph | PG149 | 1.56 | 2019-05-15T01:00:00Z | 9.42 | 25 | < 25mph | PG056 | 7.33 | 2019-05-14T23:50:00Z | 14.03 | 60 | < 25mph
PG&E | 2018-10-20 | 14:31 | 40.5218 | -124.1137 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Str. 003/000 | None | 60000 | Conductor | Overhead | Yes | 43393 | 14:31 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1947 | 2018 | 10 | 20 | 14 | 31 | INT-11477 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 410982 | 9.6901 | 69_380 | <25mph | <15mph | HFTD - Transmission | 2018-10-20 14:31:00 | 1686 | 10.3412 | FALSE | <25mph | AT493 | 3.34 | 2018-01-04T09:27:00Z | 14.99 | 19 | < 25mph | AT493 | 3.34 | 2018-01-04T09:27:00Z | 14.99 | 19 | < 25mph | AT493 | 3.34 | 2018-01-04T09:27:00Z | 14.99 | 38 | < 25mph | AT493 | 3.34 | 2018-01-04T09:27:00Z | 14.99 | 38 | < 25mph
PG&E | 2018-08-08 | 16:03 | 37.2974 | -122.2651 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 100307515 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 16:03 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1831 | 2018 | 8 | 8 | 16 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.1654 | 144_201 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:03:00 | 1570 | 9.1654 | FALSE | <25mph | LAHC1 | 0.77 | 2017-09-06T07:07:00Z | 4 | 1 | < 25mph | LAHC1 | 0.77 | 2017-09-06T07:07:00Z | 4 | 23 | < 25mph | LAHC1 | 0.77 | 2017-09-06T08:07:00Z | 4.99 | 2 | < 25mph | LAHC1 | 0.77 | 2017-09-06T08:07:00Z | 4.99 | 46 | < 25mph
PG&E | 2018-11-16 | 17:02 | 38.7574 | -120.9012 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101409894 | AT&T | 21000 | Conductor | Overhead | Yes | 43420 | 17:02 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1976 | 2018 | 11 | 16 | 17 | 2 | 18-0100490 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 119860 | 5.5125 | 204_281 | <25mph | <15mph | HFTD - Distribution | 2018-11-16 17:02:00 | 1716 | 12.5682 | FALSE | <25mph | D2736 | 3.3 | 2016-10-22T03:30:00Z | 0 | 12 | < 25mph | PLTC1 | 7.76 | 2016-10-22T02:56:00Z | 3 | 67 | < 25mph | D2736 | 3.3 | 2016-10-22T03:45:00Z | 4 | 24 | < 25mph | D4464 | 6.31 | 2016-10-22T04:24:00Z | 4.99 | 134 | < 25mph
PG&E | 2018-07-01 | 8:13 | 39.4154 | -121.5122 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430344 | AT&T | 12000 | Conductor | Overhead | Yes | 43282 | 8:13 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1720 | 2018 | 7 | 1 | 8 | 13 | 18-0056061 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 7848 | 6.5616 | 178_317 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 08:13:00 | 1461 | 14.6967 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BNGC1 | 7.14 | 2015-02-02T10:51:00Z | 1.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | BNGC1 | 7.14 | 2015-02-02T10:51:00Z | 1.01 | 2 | < 25mph
PG&E | 2015-09-24 04:30 | 2015-09-24 04:30 | 38.6769 | -123.314 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Str. 041/007 |  | 60000 | Conductor | Overhead | Yes | 42271.1875 | 2015-09-24 04:30 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0613 | 2015 | 9 | 24 | 4 | 30 | FU-2015-057 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 22680 | 6.5939 | 100_277 | <25mph | <15mph | HFTD - Transmission | 2015-09-24 04:30:00 | 358 | 13.8122 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D2695 | 7.76 | 2015-08-11T23:15:00Z | 8.99 | 3 | < 25mph |  |  |  | 0 | 0 | No data | D2695 | 7.76 | 2015-08-12T00:30:00Z | 11.01 | 7 | < 25mph
PG&E | 2016-08-08 | 2016-08-08 15:44 | 37.1382 | -121.9672 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100519919 |  | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0912 | 2016 | 8 | 8 | 15 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 8.8992 | 157_192 | <25mph | <15mph | HFTD - Distribution | 2016-08-08 15:44:00 | 655 | 10.1741 | FALSE | <25mph | D8979 | 1.09 | 2015-01-29T03:32:00Z | 7 | 32 | < 25mph | LSGC1 | 4.65 | 2015-01-29T03:32:00Z | 8.99 | 139 | < 25mph | D8979 | 1.09 | 2015-01-29T03:32:00Z | 7 | 57 | < 25mph | LSGC1 | 4.65 | 2015-01-29T03:32:00Z | 8.99 | 261 | < 25mph
PG&E | 2016-08-13 | 2016-08-13 14:00 | 39.2009 | -121.213 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100011376 | PACIFIC BELL | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0924 | 2016 | 8 | 13 | 14 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 9.674 | 190_305 | <25mph | <15mph | HFTD - Distribution | 2016-08-13 14:00:00 | 666 | 11.9455 | FALSE | <25mph | E2572 | 2.38 | 2016-06-02T23:53:00Z | 4.99 | 12 | < 25mph | E1789 | 5.78 | 2016-06-02T23:24:00Z | 5.99 | 33 | < 25mph | E2572 | 2.38 | 2016-06-02T23:58:00Z | 4.99 | 24 | < 25mph | E1789 | 5.78 | 2016-06-03T00:36:00Z | 7 | 67 | < 25mph
PG&E | 2016-08-10 | 2016-08-10 08:36 | 37.0575 | -121.9556 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 101680487 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0917 | 2016 | 8 | 10 | 8 | 36 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 6.3982 | 157_187 | <25mph | <15mph | HFTD - Distribution | 2016-08-10 08:36:00 | 659 | 9.833 | FALSE | <25mph | E5965 | 0.91 | 2016-08-23T23:21:00Z | 10 | 42 | < 25mph | C8539 | 7.1 | 2016-08-23T23:16:00Z | 18.01 | 169 | < 25mph | E5965 | 0.91 | 2016-08-23T23:21:00Z | 10 | 80 | < 25mph | C8539 | 7.1 | 2016-08-24T00:11:00Z | 18.01 | 330 | < 25mph
PG&E | 2017-09-08 | 17:21 | 38.6039 | -120.9275 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101379094 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42986 | 17:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1402 | 2017 | 9 | 8 | 17 | 21 | 17-0077122 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 8504 | 10.5347 | 203_272 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 17:21:00 | 1140 | 11.5767 | FALSE | <25mph | BENC1 | 0.96 | 2015-07-28T07:59:00Z | 8.01 | 13 | < 25mph | BENC1 | 0.96 | 2015-07-28T07:59:00Z | 8.01 | 40 | < 25mph | BENC1 | 0.96 | 2015-07-28T07:59:00Z | 8.01 | 26 | < 25mph | D4464 | 6.61 | 2015-07-28T09:09:00Z | 10 | 79 | < 25mph
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 9:36 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 14.8685 | 222_261 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 09:36:00 | 925 | 23.4839 | FALSE | <25mph | D9396 | 1.73 | 2018-10-29T15:02:00Z | 2.01 | 4 | < 25mph | ULBC1 | 6.95 | 2018-10-29T15:33:00Z | 8.99 | 47 | < 25mph | D9396 | 1.73 | 2018-10-29T15:02:00Z | 2.01 | 8 | < 25mph | ULBC1 | 6.95 | 2018-10-29T16:33:00Z | 12.01 | 93 | < 25mph
PG&E | 2018-08-22 | 21:56 | 39.0425 | -120.9695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100024728 | Verizon | 12000 | Conductor | Overhead | Yes | 43334 | 21:56 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1854 | 2018 | 8 | 22 | 21 | 56 | 18-0072654 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29727 | 9.3137 | 201_296 | <25mph | <15mph | HFTD - Distribution | 2018-08-22 21:56:00 | 1593 | 10.5291 | FALSE | <25mph | C5488 | 3.82 | 2018-06-05T23:40:00Z | 8.99 | 10 | < 25mph | C5488 | 3.82 | 2018-06-05T23:40:00Z | 8.99 | 30 | < 25mph | C5488 | 3.82 | 2018-06-06T00:00:00Z | 11.01 | 20 | < 25mph | C5488 | 3.82 | 2018-06-06T00:00:00Z | 11.01 | 67 | < 25mph
PG&E | 2018-06-08 | 19:03 | 35.154 | -120.594 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101852092 | AT&T | 12000 | Conductor | Overhead | Yes | 43259 | 19:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1644 | 2018 | 6 | 8 | 19 | 3 | 18-0049130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2473 | 24.0333 | 218_82 | <25mph | <15mph | HFTD - Distribution | 2018-06-08 19:03:00 | 1386 | 25.9327 | FALSE | 25-40mph | C9814 | 3.01 | 2015-01-04T03:43:00Z | 3 | 15 | < 25mph | C9814 | 3.01 | 2015-01-04T03:43:00Z | 3 | 19 | < 25mph | C9814 | 3.01 | 2015-01-04T04:33:00Z | 3 | 25 | < 25mph | C9814 | 3.01 | 2015-01-04T04:33:00Z | 3 | 33 | < 25mph
PG&E | 2016-08-10 | 2016-08-10 08:36 | 37.0575 | -121.9556 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 101680487 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0917 | 2016 | 8 | 10 | 8 | 36 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 6.3982 | 157_187 | <25mph | <15mph | HFTD - Distribution | 2016-08-10 08:36:00 | 659 | 9.833 | FALSE | <25mph | E5965 | 0.91 | 2017-04-23T22:35:00Z | 15.99 | 39 | < 25mph | E5038 | 6.34 | 2017-04-23T22:47:00Z | 18.99 | 138 | < 25mph | E5965 | 0.91 | 2017-04-23T22:35:00Z | 15.99 | 74 | < 25mph | E5038 | 6.34 | 2017-04-24T00:17:00Z | 21 | 263 | < 25mph
PG&E | 2016-10-02 16:41 | 16:41 | 39.8888 | -121.6648 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103358082 |  | 12000 | Other | Overhead | Yes | 42645.6954 | 16:41 | Other | N.A. | N.A. | N.A. | Weather | lightning strike | Other/Unknown | 1013 | 2016 | 10 | 2 | 16 | 41 | 16-0069050 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 339550 | 8.5152 | 171_343 | <25mph | <15mph | HFTD - Distribution | 2016-10-02 16:41:00 | 755 | 17.2989 | FALSE | <25mph | PG506 | 3.37 | 2019-10-08T10:40:00Z | 3.87 | 42 | < 25mph | PG333 | 6.67 | 2019-10-08T11:10:00Z | 8.55 | 73 | < 25mph | PG134 | 0.91 | 2019-10-08T12:10:00Z | 4.16 | 83 | < 25mph | PG333 | 6.67 | 2019-10-08T11:40:00Z | 9.22 | 145 | < 25mph
PG&E | 2017-06-27 09:28 | 9:23 | 37.9559 | -122.6176 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | marin county fire | 102260068 | UNFILED | 12000 | Conductor | Overhead | Yes | 42913.3944 | 9:23 | Other | N.A. | N.A. | N.A. | Unknown |  | Fell into (slight defect) | 1203 | 2017 | 6 | 27 | 9 | 23 | 17-0058882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 3920 | 16.1278 | 129_237 | <25mph | <15mph | HFTD - Distribution | 2017-06-27 09:23:00 | 942 | 18.7182 | FALSE | <25mph | MDEC1 | 2.55 | 2019-12-20T07:36:00Z | 7 | 52 | < 25mph | PG601 | 4.84 | 2019-12-20T07:40:00Z | 12.12 | 76 | < 25mph | MDEC1 | 2.55 | 2019-12-20T07:36:00Z | 7 | 103 | < 25mph | PG123 | 6.9 | 2019-12-20T07:50:00Z | 13.67 | 151 | < 25mph
PG&E | 2018-06-11 | 17:49 | 34.7329 | -120.0861 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103015183 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43262 | 17:49 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1649 | 2018 | 6 | 11 | 17 | 49 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 16.7571 | 241_59 | <25mph | <15mph | HFTD - Distribution | 2018-06-11 17:49:00 | 1391 | 18.839 | FALSE | <25mph | UCSE | 3.69 | 2015-10-25T16:20:00Z | 5.3 | 6 | < 25mph | UCSE | 3.69 | 2015-10-25T16:20:00Z | 5.3 | 7 | < 25mph | UCSE | 3.69 | 2015-10-25T16:30:00Z | 5.5 | 12 | < 25mph | FGMC1 | 4.52 | 2015-10-25T16:35:00Z | 8.01 | 14 | < 25mph
PG&E | 2019-06-03 | 14:47 | 40.4419 | -122.3036 |  | Herbaceous | 1 meter - < 3 meters | Fire Dept | Anderson FD | 101495889 |  | 12000 | Insulator | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-456 | 2019 | 6 | 3 | 14 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 9.9807 | 145_374 | <25mph | <15mph | HFTD - Distribution | 2019-06-03 14:47:00 | 1799 | 16.209 | FALSE | <25mph | AP525 | 3.17 | 2018-02-08T22:55:00Z | 3 | 6 | < 25mph | RRAC1 | 5.14 | 2018-02-08T22:24:00Z | 8.01 | 11 | < 25mph | AP525 | 3.17 | 2018-02-08T22:55:00Z | 3 | 12 | < 25mph | RRAC1 | 5.14 | 2018-02-08T22:24:00Z | 8.01 | 22 | < 25mph
PG&E | 2015-06-04 20:00 | 2015-06-04 20:00 | 38.6916 | -120.8606 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101412760 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42159.8333 | 2015-06-04 20:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0347 | 2015 | 6 | 4 | 20 | 0 | 15-0038597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 9640 | 2.0731 | 205_277 | <25mph | <15mph | HFTD - Distribution | 2015-06-04 20:00:00 | 93 | 11.0268 | FALSE | <25mph | PG106 | 2.74 | 2019-06-13T13:40:00Z | 4.16 | 36 | < 25mph | PG068 | 6.2 | 2019-06-13T13:40:00Z | 13.8 | 129 | < 25mph | PG359 | 2.98 | 2019-06-13T14:30:00Z | 5.48 | 72 | < 25mph | PG068 | 6.2 | 2019-06-13T13:40:00Z | 13.8 | 258 | < 25mph
PG&E | 2017-07-22 14:38 | 14:38 | 37.2994 | -122.1631 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100265488 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.6101 | 14:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1280 | 2017 | 7 | 22 | 14 | 38 | 17-0064738 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49181 | 4.6185 | 148_201 | <25mph | <15mph | HFTD - Distribution | 2017-07-22 14:38:00 | 1019 | 12.5156 | FALSE | <25mph | LOAC1 | 4 | 2018-03-21T19:10:00Z | 22.01 | 18 | < 25mph | AU836 | 4.73 | 2018-03-21T18:45:00Z | 41 | 117 | 40-55mph | LOAC1 | 4 | 2018-03-21T19:10:00Z | 22.01 | 35 | < 25mph | AU836 | 4.73 | 2018-03-21T18:45:00Z | 41 | 232 | 40-55mph
PG&E | 2015-12-31 19:12 | 2015-12-31 19:12 | 37.1568 | -121.9868 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LOS GATOS MONTE SERENO SARATOGA | 100518215 | Verizon | 21000 | Conductor | Overhead | Yes | 42369.8 | 2015-12-31 19:12 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0689 | 2015 | 12 | 31 | 19 | 12 | 15-0087962 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7979 | 7.4149 | 156_193 | <25mph | <15mph | HFTD - Distribution | 2015-12-31 19:12:00 | 433 | 10.9251 | FALSE | <25mph | LSGC1 | 3.83 | 2015-10-08T23:32:00Z | 11.01 | 12 | < 25mph | E3877 | 7.37 | 2015-10-08T23:58:00Z | 13 | 171 | < 25mph | LSGC1 | 3.83 | 2015-10-08T23:32:00Z | 11.01 | 23 | < 25mph | E3877 | 7.37 | 2015-10-09T00:03:00Z | 13 | 337 | < 25mph
PG&E | 2015-06-06 15:38 | 2015-06-06 15:38 | 39.0409 | -123.4019 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 11480 ANDERSON VALLEY WAY @ BRIDGE |  | 12000 | Conductor | Overhead | Yes | 42161.6514 | 2015-06-06 15:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0355 | 2015 | 6 | 6 | 15 | 38 | 15-0039056 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 1748 | 19.2204 | 97_298 | <25mph | <15mph | HFTD - Distribution | 2015-06-06 15:38:00 | 101 | 19.2204 | FALSE | <25mph | E4777 | 3.27 | 2015-02-07T18:40:00Z | 13 | 3 | < 25mph | E1763 | 6.12 | 2015-02-07T18:35:00Z | 14.99 | 8 | < 25mph | E4777 | 3.27 | 2015-02-07T19:16:00Z | 14 | 5 | < 25mph | E1763 | 6.12 | 2015-02-07T19:20:00Z | 20.98 | 15 | < 25mph
PG&E | 2016-06-26 | 2016-06-26 16:38 | 39.5042 | -121.4475 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100375810 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42547 | 2016-06-26 16:38 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0823 | 2016 | 6 | 26 | 16 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 9.04 | 180_322 | <25mph | <15mph | HFTD - Distribution | 2016-06-26 16:38:00 | 567 | 14.524 | FALSE | <25mph | TT309 | 3.14 | 2018-09-05T17:45:00Z | 12.01 | 1 | < 25mph | TT309 | 3.14 | 2018-09-05T17:45:00Z | 12.01 | 7 | < 25mph | TT309 | 3.14 | 2018-09-05T17:45:00Z | 12.01 | 2 | < 25mph | TT309 | 3.14 | 2018-09-05T17:45:00Z | 12.01 | 14 | < 25mph
PG&E | 2015-02-23 13:25 | 2015-02-23 13:25 | 38.5046 | -122.7408 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RINCON VALLEY | BEHIND 4870 CARRIAGE LN SANTA ROSA |  | 12000 | Conductor | Overhead | Yes | 42058.559 | 2015-02-23 13:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0268 | 2015 | 2 | 23 | 13 | 25 | 15-0015168 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 85762 | 20.3218 | 124_267 | <25mph | <15mph | HFTD - Distribution | 2015-02-23 13:25:00 | 15 | 32.6885 | FALSE | 25-40mph | RSAC1 | 2.39 | 2018-12-30T05:29:00Z | 7 | 1 | < 25mph | E1582 | 6.75 | 2018-12-30T05:03:00Z | 7 | 56 | < 25mph | RSAC1 | 2.39 | 2018-12-30T05:29:00Z | 7 | 2 | < 25mph | E1582 | 6.75 | 2018-12-30T06:13:00Z | 8.01 | 111 | < 25mph
PG&E | 2018-06-13 | 22:40 | 38.4901 | -122.6661 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SRS181640125 | 101966547 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 22:40 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1656 | 2018 | 6 | 13 | 22 | 40 | 18-0050782 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 295146 | 2.5247 | 128_267 | <25mph | <15mph | HFTD - Distribution | 2018-06-13 22:40:00 | 1398 | 17.8767 | FALSE | <25mph | E1582 | 2.84 | 2016-11-03T15:23:00Z | 4 | 19 | < 25mph | E1582 | 2.84 | 2016-11-03T15:23:00Z | 4 | 75 | < 25mph | E1582 | 2.84 | 2016-11-03T15:23:00Z | 4 | 37 | < 25mph | E6724 | 7.87 | 2016-11-03T16:40:00Z | 4.99 | 147 | < 25mph
PG&E | 2017-06-22 17:54 | 18:07 | 38.7583 | -120.7176 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101401088 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.7461 | 18:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1188 | 2017 | 6 | 22 | 18 | 7 | 17-0057857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 8517 | 11.5365 | 212_281 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 18:07:00 | 927 | 16.1873 | FALSE | <25mph | E3165 | 3.36 | 2018-02-15T17:27:00Z | 8.01 | 25 | < 25mph | E3165 | 3.36 | 2018-02-15T17:27:00Z | 8.01 | 38 | < 25mph | E3165 | 3.36 | 2018-02-15T17:27:00Z | 8.01 | 49 | < 25mph | E3165 | 3.36 | 2018-02-15T17:27:00Z | 8.01 | 75 | < 25mph
PG&E | 2017-07-18 | 21:40 | 38.0031 | -122.2093 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | Pole 000/002 to 000/003 | Unknown | 60000 | Conductor | Overhead | Yes | 42934 | 21:40 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1266 | 2017 | 7 | 18 | 21 | 40 | INT-09875 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 0 | 11.7142 | 147_239 | <25mph | <15mph | HFTD - Transmission | 2017-07-18 21:40:00 | 1007 | 20.8699 | FALSE | <25mph | E4251 | 2.95 | 2017-10-27T09:04:00Z | 4.99 | 6 | < 25mph | DPXC1 | 4.61 | 2017-10-27T09:06:00Z | 8.01 | 100 | < 25mph | E4251 | 2.95 | 2017-10-27T09:04:00Z | 4.99 | 12 | < 25mph | DPXC1 | 4.61 | 2017-10-27T09:06:00Z | 8.01 | 214 | < 25mph
PG&E | 2019-09-13 | 8:53 | 39.0754 | -121.1717 | Bird Found | Herbaceous | 0.25 - 10 Acres | Fire Dept | Consolidated FD | Etr0913190810 |  | 12000 | Other | Overhead | Yes | 43721 | 8:53 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-46 | 2019 | 9 | 13 | 8 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 10.4382 | 192_298 | <25mph | <15mph | HFTD - Distribution | 2019-09-13 08:53:00 | 2038 | 13.5808 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1789 | 5.17 | 2015-01-31T07:42:00Z | 10 | 15 | < 25mph |  |  |  | 0 | 0 | No data | E1789 | 5.17 | 2015-01-31T08:24:00Z | 10.98 | 31 | < 25mph
PG&E | 2019-06-19 | 11:44 | 39.8612 | -121.6907 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100400933 |  | 12000 | Conductor | Overhead | Yes | 43635 | 11:44 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-224 | 2019 | 6 | 19 | 11 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.9144 | 170_342 | <25mph | <15mph | HFTD - Distribution | 2019-06-19 11:44:00 | 1855 | 12.1329 | FALSE | <25mph | C8878 | 2.27 | 2016-10-23T08:43:00Z | 0 | 13 | < 25mph | CSTC1 | 4.21 | 2016-10-23T07:51:00Z | 10 | 21 | < 25mph | C8878 | 2.27 | 2016-10-23T09:43:00Z | 0 | 25 | < 25mph | CSTC1 | 4.21 | 2016-10-23T08:51:00Z | 10 | 40 | < 25mph
PG&E | 2016-06-19 | 2016-06-19 12:07 | 39.3811 | -123.7737 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102187888 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 12:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0807 | 2016 | 6 | 19 | 12 | 7 | 16-0044317 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6100 | 11.4602 | 81_317 | <25mph | <15mph | HFTD - Distribution | 2016-06-19 12:07:00 | 550 | 15.3844 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6025 | 6.3 | 2017-06-07T07:15:00Z | 7 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6025 | 6.3 | 2017-06-07T07:15:00Z | 7 | 8 | < 25mph
PG&E | 2016-06-12 | 2016-06-12 13:14 | 37.5096 | -120.0462 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101083986 |  | 0 – 750 | Conductor | Overhead | Yes | 42533 | 2016-06-12 13:14 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0795 | 2016 | 6 | 12 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.8806 | 241_212 | <25mph | <15mph | HFTD - Distribution | 2016-06-12 13:14:00 | 539 | 13.4596 | FALSE | <25mph | MPOC1 | 3.28 | 2017-05-05T22:07:00Z | 13 | 1 | < 25mph | MPOC1 | 3.28 | 2017-05-05T22:07:00Z | 13 | 1 | < 25mph | MPOC1 | 3.28 | 2017-05-05T23:07:00Z | 13 | 2 | < 25mph | MPOC1 | 3.28 | 2017-05-05T23:07:00Z | 13 | 2 | < 25mph
PG&E | 2015-07-24 14:30 | 2015-07-24 14:30 | 36.6913 | -119.0312 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46970 DUNLAP RD | YES | 0 – 750 | Transformer | Overhead | Yes | 42209.6042 | 2015-07-24 14:30 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0482 | 2015 | 7 | 24 | 14 | 30 | 15-0050401 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 281 | 12.3885 | 287_168 | <25mph | <15mph | HFTD - Distribution | 2015-07-24 14:30:00 | 227 | 13.0893 | FALSE | <25mph | PHRC1 | 0.81 | 2017-01-01T01:58:00Z | 4 | 1 | < 25mph | AV022 | 4.96 | 2017-01-01T02:52:00Z | 4 | 14 | < 25mph | PHRC1 | 0.81 | 2017-01-01T01:58:00Z | 4 | 2 | < 25mph | PRGC1 | 5.41 | 2017-01-01T03:00:00Z | 11.01 | 28 | < 25mph
PG&E | 2016-06-10 15:51 | 2016-06-10 15:51 | 39.9934 | -123.7883 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100992291 |  | 12000 | Conductor | Overhead | Yes | 42531.6604 | 2016-06-10 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0788 | 2016 | 6 | 10 | 15 | 51 | 16-0042501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | N.A. | 22.4156 | 82_351 | <25mph | <15mph | HFTD - Distribution | 2016-06-10 15:51:00 | 531 | 22.7996 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AV037 | 5.5 | 2019-09-09T17:53:00Z | 4 | 4 | < 25mph |  |  |  | 0 | 0 | No data | AV037 | 5.5 | 2019-09-09T18:43:00Z | 4.99 | 6 | < 25mph
PG&E | 2016-10-02 16:41 | 16:41 | 39.8888 | -121.6648 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103358082 |  | 12000 | Other | Overhead | Yes | 42645.6954 | 16:41 | Other | N.A. | N.A. | N.A. | Weather | lightning strike | Other/Unknown | 1013 | 2016 | 10 | 2 | 16 | 41 | 16-0069050 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 339550 | 8.5152 | 171_343 | <25mph | <15mph | HFTD - Distribution | 2016-10-02 16:41:00 | 755 | 17.2989 | FALSE | <25mph | C8878 | 1.4 | 2016-11-20T06:43:00Z | 12.01 | 12 | < 25mph | CSTC1 | 5.65 | 2016-11-20T06:51:00Z | 18.01 | 17 | < 25mph | C8878 | 1.4 | 2016-11-20T06:43:00Z | 12.01 | 22 | < 25mph | CSTC1 | 5.65 | 2016-11-20T07:51:00Z | 20 | 32 | < 25mph
PG&E | 2016-07-03 15:00 | 2016-07-03 15:00 | 38.0348 | -120.3809 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101050507 |  | 17000 | Conductor | Overhead | Yes | 42554.625 | 2016-07-03 15:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0837 | 2016 | 7 | 3 | 15 | 0 | 16-0047689 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38812 | 10.6263 | 226_241 | <25mph | <15mph | HFTD - Distribution | 2016-07-03 15:00:00 | 580 | 12.5395 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MOUC1 | 7.53 | 2015-11-27T00:02:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MOUC1 | 7.53 | 2015-11-27T01:02:00Z | 7 | 2 | < 25mph
PG&E | 2017-10-09 | 1:02 | 38.7037 | -120.6725 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101408485 | Unknown | 21000 | Other | Overhead | Yes | 43017 | 1:02 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1473 | 2017 | 10 | 9 | 1 | 2 | 17-0085324 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 419843 | 26.702 | 214_278 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-10-09 01:02:00 | 1216 | 29.779 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E5691 | 7.21 | 2015-06-28T16:46:00Z | 7 | 23 | < 25mph |  |  |  | 0 | 0 | No data | E5691 | 7.21 | 2015-06-28T18:36:00Z | 8.99 | 48 | < 25mph
PG&E | 2015-06-21 13:31 | 2015-06-21 13:31 | 37.375 | -119.6116 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103204866 |  | 0 – 750 | Conductor | Overhead | No |  |  | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0399 | 2015 | 6 | 21 | 13 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 11.8124 | 260_205 | <25mph | <15mph | HFTD - Distribution | 2015-06-21 13:31:00 | 145 | 12.2407 | FALSE | <25mph | BSNC1 | 1.01 | 2017-06-06T14:48:00Z | 8.01 | 14 | < 25mph | BSNC1 | 1.01 | 2017-06-06T14:48:00Z | 8.01 | 57 | < 25mph | BSNC1 | 1.01 | 2017-06-06T14:48:00Z | 8.01 | 31 | < 25mph | BSNC1 | 1.01 | 2017-06-06T14:48:00Z | 8.01 | 115 | < 25mph
PG&E | 2018-02-07 | 5:44 | 40.6543 | -122.5198 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 103922730 | Unknown | 12000 | Conductor | Overhead | Yes | 43138 | 5:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1558 | 2018 | 2 | 7 | 5 | 44 | 18-0012073 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 9610 | 17.8768 | 136_386 | <25mph | <15mph | HFTD - Distribution | 2018-02-07 05:44:00 | 1300 | 25.5948 | FALSE | 25-40mph | AU138 | 3.45 | 2017-03-11T14:34:00Z | 7 | 4 | < 25mph | MMOC1 | 5.95 | 2017-03-11T15:00:00Z | 14.99 | 6 | < 25mph | AU138 | 3.45 | 2017-03-11T14:34:00Z | 7 | 8 | < 25mph | MMOC1 | 5.95 | 2017-03-11T15:00:00Z | 14.99 | 11 | < 25mph
PG&E | 2016-09-21 | 10:01 | 39.1173 | -121.071 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100014315 | PACIFIC BELL | 115000 | Conductor | Overhead | Yes | 42634 | 10:01 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0991 | 2016 | 9 | 21 | 10 | 1 | INT-08560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 18.3543 | 196_301 | <25mph | <15mph | HFTD - Transmission | 2016-09-21 10:01:00 | 734 | 24.3978 | FALSE | <25mph | E1789 | 3.84 | 2015-12-21T06:30:00Z | 13 | 16 | < 25mph | E1789 | 3.84 | 2015-12-21T06:30:00Z | 13 | 62 | < 25mph | C5488 | 3.79 | 2015-12-21T07:44:00Z | 18.01 | 32 | < 25mph | C5488 | 3.79 | 2015-12-21T07:44:00Z | 18.01 | 125 | < 25mph
PG&E | 2017-07-19 | 5:52 | 37.0905 | -119.6047 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Tower 003/001 | Unknown | 115000 | Conductor | Overhead | Yes | 42935 | 5:52 | Contact From Object | N.A. | Other | Electric Facility | Unknown |  | no-match | 1269 | 2017 | 7 | 19 | 5 | 52 | INT-09877 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 0 | 0.36815 | 261_189 | <25mph | <15mph | HFTD - Transmission | 2017-07-19 05:52:00 | 1008 | 14.3689 | FALSE | <25mph | PG484 | 0.44 | 2019-10-11T09:40:00Z | 14.25 | 12 | < 25mph | PG484 | 0.44 | 2019-10-11T09:40:00Z | 14.25 | 79 | < 25mph | PG484 | 0.44 | 2019-10-11T09:40:00Z | 14.25 | 24 | < 25mph | PG484 | 0.44 | 2019-10-11T09:40:00Z | 14.25 | 158 | < 25mph
PG&E | 2018-05-11 | 10:13 | 38.387 | -122.9856 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101973909 | Unknown | 12000 | Conductor | Overhead | Yes | 43231 | 10:13 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1585 | 2018 | 5 | 11 | 10 | 13 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.6545 | 114_261 | <25mph | <15mph | HFTD - Distribution | 2018-05-11 10:13:00 | 1327 | 21.7544 | FALSE | <25mph | D2849 | 0.89 | 2017-04-20T02:57:00Z | 10 | 11 | < 25mph | UCBM | 6.47 | 2017-04-20T02:50:00Z | 18.9 | 64 | < 25mph | D2849 | 0.89 | 2017-04-20T02:57:00Z | 10 | 23 | < 25mph | UCBM | 6.47 | 2017-04-20T02:50:00Z | 18.9 | 118 | < 25mph
PG&E | 2017-10-31 | 21:02 | 39.1119 | -122.9163 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Structure 020/003 | Unknown | 60000 | Conductor | Overhead | Yes | 43039 | 21:02 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | no-match | 1513 | 2017 | 10 | 31 | 21 | 2 | INT-10325 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | 50730 | 1.8727 | 117_301 | <25mph | <15mph | HFTD - Transmission | 2017-10-31 21:02:00 | 1255 | 9.8895 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5780 | 6.35 | 2016-12-05T20:35:00Z | 4 | 10 | < 25mph |  |  |  | 0 | 0 | No data | E5780 | 6.35 | 2016-12-05T20:35:00Z | 4 | 19 | < 25mph
PG&E | 2018-09-24 | 0:35 | 39.8152 | -121.6438 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Pole 3/42B | None | 60000 | Conductor | Overhead | Yes | 43367 | 0:35 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1913 | 2018 | 9 | 24 | 0 | 35 | INT-11388 | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 2407691 | 10.8571 | 172_339 | <25mph | <15mph | HFTD - Transmission | 2018-09-24 00:35:00 | 1652 | 11.6135 | FALSE | <25mph | C4565 | 2.74 | 2016-07-16T02:20:00Z | 1.01 | 14 | < 25mph | CSTC1 | 7.71 | 2016-07-16T01:51:00Z | 12.01 | 16 | < 25mph | C4565 | 2.74 | 2016-07-16T02:20:00Z | 1.01 | 32 | < 25mph | CSTC1 | 7.71 | 2016-07-16T02:51:00Z | 12.01 | 36 | < 25mph
PG&E | 2019-09-16 | 14:39 | 37.3762 | -119.8729 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 254452102 |  | 21000 | Conductor | Overhead | Yes | 43724 | 14:39 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-417 | 2019 | 9 | 16 | 14 | 39 | 19-0099772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 121254 | 13.3091 | 249_205 | <25mph | <15mph | HFTD - Distribution | 2019-09-16 14:39:00 | 2045 | 14.9838 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MIAC1 | 7.6 | 2016-01-24T01:59:00Z | 15.99 | 5 | < 25mph |  |  |  | 0 | 0 | No data | MIAC1 | 7.6 | 2016-01-24T02:59:00Z | 17 | 11 | < 25mph
PG&E | 2019-04-09 | 14:07 | 34.6311 | -119.9813 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Fire Dept | Santa Barbra County FD | 101863014 |  | 12000 | Conductor | Overhead | Yes | 43564 | 14:07 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-263 | 2019 | 4 | 9 | 14 | 7 | 19-0040969 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 70756 | 38.5369 | 246_53 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-09 14:07:00 | 1737 | 43.1384 | FALSE | 40-55mph |  |  |  | 0 | 0 | No data | FGMC1 | 7.28 | 2016-11-26T10:35:00Z | 15.99 | 10 | < 25mph |  |  |  | 0 | 0 | No data | FGMC1 | 7.28 | 2016-11-26T10:35:00Z | 15.99 | 18 | < 25mph
PG&E | 2016-08-17 | 2016-08-17 12:23 | 41.2495 | -123.7671 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103315791 |  | 12000 | Conductor | Overhead | Yes | 42599 | 2016-08-17 12:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0932 | 2016 | 8 | 17 | 12 | 23 | 16-0058002 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 16544 | 13.4388 | 84_420 | <25mph | <15mph | HFTD - Distribution | 2016-08-17 12:23:00 | 675 | 14.3475 | FALSE | <25mph |  |  |  | 0 | 0 | No data | NTCC1 | 5.46 | 2017-11-02T07:45:00Z | 4 | 1 | < 25mph |  |  |  | 0 | 0 | No data | NTCC1 | 5.46 | 2017-11-02T07:45:00Z | 4 | 2 | < 25mph
PG&E | 2018-08-13 | 15:33 | 38.708 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101377799 | Unknown | 21000 | Conductor | Overhead | Yes | 43325 | 15:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1840 | 2018 | 8 | 13 | 15 | 33 | 18-0069470 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1004 | 11.7134 | 201_278 | <25mph | <15mph | HFTD - Distribution | 2018-08-13 15:33:00 | 1579 | 13.7748 | FALSE | <25mph | PG073 | 2.99 | 2019-08-07T15:50:00Z | 8.12 | 56 | < 25mph | PG357 | 5.01 | 2019-08-07T16:20:00Z | 11.18 | 138 | < 25mph | PG073 | 2.99 | 2019-08-07T17:10:00Z | 11.18 | 112 | < 25mph | C6129 | 6.18 | 2019-08-07T17:29:00Z | 12.01 | 293 | < 25mph
PG&E | 2019-09-10 | 7:13 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 82841102 |  | 12000 | Conductor | Overhead | Yes | 43718 | 7:13 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-369 | 2019 | 9 | 10 | 7 | 13 | 19-0097264 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 23500 | 14.6244 | 147_193 | <25mph | <15mph | HFTD - Distribution | 2019-09-10 07:13:00 | 2029 | 17.7422 | FALSE | <25mph | BNDC1 | 2.84 | 2016-02-08T00:50:00Z | 20 | 1 | < 25mph | BNDC1 | 2.84 | 2016-02-08T00:50:00Z | 20 | 22 | < 25mph | BNDC1 | 2.84 | 2016-02-08T00:50:00Z | 20 | 2 | < 25mph | E6800 | 5.35 | 2016-02-08T01:36:00Z | 20 | 43 | < 25mph
PG&E | 2018-09-09 | 4:25 | 38.6534 | -122.8538 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 13/1 | None | 60000 | Conductor | Overhead | Yes | 43352 | 4:25 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1887 | 2018 | 9 | 9 | 4 | 25 | INT-11353 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 7.8888 | 120_276 | <25mph | <15mph | HFTD - Transmission | 2018-09-09 04:25:00 | 1626 | 22.3261 | FALSE | <25mph | D2144 | 3.1 | 2016-11-21T16:45:00Z | 0 | 14 | < 25mph | HWKC1 | 5.72 | 2016-11-21T15:56:00Z | 8.99 | 31 | < 25mph | D2144 | 3.1 | 2016-11-21T17:45:00Z | 0 | 22 | < 25mph | HWKC1 | 5.72 | 2016-11-21T16:56:00Z | 11.01 | 51 | < 25mph
PG&E | 2018-08-07 | 21:03 | 38.2129 | -120.9184 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102042811 | Unknown | 12000 | Conductor | Overhead | Yes | 43319 | 21:03 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1828 | 2018 | 8 | 7 | 21 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2018-08-07 21:03:00 | NA | 0 | FALSE | <25mph | PG404 | 3.58 | 2019-08-23T21:30:00Z | 14.7 | 8 | < 25mph | PG404 | 3.58 | 2019-08-23T21:30:00Z | 14.7 | 28 | < 25mph | PG404 | 3.58 | 2019-08-23T22:40:00Z | 18.19 | 15 | < 25mph | PG404 | 3.58 | 2019-08-23T22:40:00Z | 18.19 | 53 | < 25mph
PG&E | 2017-04-25 12:39 | 12:38 | 38.6583 | -120.9762 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101376746 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 42850.5271 | 12:38 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1072 | 2017 | 4 | 25 | 12 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 9.948 | 200_275 | <25mph | <15mph | HFTD - Distribution | 2017-04-25 12:38:00 | 812 | 10.5664 | FALSE | <25mph | D7401 | 2.53 | 2017-06-11T09:51:00Z | 4.99 | 4 | < 25mph | C6129 | 7.33 | 2017-06-11T09:54:00Z | 15.99 | 55 | < 25mph | D7401 | 2.53 | 2017-06-11T10:36:00Z | 4.99 | 6 | < 25mph | C6129 | 7.33 | 2017-06-11T09:54:00Z | 15.99 | 110 | < 25mph
PG&E | 2019-07-15 | 7:51 | 38.3266 | -122.568 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 42721104 |  | 12000 | Conductor | Overhead | Yes | 43661 | 7:51 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-343 | 2019 | 7 | 15 | 7 | 51 | 19-0077351 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2348 | 31.0114 | 132_257 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-07-15 07:51:00 | 1903 | 35.3209 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | D9961 | 6.31 | 2016-01-11T13:15:00Z | 8.99 | 20 | < 25mph |  |  |  | 0 | 0 | No data | D9961 | 6.31 | 2016-01-11T14:01:00Z | 11.01 | 40 | < 25mph
PG&E | 2017-06-15 04:31 | 2:58 | 40.299 | -122.4318 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101511631 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42901.1885 | 2:58 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | Other/Unknown | 1145 | 2017 | 6 | 15 | 2 | 58 | 17-0055359 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1762 | 9.755 | 139_366 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 02:58:00 | 884 | 19.4408 | FALSE | <25mph | E7114 | 1.68 | 2018-04-02T21:36:00Z | 25.99 | 4 | 25-40mph | E7114 | 1.68 | 2018-04-02T21:36:00Z | 25.99 | 4 | 25-40mph | E7114 | 1.68 | 2018-04-02T22:51:00Z | 27 | 8 | 25-40mph | E7114 | 1.68 | 2018-04-02T22:51:00Z | 27 | 8 | 25-40mph
PG&E | 2016-08-12 | 2016-08-12 10:08 | 38.8751 | -122.4223 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 102168360 |  | 12000 | Conductor | Overhead | Yes | 42594 | 2016-08-12 10:08 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0922 | 2016 | 8 | 12 | 10 | 8 | 16-0056982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 1368 | 5.1025 | 138_288 | <25mph | <15mph | HFTD - Distribution | 2016-08-12 10:08:00 | 665 | 17.0718 | FALSE | <25mph | KNXC1 | 0.95 | 2017-09-28T06:09:00Z | 4 | 1 | < 25mph | E5568 | 6.36 | 2017-09-28T06:14:00Z | 4 | 9 | < 25mph | KNXC1 | 0.95 | 2017-09-28T07:09:00Z | 5.99 | 2 | < 25mph | KNXC1 | 0.95 | 2017-09-28T07:09:00Z | 5.99 | 18 | < 25mph
PG&E | 2016-06-15 | 2016-06-15 13:09 | 38.4433 | -120.7568 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103169620 |  | 12000 | Conductor | Overhead | Yes | 42536 | 2016-06-15 13:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0801 | 2016 | 6 | 15 | 13 | 9 | 16-0043476 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 23963 | 15.7348 | 210_263 | <25mph | <15mph | HFTD - Distribution | 2016-06-15 13:09:00 | 543 | 16.8625 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.74 | 2015-08-12T03:56:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.74 | 2015-08-12T04:56:00Z | 7 | 2 | < 25mph
PG&E | 2016-01-21 21:32 | 2016-01-21 21:32 | 40.553 | -124.1116 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100994021 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42390.8972 | 2016-01-21 21:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0690 | 2016 | 1 | 21 | 21 | 32 | 16-0007239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 6468 | 26.2481 | 69_382 | 25-40mph | 15-30mph | HFTD - Distribution | 2016-01-21 21:32:00 | 434 | 29.6828 | FALSE | 25-40mph | AT493 | 1.6 | 2015-03-23T21:20:00Z | 11.99 | 26 | < 25mph | AT493 | 1.6 | 2015-03-23T21:20:00Z | 11.99 | 26 | < 25mph | KFOT | 1.14 | 2015-03-23T22:15:00Z | 19.57 | 54 | < 25mph | KFOT | 1.14 | 2015-03-23T22:15:00Z | 19.57 | 54 | < 25mph
PG&E | 2018-09-24 | 0:35 | 39.8152 | -121.6438 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Pole 3/42B | None | 60000 | Conductor | Overhead | Yes | 43367 | 0:35 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1913 | 2018 | 9 | 24 | 0 | 35 | INT-11388 | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 2407691 | 10.8571 | 172_339 | <25mph | <15mph | HFTD - Transmission | 2018-09-24 00:35:00 | 1652 | 11.6135 | FALSE | <25mph | C8878 | 3.93 | 2016-12-13T00:33:00Z | 0 | 18 | < 25mph | CSTC1 | 7.71 | 2016-12-12T23:51:00Z | 5.99 | 28 | < 25mph | C4565 | 2.74 | 2016-12-13T01:35:00Z | 1.01 | 35 | < 25mph | CSTC1 | 7.71 | 2016-12-12T23:51:00Z | 5.99 | 49 | < 25mph
PG&E | 2017-07-30 09:47 | 09:46 | 38.9132 | -122.6179 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike wink | 102151066 | None | 0 – 750 | Conductor | Overhead | Yes | 42946.4075 | 09:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1302 | 2017 | 7 | 30 | 9 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.2785 | 130_290 | <25mph | <15mph | HFTD - Distribution | 2017-07-30 09:46:00 | 1040 | 13.7198 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 4.76 | 2016-08-27T23:57:00Z | 13 | 8 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 4.76 | 2016-08-28T00:57:00Z | 20 | 16 | < 25mph
PG&E | 2018-06-30 | 22:18 | 40.6043 | -122.24 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101469808 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43281 | 22:18 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1716 | 2018 | 6 | 30 | 22 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 10.6263 | 147_383 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 22:18:00 | 1457 | 24.79 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RRAC1 | 6.7 | 2019-02-22T03:24:00Z | 21 | 1 | < 25mph |  |  |  | 0 | 0 | No data | KRDD | 6.9 | 2019-02-22T04:20:00Z | 23.02 | 3 | < 25mph
PG&E | 2018-09-06 | 16:19 | 39.0904 | -120.9464 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 100020676 | Unknown | 12000 | Conductor | Overhead | Yes | 43349 | 16:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1886 | 2018 | 9 | 6 | 16 | 19 | 18-0077280 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 30780 | 10.0605 | 202_299 | <25mph | <15mph | HFTD - Distribution | 2018-09-06 16:19:00 | 1625 | 12.3694 | FALSE | <25mph | AT999 | 2.11 | 2015-07-07T04:43:00Z | 3 | 19 | < 25mph | C0713 | 7.29 | 2015-07-07T05:04:00Z | 5.99 | 43 | < 25mph | AT999 | 2.11 | 2015-07-07T04:43:00Z | 3 | 37 | < 25mph | C0713 | 7.29 | 2015-07-07T05:04:00Z | 5.99 | 83 | < 25mph
PG&E | 2015-03-07 13:35 | 2015-03-07 13:35 | 38.7091 | -122.6484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 14417 western mine rd, Middletown |  | 12000 | Conductor | Overhead | Yes | 42070.566 | 2015-03-07 13:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0272 | 2015 | 3 | 7 | 13 | 35 | 15-0018003 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2263 | 3.8777 | 128_279 | <25mph | <15mph | HFTD - Distribution | 2015-03-07 13:35:00 | 18 | 14.4715 | FALSE | <25mph | PG132 | 2.88 | 2018-12-09T12:20:00Z | 19.06 | 18 | < 25mph | PG132 | 2.88 | 2018-12-09T12:20:00Z | 19.06 | 30 | < 25mph | PG132 | 2.88 | 2018-12-09T13:20:00Z | 19.95 | 36 | < 25mph | PG132 | 2.88 | 2018-12-09T13:20:00Z | 19.95 | 60 | < 25mph
PG&E | 2018-10-16 | 10:44 | 40.5097 | -124.1624 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101004106 | Unknown | 12000 | Conductor | Overhead | Yes | 43389 | 10:44 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1942 | 2018 | 10 | 16 | 10 | 44 | 18-0090952 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 2081 | 4.5851 | 67_380 | <25mph | <15mph | HFTD - Distribution | 2018-10-16 10:44:00 | 1681 | 13.3626 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C5061 | 4.32 | 2015-04-28T04:48:00Z | 5.99 | 12 | < 25mph |  |  |  | 0 | 0 | No data | C5061 | 4.32 | 2015-04-28T04:53:00Z | 5.99 | 24 | < 25mph
PG&E | 2018-06-15 | 10:05 | 38.6238 | -121.0221 | Vegetation | Rural | < 3 meters | Customer | N.A. | 101376538 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43266 | 10:05 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1661 | 2018 | 6 | 15 | 10 | 5 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 10.3423 | 199_273 | <25mph | <15mph | HFTD - Distribution | 2018-06-15 10:05:00 | 1403 | 17.1425 | FALSE | <25mph | PG357 | 2.61 | 2019-10-19T04:30:00Z | 4.97 | 22 | < 25mph | FSLC1 | 7.47 | 2019-10-19T04:00:00Z | 7.83 | 125 | < 25mph | PG357 | 2.61 | 2019-10-19T05:00:00Z | 7 | 44 | < 25mph | FSLC1 | 7.47 | 2019-10-19T05:15:00Z | 10.58 | 246 | < 25mph
PG&E | 2015-08-03 00:07 | 2015-08-03 00:07 | 40.5056 | -122.347 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | COTTONWOOD FIRE DEPT | 101503428 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42219.0049 | 2015-08-03 00:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0509 | 2015 | 8 | 3 | 0 | 7 | 15-0052184 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 10427 | 9.7241 | 143_378 | <25mph | <15mph | HFTD - Distribution | 2015-08-03 00:07:00 | 254 | 13.2206 | FALSE | <25mph | RRAC1 | 2.97 | 2016-07-25T00:24:00Z | 18.01 | 1 | < 25mph | RRAC1 | 2.97 | 2016-07-25T00:24:00Z | 18.01 | 17 | < 25mph | RRAC1 | 2.97 | 2016-07-25T00:24:00Z | 18.01 | 2 | < 25mph | RRAC1 | 2.97 | 2016-07-25T00:24:00Z | 18.01 | 32 | < 25mph
PG&E | 2019-07-19 | 11:59 | 37.9162 | -120.349 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 163351703 |  | 17000 | Conductor | Overhead | Yes | 43665 | 11:59 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-376 | 2019 | 7 | 19 | 11 | 59 | 19-0079030 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24042 | 10.7946 | 228_234 | <25mph | <15mph | HFTD - Distribution | 2019-07-19 11:59:00 | 1915 | 10.8841 | FALSE | <25mph | PG179 | 3.39 | 2019-12-30T14:00:00Z | 10.38 | 32 | < 25mph | PG179 | 3.39 | 2019-12-30T14:00:00Z | 10.38 | 48 | < 25mph | PG179 | 3.39 | 2019-12-30T15:10:00Z | 13.31 | 64 | < 25mph | PG179 | 3.39 | 2019-12-30T15:10:00Z | 13.31 | 96 | < 25mph
PG&E | 2017-06-24 22:27 | 22:27 | 38.2908 | -120.849 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CONTACT BOBBY BOWMAN | 101238865 | None | 12000 | Conductor | Overhead | Yes | 42910.9354 | 22:27 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1195 | 2017 | 6 | 24 | 22 | 27 | 17-0058399 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 4529 | 5.1717 | 206_255 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 22:27:00 | 934 | 13.7168 | FALSE | <25mph | PG404 | 3.35 | 2019-10-06T06:20:00Z | 6.87 | 6 | < 25mph | CFAC1 | 7.57 | 2019-10-06T06:05:00Z | 8.01 | 33 | < 25mph | PG404 | 3.35 | 2019-10-06T07:20:00Z | 9.13 | 12 | < 25mph | PG404 | 3.35 | 2019-10-06T07:20:00Z | 9.13 | 61 | < 25mph
PG&E | 2017-06-24 15:06 | 14:51 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 42910.6292 | 14:51 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1194 | 2017 | 6 | 24 | 14 | 51 | 17-0058332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 21296 | 10.4286 | 210_259 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 14:51:00 | 933 | 10.7263 | FALSE | <25mph | ANUC1 | 1.37 | 2016-07-21T04:53:00Z | 2.01 | 1 | < 25mph | MTZC1 | 6.33 | 2016-07-21T04:56:00Z | 8.01 | 2 | < 25mph | ANUC1 | 1.37 | 2016-07-21T05:53:00Z | 2.01 | 2 | < 25mph | MTZC1 | 6.33 | 2016-07-21T04:56:00Z | 8.01 | 4 | < 25mph
PG&E | 2019-07-19 | 11:59 | 37.9162 | -120.349 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 163351703 |  | 17000 | Conductor | Overhead | Yes | 43665 | 11:59 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-376 | 2019 | 7 | 19 | 11 | 59 | 19-0079030 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24042 | 10.7946 | 228_234 | <25mph | <15mph | HFTD - Distribution | 2019-07-19 11:59:00 | 1915 | 10.8841 | FALSE | <25mph | PG031 | 3.63 | 2018-06-20T07:00:00Z | 1.32 | 10 | < 25mph | PG029 | 4.44 | 2018-06-20T07:30:00Z | 4.16 | 26 | < 25mph | PG031 | 3.63 | 2018-06-20T08:30:00Z | 3.06 | 20 | < 25mph | PG029 | 4.44 | 2018-06-20T07:50:00Z | 4.38 | 52 | < 25mph
PG&E | 2016-09-25 | 19:19 | 37.0993 | -122.1155 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire ben lomond fire | 101670837 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42638 | 19:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1003 | 2016 | 9 | 25 | 19 | 19 | 16-0067346 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1497 | 2.1111 | 150_190 | <25mph | <15mph | HFTD - Distribution | 2016-09-25 19:19:00 | 746 | 9.8702 | FALSE | <25mph | PG472 | 3.75 | 2019-12-31T16:00:00Z | 20.24 | 52 | < 25mph | PG472 | 3.75 | 2019-12-31T16:00:00Z | 20.24 | 116 | < 25mph | PG472 | 3.75 | 2019-12-31T16:20:00Z | 20.47 | 101 | < 25mph | PG472 | 3.75 | 2019-12-31T16:20:00Z | 20.47 | 230 | < 25mph
PG&E | 2015-07-24 14:30 | 2015-07-24 14:30 | 36.6913 | -119.0312 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46970 DUNLAP RD | YES | 0 – 750 | Transformer | Overhead | Yes | 42209.6042 | 2015-07-24 14:30 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0482 | 2015 | 7 | 24 | 14 | 30 | 15-0050401 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 281 | 12.3885 | 287_168 | <25mph | <15mph | HFTD - Distribution | 2015-07-24 14:30:00 | 227 | 13.0893 | FALSE | <25mph | PHRC1 | 0.81 | 2019-06-09T18:58:00Z | 5.99 | 1 | < 25mph | PG200 | 7.23 | 2019-06-09T18:50:00Z | 12.06 | 28 | < 25mph | PHRC1 | 0.81 | 2019-06-09T19:58:00Z | 8.99 | 2 | < 25mph | PG200 | 7.23 | 2019-06-09T19:50:00Z | 13.8 | 55 | < 25mph
PG&E | 2015-07-15 09:00 | 2015-07-15 09:00 | 36.997 | -121.7381 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101795728 |  | 21000 | Conductor | Overhead | Yes | 42200.375 | 2015-07-15 09:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0463 | 2015 | 7 | 15 | 9 | 0 | 15-0047650 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3800 | 8.5113 | 167_184 | <25mph | <15mph | HFTD - Distribution | 2015-07-15 09:00:00 | 208 | 13.379 | FALSE | <25mph | CTOC1 | 3.71 | 2018-07-23T13:27:00Z | 2.01 | 1 | < 25mph | AU710 | 7.72 | 2018-07-23T13:00:00Z | 2.01 | 21 | < 25mph | CTOC1 | 3.71 | 2018-07-23T14:27:00Z | 2.01 | 2 | < 25mph | AU710 | 7.72 | 2018-07-23T14:45:00Z | 2.01 | 42 | < 25mph
PG&E | 2016-07-08 10:49 | 2016-07-08 10:49 | 38.3373 | -122.1211 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 102291118 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42559.4507 | 2016-07-08 10:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0842 | 2016 | 7 | 8 | 10 | 49 | 16-0048647 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 19469 | 8.3702 | 151_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-08 10:49:00 | 585 | 20.6133 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG197 | 4.4 | 2019-11-30T13:20:00Z | 18.57 | 40 | < 25mph |  |  |  | 0 | 0 | No data | PG197 | 4.4 | 2019-11-30T13:20:00Z | 18.57 | 80 | < 25mph
PG&E | 2016-07-08 10:49 | 2016-07-08 10:49 | 38.3373 | -122.1211 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 102291118 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42559.4507 | 2016-07-08 10:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0842 | 2016 | 7 | 8 | 10 | 49 | 16-0048647 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 19469 | 8.3702 | 151_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-08 10:49:00 | 585 | 20.6133 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F0187 | 5.39 | 2018-03-06T16:55:00Z | 8.01 | 16 | < 25mph |  |  |  | 0 | 0 | No data | E6079 | 6.28 | 2018-03-06T18:05:00Z | 8.99 | 31 | < 25mph
PG&E | 2018-07-31 | 7:57 | 38.9559 | -122.7274 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102162351 | AT&T | 12000 | Conductor | Overhead | Yes | 43312 | 7:57 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1803 | 2018 | 7 | 31 | 7 | 57 | 18-0065276 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 89832 | 7.6131 | 125_292 | <25mph | <15mph | HFTD - Distribution | 2018-07-31 07:57:00 | 1543 | 16.0718 | FALSE | <25mph | KELC1 | 3.24 | 2016-06-14T03:57:00Z | 27 | 1 | 25-40mph | KELC1 | 3.24 | 2016-06-14T03:57:00Z | 27 | 5 | 25-40mph | KELC1 | 3.24 | 2016-06-14T04:57:00Z | 28.01 | 2 | 25-40mph | KELC1 | 3.24 | 2016-06-14T04:57:00Z | 28.01 | 10 | 25-40mph
PG&E | 2016-08-13 | 14:31 | 37.4642 | -119.8589 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire |  |  | 21000 | Conductor | Overhead | Yes | 42595 | 14:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0923 | 2016 | 8 | 13 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.5527 | 249_210 | <25mph | <15mph | HFTD - Distribution | 2016-08-13 14:31:00 | 667 | 11.4441 | FALSE | <25mph | C1522 | 2.94 | 2018-03-30T12:32:00Z | 3 | 1 | < 25mph | MPOC1 | 7.53 | 2018-03-30T12:07:00Z | 10 | 5 | < 25mph | C1522 | 2.94 | 2018-03-30T13:32:00Z | 4.99 | 4 | < 25mph | MPOC1 | 7.53 | 2018-03-30T13:07:00Z | 10 | 12 | < 25mph
PG&E | 2015-09-04 07:49 | 2015-09-04 07:49 | 40.2318 | -122.3643 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | E/O FRONTIER RD & N/O WAGON WAY |  | 12000 | Conductor | Overhead | Yes | 42251.3257 | 2015-09-04 07:49 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0577 | 2015 | 9 | 4 | 7 | 49 | 15-0059323 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 9563 | 2.343 | 142_362 | <25mph | <15mph | HFTD - Distribution | 2015-09-04 07:49:00 | 321 | 17.9748 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 5.07 | 2016-05-04T01:01:00Z | 14 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 5.07 | 2016-05-04T01:01:00Z | 14 | 8 | < 25mph
PG&E | 2017-07-30 09:47 | 09:46 | 38.9132 | -122.6179 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike wink | 102151066 | None | 0 – 750 | Conductor | Overhead | Yes | 42946.4075 | 09:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1302 | 2017 | 7 | 30 | 9 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.2785 | 130_290 | <25mph | <15mph | HFTD - Distribution | 2017-07-30 09:46:00 | 1040 | 13.7198 | FALSE | <25mph | PG097 | 1.29 | 2019-09-24T01:50:00Z | 14.38 | 6 | < 25mph | PG128 | 4.45 | 2019-09-24T01:10:00Z | 15.77 | 45 | < 25mph | PG097 | 1.29 | 2019-09-24T03:00:00Z | 14.47 | 12 | < 25mph | PG128 | 4.45 | 2019-09-24T01:10:00Z | 15.77 | 90 | < 25mph
PG&E | 2015-08-17 20:57 | 2015-08-17 20:57 | 36.6867 | -119.0612 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46371 ORCHARD DRIVE |  | 12000 | Conductor | Overhead | Yes | 42233.8729 | 2015-08-17 20:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0540 | 2015 | 8 | 17 | 20 | 57 | 15-0055696 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 34398 | 8.6424 | 285_168 | <25mph | <15mph | HFTD - Distribution | 2015-08-17 20:57:00 | 284 | 13.6283 | FALSE | <25mph | PHRC1 | 2.47 | 2019-10-08T05:58:00Z | 10 | 7 | < 25mph | PHRC1 | 2.47 | 2019-10-08T05:58:00Z | 10 | 43 | < 25mph | PHRC1 | 2.47 | 2019-10-08T06:58:00Z | 10 | 14 | < 25mph | PHRC1 | 2.47 | 2019-10-08T06:58:00Z | 10 | 92 | < 25mph
PG&E | 2018-11-13 | 15:41 | 37.0644 | -121.9578 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101680441 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43417 | 15:41 | Other | N.A. | N.A. | N.A. | Human Error | Grow house | Other/Unknown | 1973 | 2018 | 11 | 13 | 15 | 41 | 18-0099492 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 21484 | 1.9347 | 157_188 | <25mph | <15mph | HFTD - Distribution | 2018-11-13 15:41:00 | 1713 | 13.1257 | FALSE | <25mph | E5965 | 0.43 | 2016-09-03T00:30:00Z | 8.99 | 40 | < 25mph | E5038 | 6.81 | 2016-09-03T00:30:00Z | 13 | 166 | < 25mph | E5965 | 0.43 | 2016-09-03T00:30:00Z | 8.99 | 80 | < 25mph | E5038 | 6.81 | 2016-09-03T00:30:00Z | 13 | 327 | < 25mph
PG&E | 2017-10-02 | 14:56 | 38.9102 | -120.9185 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100110800 | None | 21000 | Other | Overhead | Yes | 43010 | 14:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1447 | 2017 | 10 | 2 | 14 | 56 | 17-0083516 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 160 | 17.2967 | 203_289 | <25mph | <15mph | HFTD - Distribution | 2017-10-02 14:56:00 | 1185 | 22.7009 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.3 | 2018-08-29T01:56:00Z | 8.01 | 31 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.3 | 2018-08-29T01:56:00Z | 8.01 | 62 | < 25mph
PG&E | 2017-12-20 07:55 | 07:54 | 37.4012 | -122.3606 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100318864 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43089.3298 | 07:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1546 | 2017 | 12 | 20 | 7 | 54 | 17-0102756 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6602 | 16.1413 | 140_206 | <25mph | <15mph | HFTD - Distribution | 2017-12-20 07:54:00 | 1288 | 21.2088 | FALSE | <25mph | E4863 | 2.73 | 2016-05-29T06:15:00Z | 1.01 | 4 | < 25mph | AU824 | 7.12 | 2016-05-29T06:26:00Z | 5.99 | 22 | < 25mph | E4863 | 2.73 | 2016-05-29T07:15:00Z | 2.01 | 8 | < 25mph | AU824 | 7.12 | 2016-05-29T07:46:00Z | 7 | 43 | < 25mph
PG&E | 2018-05-11 | 10:13 | 38.387 | -122.9856 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101973909 | Unknown | 12000 | Conductor | Overhead | Yes | 43231 | 10:13 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1585 | 2018 | 5 | 11 | 10 | 13 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.6545 | 114_261 | <25mph | <15mph | HFTD - Distribution | 2018-05-11 10:13:00 | 1327 | 21.7544 | FALSE | <25mph | D2849 | 0.89 | 2016-12-20T16:28:00Z | 3 | 18 | < 25mph | UCBM | 6.47 | 2016-12-20T15:40:00Z | 10.4 | 66 | < 25mph | D2849 | 0.89 | 2016-12-20T17:33:00Z | 3 | 36 | < 25mph | UCBM | 6.47 | 2016-12-20T15:40:00Z | 10.4 | 135 | < 25mph
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 9:36 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 14.8685 | 222_261 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 09:36:00 | 925 | 23.4839 | FALSE | <25mph | AT450 | 2.61 | 2018-03-09T19:57:00Z | 11.01 | 16 | < 25mph | ULBC1 | 6.95 | 2018-03-09T20:33:00Z | 21 | 28 | < 25mph | AT450 | 2.61 | 2018-03-09T19:57:00Z | 11.01 | 32 | < 25mph | ULBC1 | 6.95 | 2018-03-09T20:33:00Z | 21 | 57 | < 25mph
PG&E | 2017-09-27 | 12:12 | 39.4845 | -121.3545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | bill lopez cell 530 521-8052 | 100429924 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 43005 | 12:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1436 | 2017 | 9 | 27 | 12 | 12 | 17-0082180 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 6370 | 7.6613 | 184_321 | <25mph | <15mph | HFTD - Distribution | 2017-09-27 12:12:00 | 1174 | 27.61 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | BNGC1 | 7.37 | 2017-03-12T09:51:00Z | 4 | 1 | < 25mph |  |  |  | 0 | 0 | No data | BNGC1 | 7.37 | 2017-03-12T10:51:00Z | 4 | 2 | < 25mph
PG&E | 2019-05-10 | 14:52 | 40.704 | -122.8314 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Fire Dept | Lewiston FD | Keswick-Trinity 60Kv Line |  | 60000 | Conductor | Overhead | Yes | 43595 | 14:52 | Vegetation |  | Contact from Object - Other | Electric Facility |  |  | no-match | 2019-301 | 2019 | 5 | 10 | 14 | 52 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.0535 | 123_389 | <25mph | <15mph | HFTD - Transmission | 2019-05-10 14:52:00 | 1766 | 13.0849 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KO54 | 5.57 | 2016-04-14T03:55:00Z | 34.52 | 10 | 25-40mph |  |  |  | 0 | 0 | No data | KO54 | 5.57 | 2016-04-14T03:55:00Z | 34.52 | 17 | 25-40mph
PG&E | 2017-09-18 | 13:01 | 39.3889 | -121.4054 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 103795057 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42996 | 13:01 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1418 | 2017 | 9 | 18 | 13 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 17.7047 | 182_316 | <25mph | <15mph | HFTD - Distribution | 2017-09-18 13:01:00 | 1156 | 19.5678 | FALSE | <25mph | BNGC1 | 1.17 | 2018-08-02T16:51:00Z | 4.99 | 1 | < 25mph | BNGC1 | 1.17 | 2018-08-02T16:51:00Z | 4.99 | 2 | < 25mph | BNGC1 | 1.17 | 2018-08-02T17:51:00Z | 7 | 2 | < 25mph | BNGC1 | 1.17 | 2018-08-02T17:51:00Z | 7 | 4 | < 25mph
PG&E | 2018-06-05 | 13:45 | 38.5432 | -122.7202 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 102031673 | Unknown | 12000 | Conductor | Overhead | Yes | 43256 | 13:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1633 | 2018 | 6 | 5 | 13 | 45 | 18-0047625 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 40599 | 7.3889 | 125_270 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 13:45:00 | 1375 | 15.9614 | FALSE | <25mph | E6724 | 3.93 | 2017-02-05T21:10:00Z | 14 | 11 | < 25mph | C0677 | 6.65 | 2017-02-05T21:12:00Z | 20 | 83 | < 25mph | E6724 | 3.93 | 2017-02-05T22:10:00Z | 14.99 | 19 | < 25mph | C0677 | 6.65 | 2017-02-05T21:12:00Z | 20 | 158 | < 25mph
PG&E | 2018-08-28 | 12:50 | 40.2139 | -123.5966 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100994840 | Unknown | 12000 | Conductor | Overhead | Yes | 43340 | 12:50 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1866 | 2018 | 8 | 28 | 12 | 50 | 18-0074371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 82754 | 9.6027 | 90_363 | <25mph | <15mph | HFTD - Distribution | 2018-08-28 12:50:00 | 1605 | 19.5452 | FALSE | <25mph | ALDC1 | 1.95 | 2017-08-12T07:51:00Z | 3 | 1 | < 25mph | ALDC1 | 1.95 | 2017-08-12T07:51:00Z | 3 | 1 | < 25mph | ALDC1 | 1.95 | 2017-08-12T08:51:00Z | 3 | 2 | < 25mph | ALDC1 | 1.95 | 2017-08-12T08:51:00Z | 3 | 2 | < 25mph
PG&E | 2015-03-04 18:44 | 2015-03-04 18:44 | 38.9995 | -122.7545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kelseyville FD | 102156367 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42067.7806 | 2015-03-04 18:44 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0271 | 2015 | 3 | 4 | 18 | 44 | 15-0017374 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29532 | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2015-03-04 18:44:00 | NA | 0 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG128 | 7.27 | 2019-05-23T23:20:00Z | 18.86 | 23 | < 25mph |  |  |  | 0 | 0 | No data | PG128 | 7.27 | 2019-05-24T00:20:00Z | 19.73 | 46 | < 25mph
PG&E | 2016-07-28 08:12 | 2016-07-28 08:12 | 37.8207 | -120.1388 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101037043 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0884 | 2016 | 7 | 28 | 8 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 1.7128 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 08:12:00 | 627 | 11.4062 | FALSE | <25mph | SEWC1 | 2.5 | 2015-05-15T12:16:00Z | 8.99 | 5 | < 25mph | SEWC1 | 2.5 | 2015-05-15T12:16:00Z | 8.99 | 7 | < 25mph | SEWC1 | 2.5 | 2015-05-15T12:16:00Z | 8.99 | 10 | < 25mph | SEWC1 | 2.5 | 2015-05-15T12:16:00Z | 8.99 | 15 | < 25mph
PG&E | 2018-06-28 | 12:27 | 38.5982 | -121.0081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | John Reis, 530-622-3858 | 101376954 | Unknown | 21000 | Conductor | Overhead | Yes | 43279 | 12:27 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1702 | 2018 | 6 | 28 | 12 | 27 | 18-0055479 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 24671 | 12.7651 | 199_272 | <25mph | <15mph | HFTD - Distribution | 2018-06-28 12:27:00 | 1443 | 13.4512 | FALSE | <25mph | E8856 | 2.62 | 2016-09-28T06:35:00Z | 1.01 | 12 | < 25mph | BENC1 | 4.05 | 2016-09-28T06:59:00Z | 8.01 | 33 | < 25mph | E8856 | 2.62 | 2016-09-28T06:35:00Z | 1.01 | 24 | < 25mph | BENC1 | 4.05 | 2016-09-28T07:59:00Z | 8.01 | 64 | < 25mph
PG&E | 2016-08-30 | 2016-08-30 16:01 | 36.5941 | -121.9212 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Unknown | 101734977 |  | 21000 | Conductor | Overhead | Yes | 42612 | 2016-08-30 16:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0951 | 2016 | 8 | 30 | 16 | 1 | 16-0061130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 199327 | 14.6893 | 159_162 | <25mph | <15mph | HFTD - Distribution | 2016-08-30 16:01:00 | 694 | 14.6893 | FALSE | <25mph | E6407 | 1.51 | 2015-06-12T23:38:00Z | 15.99 | 52 | < 25mph | E6407 | 1.51 | 2015-06-12T23:38:00Z | 15.99 | 52 | < 25mph | E6407 | 1.51 | 2015-06-12T23:38:00Z | 15.99 | 96 | < 25mph | E6407 | 1.51 | 2015-06-12T23:38:00Z | 15.99 | 96 | < 25mph
PG&E | 2017-09-06 | 20:08 | 37.2925 | -122.294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100256917 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1400 | 2017 | 9 | 6 | 20 | 8 | 17-0076502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4914 | 6.7999 | 143_200 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 20:08:00 | 1138 | 13.6021 | FALSE | <25mph | LAHC1 | 2.3 | 2017-12-10T23:07:00Z | 4.99 | 1 | < 25mph | LAHC1 | 2.3 | 2017-12-10T23:07:00Z | 4.99 | 7 | < 25mph | LAHC1 | 2.3 | 2017-12-11T00:07:00Z | 4.99 | 2 | < 25mph | LAHC1 | 2.3 | 2017-12-11T00:07:00Z | 4.99 | 14 | < 25mph
PG&E | 2019-08-20 | 9:03 | 41.1088 | -121.5034 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-297 | 2019 | 8 | 20 | 9 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 2.4258 | 178_411 | <25mph | <15mph | HFTD - Distribution | 2019-08-20 09:03:00 | 1990 | 15.6046 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
3. Redwood Valley (Mendocino Lake Complex) | 2017-10-08 | 23:36 | 39.2487 | -123.1663 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1989 | 2017 | 10 | 8 | 23 | 36 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 24.7673 | 107_309 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 23:36:00 | 1212 | 30.3049 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E7513 | 5.24 | 2016-11-30T23:33:00Z | 8.01 | 12 | < 25mph |  |  |  | 0 | 0 | No data | E7513 | 5.24 | 2016-11-30T23:33:00Z | 8.01 | 24 | < 25mph
PG&E | 2017-09-11 | 8:50 | 36.9515 | -121.842 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101790954 | PACIFIC BELL | 21000 | Fuse | Overhead | Yes | 42989 | 8:50 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | no-match | 1408 | 2017 | 9 | 11 | 8 | 50 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | N.A. | 9.6414 | 162_181 | <25mph | <15mph | HFTD - Distribution | 2017-09-11 08:50:00 | 1146 | 17.9559 | FALSE | <25mph | E7291 | 2.85 | 2019-04-22T11:18:00Z | 3 | 28 | < 25mph | E7291 | 2.85 | 2019-04-22T11:18:00Z | 3 | 55 | < 25mph | E7291 | 2.85 | 2019-04-22T12:00:00Z | 4 | 57 | < 25mph | E7291 | 2.85 | 2019-04-22T12:00:00Z | 4 | 113 | < 25mph
PG&E | 2017-08-28 | 14:06 | 38.634 | -122.4194 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102253236 | Unknown | 21000 | Conductor | Overhead | Yes | 42975 | 14:06 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1359 | 2017 | 8 | 28 | 14 | 6 | 17-0073526 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 1896 | 12.4455 | 138_274 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 14:06:00 | 1097 | 13.1602 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AT925 | 4.29 | 2015-04-12T14:15:00Z | 2.01 | 13 | < 25mph |  |  |  | 0 | 0 | No data | AT925 | 4.29 | 2015-04-12T15:20:00Z | 4 | 25 | < 25mph
PG&E | 2015-06-30 18:18 | 2015-06-30 18:18 | 36.2199 | -121.7534 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | loadside of 88973 | unknown | 12000 | Conductor | Overhead | Yes | 42185.7625 | 2015-06-30 18:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0432 | 2015 | 6 | 30 | 18 | 18 | 15-0044405 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 158 | 5.7006 | 166_141 | <25mph | <15mph | HFTD - Distribution | 2015-06-30 18:18:00 | 177 | 8.2628 | FALSE | <25mph | PPSC1 | 2.3 | 2015-12-06T08:04:00Z | 7 | 1 | < 25mph | TR419 | 7.53 | 2015-12-06T08:15:00Z | 8.99 | 6 | < 25mph | PPSC1 | 2.3 | 2015-12-06T08:04:00Z | 7 | 2 | < 25mph | TR419 | 7.53 | 2015-12-06T09:15:00Z | 10 | 12 | < 25mph
PG&E | 2016-05-20 15:01 | 15:01 | 39.0559 | -123.4581 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102198323 |  | 12000 | Conductor | Overhead | Yes | 42510.6257 | 15:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0741 | 2016 | 5 | 20 | 15 | 1 | 16-0037479 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2720 | 20.9117 | 94_299 | <25mph | <15mph | HFTD - Distribution | 2016-05-20 15:01:00 | 484 | 20.9117 | FALSE | <25mph | E1763 | 3.93 | 2018-10-28T20:45:00Z | 4 | 4 | < 25mph | BNVC1 | 7.56 | 2018-10-28T20:50:00Z | 14 | 9 | < 25mph | E1763 | 3.93 | 2018-10-28T21:15:00Z | 5.99 | 8 | < 25mph | E4777 | 6.25 | 2018-10-28T21:50:00Z | 18.99 | 17 | < 25mph
PG&E | 2019-07-23 | 16:55 | 37.2128 | -119.505 | Gun Shot | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | 252521103 |  | 12000 | Conductor | Overhead | Yes | 43669 | 16:55 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-434 | 2019 | 7 | 23 | 16 | 55 | 19-0080383 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 513358 | 13.6168 | 265_196 | <25mph | <15mph | HFTD - Distribution | 2019-07-23 16:55:00 | 1923 | 13.6168 | FALSE | <25mph | PG467 | 3.77 | 2019-11-05T13:10:00Z | 10.29 | 13 | < 25mph | SE370 | 7.71 | 2019-11-05T12:20:00Z | 15.35 | 49 | < 25mph | PG467 | 3.77 | 2019-11-05T14:10:00Z | 12.12 | 26 | < 25mph | SE370 | 7.71 | 2019-11-05T13:50:00Z | 21.7 | 98 | < 25mph
PG&E | 2015-06-06 15:38 | 2015-06-06 15:38 | 39.0409 | -123.4019 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 11480 ANDERSON VALLEY WAY @ BRIDGE |  | 12000 | Conductor | Overhead | Yes | 42161.6514 | 2015-06-06 15:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0355 | 2015 | 6 | 6 | 15 | 38 | 15-0039056 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 1748 | 19.2204 | 97_298 | <25mph | <15mph | HFTD - Distribution | 2015-06-06 15:38:00 | 101 | 19.2204 | FALSE | <25mph | E4777 | 3.27 | 2018-02-11T14:46:00Z | 8.01 | 4 | < 25mph | BNVC1 | 4.68 | 2018-02-11T14:50:00Z | 8.99 | 9 | < 25mph | E4777 | 3.27 | 2018-02-11T16:11:00Z | 11.01 | 7 | < 25mph | E4777 | 3.27 | 2018-02-11T16:11:00Z | 11.01 | 17 | < 25mph
PG&E | 2019-06-10 | 16:34 | 38.821 | -120.846 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Garden Valley FD | 153082106 |  | 21000 | Conductor | Overhead | Yes | 43626 | 16:34 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-372 | 2019 | 6 | 10 | 16 | 34 | 19-0065481 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14169 | 8.5329 | 206_284 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 16:34:00 | 1827 | 15.7607 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5691 | 5.53 | 2017-02-07T03:57:00Z | 15.99 | 26 | < 25mph |  |  |  | 0 | 0 | No data | E3165 | 5.57 | 2017-02-07T04:55:00Z | 18.01 | 56 | < 25mph
PG&E | 2019-08-16 | 8:19 | 40.1235 | -123.8758 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Self Extinguished |  | 192221102-2101118022{5563} |  | 12000 | Conductor | Overhead | Yes | 43693 | 8:19 | Vegetation | [5 empty] | Other/Unknown |  | 2019 | 8 | 16 | 8 | 19 | 19-0088744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 2979 | 5.7689 | 78_358 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 08:19:00 | 1983 | 18.468 | FALSE | <25mph | ERCC1 | 2.93 | 2016-03-19T17:28:00Z | 3 | 1 | < 25mph | AV037 | 6 | 2016-03-19T18:13:00Z | 3 | 5 | < 25mph | ERCC1 | 2.93 | 2016-03-19T18:28:00Z | 3 | 2 | < 25mph | AV037 | 6 | 2016-03-19T19:03:00Z | 3 | 9 | < 25mph
PG&E | 2015-09-24 13:56 | 2015-09-24 13:56 | 39.3508 | -121.2454 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 9692 Rices-Texas Hill rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42271.5806 | 2015-09-24 13:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0614 | 2015 | 9 | 24 | 13 | 56 | 15-0063159 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 51917 | 10.3419 | 189_313 | <25mph | <15mph | HFTD - Distribution | 2015-09-24 13:56:00 | 359 | 13.3743 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RRRC1 | 7.59 | 2017-02-03T20:13:00Z | 25.99 | 2 | 25-40mph |  |  |  | 0 | 0 | No data | RRRC1 | 7.59 | 2017-02-03T20:13:00Z | 25.99 | 4 | 25-40mph
PG&E | 2017-07-01 | 12:02 | 39.8209 | -121.6418 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 003/039 | Unknown | 60000 | Conductor | Overhead | Yes | 42917 | 12:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1212 | 2017 | 7 | 1 | 12 | 2 | INT-09792 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.6345 | 172_339 | <25mph | <15mph | HFTD - Transmission | 2017-07-01 12:02:00 | 954 | 9.664 | FALSE | <25mph | E4833 | 2.14 | 2015-12-02T14:48:00Z | 0 | 21 | < 25mph | CSTC1 | 7.61 | 2015-12-02T13:51:00Z | 7 | 24 | < 25mph | E4833 | 2.14 | 2015-12-02T15:24:00Z | 1.01 | 45 | < 25mph | CSTC1 | 7.61 | 2015-12-02T13:51:00Z | 7 | 50 | < 25mph
PG&E | 2018-09-24 | 0:35 | 39.8152 | -121.6438 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Pole 3/42B | None | 60000 | Conductor | Overhead | Yes | 43367 | 0:35 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1913 | 2018 | 9 | 24 | 0 | 35 | INT-11388 | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 2407691 | 10.8571 | 172_339 | <25mph | <15mph | HFTD - Transmission | 2018-09-24 00:35:00 | 1652 | 11.6135 | FALSE | <25mph | PG333 | 3.19 | 2019-11-18T12:40:00Z | 8.77 | 55 | < 25mph | PG300 | 4.28 | 2019-11-18T12:20:00Z | 14.32 | 105 | < 25mph | PG333 | 3.19 | 2019-11-18T13:40:00Z | 9.35 | 108 | < 25mph | PG300 | 4.28 | 2019-11-18T13:40:00Z | 18.99 | 208 | < 25mph
PG&E | 2017-07-04 20:17 | 20:16 | 40.4228 | -122.3975 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SCOTT CORN 530-448-2414 | 101481860 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42920.8451 | 20:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1221 | 2017 | 7 | 4 | 20 | 16 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 13.3568 | 141_373 | <25mph | <15mph | HFTD - Distribution | 2017-07-04 20:16:00 | 960 | 18.8443 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6886 | 4.89 | 2017-01-29T04:09:00Z | 2.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6886 | 4.89 | 2017-01-29T05:09:00Z | 2.01 | 7 | < 25mph
PG&E | 2015-08-28 12:02 | 2015-08-28 12:02 | 37.9047 | -122.2058 | Vegetation | Rural | < 0.25 Acres | Fire Agency | EB MUD | 103623279 |  | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0563 | 2015 | 8 | 28 | 12 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 10.0355 | 147_234 | <25mph | <15mph | HFTD - Distribution | 2015-08-28 12:02:00 | 307 | 16.9223 | FALSE | <25mph | E0993 | 3.45 | 2017-12-20T03:53:00Z | 24 | 26 | < 25mph | E0993 | 3.45 | 2017-12-20T03:53:00Z | 24 | 201 | < 25mph | E0993 | 3.45 | 2017-12-20T03:53:00Z | 24 | 51 | < 25mph | E0993 | 3.45 | 2017-12-20T03:53:00Z | 24 | 410 | < 25mph
PG&E | 2015-07-12 17:04 | 2015-07-12 17:04 | 37.4713 | -122.4256 | Vegetation | Rural | < 0.25 Acres | Fire Agency | COUNTY FIRE | 1 s w c509 |  | 12000 | Conductor | Overhead | Yes | 42197.7111 | 2015-07-12 17:04 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown | Jumper | Other/Unknown | 0456 | 2015 | 7 | 12 | 17 | 4 | 15-0047023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 117853 | 14.8289 | 137_210 | <25mph | <15mph | HFTD - Distribution | 2015-07-12 17:04:00 | 201 | 14.9925 | FALSE | <25mph |  |  |  | 0 | 0 | No data | HSPC1 | 6.33 | 2016-11-28T07:18:00Z | 8.99 | 46 | < 25mph |  |  |  | 0 | 0 | No data | HSPC1 | 6.33 | 2016-11-28T08:18:00Z | 13 | 90 | < 25mph
PG&E | 2017-08-28 | 9:14 | 38.7443 | -122.6491 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 103781085 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42975 | 9:14 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1356 | 2017 | 8 | 28 | 9 | 14 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 4.693 | 128_281 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 09:14:00 | 1094 | 16.6198 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LKRC1 | 6.54 | 2017-04-30T04:05:00Z | 13 | 3 | < 25mph |  |  |  | 0 | 0 | No data | LKRC1 | 6.54 | 2017-04-30T04:05:00Z | 13 | 8 | < 25mph
PG&E | 2019-09-10 | 7:13 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 82841102 |  | 12000 | Conductor | Overhead | Yes | 43718 | 7:13 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-369 | 2019 | 9 | 10 | 7 | 13 | 19-0097264 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 23500 | 14.6244 | 147_193 | <25mph | <15mph | HFTD - Distribution | 2019-09-10 07:13:00 | 2029 | 17.7422 | FALSE | <25mph | BNDC1 | 2.84 | 2017-04-29T14:50:00Z | 21 | 1 | < 25mph | BNDC1 | 2.84 | 2017-04-29T14:50:00Z | 21 | 28 | < 25mph | BNDC1 | 2.84 | 2017-04-29T14:50:00Z | 21 | 2 | < 25mph | BNDC1 | 2.84 | 2017-04-29T14:50:00Z | 21 | 51 | < 25mph
PG&E | 2015-06-30 18:18 | 2015-06-30 18:18 | 36.2199 | -121.7534 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | loadside of 88973 | unknown | 12000 | Conductor | Overhead | Yes | 42185.7625 | 2015-06-30 18:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0432 | 2015 | 6 | 30 | 18 | 18 | 15-0044405 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 158 | 5.7006 | 166_141 | <25mph | <15mph | HFTD - Distribution | 2015-06-30 18:18:00 | 177 | 8.2628 | FALSE | <25mph | PPSC1 | 2.3 | 2016-12-15T19:04:00Z | 15.99 | 1 | < 25mph | TR419 | 7.53 | 2016-12-15T19:15:00Z | 28.01 | 2 | 25-40mph | PPSC1 | 2.3 | 2016-12-15T19:04:00Z | 15.99 | 2 | < 25mph | TR419 | 7.53 | 2016-12-15T19:15:00Z | 28.01 | 4 | 25-40mph
PG&E | 2017-05-15 16:14 | 16:00 | 37.1766 | -119.8189 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SHAUN FAIRBANKS 559-683-4823 | 101108423 | SIERRA | 21000 | Conductor | Overhead | Yes | 42870.6767 | 16:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1099 | 2017 | 5 | 15 | 16 | 0 | 17-0048096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20007 | 15.7465 | 251_194 | <25mph | <15mph | HFTD - Distribution | 2017-05-15 16:00:00 | 839 | 20.7849 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5766 | 4.44 | 2018-07-01T09:49:00Z | 0 | 12 | < 25mph |  |  |  | 0 | 0 | No data | E5766 | 4.44 | 2018-07-01T10:44:00Z | 2.01 | 24 | < 25mph
PG&E | 2018-06-30 | 11:14 | 39.3621 | -121.0809 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ENGINEER YUREK | 100091354 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 11:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1713 | 2018 | 6 | 30 | 11 | 14 | 18-0055945 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5724 | 3.7745 | 196_314 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 11:14:00 | 1454 | 12.1468 | FALSE | <25mph | E3651 | 2.44 | 2016-11-03T11:15:00Z | 2.01 | 12 | < 25mph | RRRC1 | 4.49 | 2016-11-03T11:13:00Z | 8.99 | 19 | < 25mph | E3651 | 2.44 | 2016-11-03T11:15:00Z | 2.01 | 24 | < 25mph | RRRC1 | 4.49 | 2016-11-03T12:13:00Z | 8.99 | 38 | < 25mph
PG&E | 2017-08-09 11:29 | 11:29 | 38.6532 | -120.6273 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101402496 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42956.4786 | 11:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1328 | 2017 | 8 | 9 | 11 | 29 | 17-0069107 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 54216 | 9.4272 | 216_275 | <25mph | <15mph | HFTD - Distribution | 2017-08-09 11:29:00 | 1066 | 11.5652 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GZFC1 | 5.69 | 2018-03-10T07:17:00Z | 7 | 3 | < 25mph |  |  |  | 0 | 0 | No data | GZFC1 | 5.69 | 2018-03-10T08:17:00Z | 8.99 | 5 | < 25mph
PG&E | 2017-09-23 | 14:17 | 40.6509 | -122.2974 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DARREN STEWART 448-2421 | 101467221 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43001 | 14:17 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1429 | 2017 | 9 | 23 | 14 | 17 | 17-0081216 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 98820 | 17.9072 | 145_386 | <25mph | <15mph | HFTD - Distribution | 2017-09-23 14:17:00 | 1167 | 24.6958 | FALSE | <25mph | C5599 | 3.73 | 2017-05-12T05:01:00Z | 5.99 | 4 | < 25mph | C5599 | 3.73 | 2017-05-12T05:01:00Z | 5.99 | 4 | < 25mph | C5599 | 3.73 | 2017-05-12T05:16:00Z | 7 | 7 | < 25mph | C5599 | 3.73 | 2017-05-12T05:16:00Z | 7 | 7 | < 25mph
PG&E | 2019-03-19 | 12:52 | 37.9956 | -120.3244 | Tree - cutting, 3rd party | Hardwood Forest | 1 meter - < 3 meters | Self Extinguished |  | 101045032 |  | 17000 | Conductor | Overhead | Yes | 43543 | 12:52 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-187 | 2019 | 3 | 19 | 12 | 52 | 19-0035101 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 70602 | 12.9023 | 229_239 | <25mph | <15mph | HFTD - Distribution | 2019-03-19 12:52:00 | 1736 | 14.3226 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.27 | 2015-10-23T14:02:00Z | 14 | 5 | < 25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.27 | 2015-10-23T15:02:00Z | 14.99 | 10 | < 25mph
PG&E | 2018-11-13 | 15:41 | 37.0644 | -121.9578 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101680441 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43417 | 15:41 | Other | N.A. | N.A. | N.A. | Human Error | Grow house | Other/Unknown | 1973 | 2018 | 11 | 13 | 15 | 41 | 18-0099492 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 21484 | 1.9347 | 157_188 | <25mph | <15mph | HFTD - Distribution | 2018-11-13 15:41:00 | 1713 | 13.1257 | FALSE | <25mph | D8700 | 0.73 | 2018-04-07T23:07:00Z | 14.99 | 35 | < 25mph | E5038 | 6.81 | 2018-04-07T22:43:00Z | 22.01 | 140 | < 25mph | D4738 | 3.92 | 2018-04-08T00:00:00Z | 15.99 | 66 | < 25mph | E5038 | 6.81 | 2018-04-07T22:43:00Z | 22.01 | 265 | < 25mph
PG&E | 2018-09-10 | 20:37 | 38.0188 | -122.7225 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 102252760 | Unknown | 12000 | Conductor | Overhead | Yes | 43353 | 20:37 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1889 | 2018 | 9 | 10 | 20 | 37 | 18-0078359 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 219903 | 12.2581 | 125_241 | <25mph | <15mph | HFTD - Distribution | 2018-09-10 20:37:00 | 1628 | 18.8462 | FALSE | <25mph | BBEC1 | 1.27 | 2015-06-28T04:11:00Z | 8.99 | 1 | < 25mph | BBEC1 | 1.27 | 2015-06-28T04:11:00Z | 8.99 | 2 | < 25mph | BBEC1 | 1.27 | 2015-06-28T05:11:00Z | 8.99 | 2 | < 25mph | BBEC1 | 1.27 | 2015-06-28T05:11:00Z | 8.99 | 4 | < 25mph
PG&E | 2017-08-27 | 20:04 | 38.9165 | -121.151 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-477-0641 x7, log 22629 | 100077184 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42974 | 20:04 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1352 | 2017 | 8 | 27 | 20 | 4 | 17-0073228 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 905 | 9.7822 | 193_290 | <25mph | <15mph | HFTD - Distribution | 2017-08-27 20:04:00 | 1090 | 16.757 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LICC1 | 6.69 | 2018-02-15T03:13:00Z | 12.01 | 19 | < 25mph |  |  |  | 0 | 0 | No data | LICC1 | 6.69 | 2018-02-15T03:13:00Z | 12.01 | 38 | < 25mph
PG&E | 2018-06-15 | 2:56 | 37.4869 | -122.4223 | Vegetation | Rural | < 0.25 Acres | Utility: PG&E | N.A. | Pole 10/5 | None | 60000 | Conductor | Overhead | Yes | 43266 | 2:56 | Contamination | N.A. | N.A. | N.A. | Unknown |  | no-match | 1659 | 2018 | 6 | 15 | 2 | 56 | INT-11115 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 0 | 6.5721 | 137_211 | <25mph | <15mph | HFTD - Transmission | 2018-06-15 02:56:00 | 1401 | 18.0175 | FALSE | <25mph | C3295 | 3.73 | 2015-06-24T05:22:00Z | 3 | 5 | < 25mph | HSPC1 | 5.28 | 2015-06-24T05:18:00Z | 30 | 62 | 25-40mph | C3295 | 3.73 | 2015-06-24T06:42:00Z | 7 | 8 | < 25mph | HSPC1 | 5.28 | 2015-06-24T06:18:00Z | 31 | 120 | 25-40mph
PG&E | 2016-08-10 | 2016-08-10 08:36 | 37.0575 | -121.9556 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 101680487 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0917 | 2016 | 8 | 10 | 8 | 36 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 6.3982 | 157_187 | <25mph | <15mph | HFTD - Distribution | 2016-08-10 08:36:00 | 659 | 9.833 | FALSE | <25mph | E5965 | 0.91 | 2015-07-29T19:24:00Z | 13 | 35 | < 25mph | E5965 | 0.91 | 2015-07-29T19:24:00Z | 13 | 141 | < 25mph | E5965 | 0.91 | 2015-07-29T19:24:00Z | 13 | 70 | < 25mph | E5965 | 0.91 | 2015-07-29T19:24:00Z | 13 | 275 | < 25mph
PG&E | 2015-02-07 18:38 | 2015-02-07 18:38 | 40.4674 | -123.6545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | mile marker 36.61, hwy 36, bridgeville |  | 12000 | Conductor | Overhead | Yes | 42042.7764 | 2015-02-07 18:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0262 | 2015 | 2 | 7 | 18 | 38 | 15-0011390 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 7691 | 20.9308 | 88_377 | <25mph | <15mph | HFTD - Distribution | 2015-02-07 18:38:00 | 9 | 24.639 | FALSE | <25mph | PG204 | 2.28 | 2019-09-01T03:10:00Z | 3.22 | 6 | < 25mph | PG250 | 6.89 | 2019-09-01T02:50:00Z | 7 | 18 | < 25mph | PG204 | 2.28 | 2019-09-01T03:10:00Z | 3.22 | 12 | < 25mph | PG250 | 6.89 | 2019-09-01T02:50:00Z | 7 | 36 | < 25mph
PG&E | 2016-07-20 19:15 | 2016-07-20 19:15 | 37.7712 | -121.8104 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100898986 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42571.8021 | 2016-07-20 19:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0865 | 2016 | 7 | 20 | 19 | 15 | 16-0051308 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3013 | 17.1873 | 164_226 | <25mph | <15mph | HFTD - Distribution | 2016-07-20 19:15:00 | 608 | 18.9944 | FALSE | <25mph | LVMC1 | 3.62 | 2015-01-06T12:02:00Z | 14.99 | 1 | < 25mph | LVMC1 | 3.62 | 2015-01-06T12:02:00Z | 14.99 | 49 | < 25mph | LVMC1 | 3.62 | 2015-01-06T13:02:00Z | 18.01 | 2 | < 25mph | LVMC1 | 3.62 | 2015-01-06T13:02:00Z | 18.01 | 98 | < 25mph
PG&E | 2016-07-25 15:32 | 2016-07-25 15:32 | 38.3522 | -120.7107 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42576.6472 | 2016-07-25 15:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0878 | 2016 | 7 | 25 | 15 | 32 | 16-0052398 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 19951 | 10.4912 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-25 15:32:00 | 621 | 14.4675 | FALSE | <25mph | PG372 | 3.34 | 2019-05-26T20:10:00Z | 23.02 | 18 | < 25mph | PG372 | 3.34 | 2019-05-26T20:10:00Z | 23.02 | 45 | < 25mph | PG372 | 3.34 | 2019-05-26T20:10:00Z | 23.02 | 36 | < 25mph | PG372 | 3.34 | 2019-05-26T20:10:00Z | 23.02 | 90 | < 25mph
PG&E | 2015-09-10 16:24 | 2015-09-10 16:24 | 38.5049 | -122.3535 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103159970 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42257.6833 | 2015-09-10 16:24 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0589 | 2015 | 9 | 10 | 16 | 24 | 15-0060610 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 130124 | 14.3548 | 141_267 | <25mph | <15mph | HFTD - Distribution | 2015-09-10 16:24:00 | 334 | 16.5969 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.22 | 2015-01-17T18:29:00Z | 8.01 | 25 | < 25mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.22 | 2015-01-17T18:29:00Z | 8.01 | 50 | < 25mph
PG&E | 2017-07-23 09:22 | 09:22 | 40.642 | -122.2302 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT? | 101459708 | FRONTIER COMMUNICATI | 12000 | Conductor | Overhead | Yes | 42939.3906 | 09:22 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1282 | 2017 | 7 | 23 | 9 | 22 | 17-0064801 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 184712 | 3.9314 | 148_385 | <25mph | <15mph | HFTD - Distribution | 2017-07-23 09:22:00 | 1021 | 13.6933 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C5599 | 5.97 | 2017-10-11T19:02:00Z | 8.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | C5599 | 5.97 | 2017-10-11T20:01:00Z | 10 | 8 | < 25mph
PG&E | 2016-07-15 14:09 | 2016-07-15 14:09 | 38.6965 | -120.8598 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412774 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.5896 | 2016-07-15 14:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0852 | 2016 | 7 | 15 | 14 | 9 | 16-0050274 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 11253 | 10.7453 | 205_277 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 14:09:00 | 595 | 14.2057 | FALSE | <25mph | PG027 | 3.79 | 2019-11-07T21:00:00Z | 9.93 | 42 | < 25mph | PG027 | 3.79 | 2019-11-07T21:00:00Z | 9.93 | 116 | < 25mph | PG359 | 3.32 | 2019-11-07T21:40:00Z | 10.51 | 84 | < 25mph | PG072 | 6.05 | 2019-11-07T22:10:00Z | 10.67 | 234 | < 25mph
PG&E | 2018-07-17 | 19:40 | 40.5927 | -122.4886 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101477082 | AT&T | 12000 | Conductor | Overhead | Yes | 43298 | 19:40 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1760 | 2018 | 7 | 17 | 19 | 40 | 18-0060840 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 30162 | 14.3022 | 137_382 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 19:40:00 | 1500 | 21.6282 | FALSE | <25mph | MMOC1 | 1.8 | 2015-08-06T17:00:00Z | 7 | 5 | < 25mph | E6886 | 7.8 | 2015-08-06T16:39:00Z | 8.01 | 14 | < 25mph | MMOC1 | 1.8 | 2015-08-06T17:00:00Z | 7 | 10 | < 25mph | E6886 | 7.8 | 2015-08-06T17:25:00Z | 8.99 | 28 | < 25mph
PG&E | 2017-08-05 18:13 | 18:08 | 39.0968 | -123.2147 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102196629 | Unknown | 12000 | Conductor | Overhead | Yes | 42952.7592 | 18:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1318 | 2017 | 8 | 5 | 18 | 8 | 17-0068200 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 134239 | 10.1139 | 105_301 | <25mph | <15mph | HFTD - Distribution | 2017-08-05 18:08:00 | 1056 | 16.2126 | FALSE | <25mph |  |  |  | 0 | 0 | No data | COWC1 | 7.84 | 2018-04-23T02:01:00Z | 14 | 13 | < 25mph |  |  |  | 0 | 0 | No data | COWC1 | 7.84 | 2018-04-23T02:01:00Z | 14 | 26 | < 25mph
PG&E | 2017-07-24 14:02 | 14:01 | 37.2635 | -122.3364 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike klink 650-879-0121 | 100322130 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42940.5845 | 14:01 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1286 | 2017 | 7 | 24 | 14 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 18.4533 | 141_199 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 14:01:00 | 1025 | 18.6394 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 5.31 | 2017-11-14T04:07:00Z | 3 | 1 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 5.31 | 2017-11-14T05:07:00Z | 3 | 2 | < 25mph
PG&E | 2017-07-08 19:23 | 18:49 | 40.2935 | -122.4089 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | TOM STROING, RED BLUFF | 101526269 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42924.8076 | 18:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1234 | 2017 | 7 | 8 | 18 | 49 | 17-0061469 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 157484 | 8.2983 | 140_366 | <25mph | <15mph | HFTD - Distribution | 2017-07-08 18:49:00 | 973 | 15.6109 | FALSE | <25mph | E7114 | 0.65 | 2016-01-15T05:03:00Z | 17 | 4 | < 25mph | E7114 | 0.65 | 2016-01-15T05:03:00Z | 17 | 4 | < 25mph | E7114 | 0.65 | 2016-01-15T05:03:00Z | 17 | 8 | < 25mph | E7114 | 0.65 | 2016-01-15T05:03:00Z | 17 | 8 | < 25mph
PG&E | 2015-09-06 19:27 | 2015-09-06 19:27 | 34.6195 | -120.2534 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Santa Barbara County Fire | meter# 1008400678 | Verizon | 12000 | Conductor | Overhead | Yes | 42253.8104 | 2015-09-06 19:27 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0582 | 2015 | 9 | 6 | 19 | 27 | 15-0059612 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 863 | 14.7315 | 234_53 | <25mph | <15mph | HFTD - Distribution | 2015-09-06 19:27:00 | 326 | 17.7534 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TT480 | 6.18 | 2019-06-23T00:20:00Z | 13 | 14 | < 25mph |  |  |  | 0 | 0 | No data | TT480 | 6.18 | 2019-06-23T00:20:00Z | 13 | 27 | < 25mph
PG&E | 2018-09-03 | 18:29 | 39.4547 | -121.4955 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100395672 | Unknown | 12000 | Conductor | Overhead | Yes | 43346 | 18:29 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1880 | 2018 | 9 | 3 | 18 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 6.2719 | 178_319 | <25mph | <15mph | HFTD - Distribution | 2018-09-03 18:29:00 | 1619 | 14.7897 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TT309 | 4.73 | 2019-03-19T02:45:00Z | 3 | 2 | < 25mph |  |  |  | 0 | 0 | No data | TT309 | 4.73 | 2019-03-19T03:45:00Z | 4 | 4 | < 25mph
PG&E | 2018-08-08 | 16:03 | 37.2974 | -122.2651 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 100307515 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 16:03 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1831 | 2018 | 8 | 8 | 16 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.1654 | 144_201 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:03:00 | 1570 | 9.1654 | FALSE | <25mph | LAHC1 | 0.77 | 2016-09-04T10:07:00Z | 11.01 | 1 | < 25mph | AU836 | 7.23 | 2016-09-04T10:05:00Z | 25.99 | 24 | 25-40mph | LAHC1 | 0.77 | 2016-09-04T10:07:00Z | 11.01 | 2 | < 25mph | AU836 | 7.23 | 2016-09-04T10:55:00Z | 30 | 48 | 25-40mph
PG&E | 2016-06-30 | 0:03 | 39.8157 | -121.5994 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42551 | 0:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0832 | 2016 | 6 | 30 | 0 | 3 | 16-0046763 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 299100 | 7.8781 | 174_339 | <25mph | <15mph | HFTD - Distribution | 2016-06-30 00:03:00 | 575 | 11.8323 | FALSE | <25mph | E2076 | 3.91 | 2017-04-19T15:43:00Z | 4 | 11 | < 25mph | C8878 | 4.73 | 2017-04-19T15:48:00Z | 8.01 | 24 | < 25mph | E2076 | 3.91 | 2017-04-19T16:33:00Z | 10 | 18 | < 25mph | C8878 | 4.73 | 2017-04-19T16:48:00Z | 12.01 | 41 | < 25mph
PG&E | 2019-05-17 | 15:12 | 38.4797 | -123.1486 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 42811111 |  | 12000 | Conductor | Overhead | Yes | 43602 | 15:12 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-200 | 2019 | 5 | 17 | 15 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 19.5511 | 107_266 | <25mph | <15mph | HFTD - Distribution | 2019-05-17 15:12:00 | 1775 | 20.334 | FALSE | <25mph | E8483 | 3.61 | 2016-04-10T12:08:00Z | 3 | 4 | < 25mph | E8483 | 3.61 | 2016-04-10T12:08:00Z | 3 | 25 | < 25mph | E8483 | 3.61 | 2016-04-10T12:08:00Z | 3 | 8 | < 25mph | E8483 | 3.61 | 2016-04-10T12:08:00Z | 3 | 48 | < 25mph
PG&E | 2019-06-18 | 19:49 | 35.8876 | -120.9217 | Bird Found | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Pole | Overhead | Yes | 43634 | 19:49 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | no-match | 2019-55 | 2019 | 6 | 18 | 19 | 49 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 15.5935 | 203_122 | <25mph | <15mph | HFTD - Distribution | 2019-06-18 19:49:00 | 1852 | 21.7258 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RBYC1 | 6.84 | 2015-03-30T04:12:00Z | 10 | 1 | < 25mph |  |  |  | 0 | 0 | No data | RBYC1 | 6.84 | 2015-03-30T05:12:00Z | 21 | 2 | < 25mph
PG&E | 2019-07-27 | 8:22 | 40.3789 | -122.1873 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Self Extinguished |  | 103461102 |  | 12000 | Conductor | Overhead | Yes | 43673 | 8:22 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-382 | 2019 | 7 | 27 | 8 | 22 | 19-0081756 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 456 | 4.4493 | 149_370 | <25mph | <15mph | HFTD - Distribution | 2019-07-27 08:22:00 | 1935 | 12.5056 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AP525 | 5.17 | 2016-12-27T12:45:00Z | 0 | 6 | < 25mph |  |  |  | 0 | 0 | No data | AP525 | 5.17 | 2016-12-27T13:45:00Z | 0 | 12 | < 25mph
PG&E | 2015-09-25 17:28 | 2015-09-25 17:28 | 38.7169 | -120.7693 | Vegetation | Rural | < 0.25 Acres | Fire Agency | el dorado F D | 101405928 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42272.7278 | 2015-09-25 17:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0616 | 2015 | 9 | 25 | 17 | 28 | 15-0063666 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 111180 | 8.3925 | 209_279 | <25mph | <15mph | HFTD - Distribution | 2015-09-25 17:28:00 | 361 | 11.4196 | FALSE | <25mph | E5691 | 2.8 | 2015-08-15T17:16:00Z | 4 | 16 | < 25mph | C6129 | 4.54 | 2015-08-15T17:09:00Z | 10 | 41 | < 25mph | E5691 | 2.8 | 2015-08-15T18:01:00Z | 8.01 | 32 | < 25mph | C6129 | 4.54 | 2015-08-15T17:49:00Z | 14.99 | 81 | < 25mph
PG&E | 2016-07-08 10:49 | 2016-07-08 10:49 | 38.3373 | -122.1211 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 102291118 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42559.4507 | 2016-07-08 10:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0842 | 2016 | 7 | 8 | 10 | 49 | 16-0048647 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 19469 | 8.3702 | 151_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-08 10:49:00 | 585 | 20.6133 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6079 | 6.28 | 2016-07-17T18:51:00Z | 17 | 11 | < 25mph |  |  |  | 0 | 0 | No data | E6079 | 6.28 | 2016-07-17T19:58:00Z | 17 | 23 | < 25mph
PG&E | 2018-06-08 | 19:03 | 35.154 | -120.594 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101852092 | AT&T | 12000 | Conductor | Overhead | Yes | 43259 | 19:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1644 | 2018 | 6 | 8 | 19 | 3 | 18-0049130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2473 | 24.0333 | 218_82 | <25mph | <15mph | HFTD - Distribution | 2018-06-08 19:03:00 | 1386 | 25.9327 | FALSE | 25-40mph | C9687 | 2.18 | 2017-12-05T22:18:00Z | 18.01 | 26 | < 25mph | C9687 | 2.18 | 2017-12-05T22:18:00Z | 18.01 | 34 | < 25mph | C9687 | 2.18 | 2017-12-05T22:18:00Z | 18.01 | 44 | < 25mph | C9687 | 2.18 | 2017-12-05T22:18:00Z | 18.01 | 62 | < 25mph
PG&E | 2017-07-02 | 13:28 | 39.8605 | -121.6274 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 000/017c | Unknown | 60000 | Conductor | Overhead | Yes | 42918 | 13:28 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1216 | 2017 | 7 | 2 | 13 | 28 | INT-09794 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 10.1141 | 173_342 | <25mph | <15mph | HFTD - Transmission | 2017-07-02 13:28:00 | 956 | 11.4462 | FALSE | <25mph | C8878 | 1.44 | 2016-11-05T00:38:00Z | 0 | 19 | < 25mph | CSTC1 | 7.55 | 2016-11-04T23:51:00Z | 8.99 | 24 | < 25mph | C4565 | 1.76 | 2016-11-05T00:53:00Z | 1.01 | 37 | < 25mph | CSTC1 | 7.55 | 2016-11-04T23:51:00Z | 8.99 | 44 | < 25mph
PG&E | 2016-08-03 | 2016-08-03 04:38 | 38.8474 | -120.812 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire garden valley fire | 103809676 |  | 21000 | Conductor | Overhead | Yes | 42585 | 2016-08-03 04:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0901 | 2016 | 8 | 3 | 4 | 38 | 16-0054597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2751 | 9.4989 | 208_286 | <25mph | <15mph | HFTD - Distribution | 2016-08-03 04:38:00 | 644 | 11.5219 | FALSE | <25mph | PG022 | 1.4 | 2018-07-19T10:40:00Z | 1.1 | 18 | < 25mph | E3165 | 4.76 | 2018-07-19T10:37:00Z | 8.01 | 44 | < 25mph | PG022 | 1.4 | 2018-07-19T10:40:00Z | 1.1 | 36 | < 25mph | E3165 | 4.76 | 2018-07-19T11:37:00Z | 8.99 | 88 | < 25mph
7. Camp Fire | 2018-11-08 | 6:33 | 39.8134 | -121.4347 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 60000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1993 | 2018 | 11 | 8 | 6 | 33 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Conductor | 826291590 | 33.1236 | 181_339 | 25-40mph | 30-45mph | HFTD - Transmission | 2018-11-08 06:33:00 | 1699 | 39.0185 | FALSE | 25-40mph | PG328 | 2.77 | 2019-10-03T11:40:00Z | 18.7 | 12 | < 25mph | JBGC1 | 6.08 | 2019-10-03T11:13:00Z | 21 | 31 | < 25mph | PG328 | 2.77 | 2019-10-03T12:30:00Z | 19.66 | 24 | < 25mph | JBGC1 | 6.08 | 2019-10-03T11:13:00Z | 21 | 62 | < 25mph
PG&E | 2016-08-01 | 2016-08-01 12:50 | 38.9044 | -121.1274 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100078299 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42583 | 2016-08-01 12:50 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0896 | 2016 | 8 | 1 | 12 | 50 | 16-0054142 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 855 | 9.1677 | 194_289 | <25mph | <15mph | HFTD - Distribution | 2016-08-01 12:50:00 | 639 | 14.2258 | FALSE | <25mph | D8862 | 3.4 | 2016-12-03T18:29:00Z | 0 | 4 | < 25mph | LICC1 | 7.66 | 2016-12-03T18:13:00Z | 5.99 | 7 | < 25mph | D8862 | 3.4 | 2016-12-03T19:29:00Z | 0 | 8 | < 25mph | LICC1 | 7.66 | 2016-12-03T19:13:00Z | 5.99 | 18 | < 25mph
PG&E | 2018-06-22 | 17:44 | 37.2485 | -119.5625 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Madera County | 101117749 | None | 0 – 750 | Conductor | Overhead | Yes | 43273 | 17:44 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1686 | 2018 | 6 | 22 | 17 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 10.123 | 263_198 | <25mph | <15mph | HFTD - Distribution | 2018-06-22 17:44:00 | 1428 | 12.3323 | FALSE | <25mph | NFRC1 | 3.29 | 2015-07-06T22:55:00Z | 13 | 4 | < 25mph | D7778 | 5.05 | 2015-07-06T22:47:00Z | 14.99 | 45 | < 25mph | NFRC1 | 3.29 | 2015-07-06T23:55:00Z | 13 | 8 | < 25mph | D7778 | 5.05 | 2015-07-06T22:47:00Z | 14.99 | 92 | < 25mph
PG&E | 2015-12-31 19:12 | 2015-12-31 19:12 | 37.1568 | -121.9868 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LOS GATOS MONTE SERENO SARATOGA | 100518215 | Verizon | 21000 | Conductor | Overhead | Yes | 42369.8 | 2015-12-31 19:12 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0689 | 2015 | 12 | 31 | 19 | 12 | 15-0087962 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7979 | 7.4149 | 156_193 | <25mph | <15mph | HFTD - Distribution | 2015-12-31 19:12:00 | 433 | 10.9251 | FALSE | <25mph | LSGC1 | 3.83 | 2018-05-12T11:32:00Z | 14 | 17 | < 25mph | E6085 | 6.01 | 2018-05-12T12:00:00Z | 14.99 | 171 | < 25mph | LSGC1 | 3.83 | 2018-05-12T11:32:00Z | 14 | 35 | < 25mph | E6085 | 6.01 | 2018-05-12T12:00:00Z | 14.99 | 344 | < 25mph
PG&E | 2017-09-03 | 17:52 | 37.4956 | -119.8367 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101086621 | Unknown | 21000 | Transformer | Overhead | Yes | 42981 | 17:52 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 1389 | 2017 | 9 | 3 | 17 | 52 | 17-0075617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 4512 | 13.9592 | 250_212 | <25mph | <15mph | HFTD - Distribution | 2017-09-03 17:52:00 | 1127 | 22.0754 | FALSE | <25mph | PG456 | 2.07 | 2019-10-11T17:00:00Z | 5.64 | 19 | < 25mph | PG189 | 4.68 | 2019-10-11T17:20:00Z | 9.73 | 41 | < 25mph | PG522 | 3.37 | 2019-10-11T17:40:00Z | 7.45 | 38 | < 25mph | PG189 | 4.68 | 2019-10-11T18:20:00Z | 10.67 | 81 | < 25mph
PG&E | 2015-09-18 17:05 | 2015-09-18 17:05 | 37.8992 | -120.4551 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101019893 |  | 17000 | Conductor | Overhead | Yes | 42265.7118 | 2015-09-18 17:05 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0602 | 2015 | 9 | 18 | 17 | 5 | 15-0062207 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 35222 | 9.055 | 223_234 | <25mph | <15mph | HFTD - Distribution | 2015-09-18 17:05:00 | 347 | 11.0018 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.2 | 2018-07-24T09:03:00Z | 4 | 1 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.2 | 2018-07-24T10:03:00Z | 4 | 2 | < 25mph
PG&E | 2015-03-15 22:47 | 2015-03-15 22:47 | 38.3346 | -120.5325 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 103106530 |  | 12000 | Conductor | Overhead | Yes | 42078.9493 | 2015-03-15 22:47 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0279 | 2015 | 3 | 15 | 22 | 47 | 15-0019709 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 14520 | 7.4897 | 220_257 | <25mph | <15mph | HFTD - Distribution | 2015-03-15 22:47:00 | 25 | 18.5478 | FALSE | <25mph | AT317 | 2.19 | 2017-04-06T21:20:00Z | 27 | 15 | 25-40mph | ESPC1 | 4.17 | 2017-04-06T21:13:00Z | 38.99 | 37 | 25-40mph | AT317 | 2.19 | 2017-04-06T21:20:00Z | 27 | 29 | 25-40mph | ESPC1 | 4.17 | 2017-04-06T22:13:00Z | 42.01 | 74 | 40-55mph
PG&E | 2018-06-19 | 0:27 | 38.7604 | -120.8224 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101388356 | Unknown | 12000 | Conductor | Overhead | Yes | 43270 | 0:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1675 | 2018 | 6 | 19 | 0 | 27 | 18-0052111 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 141652 | 7.2853 | 207_281 | <25mph | <15mph | HFTD - Distribution | 2018-06-19 00:27:00 | 1417 | 13.5304 | FALSE | <25mph | E5691 | 1.82 | 2015-08-10T14:54:00Z | 4 | 12 | < 25mph | D2736 | 6.02 | 2015-08-10T15:25:00Z | 8.01 | 42 | < 25mph | E5691 | 1.82 | 2015-08-10T16:34:00Z | 4 | 24 | < 25mph | D2736 | 6.02 | 2015-08-10T16:35:00Z | 8.01 | 84 | < 25mph
PG&E | 2015-05-06 17:17 | 2015-05-06 17:17 | 37.4273 | -119.8803 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | BOOSTER 8179 INDIAN PEEK N/O MIWUK | None | 21000 | Other | Overhead | Yes | 42130.7201 | 2015-05-06 17:17 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0307 | 2015 | 5 | 6 | 17 | 17 | 15-0032311 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 81600 | 12.4413 | 249_208 | <25mph | <15mph | HFTD - Distribution | 2015-05-06 17:17:00 | 53 | 13.2212 | FALSE | <25mph | C1522 | 2.85 | 2015-11-08T10:07:00Z | 3 | 5 | < 25mph | MIAC1 | 7.42 | 2015-11-08T09:59:00Z | 11.01 | 8 | < 25mph | C1522 | 2.85 | 2015-11-08T10:57:00Z | 3 | 7 | < 25mph | MIAC1 | 7.42 | 2015-11-08T10:59:00Z | 12.01 | 13 | < 25mph
PG&E | 2015-08-19 06:20 | 2015-08-19 06:20 | 39.2831 | -123.2931 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | MTR#50001225 | None | 12000 | Conductor | Overhead | Yes | 42235.2639 | 2015-08-19 06:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0545 | 2015 | 8 | 19 | 6 | 20 | 15-0055982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5403 | 1.4303 | 102_311 | <25mph | <15mph | HFTD - Distribution | 2015-08-19 06:20:00 | 289 | 19.8186 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AT319 | 6.89 | 2015-01-29T18:24:00Z | 4 | 15 | < 25mph |  |  |  | 0 | 0 | No data | AT319 | 6.89 | 2015-01-29T19:09:00Z | 4.99 | 31 | < 25mph
PG&E | 2015-09-06 19:27 | 2015-09-06 19:27 | 34.6195 | -120.2534 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Santa Barbara County Fire | meter# 1008400678 | Verizon | 12000 | Conductor | Overhead | Yes | 42253.8104 | 2015-09-06 19:27 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0582 | 2015 | 9 | 6 | 19 | 27 | 15-0059612 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 863 | 14.7315 | 234_53 | <25mph | <15mph | HFTD - Distribution | 2015-09-06 19:27:00 | 326 | 17.7534 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2015-04-11 17:16 | 2015-04-11 17:16 | 40.5462 | -122.2343 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101491414 |  | 12000 | Conductor | Overhead | Yes | 42105.7194 | 2015-04-11 17:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0286 | 2015 | 4 | 11 | 17 | 16 | 15-0026023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 11914 | 19.429 | 148_380 | <25mph | <15mph | HFTD - Distribution | 2015-04-11 17:16:00 | 32 | 19.429 | FALSE | <25mph | RRAC1 | 3.7 | 2015-07-20T08:24:00Z | 4 | 1 | < 25mph | RRAC1 | 3.7 | 2015-07-20T08:24:00Z | 4 | 2 | < 25mph | RRAC1 | 3.7 | 2015-07-20T09:24:00Z | 4.99 | 2 | < 25mph | RRAC1 | 3.7 | 2015-07-20T09:24:00Z | 4.99 | 4 | < 25mph
PG&E | 2016-07-15 05:19 | 2016-07-15 05:19 | 35.1839 | -120.5018 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101846594 |  | 12000 | Conductor | Overhead | Yes | 42566.2215 | 2016-07-15 05:19 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0851 | 2016 | 7 | 15 | 5 | 19 | 16-0050086 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 62404 | 2.6454 | 222_84 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 05:19:00 | 594 | 14.1102 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-06-04 | 9:25 | 35.4593 | -120.4921 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101895513 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43255 | 9:25 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1624 | 2018 | 6 | 4 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 12.0315 | 222_99 | <25mph | <15mph | HFTD - Distribution | 2018-06-04 09:25:00 | 1366 | 20.4837 | FALSE | <25mph | PG271 | 3.63 | 2019-12-13T11:30:00Z | 5.99 | 19 | < 25mph | PG205 | 7.15 | 2019-12-13T11:30:00Z | 8.84 | 59 | < 25mph | PG271 | 3.63 | 2019-12-13T12:50:00Z | 7.16 | 38 | < 25mph | PG205 | 7.15 | 2019-12-13T11:30:00Z | 8.84 | 117 | < 25mph
PG&E | 2016-08-17 | 2016-08-17 12:23 | 41.2495 | -123.7671 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103315791 |  | 12000 | Conductor | Overhead | Yes | 42599 | 2016-08-17 12:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0932 | 2016 | 8 | 17 | 12 | 23 | 16-0058002 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 16544 | 13.4388 | 84_420 | <25mph | <15mph | HFTD - Distribution | 2016-08-17 12:23:00 | 675 | 14.3475 | FALSE | <25mph |  |  |  | 0 | 0 | No data | NTCC1 | 5.46 | 2019-07-24T12:45:00Z | 4.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | NTCC1 | 5.46 | 2019-07-24T13:45:00Z | 5.99 | 2 | < 25mph
PG&E | 2018-09-21 | 21:10 | 39.0273 | -122.6627 | Vegetation | Rural | < 3 meters | Customer | N.A. | 102147414 | Unknown | 12000 | Conductor | Overhead | Yes | 43364 | 21:10 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1908 | 2018 | 9 | 21 | 21 | 10 | 18-0082278 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 281055 | 11.7868 | 128_296 | <25mph | <15mph | HFTD - Distribution | 2018-09-21 21:10:00 | 1647 | 15.5314 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2017-07-07 | 15:09 | 40.9054 | -122.3806 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101455950 | Unknown | 12000 | Conductor | Overhead | Yes | 42923 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1229 | 2017 | 7 | 7 | 15 | 9 | 17-0061903 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.0906 | 142_400 | <25mph | <15mph | HFTD - Distribution | 2017-07-07 15:09:00 | 969 | 11.4161 | FALSE | <25mph | SLFC1 | 2.92 | 2016-06-22T22:19:00Z | 15.99 | 5 | < 25mph | SLFC1 | 2.92 | 2016-06-22T22:19:00Z | 15.99 | 5 | < 25mph | SLFC1 | 2.92 | 2016-06-22T23:19:00Z | 15.99 | 10 | < 25mph | SLFC1 | 2.92 | 2016-06-22T23:19:00Z | 15.99 | 10 | < 25mph
PG&E | 2017-10-08 | 22:19 | 39.7371 | -121.6464 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 103319605 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43016 | 22:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1468 | 2017 | 10 | 8 | 22 | 19 | 17-0085504 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 42839 | 9.4272 | 172_335 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 22:19:00 | 1208 | 31.7535 | FALSE | 25-40mph | PDEC1 | 1.62 | 2017-08-13T03:00:00Z | 4 | 1 | < 25mph | PDEC1 | 1.62 | 2017-08-13T03:00:00Z | 4 | 6 | < 25mph | PDEC1 | 1.62 | 2017-08-13T03:00:00Z | 4 | 2 | < 25mph | PDEC1 | 1.62 | 2017-08-13T03:00:00Z | 4 | 13 | < 25mph
PG&E | 2017-11-11 12:17 | 11:57 | 35.1191 | -120.3936 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Jordan Dayley ph#929-3911,engine#3467 | 101931190 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43050.5115 | 11:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1518 | 2017 | 11 | 11 | 11 | 57 | 17-0094408 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29093 | 8.6182 | 227_80 | <25mph | <15mph | HFTD - Distribution | 2017-11-11 11:57:00 | 1260 | 14.1707 | FALSE | <25mph | AU609 | 1.13 | 2017-06-20T10:37:00Z | 1.01 | 3 | < 25mph | AU609 | 1.13 | 2017-06-20T10:37:00Z | 1.01 | 10 | < 25mph | AU609 | 1.13 | 2017-06-20T10:37:00Z | 1.01 | 7 | < 25mph | AU609 | 1.13 | 2017-06-20T10:37:00Z | 1.01 | 19 | < 25mph
PG&E | 2017-06-27 09:28 | 9:23 | 37.9559 | -122.6176 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | marin county fire | 102260068 | UNFILED | 12000 | Conductor | Overhead | Yes | 42913.3944 | 9:23 | Other | N.A. | N.A. | N.A. | Unknown |  | Fell into (slight defect) | 1203 | 2017 | 6 | 27 | 9 | 23 | 17-0058882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 3920 | 16.1278 | 129_237 | <25mph | <15mph | HFTD - Distribution | 2017-06-27 09:23:00 | 942 | 18.7182 | FALSE | <25mph | WDAC1 | 2.81 | 2018-05-20T01:51:00Z | 35.99 | 23 | 25-40mph | NBRC1 | 6.33 | 2018-05-20T01:33:00Z | 48 | 29 | 40-55mph | WDAC1 | 2.81 | 2018-05-20T01:51:00Z | 35.99 | 46 | 25-40mph | NBRC1 | 6.33 | 2018-05-20T02:33:00Z | 49.01 | 58 | 40-55mph
PG&E | 2015-12-03 12:10 | 2015-12-03 12:10 | 40.0277 | -120.9652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | usfs | spanish creek campground |  | 12000 | Conductor | Overhead | Yes | 42341.5069 | 2015-12-03 12:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0683 | 2015 | 12 | 3 | 12 | 10 | 15-0082505 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 196854 | 26.293 | 201_351 | 25-40mph | 15-30mph | HFTD - Distribution | 2015-12-03 12:10:00 | 427 | 26.9543 | FALSE | 25-40mph | CHAC1 | 3.2 | 2018-07-16T02:47:00Z | 14.99 | 2 | < 25mph | CHAC1 | 3.2 | 2018-07-16T02:47:00Z | 14.99 | 3 | < 25mph | CHAC1 | 3.2 | 2018-07-16T02:47:00Z | 14.99 | 4 | < 25mph | CHAC1 | 3.2 | 2018-07-16T02:47:00Z | 14.99 | 6 | < 25mph
PG&E | 2019-06-10 | 13:29 | 38.8137 | -120.9433 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Other | Customer | 153652109 |  | 21000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-243 | 2019 | 6 | 10 | 13 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.2437 | 202_284 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 13:29:00 | 1823 | 9.9566 | FALSE | <25mph | PLTC1 | 3.76 | 2015-02-11T20:56:00Z | 8.99 | 1 | < 25mph | PLTC1 | 3.76 | 2015-02-11T20:56:00Z | 8.99 | 25 | < 25mph | PLTC1 | 3.76 | 2015-02-11T20:56:00Z | 8.99 | 2 | < 25mph | PLTC1 | 3.76 | 2015-02-11T20:56:00Z | 8.99 | 50 | < 25mph
PG&E | 2018-04-27 | 12:48 | 39.1717 | -120.8652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | incident # 9960 ph # 530-8850111 | 100075314 | Unknown | 12000 | Conductor | Overhead | Yes | 43217 | 12:48 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Dead | 1577 | 2018 | 4 | 27 | 12 | 48 | 18-0036310 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 28650 | 12.9115 | 205_304 | <25mph | <15mph | HFTD - Distribution | 2018-04-27 12:48:00 | 1319 | 12.9115 | FALSE | <25mph | PG059 | 3.05 | 2019-01-02T15:10:00Z | 5.03 | 13 | < 25mph | PG059 | 3.05 | 2019-01-02T15:10:00Z | 5.03 | 38 | < 25mph | PG059 | 3.05 | 2019-01-02T15:10:00Z | 5.03 | 26 | < 25mph | PG059 | 3.05 | 2019-01-02T15:10:00Z | 5.03 | 65 | < 25mph
PG&E | 2019-06-26 | 13:14 | 40.0185 | -122.4107 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | Circuit Id 103331101 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43642 | 13:14 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-331 | 2019 | 6 | 26 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2684 | 140_351 | <25mph | <15mph | HFTD - Distribution | 2019-06-26 13:14:00 | 1870 | 19.4401 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG276 | 6.5 | 2019-06-10T08:40:00Z | 6.58 | 12 | < 25mph |  |  |  | 0 | 0 | No data | PG276 | 6.5 | 2019-06-10T09:40:00Z | 8.99 | 24 | < 25mph
PG&E | 2018-02-07 | 9:16 | 38.0369 | -120.2096 | Vegetation | Rural | < 3 meters | Fire Agency | Jason Podesta 209-586-3362 | 101038120 | AT&T | 17000 | Conductor | Overhead | Yes | 43138 | 9:16 | Contact From Object | N.A. | Other | Electric Facility | Human Error | third-party caused | Other/Unknown | 1559 | 2018 | 2 | 7 | 9 | 16 | 18-0012146 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 78738 | 9.6764 | 234_241 | <25mph | <15mph | HFTD - Distribution | 2018-02-07 09:16:00 | 1301 | 13.44 | FALSE | <25mph | MOUC1 | 2.73 | 2017-08-19T02:02:00Z | 18.99 | 1 | < 25mph | MOUC1 | 2.73 | 2017-08-19T02:02:00Z | 18.99 | 1 | < 25mph | MOUC1 | 2.73 | 2017-08-19T02:02:00Z | 18.99 | 2 | < 25mph | MOUC1 | 2.73 | 2017-08-19T02:02:00Z | 18.99 | 2 | < 25mph
PG&E | 2017-09-12 | 9:24 | 39.741 | -121.6079 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 911 | 100330302 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42990 | 9:24 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1410 | 2017 | 9 | 12 | 9 | 24 | 17-0078149 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 402890 | 5.7135 | 174_335 | <25mph | <15mph | HFTD - Distribution | 2017-09-12 09:24:00 | 1148 | 23.672 | FALSE | <25mph | PDEC1 | 1.25 | 2018-11-28T10:00:00Z | 7 | 1 | < 25mph | PDEC1 | 1.25 | 2018-11-28T10:00:00Z | 7 | 6 | < 25mph | PDEC1 | 1.25 | 2018-11-28T10:00:00Z | 7 | 2 | < 25mph | JBGC1 | 6.33 | 2018-11-28T11:13:00Z | 8.99 | 12 | < 25mph
PG&E | 2017-09-12 | 9:24 | 39.741 | -121.6079 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 911 | 100330302 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42990 | 9:24 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1410 | 2017 | 9 | 12 | 9 | 24 | 17-0078149 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 402890 | 5.7135 | 174_335 | <25mph | <15mph | HFTD - Distribution | 2017-09-12 09:24:00 | 1148 | 23.672 | FALSE | <25mph | PDEC1 | 1.25 | 2018-12-15T23:00:00Z | 4 | 1 | < 25mph | JBGC1 | 6.33 | 2018-12-15T23:13:00Z | 8.01 | 7 | < 25mph | PDEC1 | 1.25 | 2018-12-16T00:00:00Z | 5.99 | 2 | < 25mph | JBGC1 | 6.33 | 2018-12-16T00:13:00Z | 8.01 | 12 | < 25mph
PG&E | 2016-11-15 | 17:27 | 39.7275 | -121.6557 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100327525 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42689 | 17:27 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 1049 | 2016 | 11 | 15 | 17 | 27 | 16-0080083 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 69231 | 9.6883 | 172_334 | <25mph | <15mph | HFTD - Distribution | 2016-11-15 17:27:00 | 790 | 16.6369 | FALSE | <25mph | PDEC1 | 2.44 | 2015-03-24T20:00:00Z | 4 | 1 | < 25mph | E2076 | 4.45 | 2015-03-24T20:24:00Z | 4 | 16 | < 25mph | PDEC1 | 2.44 | 2015-03-24T21:00:00Z | 4 | 2 | < 25mph | E2076 | 4.45 | 2015-03-24T21:27:00Z | 5.99 | 32 | < 25mph
PG&E | 2015-08-30 17:05 | 2015-08-30 17:05 | 38.4039 | -120.5559 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | centennial mine rd |  | 12000 | Conductor | Overhead | Yes | 42246.7118 | 2015-08-30 17:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0567 | 2015 | 8 | 30 | 17 | 5 | 15-0058273 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 40298 | 10.8566 | 219_261 | <25mph | <15mph | HFTD - Distribution | 2015-08-30 17:05:00 | 311 | 12.2451 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C9148 | 6.15 | 2018-06-03T05:34:00Z | 7 | 22 | < 25mph |  |  |  | 0 | 0 | No data | C9148 | 6.15 | 2018-06-03T07:18:00Z | 8.99 | 43 | < 25mph
PG&E | 2018-09-01 | 14:25 | 36.8088 | -121.5916 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Twr 35/222 | None | 115000 | Conductor | Overhead | Yes | 43344 | 14:25 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1875 | 2018 | 9 | 1 | 14 | 25 | INT-11331 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 702145 | 13.8683 | 173_173 | <25mph | <15mph | HFTD - Transmission | 2018-09-01 14:25:00 | 1614 | 16.3299 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-06-22 | 17:44 | 37.2485 | -119.5625 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Madera County | 101117749 | None | 0 – 750 | Conductor | Overhead | Yes | 43273 | 17:44 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1686 | 2018 | 6 | 22 | 17 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 10.123 | 263_198 | <25mph | <15mph | HFTD - Distribution | 2018-06-22 17:44:00 | 1428 | 12.3323 | FALSE | <25mph | NFRC1 | 3.29 | 2018-02-06T13:55:00Z | 8.01 | 4 | < 25mph | NFRC1 | 3.29 | 2018-02-06T13:55:00Z | 8.01 | 42 | < 25mph | C6459 | 2.53 | 2018-02-06T15:00:00Z | 8.01 | 8 | < 25mph | C6459 | 2.53 | 2018-02-06T15:00:00Z | 8.01 | 84 | < 25mph
PG&E | 2016-06-12 | 2016-06-12 13:14 | 37.5096 | -120.0462 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101083986 |  | 0 – 750 | Conductor | Overhead | Yes | 42533 | 2016-06-12 13:14 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0795 | 2016 | 6 | 12 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.8806 | 241_212 | <25mph | <15mph | HFTD - Distribution | 2016-06-12 13:14:00 | 539 | 13.4596 | FALSE | <25mph | MPOC1 | 3.28 | 2017-04-15T09:07:00Z | 7 | 1 | < 25mph | MPOC1 | 3.28 | 2017-04-15T09:07:00Z | 7 | 1 | < 25mph | MPOC1 | 3.28 | 2017-04-15T10:07:00Z | 8.99 | 2 | < 25mph | MPOC1 | 3.28 | 2017-04-15T10:07:00Z | 8.99 | 2 | < 25mph
PG&E | 2018-06-19 | 0:27 | 38.7604 | -120.8224 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101388356 | Unknown | 12000 | Conductor | Overhead | Yes | 43270 | 0:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1675 | 2018 | 6 | 19 | 0 | 27 | 18-0052111 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 141652 | 7.2853 | 207_281 | <25mph | <15mph | HFTD - Distribution | 2018-06-19 00:27:00 | 1417 | 13.5304 | FALSE | <25mph | E5691 | 1.82 | 2017-07-16T07:48:00Z | 0 | 11 | < 25mph | E3165 | 5.03 | 2017-07-16T06:55:00Z | 2.01 | 57 | < 25mph | E5691 | 1.82 | 2017-07-16T08:48:00Z | 0 | 22 | < 25mph | D2736 | 6.02 | 2017-07-16T08:25:00Z | 4 | 116 | < 25mph
PG&E | 2015-09-18 17:05 | 2015-09-18 17:05 | 37.8992 | -120.4551 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101019893 |  | 17000 | Conductor | Overhead | Yes | 42265.7118 | 2015-09-18 17:05 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0602 | 2015 | 9 | 18 | 17 | 5 | 15-0062207 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 35222 | 9.055 | 223_234 | <25mph | <15mph | HFTD - Distribution | 2015-09-18 17:05:00 | 347 | 11.0018 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.2 | 2015-04-05T03:03:00Z | 17 | 1 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.2 | 2015-04-05T04:03:00Z | 17 | 2 | < 25mph
PG&E | 2016-08-10 | 2016-08-10 08:36 | 37.0575 | -121.9556 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 101680487 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0917 | 2016 | 8 | 10 | 8 | 36 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 6.3982 | 157_187 | <25mph | <15mph | HFTD - Distribution | 2016-08-10 08:36:00 | 659 | 9.833 | FALSE | <25mph | PG262 | 3.76 | 2019-08-08T03:50:00Z | 14.7 | 61 | < 25mph | PG476 | 6.38 | 2019-08-08T03:30:00Z | 15.12 | 236 | < 25mph | PG262 | 3.76 | 2019-08-08T03:50:00Z | 14.7 | 121 | < 25mph | PG476 | 6.38 | 2019-08-08T04:30:00Z | 15.35 | 466 | < 25mph
PG&E | 2019-07-27 | 8:22 | 40.3789 | -122.1873 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Self Extinguished |  | 103461102 |  | 12000 | Conductor | Overhead | Yes | 43673 | 8:22 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-382 | 2019 | 7 | 27 | 8 | 22 | 19-0081756 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 456 | 4.4493 | 149_370 | <25mph | <15mph | HFTD - Distribution | 2019-07-27 08:22:00 | 1935 | 12.5056 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AP525 | 5.17 | 2016-05-09T22:15:00Z | 5.99 | 7 | < 25mph |  |  |  | 0 | 0 | No data | AP525 | 5.17 | 2016-05-09T22:15:00Z | 5.99 | 13 | < 25mph
PG&E | 2017-07-07 20:49 | 14:31 | 37.499 | -119.799 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVEN WARD OFFICE 209-966-3542 CELL559-706-8811 | 103855637 | Unknown | 21000 | Conductor | Overhead | Yes | 42923.8675 | 14:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1230 | 2017 | 7 | 7 | 14 | 31 | 17-0061288 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 554306 | 11.2535 | 252_212 | <25mph | <15mph | HFTD - Distribution | 2017-07-07 14:31:00 | 968 | 22.3608 | FALSE | <25mph | JSDC1 | 3.81 | 2017-06-21T02:47:00Z | 8.99 | 1 | < 25mph | MIAC1 | 6.24 | 2017-06-21T02:59:00Z | 17 | 9 | < 25mph | JSDC1 | 3.81 | 2017-06-21T02:47:00Z | 8.99 | 2 | < 25mph | MIAC1 | 6.24 | 2017-06-21T03:59:00Z | 18.99 | 16 | < 25mph
PG&E | 2015-03-04 18:44 | 2015-03-04 18:44 | 38.9995 | -122.7545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kelseyville FD | 102156367 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42067.7806 | 2015-03-04 18:44 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0271 | 2015 | 3 | 4 | 18 | 44 | 15-0017374 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29532 | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2015-03-04 18:44:00 | NA | 0 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.58 | 2016-06-10T11:57:00Z | 15.99 | 5 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.58 | 2016-06-10T12:57:00Z | 21 | 10 | < 25mph
PG&E | 2018-08-24 | 5:03 | 39.1184 | -121.0154 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JIM SMITH BATT CHIEF 3 | 100097647 | Unknown | 12000 | Conductor | Overhead | Yes | 43336 | 5:03 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1858 | 2018 | 8 | 24 | 5 | 3 | 18-0073024 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 4048 | 6.5682 | 199_301 | <25mph | <15mph | HFTD - Distribution | 2018-08-24 05:03:00 | 1597 | 12.3049 | FALSE | <25mph | C5488 | 3.16 | 2017-05-25T18:53:00Z | 14 | 29 | < 25mph | C5488 | 3.16 | 2017-05-25T18:53:00Z | 14 | 64 | < 25mph | C5488 | 3.16 | 2017-05-25T18:53:00Z | 14 | 60 | < 25mph | C5488 | 3.16 | 2017-05-25T18:53:00Z | 14 | 132 | < 25mph
PG&E | 2018-07-30 | 14:36 | 38.1987 | -120.3638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NICK WEBB ( 209) 532-7424 | 103336176 | Unknown | 17000 | Conductor | Overhead | Yes | 43311 | 14:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1800 | 2018 | 7 | 30 | 14 | 36 | 18-0065131 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18530 | 10.5817 | 227_250 | <25mph | <15mph | HFTD - Distribution | 2018-07-30 14:36:00 | 1540 | 14.4256 | FALSE | <25mph | E8204 | 0 | 2018-06-06T07:24:00Z | 0 | 4 | < 25mph | E9838 | 7.59 | 2018-06-06T07:27:00Z | 2.01 | 20 | < 25mph | E8204 | 0 | 2018-06-06T08:24:00Z | 0 | 8 | < 25mph | E9838 | 7.59 | 2018-06-06T08:24:00Z | 4.99 | 40 | < 25mph
PG&E | 2015-09-10 18:39 | 2015-09-10 18:39 | 40.7569 | -123.7958 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 096/004 |  | 115000 | Conductor | Overhead | Yes | 42257.7771 | 2015-09-10 18:39 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0590 | 2015 | 9 | 10 | 18 | 39 | RM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 2.2423 | 82_393 | <25mph | <15mph | HFTD - Transmission | 2015-09-10 18:39:00 | 335 | 12.4043 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.39 | 2017-07-27T10:55:00Z | 4.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.39 | 2017-07-27T11:55:00Z | 5.99 | 2 | < 25mph
PG&E | 2019-08-14 | 10:16 | 35.379 | -120.4232 | Vegetation | Hardwood Woodland | < 1 meter | Cal Fire |  | 512769069280 |  | 21000 | Conductor | Overhead | Yes | 43691 | 10:16 | Vegetation | [5 empty] | no-match |  | 2019 | 8 | 14 | 10 | 16 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.0314 | 226_94 | <25mph | <15mph | HFTD - Distribution | 2019-08-14 10:16:00 | 1976 | 14.3934 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-07-15 05:19 | 2016-07-15 05:19 | 35.1839 | -120.5018 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101846594 |  | 12000 | Conductor | Overhead | Yes | 42566.2215 | 2016-07-15 05:19 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0851 | 2016 | 7 | 15 | 5 | 19 | 16-0050086 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 62404 | 2.6454 | 222_84 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 05:19:00 | 594 | 14.1102 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D6295 | 5.2 | 2016-08-17T23:06:00Z | 11.01 | 7 | < 25mph |  |  |  | 0 | 0 | No data | D6295 | 5.2 | 2016-08-17T23:06:00Z | 11.01 | 15 | < 25mph
PG&E | 2015-12-03 12:10 | 2015-12-03 12:10 | 40.0277 | -120.9652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | usfs | spanish creek campground |  | 12000 | Conductor | Overhead | Yes | 42341.5069 | 2015-12-03 12:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0683 | 2015 | 12 | 3 | 12 | 10 | 15-0082505 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 196854 | 26.293 | 201_351 | 25-40mph | 15-30mph | HFTD - Distribution | 2015-12-03 12:10:00 | 427 | 26.9543 | FALSE | 25-40mph | CHAC1 | 3.2 | 2016-09-01T13:47:00Z | 2.01 | 2 | < 25mph | TAYC1 | 7.71 | 2016-09-01T13:00:00Z | 3.53 | 3 | < 25mph | CHAC1 | 3.2 | 2016-09-01T14:47:00Z | 3 | 4 | < 25mph | TAYC1 | 7.71 | 2016-09-01T13:00:00Z | 3.53 | 6 | < 25mph
PG&E | 2016-06-11 | 2016-06-11 19:45 | 39.3265 | -121.3921 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101292512 |  | 0 – 750 | Transformer | Overhead | Yes | 42532 | 2016-06-11 19:45 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0790 | 2016 | 6 | 11 | 19 | 45 | 16-0042611 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 642 | 8.1809 | 183_312 | <25mph | <15mph | HFTD - Distribution | 2016-06-11 19:45:00 | 533 | 16.0839 | FALSE | <25mph | BNGC1 | 3.76 | 2018-03-13T15:51:00Z | 15.99 | 1 | < 25mph | BNGC1 | 3.76 | 2018-03-13T15:51:00Z | 15.99 | 1 | < 25mph | BNGC1 | 3.76 | 2018-03-13T16:51:00Z | 20 | 2 | < 25mph | BNGC1 | 3.76 | 2018-03-13T16:51:00Z | 20 | 2 | < 25mph
PG&E | 2019-06-07 | 9:58 | 38.7285 | -123.3528 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 042861101 |  | 21000 | Conductor | Overhead | Yes | 43623 | 9:58 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-358 | 2019 | 6 | 7 | 9 | 58 | 19-0064216 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 5301 | 16.456 | 98_280 | <25mph | <15mph | HFTD - Distribution | 2019-06-07 09:58:00 | 1805 | 19.4921 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D2695 | 5.46 | 2015-12-14T10:52:00Z | 4.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | D2695 | 5.46 | 2015-12-14T12:08:00Z | 8.99 | 8 | < 25mph
PG&E | 2015-05-27 21:44 | 2015-05-27 21:44 | 39.169 | -120.9612 | Vegetation | Rural | < 0.25 Acres | Fire Agency | PEARDALE F.D. | 100077687 |  | 12000 | Conductor | Overhead | Yes | 42151.9056 | 2015-05-27 21:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0329 | 2015 | 5 | 27 | 21 | 44 | 15-0036850 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10828 | 3.691 | 201_303 | <25mph | <15mph | HFTD - Distribution | 2015-05-27 21:44:00 | 75 | 11.9096 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C5488 | 7.5 | 2015-12-23T08:35:00Z | 13 | 45 | < 25mph |  |  |  | 0 | 0 | No data | C5488 | 7.5 | 2015-12-23T08:35:00Z | 13 | 88 | < 25mph
PG&E | 2019-06-10 | 16:34 | 38.821 | -120.846 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Garden Valley FD | 153082106 |  | 21000 | Conductor | Overhead | Yes | 43626 | 16:34 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-372 | 2019 | 6 | 10 | 16 | 34 | 19-0065481 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14169 | 8.5329 | 206_284 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 16:34:00 | 1827 | 15.7607 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E3165 | 5.57 | 2017-03-31T14:29:00Z | 10 | 38 | < 25mph |  |  |  | 0 | 0 | No data | E3165 | 5.57 | 2017-03-31T14:29:00Z | 10 | 75 | < 25mph
PG&E | 2018-08-31 | 13:02 | 40.4775 | -122.4847 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103918932 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 13:02 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1872 | 2018 | 8 | 31 | 13 | 2 | 18-0075616 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18300 | 0.9461 | 137_376 | <25mph | <15mph | HFTD - Distribution | 2018-08-31 13:02:00 | 1611 | 11.7486 | FALSE | <25mph | PG086 | 3.07 | 2019-09-11T11:30:00Z | 16.06 | 10 | < 25mph | PG296 | 7.98 | 2019-09-11T11:50:00Z | 17.38 | 35 | < 25mph | PG086 | 3.07 | 2019-09-11T12:20:00Z | 17.54 | 20 | < 25mph | PG296 | 7.98 | 2019-09-11T12:00:00Z | 17.9 | 70 | < 25mph
PG&E | 2018-08-08 | 10:03 | 40.7933 | -124.0242 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CHIEF | 100983089 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 10:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1829 | 2018 | 8 | 8 | 10 | 3 | 18-0067921 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 27379 | 3.1403 | 73_395 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 10:03:00 | 1568 | 7.3376 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8223 | 6.38 | 2016-07-25T08:50:00Z | 8.99 | 46 | < 25mph |  |  |  | 0 | 0 | No data | D8223 | 6.38 | 2016-07-25T08:50:00Z | 8.99 | 87 | < 25mph
PG&E | 2017-08-28 | 10:07 | 39.0472 | -120.7859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | FORESTHILL | 100019525 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 10:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1357 | 2017 | 8 | 28 | 10 | 7 | 17-0073379 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 10077 | 5.9792 | 209_297 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 10:07:00 | 1095 | 13.4783 | FALSE | <25mph | AU268 | 3.78 | 2018-11-19T10:53:00Z | 4 | 8 | < 25mph | PG032 | 5.39 | 2018-11-19T10:40:00Z | 11.18 | 15 | < 25mph | AU268 | 3.78 | 2018-11-19T10:53:00Z | 4 | 18 | < 25mph | PG032 | 5.39 | 2018-11-19T10:40:00Z | 11.18 | 32 | < 25mph
PG&E | 2017-09-18 | 23:50 | 37.9088 | -120.4865 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | incident comander geoff marshall 209-419-4407 | 101040882 | Unknown | 17000 | Conductor | Overhead | Yes | 42996 | 23:50 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1422 | 2017 | 9 | 18 | 23 | 50 | 17-0079858 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 382303 | 9.0814 | 222_234 | <25mph | <15mph | HFTD - Distribution | 2017-09-18 23:50:00 | 1160 | 16.9339 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2861 | 7.91 | 2016-11-02T10:13:00Z | 4 | 8 | < 25mph |  |  |  | 0 | 0 | No data | E2861 | 7.91 | 2016-11-02T10:13:00Z | 4 | 16 | < 25mph
PG&E | 2015-03-04 18:44 | 2015-03-04 18:44 | 38.9995 | -122.7545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kelseyville FD | 102156367 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42067.7806 | 2015-03-04 18:44 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0271 | 2015 | 3 | 4 | 18 | 44 | 15-0017374 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29532 | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2015-03-04 18:44:00 | NA | 0 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.58 | 2019-01-01T12:57:00Z | 15.99 | 23 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.58 | 2019-01-01T13:57:00Z | 21 | 46 | < 25mph
PG&E | 2017-04-29 15:29 | 15:07 | 37.0349 | -119.5242 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100678661 | Unknown | 12000 | Conductor | Overhead | Yes | 42854.6453 | 15:07 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1078 | 2017 | 4 | 29 | 15 | 7 | 17-0043911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 7.6275 | 265_186 | <25mph | <15mph | HFTD - Distribution | 2017-04-29 15:07:00 | 818 | 19.1329 | FALSE | <25mph | PRHC1 | 2.76 | 2019-01-11T12:27:00Z | 3 | 1 | < 25mph | PG202 | 6.42 | 2019-01-11T13:10:00Z | 5.7 | 7 | < 25mph | PRHC1 | 2.76 | 2019-01-11T13:27:00Z | 3 | 2 | < 25mph | PG202 | 6.42 | 2019-01-11T13:30:00Z | 7.25 | 14 | < 25mph
PG&E | 2017-08-29 | 12:49 | 37.4507 | -119.6454 | Vegetation | Rural | > 5000 Acres | Fire Agency | USFS | 101017368 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-29 | 12:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1366 | 2017 | 8 | 29 | 12 | 49 | 17-0073823 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | 3rd Party | 3rd Party - Unknown | 5894785 | 7.4398 | 259_209 | <25mph | <15mph | HFTD - Distribution | 2017-08-29 12:49:00 | 1104 | 13.5545 | FALSE | <25mph | D0826 | 0.24 | 2015-01-29T20:32:00Z | 4 | 2 | < 25mph | AT301 | 7.64 | 2015-01-29T20:55:00Z | 7 | 27 | < 25mph | D0826 | 0.24 | 2015-01-29T21:32:00Z | 4.99 | 4 | < 25mph | WWNC1 | 5.79 | 2015-01-29T21:51:00Z | 11.01 | 56 | < 25mph
PG&E | 2019-08-16 | 8:19 | 40.1235 | -123.8758 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Self Extinguished |  | 192221102-2101118022{5563} |  | 12000 | Conductor | Overhead | Yes | 43693 | 8:19 | Vegetation | [5 empty] | Other/Unknown |  | 2019 | 8 | 16 | 8 | 19 | 19-0088744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 2979 | 5.7689 | 78_358 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 08:19:00 | 1983 | 18.468 | FALSE | <25mph | ERCC1 | 2.93 | 2016-06-10T22:28:00Z | 18.01 | 1 | < 25mph | ERCC1 | 2.93 | 2016-06-10T22:28:00Z | 18.01 | 4 | < 25mph | ERCC1 | 2.93 | 2016-06-10T22:28:00Z | 18.01 | 2 | < 25mph | ERCC1 | 2.93 | 2016-06-10T22:28:00Z | 18.01 | 8 | < 25mph
PG&E | 2017-11-29 17:35 | 17:34 | 38.6841 | -120.6546 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 101419450 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 43068.7326 | 17:34 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1533 | 2017 | 11 | 29 | 17 | 34 | 17-0098456 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 582825 | 2.2539 | 214_277 | <25mph | <15mph | HFTD - Distribution | 2017-11-29 17:34:00 | 1275 | 13.1335 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GZFC1 | 7.93 | 2018-01-07T13:17:00Z | 8.99 | 7 | < 25mph |  |  |  | 0 | 0 | No data | GZFC1 | 7.93 | 2018-01-07T14:17:00Z | 8.99 | 14 | < 25mph
PG&E | 2017-09-02 | 12:01 | 37.6645 | -121.9223 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 100956020 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42980 | 12:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1384 | 2017 | 9 | 2 | 12 | 1 | 17-0075132 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 7152 | 6.3171 | 159_221 | <25mph | <15mph | HFTD - Distribution | 2017-09-02 12:01:00 | 1122 | 21.2394 | FALSE | <25mph | AU719 | 3.94 | 2016-05-31T04:21:00Z | 14 | 46 | < 25mph | AU719 | 3.94 | 2016-05-31T04:21:00Z | 14 | 67 | < 25mph | AU719 | 3.94 | 2016-05-31T05:06:00Z | 15.99 | 90 | < 25mph | AU719 | 3.94 | 2016-05-31T05:06:00Z | 15.99 | 132 | < 25mph
PG&E | 2017-07-22 14:38 | 14:38 | 37.2994 | -122.1631 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100265488 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.6101 | 14:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1280 | 2017 | 7 | 22 | 14 | 38 | 17-0064738 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49181 | 4.6185 | 148_201 | <25mph | <15mph | HFTD - Distribution | 2017-07-22 14:38:00 | 1019 | 12.5156 | FALSE | <25mph | E0516 | 3.56 | 2018-05-12T10:14:00Z | 27 | 23 | 25-40mph | E0516 | 3.56 | 2018-05-12T10:14:00Z | 27 | 122 | 25-40mph | E0516 | 3.56 | 2018-05-12T10:14:00Z | 27 | 46 | 25-40mph | E0516 | 3.56 | 2018-05-12T10:14:00Z | 27 | 242 | 25-40mph
PG&E | 2018-11-15 | 6:09 | 38.3599 | -122.3682 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102241814 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43419 | 6:09 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1974 | 2018 | 11 | 15 | 6 | 9 | 18-0099862 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 441 | 10.2454 | 140_259 | <25mph | <15mph | HFTD - Distribution | 2018-11-15 06:09:00 | 1714 | 12.9788 | FALSE | <25mph | AS725 | 3.41 | 2016-04-25T11:07:00Z | 4 | 8 | < 25mph | AS725 | 3.41 | 2016-04-25T11:07:00Z | 4 | 12 | < 25mph | AS725 | 3.41 | 2016-04-25T11:07:00Z | 4 | 15 | < 25mph | E6860 | 7.62 | 2016-04-25T12:15:00Z | 4 | 23 | < 25mph
PG&E | 2018-10-24 | 7:08 | 37.9475 | -120.2671 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SCOTT PITTMAN 209-768-8182 TCU INCIDENT# 012528 | 101047865 | Unknown | 17000 | Conductor | Overhead | Yes | 43397 | 7:08 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1949 | 2018 | 10 | 24 | 7 | 8 | 18-0093599 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 13433 | 8.6394 | 231_236 | <25mph | <15mph | HFTD - Distribution | 2018-10-24 07:08:00 | 1688 | 12.0171 | FALSE | <25mph | C3161 | 2.32 | 2019-03-04T22:00:00Z | 10 | 22 | < 25mph | PG166 | 7.04 | 2019-03-04T22:10:00Z | 10.96 | 52 | < 25mph | PG029 | 0.63 | 2019-03-04T22:30:00Z | 10.29 | 44 | < 25mph | PG166 | 7.04 | 2019-03-04T22:10:00Z | 10.96 | 104 | < 25mph
PG&E | 2015-09-24 04:30 | 2015-09-24 04:30 | 38.6769 | -123.314 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Str. 041/007 |  | 60000 | Conductor | Overhead | Yes | 42271.1875 | 2015-09-24 04:30 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0613 | 2015 | 9 | 24 | 4 | 30 | FU-2015-057 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 22680 | 6.5939 | 100_277 | <25mph | <15mph | HFTD - Transmission | 2015-09-24 04:30:00 | 358 | 13.8122 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D2695 | 7.76 | 2015-06-11T17:18:00Z | 8.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | D2695 | 7.76 | 2015-06-11T17:18:00Z | 8.99 | 8 | < 25mph
PG&E | 2017-06-22 17:54 | 18:07 | 38.7583 | -120.7176 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101401088 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.7461 | 18:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1188 | 2017 | 6 | 22 | 18 | 7 | 17-0057857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 8517 | 11.5365 | 212_281 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 18:07:00 | 927 | 16.1873 | FALSE | <25mph | E5691 | 3.88 | 2017-02-12T18:31:00Z | 4 | 25 | < 25mph | E6490 | 7.72 | 2017-02-12T18:31:00Z | 4.99 | 38 | < 25mph | E5691 | 3.88 | 2017-02-12T18:56:00Z | 4.99 | 49 | < 25mph | E6490 | 7.72 | 2017-02-12T19:27:00Z | 7 | 73 | < 25mph
PG&E | 2016-10-09 18:52 | 18:52 | 38.656 | -120.9725 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101376768 |  | 12000 | Conductor | Overhead | Yes | 42652.7862 | 18:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1024 | 2016 | 10 | 9 | 18 | 52 | 16-0070676 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 98361 | 11.3582 | 201_275 | <25mph | <15mph | HFTD - Distribution | 2016-10-09 18:52:00 | 765 | 14.948 | FALSE | <25mph | PG076 | 3.1 | 2018-10-11T10:40:00Z | 6.35 | 22 | < 25mph | PG073 | 5.23 | 2018-10-11T10:40:00Z | 9.86 | 126 | < 25mph | PG076 | 3.1 | 2018-10-11T10:40:00Z | 6.35 | 42 | < 25mph | PG073 | 5.23 | 2018-10-11T10:40:00Z | 9.86 | 249 | < 25mph
PG&E | 2018-06-22 | 17:44 | 37.2485 | -119.5625 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Madera County | 101117749 | None | 0 – 750 | Conductor | Overhead | Yes | 43273 | 17:44 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1686 | 2018 | 6 | 22 | 17 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 10.123 | 263_198 | <25mph | <15mph | HFTD - Distribution | 2018-06-22 17:44:00 | 1428 | 12.3323 | FALSE | <25mph | NFRC1 | 3.29 | 2016-02-11T14:55:00Z | 10 | 3 | < 25mph | NFRC1 | 3.29 | 2016-02-11T14:55:00Z | 10 | 40 | < 25mph | NFRC1 | 3.29 | 2016-02-11T14:55:00Z | 10 | 7 | < 25mph | NFRC1 | 3.29 | 2016-02-11T14:55:00Z | 10 | 82 | < 25mph
PG&E | 2017-10-16 | 12:10 | 36.5831 | -121.9368 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101781248 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43024 | 12:10 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | Other/Unknown | 1493 | 2017 | 10 | 16 | 12 | 10 | 17-0087767 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 6313 | 5.0415 | 158_161 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:10:00 | 1236 | 13.6905 | FALSE | <25mph | E4129 | 2.99 | 2018-04-23T14:30:00Z | 4.99 | 45 | < 25mph | E8875 | 5.44 | 2018-04-23T15:00:00Z | 5.99 | 50 | < 25mph | E4129 | 2.99 | 2018-04-23T14:30:00Z | 4.99 | 88 | < 25mph | E8875 | 5.44 | 2018-04-23T15:00:00Z | 5.99 | 97 | < 25mph
PG&E | 2017-09-24 | 16:42 | 38.3869 | -122.9667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DOUG JONES | 101973946 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43002 | 16:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1432 | 2017 | 9 | 24 | 16 | 42 | 17-0081329 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 22574 | 19.6154 | 114_261 | <25mph | <15mph | HFTD - Distribution | 2017-09-24 16:42:00 | 1170 | 19.6154 | FALSE | <25mph | D2849 | 0.23 | 2019-03-05T13:23:00Z | 2.01 | 12 | < 25mph | BDZC1 | 7.15 | 2019-03-05T13:10:00Z | 20.02 | 76 | < 25mph | D2849 | 0.23 | 2019-03-05T13:23:00Z | 2.01 | 24 | < 25mph | BDZC1 | 7.15 | 2019-03-05T13:10:00Z | 20.02 | 149 | < 25mph
PG&E | 2016-05-29 14:19 | 2016-05-29 14:19 | 40.5795 | -122.4694 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103156596 | Yes | 12000 | Conductor | Overhead | Yes | 42519.5965 | 2016-05-29 14:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0751 | 2016 | 5 | 29 | 14 | 19 | 16-0039619 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3860 | 1.6611 | 138_382 | <25mph | <15mph | HFTD - Distribution | 2016-05-29 14:19:00 | 494 | 20.6013 | FALSE | <25mph | MMOC1 | 1.91 | 2017-09-04T04:00:00Z | 13 | 5 | < 25mph | MMOC1 | 1.91 | 2017-09-04T04:00:00Z | 13 | 23 | < 25mph | MMOC1 | 1.91 | 2017-09-04T05:00:00Z | 18.01 | 10 | < 25mph | MMOC1 | 1.91 | 2017-09-04T05:00:00Z | 18.01 | 47 | < 25mph
PG&E | 2017-06-10 07:38 | 07:37 | 35.4359 | -120.4957 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101890429 | Unknown | 21000 | Conductor | Overhead | Yes | 42896.3177 | 07:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1140 | 2017 | 6 | 10 | 7 | 37 | 17-0054182 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 34397 | 9.2577 | 222_98 | <25mph | <15mph | HFTD - Distribution | 2017-06-10 07:37:00 | 879 | 18.05 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2260 | 7.67 | 2017-02-16T20:40:00Z | 8.99 | 6 | < 25mph |  |  |  | 0 | 0 | No data | E2260 | 7.67 | 2017-02-16T22:19:00Z | 11.01 | 13 | < 25mph
PG&E | 2018-10-16 | 16:30 | 38.7754 | -122.8976 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MARK GRADEK (707) 889-4303 | 101962692 | AT&T | 12000 | Conductor | Overhead | Yes | 43389 | 16:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1943 | 2018 | 10 | 16 | 16 | 30 | 18-0091127 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 744 | 10.3513 | 118_282 | <25mph | <15mph | HFTD - Distribution | 2018-10-16 16:30:00 | 1682 | 19.9126 | FALSE | <25mph | PG090 | 1.05 | 2019-05-07T23:50:00Z | 13.8 | 12 | < 25mph | PG040 | 5.7 | 2019-05-07T23:20:00Z | 16.89 | 42 | < 25mph | PG090 | 1.05 | 2019-05-08T00:30:00Z | 14.03 | 24 | < 25mph | PG125 | 5.67 | 2019-05-08T00:10:00Z | 17.98 | 83 | < 25mph
PG&E | 2018-10-15 | 3:23 | 38.2897 | -120.5803 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103378003 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43388 | 3:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1941 | 2018 | 10 | 15 | 3 | 23 | 18-0090342 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1464 | 26.0611 | 218_255 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-15 03:23:00 | 1680 | 26.2858 | FALSE | 25-40mph | AT317 | 3.74 | 2015-02-12T07:56:00Z | 0 | 6 | < 25mph | MTZC1 | 7.96 | 2015-02-12T07:56:00Z | 11.01 | 12 | < 25mph | AT317 | 3.74 | 2015-02-12T08:16:00Z | 3 | 12 | < 25mph | MTZC1 | 7.96 | 2015-02-12T08:56:00Z | 11.01 | 24 | < 25mph
PG&E | 2019-07-21 | 10:14 | 38.9716 | -120.9991 |  | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire | Placer Hill FD | 152241102 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43667 | 10:14 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-127 | 2019 | 7 | 21 | 10 | 14 | 19-0079578 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 32850 | 6.8026 | 199_293 | <25mph | <15mph | HFTD - Distribution | 2019-07-21 10:14:00 | 1916 | 10.8012 | FALSE | <25mph | C0713 | 3.87 | 2016-04-25T17:44:00Z | 8.01 | 15 | < 25mph | C0713 | 3.87 | 2016-04-25T17:44:00Z | 8.01 | 35 | < 25mph | C0713 | 3.87 | 2016-04-25T18:29:00Z | 11.01 | 31 | < 25mph | C0713 | 3.87 | 2016-04-25T18:29:00Z | 11.01 | 71 | < 25mph
PG&E | 2016-06-15 | 2016-06-15 13:09 | 38.4433 | -120.7568 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103169620 |  | 12000 | Conductor | Overhead | Yes | 42536 | 2016-06-15 13:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0801 | 2016 | 6 | 15 | 13 | 9 | 16-0043476 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 23963 | 15.7348 | 210_263 | <25mph | <15mph | HFTD - Distribution | 2016-06-15 13:09:00 | 543 | 16.8625 | FALSE | <25mph | PG116 | 2.93 | 2019-06-10T01:30:00Z | 7.67 | 6 | < 25mph | TS389 | 6.49 | 2019-06-10T01:53:00Z | 8.99 | 51 | < 25mph | PG116 | 2.93 | 2019-06-10T01:30:00Z | 7.67 | 12 | < 25mph | TS389 | 6.49 | 2019-06-10T01:53:00Z | 8.99 | 102 | < 25mph
PG&E | 2017-08-30 | 22:37 | 38.9993 | -120.9887 | Vegetation | Rural | < 3 Meters | Fire Agency | Andy 530-889-0111 | 100026238 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42977 | 22:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1370 | 2017 | 8 | 30 | 22 | 37 | 17-0074333 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 3750 | 7.3126 | 200_294 | <25mph | <15mph | HFTD - Distribution | 2017-08-30 22:37:00 | 1108 | 12.9461 | FALSE | <25mph | C0713 | 3.13 | 2017-04-09T20:26:00Z | 5.99 | 16 | < 25mph | C5488 | 5.56 | 2017-04-09T20:38:00Z | 11.01 | 28 | < 25mph | C0713 | 3.13 | 2017-04-09T21:19:00Z | 10 | 32 | < 25mph | C5488 | 5.56 | 2017-04-09T21:39:00Z | 11.01 | 57 | < 25mph
PG&E | 2016-06-19 | 2016-06-19 12:07 | 39.3811 | -123.7737 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102187888 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 12:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0807 | 2016 | 6 | 19 | 12 | 7 | 16-0044317 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6100 | 11.4602 | 81_317 | <25mph | <15mph | HFTD - Distribution | 2016-06-19 12:07:00 | 550 | 15.3844 | FALSE | <25mph | E2582 | 0.37 | 2015-01-21T00:33:00Z | 4 | 2 | < 25mph | E2582 | 0.37 | 2015-01-21T00:33:00Z | 4 | 8 | < 25mph | E2582 | 0.37 | 2015-01-21T00:33:00Z | 4 | 4 | < 25mph | E2582 | 0.37 | 2015-01-21T00:33:00Z | 4 | 16 | < 25mph
PG&E | 2017-09-23 | 14:17 | 40.6509 | -122.2974 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DARREN STEWART 448-2421 | 101467221 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43001 | 14:17 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1429 | 2017 | 9 | 23 | 14 | 17 | 17-0081216 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 98820 | 17.9072 | 145_386 | <25mph | <15mph | HFTD - Distribution | 2017-09-23 14:17:00 | 1167 | 24.6958 | FALSE | <25mph | PG516 | 2.66 | 2019-11-16T02:50:00Z | 3.65 | 25 | < 25mph | PG519 | 6.92 | 2019-11-16T03:10:00Z | 17.18 | 47 | < 25mph | PG516 | 2.66 | 2019-11-16T02:50:00Z | 3.65 | 49 | < 25mph | PG519 | 6.92 | 2019-11-16T03:10:00Z | 17.18 | 93 | < 25mph
PG&E | 2018-11-13 | 15:41 | 37.0644 | -121.9578 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101680441 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43417 | 15:41 | Other | N.A. | N.A. | N.A. | Human Error | Grow house | Other/Unknown | 1973 | 2018 | 11 | 13 | 15 | 41 | 18-0099492 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 21484 | 1.9347 | 157_188 | <25mph | <15mph | HFTD - Distribution | 2018-11-13 15:41:00 | 1713 | 13.1257 | FALSE | <25mph | PG062 | 0.72 | 2018-10-28T05:40:00Z | 8.12 | 42 | < 25mph | D8979 | 4.33 | 2018-10-28T05:31:00Z | 14.99 | 172 | < 25mph | PG062 | 0.72 | 2018-10-28T05:40:00Z | 8.12 | 84 | < 25mph | D8979 | 4.33 | 2018-10-28T06:31:00Z | 14.99 | 340 | < 25mph
PG&E | 2019-07-18 | 10:27 | 38.3033 | -120.6718 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | B561 |  | 12000 | Other | Overhead | Yes | 43664 | 10:27 | Equipment - PG&E | Other |  |  |  |  | Other/Unknown | 2019-68 | 2019 | 7 | 18 | 10 | 27 | 19-0078904 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45558 | 8.6789 | 214_256 | <25mph | <15mph | HFTD - Distribution | 2019-07-18 10:27:00 | 1910 | 16.0413 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ANUC1 | 7.14 | 2016-05-06T00:53:00Z | 10 | 2 | < 25mph |  |  |  | 0 | 0 | No data | ANUC1 | 7.14 | 2016-05-06T01:53:00Z | 10 | 4 | < 25mph
PG&E | 2018-03-06 | 17:57 | 38.2811 | -120.8965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-647-5220 | 101238429 | AT&T | 12000 | Conductor | Overhead | Yes | 43165 | 17:57 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1566 | 2018 | 3 | 6 | 17 | 57 | 18-0020396 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 142000 | 3.9357 | 204_254 | <25mph | <15mph | HFTD - Distribution | 2018-03-06 17:57:00 | 1308 | 12.1612 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.07 | 2015-04-20T22:05:00Z | 12.01 | 2 | < 25mph |  |  |  | 0 | 0 | No data | CMAC1 | 4.3 | 2015-04-20T22:59:00Z | 12.01 | 4 | < 25mph
PG&E | 2017-07-07 20:49 | 14:31 | 37.499 | -119.799 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVEN WARD OFFICE 209-966-3542 CELL559-706-8811 | 103855637 | Unknown | 21000 | Conductor | Overhead | Yes | 42923.8675 | 14:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1230 | 2017 | 7 | 7 | 14 | 31 | 17-0061288 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 554306 | 11.2535 | 252_212 | <25mph | <15mph | HFTD - Distribution | 2017-07-07 14:31:00 | 968 | 22.3608 | FALSE | <25mph | JSDC1 | 3.81 | 2019-07-31T12:47:00Z | 4.99 | 7 | < 25mph | MIAC1 | 6.24 | 2019-07-31T12:59:00Z | 8.01 | 29 | < 25mph | JSDC1 | 3.81 | 2019-07-31T13:47:00Z | 4.99 | 14 | < 25mph | MIAC1 | 6.24 | 2019-07-31T13:59:00Z | 8.99 | 60 | < 25mph
PG&E | 2016-06-15 | 2016-06-15 13:09 | 38.4433 | -120.7568 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103169620 |  | 12000 | Conductor | Overhead | Yes | 42536 | 2016-06-15 13:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0801 | 2016 | 6 | 15 | 13 | 9 | 16-0043476 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 23963 | 15.7348 | 210_263 | <25mph | <15mph | HFTD - Distribution | 2016-06-15 13:09:00 | 543 | 16.8625 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.74 | 2015-12-23T04:56:00Z | 14 | 2 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.74 | 2015-12-23T04:56:00Z | 14 | 4 | < 25mph
PG&E | 2019-05-15 | 21:31 | 38.5731 | -122.9603 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Unknown |  | 103931177 |  | 12000 | Conductor | Overhead | Yes | 43600 | 21:31 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-316 | 2019 | 5 | 15 | 21 | 31 | 19-0052480 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 27780 | 16.5892 | 115_271 | <25mph | <15mph | HFTD - Distribution | 2019-05-15 21:31:00 | 1774 | 23.8094 | FALSE | <25mph | D9841 | 3.34 | 2019-04-14T05:47:00Z | 1.01 | 5 | < 25mph | D9841 | 3.34 | 2019-04-14T05:47:00Z | 1.01 | 43 | < 25mph | D9841 | 3.34 | 2019-04-14T06:16:00Z | 1.01 | 9 | < 25mph | D9841 | 3.34 | 2019-04-14T06:16:00Z | 1.01 | 83 | < 25mph
PG&E | 2015-06-27 21:15 | 2015-06-27 21:15 | 39.2699 | -121.0403 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 16151 INDAIN FLAT RD |  | 12000 | Conductor | Overhead | Yes | 42182.8854 | 2015-06-27 21:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0416 | 2015 | 6 | 27 | 21 | 15 | 15-0043789 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4210 | 5.8168 | 198_309 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 21:15:00 | 161 | 11.6482 | FALSE | <25mph | E5439 | 2.06 | 2015-11-14T15:55:00Z | 2.01 | 46 | < 25mph | RRRC1 | 4.73 | 2015-11-14T15:13:00Z | 7 | 68 | < 25mph | E5439 | 2.06 | 2015-11-14T16:45:00Z | 5.99 | 92 | < 25mph | RRRC1 | 4.73 | 2015-11-14T15:13:00Z | 7 | 139 | < 25mph
3. Redwood Valley (Mendocino Lake Complex) | 2017-10-08 | 23:36 | 39.2487 | -123.1663 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1989 | 2017 | 10 | 8 | 23 | 36 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 24.7673 | 107_309 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 23:36:00 | 1212 | 30.3049 | FALSE | 25-40mph | D1660 | 3 | 2015-01-11T12:40:00Z | 1.01 | 3 | < 25mph | D9878 | 7.09 | 2015-01-11T12:05:00Z | 4 | 15 | < 25mph | D1660 | 3 | 2015-01-11T12:40:00Z | 1.01 | 5 | < 25mph | D9878 | 7.09 | 2015-01-11T12:05:00Z | 4 | 29 | < 25mph
PG&E | 2016-08-15 | 2016-08-15 15:43 | 37.8784 | -120.4488 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101020079 |  | 17000 | Conductor | Overhead | Yes | 42597 | 2016-08-15 15:43 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0928 | 2016 | 8 | 15 | 15 | 43 | 16-0057465 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 122905 | 10.0906 | 223_232 | <25mph | <15mph | HFTD - Distribution | 2016-08-15 15:43:00 | 671 | 12.9875 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.26 | 2017-08-21T18:03:00Z | 8.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.26 | 2017-08-21T19:03:00Z | 10 | 2 | < 25mph
PG&E | 2019-10-04 | 19:07 | 40.4964 | -122.0448 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | Yes | 43742 | 19:07 | Equipment - Overloaded | Other |  |  |  |  | no-match | 2019-257 | 2019 | 10 | 4 | 19 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 6.2955 | 155_377 | <25mph | <15mph | HFTD - Distribution | 2019-10-04 19:07:00 | 2076 | 10.3362 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-10-13 23:23 | 23:14 | 40.4901 | -122.3729 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | SHASTA COUNTY FIRE | 101502366 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42656.9745 | 23:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1029 | 2016 | 10 | 13 | 23 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 30.3025 | 142_377 | 25-40mph | 30-45mph | HFTD - Distribution | 2016-10-13 23:14:00 | 770 | 30.3025 | FALSE | 25-40mph | E6886 | 3.41 | 2018-12-21T01:46:00Z | 0 | 4 | < 25mph | RRAC1 | 4.59 | 2018-12-21T01:24:00Z | 5.99 | 23 | < 25mph | E6886 | 3.41 | 2018-12-21T02:46:00Z | 0 | 8 | < 25mph | RRAC1 | 4.59 | 2018-12-21T01:24:00Z | 5.99 | 46 | < 25mph
PG&E | 2017-08-30 | 18:21 | 40.6243 | -122.3039 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CASHU008896 | 103151338 | YES | 12000 | Conductor | Overhead | Yes | 42977 | 18:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1369 | 2017 | 8 | 30 | 18 | 21 | 17-0074287 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 76344 | 5.8461 | 145_384 | <25mph | <15mph | HFTD - Distribution | 2017-08-30 18:21:00 | 1107 | 16.2636 | FALSE | <25mph | C5599 | 2.06 | 2016-12-28T20:32:00Z | 14 | 4 | < 25mph | RRAC1 | 7.52 | 2016-12-28T20:24:00Z | 18.99 | 5 | < 25mph | C5599 | 2.06 | 2016-12-28T21:31:00Z | 15.99 | 8 | < 25mph | RRAC1 | 7.52 | 2016-12-28T20:24:00Z | 18.99 | 10 | < 25mph
PG&E | 2015-05-06 17:17 | 2015-05-06 17:17 | 37.4273 | -119.8803 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | BOOSTER 8179 INDIAN PEEK N/O MIWUK | None | 21000 | Other | Overhead | Yes | 42130.7201 | 2015-05-06 17:17 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0307 | 2015 | 5 | 6 | 17 | 17 | 15-0032311 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 81600 | 12.4413 | 249_208 | <25mph | <15mph | HFTD - Distribution | 2015-05-06 17:17:00 | 53 | 13.2212 | FALSE | <25mph | C1522 | 2.85 | 2019-01-16T15:32:00Z | 14 | 5 | < 25mph | MIAC1 | 7.42 | 2019-01-16T15:59:00Z | 25.99 | 14 | 25-40mph | C1522 | 2.85 | 2019-01-16T15:32:00Z | 14 | 13 | < 25mph | MIAC1 | 7.42 | 2019-01-16T15:59:00Z | 25.99 | 30 | 25-40mph
PG&E | 2019-04-09 | 15:27 | 37.7341 | -120.0776 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 101076921 |  | 21000 | Pole | Overhead | Yes | 43564 | 15:27 | Vegetation |  | Veg. contact | Pole |  |  | Branch (Not overhanging, > 12ft) | 2019-313 | 2019 | 4 | 9 | 15 | 27 | 19-0041008 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 179862 | 22.8983 | 240_225 | <25mph | <15mph | HFTD - Distribution | 2019-04-09 15:27:00 | 1738 | 29.8749 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | SEWC1 | 4.76 | 2016-11-13T18:16:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | SEWC1 | 4.76 | 2016-11-13T18:16:00Z | 7 | 2 | < 25mph
PG&E | 2018-11-09 | 8:59 | 37.2809 | -122.1214 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100546562 | AT&T | 12000 | Conductor | Overhead | Yes | 43413 | 8:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1964 | 2018 | 11 | 9 | 8 | 59 | 18-0098521 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 77077 | 5.2345 | 150_200 | <25mph | <15mph | HFTD - Distribution | 2018-11-09 08:59:00 | 1704 | 17.3931 | FALSE | <25mph | E6800 | 3.85 | 2018-09-21T12:30:00Z | 8.01 | 36 | < 25mph | E6800 | 3.85 | 2018-09-21T12:30:00Z | 8.01 | 165 | < 25mph | E6800 | 3.85 | 2018-09-21T13:50:00Z | 8.01 | 72 | < 25mph | PG050 | 7.13 | 2018-09-21T13:50:00Z | 11.18 | 315 | < 25mph
PG&E | 2018-09-06 | 16:19 | 39.0904 | -120.9464 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 100020676 | Unknown | 12000 | Conductor | Overhead | Yes | 43349 | 16:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1886 | 2018 | 9 | 6 | 16 | 19 | 18-0077280 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 30780 | 10.0605 | 202_299 | <25mph | <15mph | HFTD - Distribution | 2018-09-06 16:19:00 | 1625 | 12.3694 | FALSE | <25mph | D9434 | 3.62 | 2018-03-15T05:20:00Z | 3 | 8 | < 25mph | C5488 | 4.54 | 2018-03-15T05:07:00Z | 11.01 | 46 | < 25mph | AT999 | 2.11 | 2018-03-15T06:11:00Z | 7 | 16 | < 25mph | C5488 | 4.54 | 2018-03-15T05:07:00Z | 11.01 | 90 | < 25mph
PG&E | 2019-01-16 | 0:17 | 38.0621 | -120.1964 | Vegetation | Conifer Forest | Structure Only | Cal Fire |  | 163661701 |  | 17000 | Conductor | Overhead | Yes | 43481 | 0:17 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-01 | 2019 | 1 | 16 | 0 | 17 | 19-0010443 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1041827 | 14.8061 | 234_243 | <25mph | <15mph | HFTD - Distribution | 2019-01-16 00:17:00 | 1728 | 28.2081 | FALSE | 25-40mph | MOUC1 | 2.77 | 2019-02-24T07:02:00Z | 8.99 | 1 | < 25mph | MOUC1 | 2.77 | 2019-02-24T07:02:00Z | 8.99 | 19 | < 25mph | MOUC1 | 2.77 | 2019-02-24T08:02:00Z | 8.99 | 2 | < 25mph | MOUC1 | 2.77 | 2019-02-24T08:02:00Z | 8.99 | 38 | < 25mph
PG&E | 2015-06-15 15:35 | 2015-06-15 15:35 | 37.1852 | -121.7595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Jose city | 100618215 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42170.6493 | 2015-06-15 15:35 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0384 | 2015 | 6 | 15 | 15 | 35 | 15-0041178 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 345 | 20.7397 | 166_194 | <25mph | <15mph | HFTD - Distribution | 2015-06-15 15:35:00 | 130 | 21.599 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5617 | 5.37 | 2016-05-25T04:03:00Z | 5.99 | 72 | < 25mph |  |  |  | 0 | 0 | No data | E5617 | 5.37 | 2016-05-25T05:53:00Z | 7 | 140 | < 25mph
PG&E | 2017-09-02 | 12:01 | 37.6645 | -121.9223 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 100956020 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42980 | 12:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1384 | 2017 | 9 | 2 | 12 | 1 | 17-0075132 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 7152 | 6.3171 | 159_221 | <25mph | <15mph | HFTD - Distribution | 2017-09-02 12:01:00 | 1122 | 21.2394 | FALSE | <25mph | AU719 | 3.94 | 2018-01-27T13:41:00Z | 2.01 | 15 | < 25mph | D3560 | 6.84 | 2018-01-27T13:15:00Z | 4 | 40 | < 25mph | AU719 | 3.94 | 2018-01-27T13:46:00Z | 2.01 | 30 | < 25mph | D3560 | 6.84 | 2018-01-27T14:31:00Z | 5.99 | 80 | < 25mph
PG&E | 2015-06-04 20:00 | 2015-06-04 20:00 | 38.6916 | -120.8606 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101412760 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42159.8333 | 2015-06-04 20:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0347 | 2015 | 6 | 4 | 20 | 0 | 15-0038597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 9640 | 2.0731 | 205_277 | <25mph | <15mph | HFTD - Distribution | 2015-06-04 20:00:00 | 93 | 11.0268 | FALSE | <25mph | C6129 | 0.68 | 2017-08-24T22:54:00Z | 10 | 36 | < 25mph | E5691 | 5.78 | 2017-08-24T22:25:00Z | 14.99 | 71 | < 25mph | C6129 | 0.68 | 2017-08-25T00:04:00Z | 13 | 72 | < 25mph | E5691 | 5.78 | 2017-08-24T22:25:00Z | 14.99 | 142 | < 25mph
PG&E | 2016-04-08 13:14 | 2016-04-08 13:14 | 39.0429 | -121.1002 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100086751 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42468.5514 | 2016-04-08 13:14 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0705 | 2016 | 4 | 8 | 13 | 14 | 16-0027237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 11817 | 10.7666 | 195_296 | <25mph | <15mph | HFTD - Distribution | 2016-04-08 13:14:00 | 449 | 10.7666 | FALSE | <25mph | C0713 | 3.59 | 2019-05-16T09:19:00Z | 18.01 | 17 | < 25mph | C5488 | 4.41 | 2019-05-16T09:52:00Z | 24.99 | 58 | < 25mph | C0713 | 3.59 | 2019-05-16T09:19:00Z | 18.01 | 32 | < 25mph | C5488 | 4.41 | 2019-05-16T09:52:00Z | 24.99 | 109 | < 25mph
PG&E | 2016-08-12 | 2016-08-12 10:08 | 38.8751 | -122.4223 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 102168360 |  | 12000 | Conductor | Overhead | Yes | 42594 | 2016-08-12 10:08 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0922 | 2016 | 8 | 12 | 10 | 8 | 16-0056982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 1368 | 5.1025 | 138_288 | <25mph | <15mph | HFTD - Distribution | 2016-08-12 10:08:00 | 665 | 17.0718 | FALSE | <25mph | PG358 | 3.68 | 2019-12-13T20:50:00Z | 21.77 | 8 | < 25mph | PG358 | 3.68 | 2019-12-13T20:50:00Z | 21.77 | 29 | < 25mph | PG358 | 3.68 | 2019-12-13T20:50:00Z | 21.77 | 15 | < 25mph | PG358 | 3.68 | 2019-12-13T20:50:00Z | 21.77 | 55 | < 25mph
PG&E | 2017-10-11 | 11:57 | 38.5015 | -123.0237 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101974930 | Unknown | 12000 | Conductor | Overhead | Yes | 43019 | 11:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1484 | 2017 | 10 | 11 | 11 | 57 | 17-0086350 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 226925 | 16.5068 | 112_268 | <25mph | <15mph | HFTD - Distribution | 2017-10-11 11:57:00 | 1227 | 19.0479 | FALSE | <25mph | D3481 | 2.38 | 2015-05-12T22:37:00Z | 14.99 | 29 | < 25mph | D3481 | 2.38 | 2015-05-12T22:37:00Z | 14.99 | 29 | < 25mph | D3481 | 2.38 | 2015-05-12T22:37:00Z | 14.99 | 57 | < 25mph | D3481 | 2.38 | 2015-05-12T22:37:00Z | 14.99 | 57 | < 25mph
PG&E | 2016-08-08 | 2016-08-08 15:44 | 37.1382 | -121.9672 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100519919 |  | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0912 | 2016 | 8 | 8 | 15 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 8.8992 | 157_192 | <25mph | <15mph | HFTD - Distribution | 2016-08-08 15:44:00 | 655 | 10.1741 | FALSE | <25mph | D8979 | 1.09 | 2018-09-05T13:58:00Z | 4.99 | 28 | < 25mph | PG050 | 6.05 | 2018-09-05T13:50:00Z | 6.35 | 128 | < 25mph | D8979 | 1.09 | 2018-09-05T15:21:00Z | 4.99 | 56 | < 25mph | PG050 | 6.05 | 2018-09-05T13:50:00Z | 6.35 | 251 | < 25mph
PG&E | 2018-08-14 | 15:46 | 38.0878 | -122.6002 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103916882 | Verizon | 0 – 750 | Conductor | Overhead | Yes | 43326 | 15:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1844 | 2018 | 8 | 14 | 15 | 46 | 18-0069929 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 546 | 20.6189 | 130_244 | <25mph | <15mph | HFTD - Distribution | 2018-08-14 15:46:00 | 1583 | 26.2074 | FALSE | 25-40mph | PG123 | 2.32 | 2019-04-16T16:20:00Z | 19.73 | 48 | < 25mph | PG123 | 2.32 | 2019-04-16T16:20:00Z | 19.73 | 87 | < 25mph | NBRC1 | 3.72 | 2019-04-16T17:33:00Z | 24 | 95 | < 25mph | NBRC1 | 3.72 | 2019-04-16T17:33:00Z | 24 | 172 | < 25mph
PG&E | 2017-08-30 | 22:37 | 38.9993 | -120.9887 | Vegetation | Rural | < 3 Meters | Fire Agency | Andy 530-889-0111 | 100026238 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42977 | 22:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1370 | 2017 | 8 | 30 | 22 | 37 | 17-0074333 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 3750 | 7.3126 | 200_294 | <25mph | <15mph | HFTD - Distribution | 2017-08-30 22:37:00 | 1108 | 12.9461 | FALSE | <25mph | D9434 | 3.56 | 2015-06-05T02:09:00Z | 2.01 | 19 | < 25mph | AT999 | 7.28 | 2015-06-05T02:09:00Z | 7 | 43 | < 25mph | D9434 | 3.56 | 2015-06-05T02:09:00Z | 2.01 | 35 | < 25mph | AT999 | 7.28 | 2015-06-05T02:09:00Z | 7 | 83 | < 25mph
PG&E | 2016-11-15 | 17:27 | 39.7275 | -121.6557 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100327525 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42689 | 17:27 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 1049 | 2016 | 11 | 15 | 17 | 27 | 16-0080083 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 69231 | 9.6883 | 172_334 | <25mph | <15mph | HFTD - Distribution | 2016-11-15 17:27:00 | 790 | 16.6369 | FALSE | <25mph | PDEC1 | 2.44 | 2018-08-11T23:00:00Z | 7 | 1 | < 25mph | E2076 | 4.45 | 2018-08-11T22:33:00Z | 8.01 | 11 | < 25mph | PDEC1 | 2.44 | 2018-08-12T00:00:00Z | 7 | 2 | < 25mph | E2076 | 4.45 | 2018-08-11T22:33:00Z | 8.01 | 22 | < 25mph
PG&E | 2015-07-03 03:23 | 2015-07-03 03:23 | 35.6785 | -120.9567 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 1 soan 1 conducter 1 span loade side transformer formtr 1008493290 |  | 21000 | Conductor | Overhead | Yes | 42188.141 | 2015-07-03 03:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0438 | 2015 | 7 | 3 | 3 | 23 | 15-0045239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 978 | 7.7054 | 202_111 | <25mph | <15mph | HFTD - Distribution | 2015-07-03 03:23:00 | 183 | 16.8894 | FALSE | <25mph | TABC1 | 2.38 | 2016-08-08T18:07:00Z | 5.99 | 1 | < 25mph | D4060 | 6.58 | 2016-08-08T18:10:00Z | 5.99 | 16 | < 25mph | TABC1 | 2.38 | 2016-08-08T19:07:00Z | 7 | 2 | < 25mph | D4060 | 6.58 | 2016-08-08T19:26:00Z | 8.99 | 33 | < 25mph
PG&E | 2017-08-09 11:29 | 11:29 | 38.6532 | -120.6273 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101402496 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42956.4786 | 11:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1328 | 2017 | 8 | 9 | 11 | 29 | 17-0069107 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 54216 | 9.4272 | 216_275 | <25mph | <15mph | HFTD - Distribution | 2017-08-09 11:29:00 | 1066 | 11.5652 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GZFC1 | 5.69 | 2016-08-17T06:17:00Z | 5.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | GZFC1 | 5.69 | 2016-08-17T06:17:00Z | 5.99 | 14 | < 25mph
PG&E | 2018-08-22 | 21:56 | 39.0425 | -120.9695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100024728 | Verizon | 12000 | Conductor | Overhead | Yes | 43334 | 21:56 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1854 | 2018 | 8 | 22 | 21 | 56 | 18-0072654 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29727 | 9.3137 | 201_296 | <25mph | <15mph | HFTD - Distribution | 2018-08-22 21:56:00 | 1593 | 10.5291 | FALSE | <25mph | D9434 | 1.28 | 2018-05-21T15:01:00Z | 2.01 | 10 | < 25mph | AT999 | 4.33 | 2018-05-21T14:53:00Z | 3 | 43 | < 25mph | C5488 | 3.82 | 2018-05-21T15:59:00Z | 4 | 20 | < 25mph | C5488 | 3.82 | 2018-05-21T15:59:00Z | 4 | 85 | < 25mph
PG&E | 2019-06-03 | 14:47 | 40.4419 | -122.3036 |  | Herbaceous | 1 meter - < 3 meters | Fire Dept | Anderson FD | 101495889 |  | 12000 | Insulator | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-456 | 2019 | 6 | 3 | 14 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 9.9807 | 145_374 | <25mph | <15mph | HFTD - Distribution | 2019-06-03 14:47:00 | 1799 | 16.209 | FALSE | <25mph | AP525 | 3.17 | 2015-04-26T10:30:00Z | 0 | 6 | < 25mph | E6886 | 7.7 | 2015-04-26T09:37:00Z | 13 | 17 | < 25mph | AP525 | 3.17 | 2015-04-26T11:00:00Z | 1.01 | 12 | < 25mph | E6886 | 7.7 | 2015-04-26T09:37:00Z | 13 | 33 | < 25mph
PG&E | 2016-04-30 | 17:59 | 38.3142 | -120.9015 | Vegetation | RURAL | < 3 meters | Fire Agency | Kern County FD |  |  | 12000 | Conductor | Overhead | Yes | 42490 | 17:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0719 | 2016 | 4 | 30 | 17 | 59 | 16-0032910 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 722 | 19.7396 | 204_256 | <25mph | <15mph | HFTD - Distribution | 2016-04-30 17:59:00 | 465 | 19.7396 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 4.81 | 2019-04-16T17:05:00Z | 7 | 3 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 4.81 | 2019-04-16T17:05:00Z | 7 | 5 | < 25mph
PG&E | 2018-06-21 | 18:58 | 35.1224 | -120.3938 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101878933 | AT&T | 12000 | Conductor | Overhead | Yes | 43272 | 18:58 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1683 | 2018 | 6 | 21 | 18 | 58 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 13.9909 | 227_80 | <25mph | <15mph | HFTD - Distribution | 2018-06-21 18:58:00 | 1425 | 15.3983 | FALSE | <25mph | AU609 | 1.36 | 2019-02-19T15:15:00Z | 0 | 4 | < 25mph | PG168 | 5.83 | 2019-02-19T15:00:00Z | 16.89 | 16 | < 25mph | AU609 | 1.36 | 2019-02-19T16:15:00Z | 0 | 8 | < 25mph | PG168 | 5.83 | 2019-02-19T15:00:00Z | 16.89 | 32 | < 25mph
PG&E | 2019-07-25 | 7:39 | 39.1735 | -123.5763 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Oj 2 P/Ss Of Cgc# 215532055340 |  | 12000 | Other | Overhead | Yes | 43671 | 7:39 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-380 | 2019 | 7 | 25 | 7 | 39 | 19-0080947 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 790 | 2.0398 | 89_305 | <25mph | <15mph | HFTD - Distribution | 2019-07-25 07:39:00 | 1928 | 13.3511 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1763 | 7.11 | 2018-04-29T23:43:00Z | 12.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E1763 | 7.11 | 2018-04-29T23:43:00Z | 12.01 | 8 | < 25mph
7. Camp Fire | 2018-11-08 | 6:33 | 39.8134 | -121.4347 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 60000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1993 | 2018 | 11 | 8 | 6 | 33 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Conductor | 826291590 | 33.1236 | 181_339 | 25-40mph | 30-45mph | HFTD - Transmission | 2018-11-08 06:33:00 | 1699 | 39.0185 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | JBGC1 | 6.08 | 2019-02-11T11:13:00Z | 8.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | JBGC1 | 6.08 | 2019-02-11T12:13:00Z | 8.99 | 2 | < 25mph
PG&E | 2016-06-19 | 2016-06-19 12:07 | 39.3811 | -123.7737 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102187888 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 12:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0807 | 2016 | 6 | 19 | 12 | 7 | 16-0044317 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6100 | 11.4602 | 81_317 | <25mph | <15mph | HFTD - Distribution | 2016-06-19 12:07:00 | 550 | 15.3844 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F1771 | 5.2 | 2017-12-17T07:01:00Z | 14 | 10 | < 25mph |  |  |  | 0 | 0 | No data | F1771 | 5.2 | 2017-12-17T07:01:00Z | 14 | 20 | < 25mph
PG&E | 2016-09-12 | 12:38 | 38.7832 | -120.6006 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101421708 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42625 | 12:38 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0974 | 2016 | 9 | 12 | 12 | 38 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 15.5165 | 217_282 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 12:38:00 | 716 | 15.5342 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E3165 | 7.91 | 2017-01-06T10:11:00Z | 8.99 | 6 | < 25mph |  |  |  | 0 | 0 | No data | E3165 | 7.91 | 2017-01-06T10:51:00Z | 8.99 | 12 | < 25mph
PG&E | 2018-06-16 | 19:58 | 37.907 | -121.8063 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100483910 | Unknown | 21000 | Conductor | Overhead | Yes | 43267 | 19:58 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1670 | 2018 | 6 | 16 | 19 | 58 | 18-0051687 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 3322 | 40.9858 | 164_234 | 40-55mph | 30-45mph | HFTD - Distribution | 2018-06-16 19:58:00 | 1412 | 43.1884 | FALSE | 40-55mph | D2814 | 3.84 | 2015-03-06T16:47:00Z | 3 | 3 | < 25mph | SJS02 | 6.13 | 2015-03-06T16:20:00Z | 16.89 | 20 | < 25mph | D2814 | 3.84 | 2015-03-06T17:07:00Z | 3 | 8 | < 25mph | SJS02 | 6.13 | 2015-03-06T16:20:00Z | 16.89 | 41 | < 25mph
PG&E | 2015-04-27 12:54 | 2015-04-27 12:54 | 35.4871 | -120.6756 | Vegetation | Rural | < 3 meters | Unknown |  | 103310601 |  | 21000 | Conductor | Overhead | Yes | 42121.5375 | 2015-04-27 12:54 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0301 | 2015 | 4 | 27 | 12 | 54 | 15-0029875 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 5836 | 7.5834 | 214_100 | <25mph | <15mph | HFTD - Distribution | 2015-04-27 12:54:00 | 47 | 19.0974 | FALSE | <25mph | E1179 | 1.84 | 2015-10-10T01:40:00Z | 5.99 | 8 | < 25mph | E2260 | 4.42 | 2015-10-10T02:12:00Z | 8.99 | 14 | < 25mph | E1179 | 1.84 | 2015-10-10T01:40:00Z | 5.99 | 16 | < 25mph | E2260 | 4.42 | 2015-10-10T02:12:00Z | 8.99 | 29 | < 25mph
PG&E | 2015-05-09 13:10 | 2015-05-09 13:10 | 39.2343 | -121.2468 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100000103 | None | 21000 | Conductor | Overhead | Yes | 42133.5486 | 2015-05-09 13:10 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0311 | 2015 | 5 | 9 | 13 | 10 | 15-0033085 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 382926 | 12.172 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 13:10:00 | 57 | 17.071 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6355 | 7.8 | 2018-05-21T10:46:00Z | 1.01 | 6 | < 25mph |  |  |  | 0 | 0 | No data | E6355 | 7.8 | 2018-05-21T10:46:00Z | 1.01 | 12 | < 25mph
PG&E | 2016-08-02 | 2016-08-02 16:15 | 37.0312 | -119.4395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Fresno County FD | 100675986 |  | 12000 | Conductor | Overhead | Yes | 42584 | 2016-08-02 16:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0900 | 2016 | 8 | 2 | 16 | 15 | 16-0054552 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 265566 | 14.0604 | 268_186 | <25mph | <15mph | HFTD - Distribution | 2016-08-02 16:15:00 | 643 | 14.6638 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5633 | 8 | 2016-10-06T21:26:00Z | 10 | 6 | < 25mph |  |  |  | 0 | 0 | No data | E5633 | 8 | 2016-10-06T22:26:00Z | 11.01 | 12 | < 25mph
PG&E | 2017-06-24 22:27 | 22:27 | 38.2908 | -120.849 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CONTACT BOBBY BOWMAN | 101238865 | None | 12000 | Conductor | Overhead | Yes | 42910.9354 | 22:27 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1195 | 2017 | 6 | 24 | 22 | 27 | 17-0058399 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 4529 | 5.1717 | 206_255 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 22:27:00 | 934 | 13.7168 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.57 | 2015-04-16T16:05:00Z | 11.01 | 3 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.57 | 2015-04-16T16:05:00Z | 11.01 | 5 | < 25mph
PG&E | 2017-07-05 12:11 | 11:58 | 39.2105 | -121.2266 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVE ROBERTSON 530 906 4892 | 100010286 | Unknown | 21000 | Conductor | Overhead | Yes | 42921.5077 | 11:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1223 | 2017 | 7 | 5 | 11 | 58 | 17-0060605 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 10231 | 9.71 | 190_306 | <25mph | <15mph | HFTD - Distribution | 2017-07-05 11:58:00 | 962 | 14.0848 | FALSE | <25mph | E2572 | 2.49 | 2016-10-01T05:28:00Z | 8.01 | 12 | < 25mph | E1789 | 6.76 | 2016-10-01T06:00:00Z | 11.01 | 29 | < 25mph | E2572 | 2.49 | 2016-10-01T06:53:00Z | 8.01 | 24 | < 25mph | E1789 | 6.76 | 2016-10-01T06:00:00Z | 11.01 | 56 | < 25mph
PG&E | 2019-09-01 | 16:50 | 35.908 | -121.011 |  | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 103477437 |  | 12000 | Pole | Overhead | Yes | 43709 | 16:50 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-17 | 2019 | 9 | 1 | 16 | 50 | 19-0094475 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45432 | 5.8888 | 199_124 | <25mph | <15mph | HFTD - Distribution | 2019-09-01 16:50:00 | 2009 | 25.5842 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2019-05-29 | 16:54 | 37.0371 | -119.5209 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 100680674 |  | 12000 | Pole | Overhead | Yes | 43614 | 16:54 | Vegetation |  | Veg. contact | Pole |  |  | Dead | 2019-202 | 2019 | 5 | 29 | 16 | 54 | 19-0059237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 6780 | 6.6167 | 265_186 | <25mph | <15mph | HFTD - Distribution | 2019-05-29 16:54:00 | 1787 | 9.3593 | FALSE | <25mph | D0955 | 0.46 | 2015-02-23T21:15:00Z | 15.99 | 5 | < 25mph | D0955 | 0.46 | 2015-02-23T21:15:00Z | 15.99 | 5 | < 25mph | D0955 | 0.46 | 2015-02-23T21:15:00Z | 15.99 | 10 | < 25mph | D0955 | 0.46 | 2015-02-23T21:15:00Z | 15.99 | 10 | < 25mph
PG&E | 2017-08-30 | 22:37 | 38.9993 | -120.9887 | Vegetation | Rural | < 3 Meters | Fire Agency | Andy 530-889-0111 | 100026238 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42977 | 22:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1370 | 2017 | 8 | 30 | 22 | 37 | 17-0074333 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 3750 | 7.3126 | 200_294 | <25mph | <15mph | HFTD - Distribution | 2017-08-30 22:37:00 | 1108 | 12.9461 | FALSE | <25mph | D9434 | 3.56 | 2018-10-17T15:46:00Z | 0 | 21 | < 25mph | PG032 | 6.61 | 2018-10-17T15:40:00Z | 8.12 | 46 | < 25mph | D9434 | 3.56 | 2018-10-17T16:46:00Z | 0 | 41 | < 25mph | PG032 | 6.61 | 2018-10-17T15:40:00Z | 8.12 | 85 | < 25mph
PG&E | 2019-09-01 | 16:50 | 35.908 | -121.011 |  | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 103477437 |  | 12000 | Pole | Overhead | Yes | 43709 | 16:50 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-17 | 2019 | 9 | 1 | 16 | 50 | 19-0094475 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45432 | 5.8888 | 199_124 | <25mph | <15mph | HFTD - Distribution | 2019-09-01 16:50:00 | 2009 | 25.5842 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-07-21 21:45 | 2016-07-21 21:45 | 40.8566 | -122.3387 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101455670 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0870 | 2016 | 7 | 21 | 21 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.7351 | 143_397 | <25mph | <15mph | HFTD - Distribution | 2016-07-21 21:45:00 | 613 | 15.1303 | FALSE | <25mph | CTANT | 1.58 | 2015-12-13T05:00:00Z | 6.85 | 3 | < 25mph | SLFC1 | 6.48 | 2015-12-13T05:19:00Z | 23 | 8 | < 25mph | CTANT | 1.58 | 2015-12-13T06:00:00Z | 9.33 | 7 | < 25mph | SLFC1 | 6.48 | 2015-12-13T06:19:00Z | 23 | 17 | < 25mph
PG&E | 2015-06-04 13:17 | 2015-06-04 13:17 | 39.2694 | -123.7841 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42159.5535 | 2015-06-04 13:17 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0344 | 2015 | 6 | 4 | 13 | 17 | 15-0038501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20525 | 22.1312 | 81_311 | <25mph | <15mph | HFTD - Distribution | 2015-06-04 13:17:00 | 90 | 22.6218 | FALSE | <25mph | E6025 | 1.61 | 2016-02-28T10:30:00Z | 4 | 4 | < 25mph | E6025 | 1.61 | 2016-02-28T10:30:00Z | 4 | 5 | < 25mph | E6025 | 1.61 | 2016-02-28T10:30:00Z | 4 | 8 | < 25mph | E6025 | 1.61 | 2016-02-28T10:30:00Z | 4 | 9 | < 25mph
PG&E | 2017-09-27 | 12:12 | 39.4845 | -121.3545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | bill lopez cell 530 521-8052 | 100429924 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 43005 | 12:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1436 | 2017 | 9 | 27 | 12 | 12 | 17-0082180 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 6370 | 7.6613 | 184_321 | <25mph | <15mph | HFTD - Distribution | 2017-09-27 12:12:00 | 1174 | 27.61 | FALSE | 25-40mph | PG080 | 2.1 | 2019-08-05T07:40:00Z | 8.32 | 12 | < 25mph | PG309 | 4.39 | 2019-08-05T06:50:00Z | 10.09 | 49 | < 25mph | PG080 | 2.1 | 2019-08-05T07:50:00Z | 8.32 | 24 | < 25mph | PG309 | 4.39 | 2019-08-05T08:40:00Z | 10.74 | 98 | < 25mph
PG&E | 2016-10-23 18:44 | 18:10 | 38.021 | -120.5991 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101272943 |  | 115000 | Conductor | Overhead | Yes | 42666.7804 | 18:10 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1043 | 2016 | 10 | 23 | 18 | 10 | INT-08709 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 0 | 9.2045 | 217_240 | <25mph | <15mph | HFTD - Transmission | 2016-10-23 18:10:00 | 784 | 15.0974 | FALSE | <25mph | PG445 | 0.51 | 2019-12-24T20:50:00Z | 16.6 | 7 | < 25mph | PG445 | 0.51 | 2019-12-24T20:50:00Z | 16.6 | 57 | < 25mph | PG445 | 0.51 | 2019-12-24T20:50:00Z | 16.6 | 14 | < 25mph | PG445 | 0.51 | 2019-12-24T20:50:00Z | 16.6 | 112 | < 25mph
PG&E | 2016-10-14 04:33 | 4:32 | 40.5228 | -121.6813 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101513661 |  | 12000 | Conductor | Overhead | Yes | 42657.1893 | 4:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1032 | 2016 | 10 | 14 | 4 | 32 | 16-0071897 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 38950 | 28.7152 | 171_378 | 25-40mph | 15-30mph | HFTD - Distribution | 2016-10-14 04:32:00 | 773 | 31.1927 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | VIOC1 | 5.45 | 2017-04-21T18:52:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | VIOC1 | 5.45 | 2017-04-21T19:52:00Z | 8.99 | 2 | < 25mph
PG&E | 2016-06-19 | 2016-06-19 12:07 | 39.3811 | -123.7737 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102187888 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 12:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0807 | 2016 | 6 | 19 | 12 | 7 | 16-0044317 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6100 | 11.4602 | 81_317 | <25mph | <15mph | HFTD - Distribution | 2016-06-19 12:07:00 | 550 | 15.3844 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6025 | 6.3 | 2017-05-18T16:00:00Z | 4.99 | 2 | < 25mph |  |  |  | 0 | 0 | No data | E6025 | 6.3 | 2017-05-18T16:30:00Z | 8.99 | 5 | < 25mph
PG&E | 2017-08-19 | 21:16 | 40.5752 | -122.2985 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464623 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42966 | 21:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1341 | 2017 | 8 | 19 | 21 | 16 | 17-0071522 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 19044 | 8.8981 | 145_381 | <25mph | <15mph | HFTD - Distribution | 2017-08-19 21:16:00 | 1079 | 13.341 | FALSE | <25mph | C5599 | 2.67 | 2015-11-09T16:16:00Z | 8.01 | 4 | < 25mph | C5599 | 2.67 | 2015-11-09T16:16:00Z | 8.01 | 9 | < 25mph | C5599 | 2.67 | 2015-11-09T16:16:00Z | 8.01 | 6 | < 25mph | RRAC1 | 4.12 | 2015-11-09T17:24:00Z | 8.99 | 16 | < 25mph
PG&E | 2019-08-16 | 8:19 | 40.1235 | -123.8758 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Self Extinguished |  | 192221102-2101118022{5563} |  | 12000 | Conductor | Overhead | Yes | 43693 | 8:19 | Vegetation | [5 empty] | Other/Unknown |  | 2019 | 8 | 16 | 8 | 19 | 19-0088744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 2979 | 5.7689 | 78_358 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 08:19:00 | 1983 | 18.468 | FALSE | <25mph | ERCC1 | 2.93 | 2017-04-09T06:28:00Z | 2.01 | 1 | < 25mph | ERCC1 | 2.93 | 2017-04-09T06:28:00Z | 2.01 | 6 | < 25mph | ERCC1 | 2.93 | 2017-04-09T07:28:00Z | 3 | 2 | < 25mph | ERCC1 | 2.93 | 2017-04-09T07:28:00Z | 3 | 10 | < 25mph
PG&E | 2018-06-21 | 18:58 | 35.1224 | -120.3938 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101878933 | AT&T | 12000 | Conductor | Overhead | Yes | 43272 | 18:58 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1683 | 2018 | 6 | 21 | 18 | 58 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 13.9909 | 227_80 | <25mph | <15mph | HFTD - Distribution | 2018-06-21 18:58:00 | 1425 | 15.3983 | FALSE | <25mph | AU609 | 1.36 | 2017-08-25T13:54:00Z | 0 | 4 | < 25mph | F0412 | 7.22 | 2017-08-25T13:25:00Z | 3 | 11 | < 25mph | AU609 | 1.36 | 2017-08-25T14:54:00Z | 0 | 8 | < 25mph | F0412 | 7.22 | 2017-08-25T14:55:00Z | 3 | 21 | < 25mph
PG&E | 2016-09-12 | 12:38 | 38.7832 | -120.6006 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101421708 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42625 | 12:38 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0974 | 2016 | 9 | 12 | 12 | 38 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 15.5165 | 217_282 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 12:38:00 | 716 | 15.5342 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TS903 | 7.53 | 2017-04-23T07:37:00Z | 2.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E3165 | 7.91 | 2017-04-23T08:33:00Z | 3 | 10 | < 25mph
PG&E | 2015-08-22 20:38 | 2015-08-22 20:38 | 38.7748 | -120.8564 | Vegetation | Rural | < 3 meters | Self Extinguished |  | at base of co pole 21721 - 720 Woodridge Rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42238.8597 | 2015-08-22 20:38 | Contact From Object | N.A. | Vegetation | Communication Facility | Unknown | tree hit phone lines | Fell into (Moderate-Severe defect) | 0549 | 2015 | 8 | 22 | 20 | 38 | 15-0056766 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26513 | 9.2929 | 206_282 | <25mph | <15mph | HFTD - Distribution | 2015-08-22 20:38:00 | 293 | 10.7008 | FALSE | <25mph | E5691 | 3.87 | 2016-04-14T04:21:00Z | 8.01 | 12 | < 25mph | E5691 | 3.87 | 2016-04-14T04:21:00Z | 8.01 | 60 | < 25mph | E5691 | 3.87 | 2016-04-14T04:21:00Z | 8.01 | 24 | < 25mph | E6490 | 6.16 | 2016-04-14T05:35:00Z | 10 | 117 | < 25mph
PG&E | 2017-09-06 | 20:08 | 37.2925 | -122.294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100256917 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1400 | 2017 | 9 | 6 | 20 | 8 | 17-0076502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4914 | 6.7999 | 143_200 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 20:08:00 | 1138 | 13.6021 | FALSE | <25mph | LAHC1 | 2.3 | 2018-12-28T16:07:00Z | 14.99 | 1 | < 25mph | PG149 | 7.67 | 2018-12-28T16:40:00Z | 31.34 | 40 | 25-40mph | LAHC1 | 2.3 | 2018-12-28T17:07:00Z | 15.99 | 2 | < 25mph | PG149 | 7.67 | 2018-12-28T16:40:00Z | 31.34 | 78 | 25-40mph
PG&E | 2016-06-19 | 2016-06-19 12:07 | 39.3811 | -123.7737 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102187888 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 12:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0807 | 2016 | 6 | 19 | 12 | 7 | 16-0044317 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6100 | 11.4602 | 81_317 | <25mph | <15mph | HFTD - Distribution | 2016-06-19 12:07:00 | 550 | 15.3844 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F1771 | 5.2 | 2018-08-17T04:44:00Z | 4.99 | 10 | < 25mph |  |  |  | 0 | 0 | No data | F1771 | 5.2 | 2018-08-17T04:44:00Z | 4.99 | 20 | < 25mph
PG&E | 2019-07-30 | 15:15 | 39.1207 | -121.072 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 152691104 |  | 12000 | Conductor | Overhead | Yes | 43676 | 15:15 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-386 | 2019 | 7 | 30 | 15 | 15 | 19-0082713 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 31302 | 12.2921 | 196_301 | <25mph | <15mph | HFTD - Distribution | 2019-07-30 15:15:00 | 1942 | 13.0851 | FALSE | <25mph | E1789 | 3.69 | 2019-05-20T18:12:00Z | 8.01 | 10 | < 25mph | PG367 | 7.57 | 2019-05-20T18:40:00Z | 13.15 | 83 | < 25mph | E1789 | 3.69 | 2019-05-20T20:00:00Z | 11.01 | 20 | < 25mph | PG377 | 4.31 | 2019-05-20T19:30:00Z | 15.35 | 165 | < 25mph
PG&E | 2018-05-28 | 6:30 | 40.4382 | -122.3001 | Building | Rural | Structure Only | Unknown | N.A. | 101495757 | Unknown | 0 – 750 | conductor | Overhead | Yes | 43248 | 6:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1610 | 2018 | 5 | 28 | 6 | 30 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 17.501 | 145_374 | <25mph | <15mph | HFTD - Distribution | 2018-05-28 06:30:00 | 1352 | 26.4092 | FALSE | 25-40mph | PG479 | 3.12 | 2019-09-22T00:10:00Z | 10.58 | 12 | < 25mph | RRAC1 | 5.38 | 2019-09-22T00:24:00Z | 17 | 22 | < 25mph | PG479 | 3.12 | 2019-09-22T00:10:00Z | 10.58 | 24 | < 25mph | RRAC1 | 5.38 | 2019-09-22T00:24:00Z | 17 | 44 | < 25mph
PG&E | 2019-08-12 | 17:42 | 38.6618 | -120.7451 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 101415488, 101404439 |  | 12000 | Pole | Overhead | Yes | 43689 | 17:42 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (slight defect) | 2019-241 | 2019 | 8 | 12 | 17 | 42 | 19-0087080 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 54604 | 8.3029 | 210_275 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 17:42:00 | 1968 | 11.2889 | FALSE | <25mph | C5121 | 3.8 | 2016-03-05T19:43:00Z | 8.99 | 6 | < 25mph | KPVF | 4.33 | 2016-03-05T19:55:00Z | 27.63 | 39 | 25-40mph | C5121 | 3.8 | 2016-03-05T19:43:00Z | 8.99 | 12 | < 25mph | KPVF | 4.33 | 2016-03-05T21:35:00Z | 29.93 | 77 | 25-40mph
PG&E | 2015-09-04 07:49 | 2015-09-04 07:49 | 40.2318 | -122.3643 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | E/O FRONTIER RD & N/O WAGON WAY |  | 12000 | Conductor | Overhead | Yes | 42251.3257 | 2015-09-04 07:49 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0577 | 2015 | 9 | 4 | 7 | 49 | 15-0059323 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 9563 | 2.343 | 142_362 | <25mph | <15mph | HFTD - Distribution | 2015-09-04 07:49:00 | 321 | 17.9748 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 5.07 | 2015-05-26T23:20:00Z | 10 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 5.07 | 2015-05-26T23:20:00Z | 10 | 7 | < 25mph
PG&E | 2016-06-04 | 22:15 | 38.5117 | -122.9373 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42525 | 22:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0768 | 2016 | 6 | 4 | 22 | 15 | 16-0041119 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7220 | 6.1483 | 116_268 | <25mph | <15mph | HFTD - Distribution | 2016-06-04 22:15:00 | 514 | 16.4728 | FALSE | <25mph | D3481 | 2.53 | 2015-05-24T21:57:00Z | 13 | 24 | < 25mph | KSTS | 6.57 | 2015-05-24T21:53:00Z | 20.71 | 66 | < 25mph | D3481 | 2.53 | 2015-05-24T21:57:00Z | 13 | 48 | < 25mph | KSTS | 6.57 | 2015-05-24T21:53:00Z | 20.71 | 131 | < 25mph
PG&E | 2016-06-03 | 2016-06-03 12:16 | 38.6435 | -120.6959 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | cal-fire and usfs | 103119737 |  | 21000 | Conductor | Overhead | Yes | 42524 | 2016-06-03 12:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0764 | 2016 | 6 | 3 | 12 | 16 | 16-0040808 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 101354 | 7.6436 | 213_274 | <25mph | <15mph | HFTD - Distribution | 2016-06-03 12:16:00 | 507 | 11.74 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E4543 | 6.2 | 2015-08-08T13:20:00Z | 0 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E4543 | 6.2 | 2015-08-08T14:20:00Z | 0 | 8 | < 25mph
PG&E | 2015-07-03 03:23 | 2015-07-03 03:23 | 35.6785 | -120.9567 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 1 soan 1 conducter 1 span loade side transformer formtr 1008493290 |  | 21000 | Conductor | Overhead | Yes | 42188.141 | 2015-07-03 03:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0438 | 2015 | 7 | 3 | 3 | 23 | 15-0045239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 978 | 7.7054 | 202_111 | <25mph | <15mph | HFTD - Distribution | 2015-07-03 03:23:00 | 183 | 16.8894 | FALSE | <25mph | TABC1 | 2.38 | 2019-02-23T12:07:00Z | 0 | 1 | < 25mph | PG169 | 7.59 | 2019-02-23T12:00:00Z | 3.29 | 23 | < 25mph | TABC1 | 2.38 | 2019-02-23T13:07:00Z | 2.01 | 2 | < 25mph | PG169 | 7.59 | 2019-02-23T12:00:00Z | 3.29 | 46 | < 25mph
PG&E | 2018-06-15 | 9:51 | 37.1986 | -119.4709 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RANCHARIA ENGINE 4255 USFS ENG 52 | 101058060 | Unknown | 12000 | Conductor | Overhead | Yes | 43266 | 9:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1660 | 2018 | 6 | 15 | 9 | 51 | 18-0051354 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 35146 | 7.0865 | 267_195 | <25mph | <15mph | HFTD - Distribution | 2018-06-15 09:51:00 | 1402 | 16.2916 | FALSE | <25mph | C6459 | 3.69 | 2015-09-02T13:00:00Z | 8.01 | 3 | < 25mph | C6459 | 3.69 | 2015-09-02T13:00:00Z | 8.01 | 3 | < 25mph | C6459 | 3.69 | 2015-09-02T13:00:00Z | 8.01 | 5 | < 25mph | C6459 | 3.69 | 2015-09-02T13:00:00Z | 8.01 | 5 | < 25mph
PG&E | 2015-06-09 16:20 | 2015-06-09 16:20 | 38.3822 | -122.4316 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102269716 | Pacific Bell | 21000 | Unknown | Overhead | Yes | 42164.6806 | 2015-06-09 16:20 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0369 | 2015 | 6 | 9 | 16 | 20 | 15-0039860 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 4184 | 20.783 | 138_260 | <25mph | <15mph | HFTD - Distribution | 2015-06-09 16:20:00 | 115 | 24.1918 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AS725 | 7.12 | 2016-04-04T00:36:00Z | 4.99 | 7 | < 25mph |  |  |  | 0 | 0 | No data | AS725 | 7.12 | 2016-04-04T00:36:00Z | 4.99 | 16 | < 25mph
PG&E | 2017-07-08 19:23 | 18:49 | 40.2935 | -122.4089 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | TOM STROING, RED BLUFF | 101526269 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42924.8076 | 18:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1234 | 2017 | 7 | 8 | 18 | 49 | 17-0061469 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 157484 | 8.2983 | 140_366 | <25mph | <15mph | HFTD - Distribution | 2017-07-08 18:49:00 | 973 | 15.6109 | FALSE | <25mph | E7114 | 0.65 | 2018-02-22T13:57:00Z | 3 | 4 | < 25mph | E7114 | 0.65 | 2018-02-22T13:57:00Z | 3 | 4 | < 25mph | E7114 | 0.65 | 2018-02-22T13:57:00Z | 3 | 7 | < 25mph | E7114 | 0.65 | 2018-02-22T13:57:00Z | 3 | 7 | < 25mph
PG&E | 2017-08-28 | 10:07 | 39.0472 | -120.7859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | FORESTHILL | 100019525 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 10:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1357 | 2017 | 8 | 28 | 10 | 7 | 17-0073379 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 10077 | 5.9792 | 209_297 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 10:07:00 | 1095 | 13.4783 | FALSE | <25mph | AU268 | 3.78 | 2016-02-04T20:28:00Z | 3 | 5 | < 25mph | FSHC1 | 4.22 | 2016-02-04T20:33:00Z | 5.99 | 6 | < 25mph | AU268 | 3.78 | 2016-02-04T20:55:00Z | 4.99 | 9 | < 25mph | FSHC1 | 4.22 | 2016-02-04T21:33:00Z | 8.99 | 11 | < 25mph
PG&E | 2017-08-03 11:01 | 10:53 | 39.0732 | -121.0868 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100072742 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42950.4588 | 10:53 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1312 | 2017 | 8 | 3 | 10 | 53 | 17-0067679 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 127440 | 9.5869 | 196_298 | <25mph | <15mph | HFTD - Distribution | 2017-08-03 10:53:00 | 1050 | 11.8038 | FALSE | <25mph | C5488 | 3.14 | 2015-05-12T11:39:00Z | 5.99 | 6 | < 25mph | E1789 | 5.51 | 2015-05-12T11:54:00Z | 11.99 | 38 | < 25mph | C5488 | 3.14 | 2015-05-12T12:50:00Z | 14.99 | 12 | < 25mph | E1789 | 5.51 | 2015-05-12T12:30:00Z | 15.99 | 78 | < 25mph
PG&E | 2015-06-21 13:31 | 2015-06-21 13:31 | 37.375 | -119.6116 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103204866 |  | 0 – 750 | Conductor | Overhead | No |  |  | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0399 | 2015 | 6 | 21 | 13 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 11.8124 | 260_205 | <25mph | <15mph | HFTD - Distribution | 2015-06-21 13:31:00 | 145 | 12.2407 | FALSE | <25mph | D7171 | 3.95 | 2019-07-06T02:45:00Z | 8.99 | 20 | < 25mph | MIAC1 | 7.96 | 2019-07-06T02:59:00Z | 14.99 | 64 | < 25mph | D7171 | 3.95 | 2019-07-06T02:45:00Z | 8.99 | 32 | < 25mph | MIAC1 | 7.96 | 2019-07-06T03:59:00Z | 15.99 | 124 | < 25mph
PG&E | 2015-08-31 14:28 | 2015-08-31 14:28 | 36.5325 | -121.1462 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 29401 Hwy 25 |  | 21000 | Conductor | Overhead | Yes | 42247.6028 | 2015-08-31 14:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0568 | 2015 | 8 | 31 | 14 | 28 | 15-0058455 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25668 | 4.8975 | 193_158 | <25mph | <15mph | HFTD - Distribution | 2015-08-31 14:28:00 | 312 | 19.6836 | FALSE | <25mph | PG406 | 3.12 | 2019-05-25T12:00:00Z | 6.13 | 8 | < 25mph | PG406 | 3.12 | 2019-05-25T12:00:00Z | 6.13 | 9 | < 25mph | PG406 | 3.12 | 2019-05-25T13:20:00Z | 8.77 | 18 | < 25mph | PG406 | 3.12 | 2019-05-25T13:20:00Z | 8.77 | 20 | < 25mph
PG&E | 2015-08-03 17:53 | 2015-08-03 17:53 | 39.3361 | -121.1894 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Pole 000/008 |  | 60000 | Conductor | Overhead | Yes | 42219.7451 | 2015-08-03 17:53 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0510 | 2015 | 8 | 3 | 17 | 53 | TM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 11.0618 | 191_313 | <25mph | <15mph | HFTD - Transmission | 2015-08-03 17:53:00 | 255 | 11.5241 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RRRC1 | 4.47 | 2016-06-14T03:13:00Z | 12.01 | 31 | < 25mph |  |  |  | 0 | 0 | No data | RRRC1 | 4.47 | 2016-06-14T03:13:00Z | 12.01 | 61 | < 25mph
PG&E | 2018-06-28 | 12:27 | 38.5982 | -121.0081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | John Reis, 530-622-3858 | 101376954 | Unknown | 21000 | Conductor | Overhead | Yes | 43279 | 12:27 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1702 | 2018 | 6 | 28 | 12 | 27 | 18-0055479 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 24671 | 12.7651 | 199_272 | <25mph | <15mph | HFTD - Distribution | 2018-06-28 12:27:00 | 1443 | 13.4512 | FALSE | <25mph | E8856 | 2.62 | 2017-11-04T19:45:00Z | 4 | 12 | < 25mph | D7413 | 5.94 | 2017-11-04T19:46:00Z | 5.99 | 32 | < 25mph | E8856 | 2.62 | 2017-11-04T20:00:00Z | 7 | 24 | < 25mph | E8856 | 2.62 | 2017-11-04T20:00:00Z | 7 | 65 | < 25mph
PG&E | 2019-08-16 | 8:19 | 40.1235 | -123.8758 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Self Extinguished |  | 192221102-2101118022{5563} |  | 12000 | Conductor | Overhead | Yes | 43693 | 8:19 | Vegetation | [5 empty] | Other/Unknown |  | 2019 | 8 | 16 | 8 | 19 | 19-0088744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 2979 | 5.7689 | 78_358 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 08:19:00 | 1983 | 18.468 | FALSE | <25mph | ERCC1 | 2.93 | 2015-03-11T10:28:00Z | 4.99 | 1 | < 25mph | ERCC1 | 2.93 | 2015-03-11T10:28:00Z | 4.99 | 1 | < 25mph | ERCC1 | 2.93 | 2015-03-11T11:28:00Z | 4.99 | 2 | < 25mph | ERCC1 | 2.93 | 2015-03-11T11:28:00Z | 4.99 | 2 | < 25mph
PG&E | 2016-08-25 | 2016-08-25 12:04 | 36.9726 | -119.3816 | Vegetation | RURAL | < 3 meters | Utility: PG&E | N.A. | 100651318 | PONDEROSA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0945 | 2016 | 8 | 25 | 12 | 4 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.3948 | 271_183 | <25mph | <15mph | HFTD - Distribution | 2016-08-25 12:04:00 | 689 | 15.1668 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTQC1 | 5.65 | 2018-04-13T14:52:00Z | 4.99 | 7 | < 25mph |  |  |  | 0 | 0 | No data | E5633 | 4.89 | 2018-04-13T16:29:00Z | 7 | 14 | < 25mph
PG&E | 2017-08-06 11:38 | 11:38 | 36.5857 | -121.7121 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101747125 | Unknown | 12000 | Conductor | Overhead | Yes | 42953.4849 | 11:38 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1321 | 2017 | 8 | 6 | 11 | 38 | 17-0068279 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 87172 | 7.0101 | 168_161 | <25mph | <15mph | HFTD - Distribution | 2017-08-06 11:38:00 | 1059 | 12.123 | FALSE | <25mph | F1964 | 0.83 | 2018-05-02T15:56:00Z | 3 | 4 | < 25mph | E8875 | 7.87 | 2018-05-02T16:11:00Z | 4 | 20 | < 25mph | F1964 | 0.83 | 2018-05-02T17:11:00Z | 4.99 | 8 | < 25mph | E8875 | 7.87 | 2018-05-02T17:12:00Z | 10 | 40 | < 25mph
PG&E | 2015-09-12 09:51 | 2015-09-12 09:51 | 39.1164 | -121.0693 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | TOP OF AVALON PLACE, GRASS VALLEY TOWER NUMBER 19/152 40689729 |  | 115000 | Conductor | Overhead | Yes | 42259.4104 | 2015-09-12 09:51 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0594 | 2015 | 9 | 12 | 9 | 51 | VD-2015-079 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.5014 | 196_301 | <25mph | <15mph | HFTD - Transmission | 2015-09-12 09:51:00 | 339 | 14.0472 | FALSE | <25mph | C5488 | 3.69 | 2017-07-20T23:37:00Z | 11.01 | 25 | < 25mph | C5488 | 3.69 | 2017-07-20T23:37:00Z | 11.01 | 67 | < 25mph | C5488 | 3.69 | 2017-07-20T23:37:00Z | 11.01 | 45 | < 25mph | C5488 | 3.69 | 2017-07-20T23:37:00Z | 11.01 | 137 | < 25mph
PG&E | 2017-09-06 | 20:08 | 37.2925 | -122.294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100256917 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1400 | 2017 | 9 | 6 | 20 | 8 | 17-0076502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4914 | 6.7999 | 143_200 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 20:08:00 | 1138 | 13.6021 | FALSE | <25mph | LAHC1 | 2.3 | 2016-08-05T19:07:00Z | 4.99 | 1 | < 25mph | LAHC1 | 2.3 | 2016-08-05T19:07:00Z | 4.99 | 1 | < 25mph | LAHC1 | 2.3 | 2016-08-05T20:07:00Z | 7 | 2 | < 25mph | LAHC1 | 2.3 | 2016-08-05T20:07:00Z | 7 | 2 | < 25mph
PG&E | 2019-04-28 | 12:36 | 39.6756 | -121.5677 |  | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 100404366 |  | 12000 | Conductor | Overhead | Yes | 43583 | 12:36 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-166 | 2019 | 4 | 28 | 12 | 36 | 19-0046853 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 79810 | 6.7497 | 175_331 | <25mph | <15mph | HFTD - Distribution | 2019-04-28 12:36:00 | 1752 | 11.2512 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JBGC1 | 5.9 | 2016-11-15T06:13:00Z | 14 | 3 | < 25mph |  |  |  | 0 | 0 | No data | JBGC1 | 5.9 | 2016-11-15T06:13:00Z | 14 | 6 | < 25mph
PG&E | 2017-09-03 | 17:52 | 37.4956 | -119.8367 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101086621 | Unknown | 21000 | Transformer | Overhead | Yes | 42981 | 17:52 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 1389 | 2017 | 9 | 3 | 17 | 52 | 17-0075617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 4512 | 13.9592 | 250_212 | <25mph | <15mph | HFTD - Distribution | 2017-09-03 17:52:00 | 1127 | 22.0754 | FALSE | <25mph | JSDC1 | 3.33 | 2017-03-01T01:47:00Z | 8.01 | 1 | < 25mph | E9110 | 4.74 | 2017-03-01T01:18:00Z | 11.01 | 9 | < 25mph | JSDC1 | 3.33 | 2017-03-01T01:47:00Z | 8.01 | 2 | < 25mph | E9110 | 4.74 | 2017-03-01T02:31:00Z | 13 | 19 | < 25mph
PG&E | 2015-08-31 14:28 | 2015-08-31 14:28 | 36.5325 | -121.1462 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 29401 Hwy 25 |  | 21000 | Conductor | Overhead | Yes | 42247.6028 | 2015-08-31 14:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0568 | 2015 | 8 | 31 | 14 | 28 | 15-0058455 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25668 | 4.8975 | 193_158 | <25mph | <15mph | HFTD - Distribution | 2015-08-31 14:28:00 | 312 | 19.6836 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.27 | 2017-09-07T21:37:00Z | 10 | 1 | < 25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.27 | 2017-09-07T22:37:00Z | 14 | 2 | < 25mph
PG&E | 2018-06-15 | 2:56 | 37.4869 | -122.4223 | Vegetation | Rural | < 0.25 Acres | Utility: PG&E | N.A. | Pole 10/5 | None | 60000 | Conductor | Overhead | Yes | 43266 | 2:56 | Contamination | N.A. | N.A. | N.A. | Unknown |  | no-match | 1659 | 2018 | 6 | 15 | 2 | 56 | INT-11115 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 0 | 6.5721 | 137_211 | <25mph | <15mph | HFTD - Transmission | 2018-06-15 02:56:00 | 1401 | 18.0175 | FALSE | <25mph | C3295 | 3.73 | 2019-07-02T22:44:00Z | 0 | 3 | < 25mph | HSPC1 | 5.28 | 2019-07-02T22:18:00Z | 34 | 84 | 25-40mph | C3295 | 3.73 | 2019-07-02T23:14:00Z | 0 | 5 | < 25mph | HSPC1 | 5.28 | 2019-07-02T22:18:00Z | 34 | 160 | 25-40mph
PG&E | 2015-09-12 09:51 | 2015-09-12 09:51 | 39.1164 | -121.0693 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | TOP OF AVALON PLACE, GRASS VALLEY TOWER NUMBER 19/152 40689729 |  | 115000 | Conductor | Overhead | Yes | 42259.4104 | 2015-09-12 09:51 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0594 | 2015 | 9 | 12 | 9 | 51 | VD-2015-079 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.5014 | 196_301 | <25mph | <15mph | HFTD - Transmission | 2015-09-12 09:51:00 | 339 | 14.0472 | FALSE | <25mph | E1789 | 3.95 | 2017-07-02T11:42:00Z | 3 | 28 | < 25mph | E1789 | 3.95 | 2017-07-02T11:42:00Z | 3 | 76 | < 25mph | E1789 | 3.95 | 2017-07-02T13:36:00Z | 3 | 56 | < 25mph | AT999 | 4.8 | 2017-07-02T13:03:00Z | 4 | 149 | < 25mph
PG&E | 2015-10-16 09:43 | 2015-10-16 09:43 | 39.187 | -123.2015 | Vegetation | Rural | < 3 meters | Unknown |  | 102196855 |  | 12000 | Conductor | Overhead | Yes | 42293.4049 | 2015-10-16 09:43 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0653 | 2015 | 10 | 16 | 9 | 43 | 15-0070948 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 65228 | 2.2696 | 105_305 | <25mph | <15mph | HFTD - Distribution | 2015-10-16 09:43:00 | 397 | 16.8813 | FALSE | <25mph | E7513 | 1.34 | 2019-12-27T06:53:00Z | 2.01 | 12 | < 25mph | PG122 | 6.24 | 2019-12-27T07:00:00Z | 15.21 | 36 | < 25mph | E7513 | 1.34 | 2019-12-27T07:38:00Z | 2.01 | 24 | < 25mph | PG109 | 5.13 | 2019-12-27T07:10:00Z | 15.41 | 72 | < 25mph
PG&E | 2017-07-01 04:43 | 3:12 | 38.1952 | -122.9197 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103855493 | Unknown | 12000 | Conductor | Overhead | Yes | 42917.1963 | 3:12 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1214 | 2017 | 7 | 1 | 3 | 12 | 17-0059935 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 41370 | 14.0388 | 116_251 | <25mph | <15mph | HFTD - Distribution | 2017-07-01 03:12:00 | 951 | 27.9197 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PRWC1 | 7.17 | 2017-08-12T01:10:00Z | 19.15 | 11 | < 25mph |  |  |  | 0 | 0 | No data | PTRCA | 7.17 | 2017-08-12T02:20:00Z | 19.3 | 20 | < 25mph
PG&E | 2018-07-20 | 6:31 | 37.4318 | -119.9441 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ZACH RUTHERFORD 209-966-3621 | 103909942 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43301 | 6:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1771 | 2018 | 7 | 20 | 6 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2004 | 246_208 | <25mph | <15mph | HFTD - Distribution | 2018-07-20 06:31:00 | 1511 | 13.5994 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MPOC1 | 5.51 | 2016-03-06T23:07:00Z | 14.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | MPOC1 | 5.51 | 2016-03-06T23:07:00Z | 14.99 | 8 | < 25mph
PG&E | 2018-10-14 | 11:40 | 40.3598 | -122.4388 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TOM STROING 530-200-5113 | 101506416 | AT&T | 12000 | Conductor | Overhead | Yes | 43387 | 11:40 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1938 | 2018 | 10 | 14 | 11 | 40 | 18-0090193 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 945 | 30.6414 | 139_370 | 25-40mph | 30-45mph | HFTD - Distribution | 2018-10-14 11:40:00 | 1677 | 30.6414 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E7114 | 4.61 | 2015-07-10T12:55:00Z | 5.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 4.61 | 2015-07-10T14:32:00Z | 13 | 8 | < 25mph
PG&E | 2019-09-13 | 6:30 | 37.3348 | -121.7716 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 83392110 |  | 21000 | Splice/Clamp/Connector | Overhead | Yes | 43721 | 6:30 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-444 | 2019 | 9 | 13 | 6 | 30 | 19-0098560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 35534 | 3.3882 | 166_202 | <25mph | <15mph | HFTD - Distribution | 2019-09-13 06:30:00 | 2037 | 14.1926 | FALSE | <25mph | C7794 | 2.64 | 2015-05-17T06:05:00Z | 10 | 12 | < 25mph | SJS01 | 6.07 | 2015-05-17T06:05:00Z | 11.41 | 82 | < 25mph | C7794 | 2.64 | 2015-05-17T06:05:00Z | 10 | 23 | < 25mph | SJS01 | 6.07 | 2015-05-17T06:05:00Z | 11.41 | 155 | < 25mph
PG&E | 2015-07-18 17:00 | 2015-07-18 17:00 | 38.8383 | -123.6297 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | off HWY 1 PA |  | 12000 | Conductor | Overhead | Yes | 42203.7083 | 2015-07-18 17:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0470 | 2015 | 7 | 18 | 17 | 0 | 15-0048394 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 51806 | 18.0824 | 86_287 | <25mph | <15mph | HFTD - Distribution | 2015-07-18 17:00:00 | 215 | 27.3037 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | ANVC1 | 6.68 | 2019-07-13T04:36:00Z | 14 | 16 | < 25mph |  |  |  | 0 | 0 | No data | ANVC1 | 6.68 | 2019-07-13T04:36:00Z | 14 | 32 | < 25mph
PG&E | 2019-07-18 | 10:27 | 38.3033 | -120.6718 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | B561 |  | 12000 | Other | Overhead | Yes | 43664 | 10:27 | Equipment - PG&E | Other |  |  |  |  | Other/Unknown | 2019-68 | 2019 | 7 | 18 | 10 | 27 | 19-0078904 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45558 | 8.6789 | 214_256 | <25mph | <15mph | HFTD - Distribution | 2019-07-18 10:27:00 | 1910 | 16.0413 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ANUC1 | 7.14 | 2018-07-27T17:53:00Z | 7 | 2 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.09 | 2018-07-27T18:56:00Z | 8.01 | 4 | < 25mph
PG&E | 2019-09-01 | 16:50 | 35.908 | -121.011 |  | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 103477437 |  | 12000 | Pole | Overhead | Yes | 43709 | 16:50 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-17 | 2019 | 9 | 1 | 16 | 50 | 19-0094475 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45432 | 5.8888 | 199_124 | <25mph | <15mph | HFTD - Distribution | 2019-09-01 16:50:00 | 2009 | 25.5842 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-09-25 10:35 | 2016-09-25 10:35 | 38.8019 | -122.8176 | Vegetation | RURAL | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103613996 |  | 115000 | Other | Overhead | Yes | 2016-09-25 10:35 | 2016-09-25 10:35 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1004 | 2016 | 9 | 25 | 10 | 35 | INT-08572 | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Equip Failure - Other | 0 | 28.1055 | 121_284 | 25-40mph | 15-30mph | HFTD - Transmission | 2016-09-25 10:35:00 | 743 | 28.9174 | FALSE | 25-40mph | PG125 | 1.13 | 2019-01-23T08:40:00Z | 8.12 | 6 | < 25mph | PG125 | 1.13 | 2019-01-23T08:40:00Z | 8.12 | 38 | < 25mph | PG125 | 1.13 | 2019-01-23T08:40:00Z | 8.12 | 12 | < 25mph | PG040 | 6.36 | 2019-01-23T10:20:00Z | 10.96 | 76 | < 25mph
PG&E | 2019-09-16 | 14:39 | 37.3762 | -119.8729 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 254452102 |  | 21000 | Conductor | Overhead | Yes | 43724 | 14:39 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-417 | 2019 | 9 | 16 | 14 | 39 | 19-0099772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 121254 | 13.3091 | 249_205 | <25mph | <15mph | HFTD - Distribution | 2019-09-16 14:39:00 | 2045 | 14.9838 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MCFC1 | 6.2 | 2015-08-11T11:02:00Z | 7 | 7 | < 25mph |  |  |  | 0 | 0 | No data | MIAC1 | 7.6 | 2015-08-11T11:59:00Z | 7 | 11 | < 25mph
PG&E | 2015-07-30 19:11 | 2015-07-30 19:11 | 37.8102 | -120.1287 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE |  |  | 17000 | Conductor | Overhead | Yes | 42215.7993 | 2015-07-30 19:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0500 | 2015 | 7 | 30 | 19 | 11 | 15-0051772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26776 | 10.007 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2015-07-30 19:11:00 | 245 | 11.7658 | FALSE | <25mph | SEWC1 | 1.66 | 2019-04-12T06:16:00Z | 20 | 17 | < 25mph | SEWC1 | 1.66 | 2019-04-12T06:16:00Z | 20 | 34 | < 25mph | SEWC1 | 1.66 | 2019-04-12T06:16:00Z | 20 | 34 | < 25mph | SEWC1 | 1.66 | 2019-04-12T06:16:00Z | 20 | 64 | < 25mph
PG&E | 2015-11-09 05:55 | 2015-11-09 05:55 | 34.9984 | -120.3634 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42317.2465 | 2015-11-09 05:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0673 | 2015 | 11 | 9 | 5 | 55 | 15-0076534 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 205393 | 8.4294 | 228_73 | <25mph | <15mph | HFTD - Distribution | 2015-11-09 05:55:00 | 417 | 17.7768 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AU609 | 7.47 | 2019-03-30T14:31:00Z | 13 | 10 | < 25mph |  |  |  | 0 | 0 | No data | AU609 | 7.47 | 2019-03-30T15:45:00Z | 17 | 20 | < 25mph
PG&E | 2016-09-18 | 14:33 | 37.1619 | -122.1347 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire & Boulder Creek Fire Dept. | 103410909 | Yes | 12000 | Conductor | Overhead | Yes | 42631 | 14:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0986 | 2016 | 9 | 18 | 14 | 33 | 16-0065437 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 54983 | 5.897 | 150_193 | <25mph | <15mph | HFTD - Distribution | 2016-09-18 14:33:00 | 728 | 11.3228 | FALSE | <25mph | BNDC1 | 2.99 | 2016-09-29T16:50:00Z | 4.99 | 21 | < 25mph | BNDC1 | 2.99 | 2016-09-29T16:50:00Z | 4.99 | 43 | < 25mph | BNDC1 | 2.99 | 2016-09-29T17:50:00Z | 4.99 | 42 | < 25mph | BNDC1 | 2.99 | 2016-09-29T17:50:00Z | 4.99 | 88 | < 25mph
PG&E | 2017-05-06 11:23 | 11:18 | 40.7951 | -124.029 | Vegetation | Rural | < 3 Meters | Fire Agency | chief rick harden 7074423352 | 103661154 | Unknown | 12000 | Conductor | Overhead | Yes | 42861.4744 | 11:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1086 | 2017 | 5 | 6 | 11 | 18 | 17-0045785 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 113630 | 26.2788 | 73_395 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-05-06 11:18:00 | 826 | 28.8261 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.4 | 2017-04-04T11:55:00Z | 10 | 29 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.4 | 2017-04-04T11:55:00Z | 10 | 56 | < 25mph
PG&E | 2019-04-28 | 12:36 | 39.6756 | -121.5677 |  | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 100404366 |  | 12000 | Conductor | Overhead | Yes | 43583 | 12:36 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-166 | 2019 | 4 | 28 | 12 | 36 | 19-0046853 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 79810 | 6.7497 | 175_331 | <25mph | <15mph | HFTD - Distribution | 2019-04-28 12:36:00 | 1752 | 11.2512 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JBGC1 | 5.9 | 2017-09-30T06:13:00Z | 8.01 | 3 | < 25mph |  |  |  | 0 | 0 | No data | JBGC1 | 5.9 | 2017-09-30T07:13:00Z | 10 | 6 | < 25mph
PG&E | 2019-06-10 | 13:29 | 38.8137 | -120.9433 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Other | Customer | 153652109 |  | 21000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-243 | 2019 | 6 | 10 | 13 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.2437 | 202_284 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 13:29:00 | 1823 | 9.9566 | FALSE | <25mph | PLTC1 | 3.76 | 2018-11-27T10:56:00Z | 2.01 | 7 | < 25mph | PG073 | 7.24 | 2018-11-27T10:20:00Z | 6.58 | 55 | < 25mph | PLTC1 | 3.76 | 2018-11-27T11:56:00Z | 4 | 14 | < 25mph | PG073 | 7.24 | 2018-11-27T12:10:00Z | 7.25 | 110 | < 25mph
PG&E | 2017-10-04 | 23:42 | 38.6554 | -120.9934 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101375442 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 43012 | 23:42 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1452 | 2017 | 10 | 4 | 23 | 42 | 17-0084323 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7553 | 12.9958 | 200_275 | <25mph | <15mph | HFTD - Distribution | 2017-10-04 23:42:00 | 1190 | 14.755 | FALSE | <25mph | PG181 | 3.15 | 2019-03-06T02:10:00Z | 19.06 | 47 | < 25mph | FSLC1 | 7.78 | 2019-03-06T02:10:00Z | 22.53 | 118 | < 25mph | PG181 | 3.15 | 2019-03-06T03:20:00Z | 23.44 | 91 | < 25mph | PG181 | 3.15 | 2019-03-06T03:20:00Z | 23.44 | 227 | < 25mph
PG&E | 2015-06-22 11:58 | 2015-06-22 11:58 | 39.1737 | -121.0667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | SENTINAL WY |  | 12000 | Conductor | Overhead | Yes | 42177.4986 | 2015-06-22 11:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0400 | 2015 | 6 | 22 | 11 | 58 | 15-0042502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 148438 | 10.8591 | 197_304 | <25mph | <15mph | HFTD - Distribution | 2015-06-22 11:58:00 | 146 | 12.4713 | FALSE | <25mph | AS856 | 3.16 | 2017-09-03T18:28:00Z | 7 | 32 | < 25mph | C5488 | 7.22 | 2017-09-03T19:07:00Z | 10 | 80 | < 25mph | AS856 | 3.16 | 2017-09-03T19:58:00Z | 7 | 64 | < 25mph | C5488 | 7.22 | 2017-09-03T20:19:00Z | 10 | 159 | < 25mph
PG&E | 2018-09-03 | 18:29 | 39.4547 | -121.4955 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100395672 | Unknown | 12000 | Conductor | Overhead | Yes | 43346 | 18:29 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1880 | 2018 | 9 | 3 | 18 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 6.2719 | 178_319 | <25mph | <15mph | HFTD - Distribution | 2018-09-03 18:29:00 | 1619 | 14.7897 | FALSE | <25mph | PG312 | 2.49 | 2019-07-01T15:10:00Z | 5.26 | 6 | < 25mph | PG288 | 4.8 | 2019-07-01T14:30:00Z | 7.45 | 25 | < 25mph | PG312 | 2.49 | 2019-07-01T16:10:00Z | 5.91 | 12 | < 25mph | PG290 | 6.48 | 2019-07-01T16:10:00Z | 7.45 | 50 | < 25mph
PG&E | 2016-09-21 | 10:01 | 39.1173 | -121.071 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100014315 | PACIFIC BELL | 115000 | Conductor | Overhead | Yes | 42634 | 10:01 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0991 | 2016 | 9 | 21 | 10 | 1 | INT-08560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 18.3543 | 196_301 | <25mph | <15mph | HFTD - Transmission | 2016-09-21 10:01:00 | 734 | 24.3978 | FALSE | <25mph | E1789 | 3.84 | 2018-03-08T21:30:00Z | 8.01 | 32 | < 25mph | E1789 | 3.84 | 2018-03-08T21:30:00Z | 8.01 | 74 | < 25mph | E1789 | 3.84 | 2018-03-08T22:36:00Z | 8.01 | 64 | < 25mph | AS856 | 7.05 | 2018-03-08T23:21:00Z | 8.99 | 148 | < 25mph
PG&E | 2015-08-28 12:02 | 2015-08-28 12:02 | 37.9047 | -122.2058 | Vegetation | Rural | < 0.25 Acres | Fire Agency | EB MUD | 103623279 |  | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0563 | 2015 | 8 | 28 | 12 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 10.0355 | 147_234 | <25mph | <15mph | HFTD - Distribution | 2015-08-28 12:02:00 | 307 | 16.9223 | FALSE | <25mph | LBNL1 | 3.01 | 2015-03-20T05:45:00Z | 6.04 | 36 | < 25mph | D7213 | 7.88 | 2015-03-20T05:24:00Z | 16.98 | 156 | < 25mph | E4855 | 3.88 | 2015-03-20T06:53:00Z | 7 | 74 | < 25mph | D7213 | 7.88 | 2015-03-20T05:24:00Z | 16.98 | 309 | < 25mph
PG&E | 2015-06-09 16:20 | 2015-06-09 16:20 | 38.3822 | -122.4316 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102269716 | Pacific Bell | 21000 | Unknown | Overhead | Yes | 42164.6806 | 2015-06-09 16:20 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0369 | 2015 | 6 | 9 | 16 | 20 | 15-0039860 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 4184 | 20.783 | 138_260 | <25mph | <15mph | HFTD - Distribution | 2015-06-09 16:20:00 | 115 | 24.1918 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KENWW | 6.21 | 2017-09-23T05:00:00Z | 4.61 | 10 | < 25mph |  |  |  | 0 | 0 | No data | KENWW | 6.21 | 2017-09-23T05:00:00Z | 4.61 | 22 | < 25mph
PG&E | 2017-07-23 18:25 | 18:25 | 39.6723 | -123.5336 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103823226 | Unknown | 12000 | Conductor | Overhead | Yes | 42939.7676 | 18:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1284 | 2017 | 7 | 23 | 18 | 25 | 17-0064854 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 12864 | 11.8402 | 92_333 | <25mph | <15mph | HFTD - Distribution | 2017-07-23 18:25:00 | 1023 | 16.2282 | FALSE | <25mph | LAYC1 | 3.32 | 2018-12-11T21:29:00Z | 3 | 1 | < 25mph | LAYC1 | 3.32 | 2018-12-11T21:29:00Z | 3 | 7 | < 25mph | LAYC1 | 3.32 | 2018-12-11T22:29:00Z | 8.01 | 2 | < 25mph | LAYC1 | 3.32 | 2018-12-11T22:29:00Z | 8.01 | 14 | < 25mph
PG&E | 2017-05-24 16:25 | 16:24 | 38.834 | -121.1197 | Vegetation | Rural | < 3 Meters | Fire Agency | Fire Capt | 103838109 | None | 12000 | Conductor | Overhead | Yes | 42879.6837 | 16:24 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | no-match | 1111 | 2017 | 5 | 24 | 16 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 20.975 | 194_285 | <25mph | <15mph | HFTD - Distribution | 2017-05-24 16:24:00 | 851 | 20.975 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 5.95 | 2017-01-02T11:56:00Z | 17 | 21 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 5.95 | 2017-01-02T11:56:00Z | 17 | 41 | < 25mph
PG&E | 2015-07-03 03:23 | 2015-07-03 03:23 | 35.6785 | -120.9567 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 1 soan 1 conducter 1 span loade side transformer formtr 1008493290 |  | 21000 | Conductor | Overhead | Yes | 42188.141 | 2015-07-03 03:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0438 | 2015 | 7 | 3 | 3 | 23 | 15-0045239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 978 | 7.7054 | 202_111 | <25mph | <15mph | HFTD - Distribution | 2015-07-03 03:23:00 | 183 | 16.8894 | FALSE | <25mph | TABC1 | 2.38 | 2016-10-29T02:07:00Z | 3 | 1 | < 25mph | E9175 | 5.22 | 2016-10-29T01:20:00Z | 4 | 18 | < 25mph | TABC1 | 2.38 | 2016-10-29T03:07:00Z | 4 | 2 | < 25mph | E9175 | 5.22 | 2016-10-29T01:20:00Z | 4 | 35 | < 25mph
PG&E | 2016-07-27 17:05 | 2016-07-27 17:05 | 38.5392 | -122.7656 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102029945 |  | 60000 | Conductor | Overhead | Yes | 42578.7118 | 2016-07-27 17:05 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0882 | 2016 | 7 | 27 | 17 | 5 | FU-2016-047 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 18.1446 | 123_269 | <25mph | <15mph | HFTD - Transmission | 2016-07-27 17:05:00 | 625 | 18.1446 | FALSE | <25mph | E6724 | 1.55 | 2015-02-15T14:20:00Z | 2.01 | 6 | < 25mph | RSAC1 | 5.1 | 2015-02-15T13:29:00Z | 4 | 51 | < 25mph | E6724 | 1.55 | 2015-02-15T15:00:00Z | 3 | 12 | < 25mph | RSAC1 | 5.1 | 2015-02-15T14:29:00Z | 7 | 108 | < 25mph
PG&E | 2017-08-05 08:33 | 08:33 | 38.4583 | -120.8695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JEFF MICHEL- 530 409 2223 | 101236223 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42952.3565 | 08:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1317 | 2017 | 8 | 5 | 8 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 6.5905 | 205_264 | <25mph | <15mph | HFTD - Distribution | 2017-08-05 08:33:00 | 1055 | 14.6063 | FALSE | <25mph | PG407 | 2.51 | 2019-06-25T16:30:00Z | 10.96 | 12 | < 25mph | PG407 | 2.51 | 2019-06-25T16:30:00Z | 10.96 | 32 | < 25mph | PG407 | 2.51 | 2019-06-25T17:20:00Z | 11.41 | 24 | < 25mph | PG116 | 7.59 | 2019-06-25T16:50:00Z | 12.06 | 69 | < 25mph
PG&E | 2017-08-05 18:13 | 18:08 | 39.0968 | -123.2147 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102196629 | Unknown | 12000 | Conductor | Overhead | Yes | 42952.7592 | 18:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1318 | 2017 | 8 | 5 | 18 | 8 | 17-0068200 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 134239 | 10.1139 | 105_301 | <25mph | <15mph | HFTD - Distribution | 2017-08-05 18:08:00 | 1056 | 16.2126 | FALSE | <25mph | E6035 | 3.84 | 2015-04-04T14:16:00Z | 2.01 | 12 | < 25mph | COWC1 | 7.84 | 2015-04-04T14:01:00Z | 22.01 | 13 | < 25mph | E6035 | 3.84 | 2015-04-04T15:31:00Z | 2.01 | 24 | < 25mph | COWC1 | 7.84 | 2015-04-04T15:01:00Z | 22.01 | 26 | < 25mph
PG&E | 2018-07-30 | 14:36 | 38.1987 | -120.3638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NICK WEBB ( 209) 532-7424 | 103336176 | Unknown | 17000 | Conductor | Overhead | Yes | 43311 | 14:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1800 | 2018 | 7 | 30 | 14 | 36 | 18-0065131 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18530 | 10.5817 | 227_250 | <25mph | <15mph | HFTD - Distribution | 2018-07-30 14:36:00 | 1540 | 14.4256 | FALSE | <25mph | E8204 | 0 | 2018-05-23T02:39:00Z | 2.01 | 4 | < 25mph | E9838 | 7.59 | 2018-05-23T03:06:00Z | 5.99 | 20 | < 25mph | E8204 | 0 | 2018-05-23T02:39:00Z | 2.01 | 8 | < 25mph | E9838 | 7.59 | 2018-05-23T03:06:00Z | 5.99 | 39 | < 25mph
PG&E | 2015-12-31 19:12 | 2015-12-31 19:12 | 37.1568 | -121.9868 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LOS GATOS MONTE SERENO SARATOGA | 100518215 | Verizon | 21000 | Conductor | Overhead | Yes | 42369.8 | 2015-12-31 19:12 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0689 | 2015 | 12 | 31 | 19 | 12 | 15-0087962 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7979 | 7.4149 | 156_193 | <25mph | <15mph | HFTD - Distribution | 2015-12-31 19:12:00 | 433 | 10.9251 | FALSE | <25mph | PG591 | 2.47 | 2019-11-20T01:10:00Z | 17.45 | 31 | < 25mph | D3546 | 6.48 | 2019-11-20T01:00:00Z | 22.01 | 218 | < 25mph | PG591 | 2.47 | 2019-11-20T01:10:00Z | 17.45 | 60 | < 25mph | PG050 | 4.4 | 2019-11-20T02:50:00Z | 22.21 | 439 | < 25mph
PG&E | 2016-07-28 14:24 | 2016-07-28 14:24 | 37.8232 | -120.1356 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101037045 |  | 17000 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Guy/Span Wire | N.A. | N.A. | Unknown |  | no-match | 0888 | 2016 | 7 | 28 | 14 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Guy/Span Wire | N.A. | 10.9021 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 14:24:00 | 631 | 11.4062 | FALSE | <25mph | SEWC1 | 2.46 | 2019-07-28T00:16:00Z | 17 | 28 | < 25mph | PG155 | 4.92 | 2019-07-28T00:00:00Z | 19.95 | 52 | < 25mph | PG398 | 4 | 2019-07-28T00:50:00Z | 17.76 | 55 | < 25mph | PG155 | 4.92 | 2019-07-28T00:00:00Z | 19.95 | 103 | < 25mph
PG&E | 2017-07-03 20:28 | 20:26 | 38.7923 | -120.9438 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101388730 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42919.853 | 20:26 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1218 | 2017 | 7 | 3 | 20 | 26 | 17-0060336 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 8134 | 10.0527 | 202_283 | <25mph | <15mph | HFTD - Distribution | 2017-07-03 20:26:00 | 957 | 12.5378 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 4.45 | 2016-04-30T13:56:00Z | 15.99 | 30 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 4.45 | 2016-04-30T14:56:00Z | 18.99 | 59 | < 25mph
PG&E | 2015-07-24 14:30 | 2015-07-24 14:30 | 36.6913 | -119.0312 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46970 DUNLAP RD | YES | 0 – 750 | Transformer | Overhead | Yes | 42209.6042 | 2015-07-24 14:30 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0482 | 2015 | 7 | 24 | 14 | 30 | 15-0050401 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 281 | 12.3885 | 287_168 | <25mph | <15mph | HFTD - Distribution | 2015-07-24 14:30:00 | 227 | 13.0893 | FALSE | <25mph | PHRC1 | 0.81 | 2018-08-10T04:58:00Z | 11.01 | 1 | < 25mph | PHRC1 | 0.81 | 2018-08-10T04:58:00Z | 11.01 | 13 | < 25mph | PHRC1 | 0.81 | 2018-08-10T05:58:00Z | 12.01 | 2 | < 25mph | PHRC1 | 0.81 | 2018-08-10T05:58:00Z | 12.01 | 27 | < 25mph
PG&E | 2019-07-01 | 2:15 | 38.2955 | -120.8335 |  | Shrub | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-252 | 2019 | 7 | 1 | 2 | 15 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.9479 | 207_255 | <25mph | <15mph | HFTD - Distribution | 2019-07-01 02:15:00 | 1878 | 14.184 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.85 | 2015-10-19T11:05:00Z | 4 | 2 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.85 | 2015-10-19T12:05:00Z | 7 | 4 | < 25mph
PG&E | 2018-09-16 | 8:26 | 35.3046 | -120.6389 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | Pole 4/23A | None | 70000 | Conductor | Overhead | Yes | 43359 | 8:26 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1903 | 2018 | 9 | 16 | 8 | 26 | INT-11371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 29925 | 32.6873 | 216_90 | 25-40mph | 30-45mph | HFTD - Transmission | 2018-09-16 08:26:00 | 1642 | 35.3808 | FALSE | 25-40mph | ARGC1 | 2.25 | 2016-10-16T12:54:00Z | 8.99 | 1 | < 25mph | ARGC1 | 2.25 | 2016-10-16T12:54:00Z | 8.99 | 5 | < 25mph | ARGC1 | 2.25 | 2016-10-16T12:54:00Z | 8.99 | 2 | < 25mph | ARGC1 | 2.25 | 2016-10-16T12:54:00Z | 8.99 | 10 | < 25mph
PG&E | 2016-06-12 | 2016-06-12 13:14 | 37.5096 | -120.0462 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101083986 |  | 0 – 750 | Conductor | Overhead | Yes | 42533 | 2016-06-12 13:14 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0795 | 2016 | 6 | 12 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.8806 | 241_212 | <25mph | <15mph | HFTD - Distribution | 2016-06-12 13:14:00 | 539 | 13.4596 | FALSE | <25mph | MPOC1 | 3.28 | 2017-12-07T07:07:00Z | 12.01 | 1 | < 25mph | MPOC1 | 3.28 | 2017-12-07T07:07:00Z | 12.01 | 1 | < 25mph | MPOC1 | 3.28 | 2017-12-07T07:07:00Z | 12.01 | 2 | < 25mph | MPOC1 | 3.28 | 2017-12-07T07:07:00Z | 12.01 | 2 | < 25mph
PG&E | 2016-11-15 | 17:27 | 39.7275 | -121.6557 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100327525 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42689 | 17:27 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 1049 | 2016 | 11 | 15 | 17 | 27 | 16-0080083 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 69231 | 9.6883 | 172_334 | <25mph | <15mph | HFTD - Distribution | 2016-11-15 17:27:00 | 790 | 16.6369 | FALSE | <25mph | PDEC1 | 2.44 | 2018-05-30T05:00:00Z | 2.01 | 2 | < 25mph | PDEC1 | 2.44 | 2018-05-30T05:00:00Z | 2.01 | 2 | < 25mph | PDEC1 | 2.44 | 2018-05-30T05:00:00Z | 2.01 | 3 | < 25mph | PDEC1 | 2.44 | 2018-05-30T05:00:00Z | 2.01 | 3 | < 25mph
PG&E | 2019-05-15 | 21:31 | 38.5731 | -122.9603 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Unknown |  | 103931177 |  | 12000 | Conductor | Overhead | Yes | 43600 | 21:31 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-316 | 2019 | 5 | 15 | 21 | 31 | 19-0052480 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 27780 | 16.5892 | 115_271 | <25mph | <15mph | HFTD - Distribution | 2019-05-15 21:31:00 | 1774 | 23.8094 | FALSE | <25mph | D9841 | 3.34 | 2018-06-21T18:39:00Z | 0 | 4 | < 25mph | DRYWW | 5.75 | 2018-06-21T18:00:00Z | 10.8 | 51 | < 25mph | D9841 | 3.34 | 2018-06-21T19:40:00Z | 1.01 | 8 | < 25mph | R30WW | 6.68 | 2018-06-21T19:00:00Z | 11.7 | 102 | < 25mph
PG&E | 2016-08-01 | 2016-08-01 18:29 | 38.6956 | -120.9283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412720 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0898 | 2016 | 8 | 1 | 18 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2359 | 203_277 | <25mph | <15mph | HFTD - Distribution | 2016-08-01 18:29:00 | 641 | 12.0255 | FALSE | <25mph | D4464 | 2.83 | 2015-01-01T15:15:00Z | 3 | 16 | < 25mph | BENC1 | 7.25 | 2015-01-01T14:59:00Z | 5.99 | 60 | < 25mph | D4464 | 2.83 | 2015-01-01T16:00:00Z | 4 | 31 | < 25mph | BENC1 | 7.25 | 2015-01-01T15:59:00Z | 7 | 118 | < 25mph
PG&E | 2015-06-12 13:07 | 2015-06-12 13:07 | 40.4077 | -122.4104 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS STREET FROM 4139 OLD HAPPY VALLEY RD |  | 12000 | Lightning Arrestor | Overhead | No |  |  | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | no-match | 0378 | 2015 | 6 | 12 | 13 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Lightning Arrestor | N.A. | 9.7698 | 140_372 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 13:07:00 | 124 | 24.3549 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 7.46 | 2017-03-08T05:24:00Z | 10 | 8 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 7.46 | 2017-03-08T05:39:00Z | 13 | 16 | < 25mph
PG&E | 2017-08-14 | 6:14 | 40.1164 | -123.8064 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100986364 | Unknown | 12000 | Conductor | Overhead | Yes | 42961 | 6:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1332 | 2017 | 8 | 14 | 6 | 14 | 17-0070003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 959989 | 9.3352 | 81_357 | <25mph | <15mph | HFTD - Distribution | 2017-08-14 06:14:00 | 1070 | 20.8696 | FALSE | <25mph | ERCC1 | 1.77 | 2019-09-27T12:28:00Z | 4.99 | 4 | < 25mph | PG282 | 6.02 | 2019-09-27T12:40:00Z | 20.6 | 28 | < 25mph | ERCC1 | 1.77 | 2019-09-27T13:28:00Z | 7 | 9 | < 25mph | PG282 | 6.02 | 2019-09-27T12:40:00Z | 20.6 | 57 | < 25mph
PG&E | 2016-09-12 | 4:24 | 36.3999 | -121.902 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire Hwy 1 Carmel Hill | 101669614 |  | 12000 | Conductor | Overhead | Yes | 42625 | 4:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0973 | 2016 | 9 | 12 | 4 | 24 | 16-0063826 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 130604 | 5.4712 | 159_151 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 04:24:00 | 715 | 8.1881 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TR419 | 7.81 | 2017-05-09T10:15:00Z | 4.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | TR419 | 7.81 | 2017-05-09T10:15:00Z | 4.99 | 2 | < 25mph
PG&E | 2018-05-19 | 19:44 | 40.2665 | -122.2727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103899310 | Unknown | 12000 | Conductor | Overhead | Yes | 43239 | 19:44 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1599 | 2018 | 5 | 19 | 19 | 44 | 18-0042559 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 31980 | 15.59 | 146_364 | <25mph | <15mph | HFTD - Distribution | 2018-05-19 19:44:00 | 1341 | 18.253 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 7.1 | 2015-08-22T07:45:00Z | 14 | 3 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 7.1 | 2015-08-22T08:01:00Z | 14 | 7 | < 25mph
PG&E | 2016-08-13 | 14:31 | 37.4642 | -119.8589 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire |  |  | 21000 | Conductor | Overhead | Yes | 42595 | 14:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0923 | 2016 | 8 | 13 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.5527 | 249_210 | <25mph | <15mph | HFTD - Distribution | 2016-08-13 14:31:00 | 667 | 11.4441 | FALSE | <25mph | C1522 | 2.94 | 2016-03-20T19:20:00Z | 8.01 | 3 | < 25mph | MIAC1 | 6.96 | 2016-03-20T18:59:00Z | 17 | 7 | < 25mph | C1522 | 2.94 | 2016-03-20T19:50:00Z | 8.99 | 6 | < 25mph | MIAC1 | 6.96 | 2016-03-20T19:59:00Z | 17 | 14 | < 25mph
PG&E | 2015-06-08 14:18 | 2015-06-08 14:18 | 38.1796 | -120.959 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 102048579 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42163.5958 | 2015-06-08 14:18 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0360 | 2015 | 6 | 8 | 14 | 18 | 15-0039368 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 65168 | 7.0021 | 201_249 | <25mph | <15mph | HFTD - Distribution | 2015-06-08 14:18:00 | 106 | 9.7763 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CMAC1 | 5.88 | 2018-06-08T07:59:00Z | 4 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CMAC1 | 5.88 | 2018-06-08T07:59:00Z | 4 | 2 | < 25mph
PG&E | 2015-08-03 00:07 | 2015-08-03 00:07 | 40.5056 | -122.347 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | COTTONWOOD FIRE DEPT | 101503428 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42219.0049 | 2015-08-03 00:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0509 | 2015 | 8 | 3 | 0 | 7 | 15-0052184 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 10427 | 9.7241 | 143_378 | <25mph | <15mph | HFTD - Distribution | 2015-08-03 00:07:00 | 254 | 13.2206 | FALSE | <25mph | KRDD | 2.66 | 2016-01-23T01:53:00Z | 32.21 | 8 | 25-40mph | KRDD | 2.66 | 2016-01-23T01:53:00Z | 32.21 | 22 | 25-40mph | KRDD | 2.66 | 2016-01-23T02:53:00Z | 36.82 | 16 | 25-40mph | KRDD | 2.66 | 2016-01-23T02:53:00Z | 36.82 | 44 | 25-40mph
PG&E | 2017-10-08 | 19:44 | 39.7446 | -121.597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100330456 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 19:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1464 | 2017 | 10 | 8 | 19 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 33.2724 | 174_335 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-08 19:44:00 | 1202 | 34.7906 | FALSE | 25-40mph | E2076 | 1.3 | 2015-03-11T08:03:00Z | 2.01 | 8 | < 25mph | JBGC1 | 5.77 | 2015-03-11T07:13:00Z | 4.99 | 22 | < 25mph | E2076 | 1.3 | 2015-03-11T09:03:00Z | 2.01 | 16 | < 25mph | JBGC1 | 5.77 | 2015-03-11T08:13:00Z | 8.01 | 42 | < 25mph
PG&E | 2017-09-24 | 16:42 | 38.3869 | -122.9667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DOUG JONES | 101973946 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43002 | 16:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1432 | 2017 | 9 | 24 | 16 | 42 | 17-0081329 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 22574 | 19.6154 | 114_261 | <25mph | <15mph | HFTD - Distribution | 2017-09-24 16:42:00 | 1170 | 19.6154 | FALSE | <25mph | PG380 | 1.69 | 2019-10-11T16:20:00Z | 8.25 | 18 | < 25mph | BGAC1 | 6.8 | 2019-10-11T16:05:00Z | 10 | 84 | < 25mph | PG380 | 1.69 | 2019-10-11T16:40:00Z | 9.35 | 36 | < 25mph | BGAC1 | 6.8 | 2019-10-11T17:05:00Z | 10 | 164 | < 25mph
PG&E | 2017-09-08 | 4:47 | 38.7478 | -120.859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101391575 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42986 | 4:47 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1401 | 2017 | 9 | 8 | 4 | 47 | 17-0076889 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 39736 | 2.1381 | 205_280 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 04:47:00 | 1139 | 10.5203 | FALSE | <25mph | C6129 | 3.66 | 2019-06-07T14:09:00Z | 8.99 | 37 | < 25mph | PG181 | 6.85 | 2019-06-07T14:30:00Z | 10.96 | 131 | < 25mph | C6129 | 3.66 | 2019-06-07T15:44:00Z | 8.99 | 73 | < 25mph | PG181 | 6.85 | 2019-06-07T14:30:00Z | 10.96 | 263 | < 25mph
PG&E | 2017-06-27 09:28 | 9:23 | 37.9559 | -122.6176 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | marin county fire | 102260068 | UNFILED | 12000 | Conductor | Overhead | Yes | 42913.3944 | 9:23 | Other | N.A. | N.A. | N.A. | Unknown |  | Fell into (slight defect) | 1203 | 2017 | 6 | 27 | 9 | 23 | 17-0058882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 3920 | 16.1278 | 129_237 | <25mph | <15mph | HFTD - Distribution | 2017-06-27 09:23:00 | 942 | 18.7182 | FALSE | <25mph | MDEC1 | 2.55 | 2016-01-01T18:36:00Z | 14.99 | 9 | < 25mph | NBRC1 | 6.33 | 2016-01-01T18:33:00Z | 17 | 19 | < 25mph | MDEC1 | 2.55 | 2016-01-01T19:36:00Z | 18.01 | 10 | < 25mph | MDEC1 | 2.55 | 2016-01-01T19:36:00Z | 18.01 | 30 | < 25mph
PG&E | 2016-07-15 05:19 | 2016-07-15 05:19 | 35.1839 | -120.5018 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101846594 |  | 12000 | Conductor | Overhead | Yes | 42566.2215 | 2016-07-15 05:19 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0851 | 2016 | 7 | 15 | 5 | 19 | 16-0050086 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 62404 | 2.6454 | 222_84 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 05:19:00 | 594 | 14.1102 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F0194 | 6.17 | 2017-12-20T08:13:00Z | 4 | 20 | < 25mph |  |  |  | 0 | 0 | No data | F0194 | 6.17 | 2017-12-20T08:13:00Z | 4 | 43 | < 25mph
PG&E | 2015-09-09 10:47 | 2015-09-09 10:47 | 37.1041 | -121.8853 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100520291 |  | 12000 | Conductor | Overhead | Yes | 42256.4493 | 2015-09-09 10:47 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0587 | 2015 | 9 | 9 | 10 | 47 | 15-0060074 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 142401 | 4.2376 | 161_190 | <25mph | <15mph | HFTD - Distribution | 2015-09-09 10:47:00 | 331 | 18.9097 | FALSE | <25mph | PG610 | 2.24 | 2019-12-07T19:40:00Z | 48.81 | 28 | 40-55mph | D2539 | 6.54 | 2019-12-07T19:45:00Z | 132 | 117 | 55mph+ | PG610 | 2.24 | 2019-12-07T20:10:00Z | 49.55 | 56 | 40-55mph | D2539 | 6.54 | 2019-12-07T20:00:00Z | 132 | 231 | 55mph+
PG&E | 2015-05-02 16:51 | 2015-05-02 16:51 | 37.3284 | -119.643 | Vegetation | Rural | < 0.25 Acres | Fire Agency | MADERA COUNTY | 103768995 |  | 12000 | Conductor | Overhead | Yes | 42126.7021 | 2015-05-02 16:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0305 | 2015 | 5 | 2 | 16 | 51 | 15-0031285 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 79805 | 9.7158 | 259_202 | <25mph | <15mph | HFTD - Distribution | 2015-05-02 16:51:00 | 51 | 12.4769 | FALSE | <25mph | AT301 | 1.62 | 2018-05-12T00:40:00Z | 15.99 | 33 | < 25mph | AT301 | 1.62 | 2018-05-12T00:40:00Z | 15.99 | 63 | < 25mph | AT301 | 1.62 | 2018-05-12T00:40:00Z | 15.99 | 62 | < 25mph | AT301 | 1.62 | 2018-05-12T00:40:00Z | 15.99 | 119 | < 25mph
PG&E | 2016-06-26 11:06 | 2016-06-26 11:06 | 40.4832 | -122.0466 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101483777 | FRONTIER | 12000 | Conductor | Overhead | Yes | 42547.4625 | 2016-06-26 11:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0826 | 2016 | 6 | 26 | 11 | 6 | 16-0045846 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 15520 | 6.1274 | 155_376 | <25mph | <15mph | HFTD - Distribution | 2016-06-26 11:06:00 | 566 | 14.8861 | FALSE | <25mph | PG107 | 2.85 | 2019-01-07T09:20:00Z | 2.86 | 6 | < 25mph | PG107 | 2.85 | 2019-01-07T09:20:00Z | 2.86 | 6 | < 25mph | PG107 | 2.85 | 2019-01-07T09:20:00Z | 2.86 | 12 | < 25mph | PG107 | 2.85 | 2019-01-07T09:20:00Z | 2.86 | 12 | < 25mph
PG&E | 2018-07-02 | 5:12 | 38.6092 | -122.4595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 707-967-1467 | 102252558 | AT&T | 21000 | Conductor | Overhead | Yes | 43283 | 5:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1722 | 2018 | 7 | 2 | 5 | 12 | 18-0056178 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 403 | 6.1424 | 137_273 | <25mph | <15mph | HFTD - Distribution | 2018-07-02 05:12:00 | 1463 | 24.2981 | FALSE | <25mph | PG018 | 2.17 | 2018-09-24T03:50:00Z | 2.86 | 6 | < 25mph | PG051 | 7.68 | 2018-09-24T03:20:00Z | 4.16 | 23 | < 25mph | PG018 | 2.17 | 2018-09-24T05:00:00Z | 3.06 | 12 | < 25mph | PG051 | 7.68 | 2018-09-24T03:20:00Z | 4.16 | 46 | < 25mph
PG&E | 2016-10-14 19:45 | 19:44 | 39.6245 | -121.5382 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100435570 |  | 0 – 750 | Conductor | Overhead | Yes | 42657.8228 | 19:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1036 | 2016 | 10 | 14 | 19 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.5623 | 177_329 | <25mph | <15mph | HFTD - Distribution | 2016-10-14 19:44:00 | 777 | 22.2526 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CICC1 | 5.69 | 2016-08-11T04:54:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CICC1 | 5.69 | 2016-08-11T05:54:00Z | 8.99 | 2 | < 25mph
PG&E | 2018-08-13 | 15:33 | 38.708 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101377799 | Unknown | 21000 | Conductor | Overhead | Yes | 43325 | 15:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1840 | 2018 | 8 | 13 | 15 | 33 | 18-0069470 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1004 | 11.7134 | 201_278 | <25mph | <15mph | HFTD - Distribution | 2018-08-13 15:33:00 | 1579 | 13.7748 | FALSE | <25mph | PG181 | 0.85 | 2019-01-13T19:20:00Z | 10.29 | 74 | < 25mph | PG181 | 0.85 | 2019-01-13T19:20:00Z | 10.29 | 143 | < 25mph | PG181 | 0.85 | 2019-01-13T19:20:00Z | 10.29 | 141 | < 25mph | PG181 | 0.85 | 2019-01-13T19:20:00Z | 10.29 | 276 | < 25mph
PG&E | 2016-06-19 | 2016-06-19 12:07 | 39.3811 | -123.7737 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102187888 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 12:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0807 | 2016 | 6 | 19 | 12 | 7 | 16-0044317 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6100 | 11.4602 | 81_317 | <25mph | <15mph | HFTD - Distribution | 2016-06-19 12:07:00 | 550 | 15.3844 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F1771 | 5.2 | 2018-03-17T18:46:00Z | 4.99 | 10 | < 25mph |  |  |  | 0 | 0 | No data | E6025 | 6.3 | 2018-03-17T19:30:00Z | 5.99 | 20 | < 25mph
PG&E | 2016-05-15 15:54 | 2016-05-15 15:54 | 36.7948 | -119.3966 | Vegetation | RURAL | 100 - 299 Acres | Fire Agency | Cal Fire | 100729685 | None | 12000 | Conductor | Overhead | Yes | 42505.6625 | 2016-05-15 15:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0730 | 2016 | 5 | 15 | 15 | 54 | 16-0036136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 180310 | 10.5903 | 270_173 | <25mph | <15mph | HFTD - Distribution | 2016-05-15 15:54:00 | 474 | 14.7659 | FALSE | <25mph |  |  |  | 0 | 0 | No data | FCHC1 | 7.54 | 2016-08-01T15:00:00Z | 5.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | FCHC1 | 7.54 | 2016-08-01T16:00:00Z | 7 | 2 | < 25mph
PG&E | 2017-06-24 15:06 | 14:51 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 42910.6292 | 14:51 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1194 | 2017 | 6 | 24 | 14 | 51 | 17-0058332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 21296 | 10.4286 | 210_259 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 14:51:00 | 933 | 10.7263 | FALSE | <25mph | PG116 | 2.81 | 2019-01-31T05:10:00Z | 6.13 | 7 | < 25mph | MTZC1 | 6.33 | 2019-01-31T05:56:00Z | 8.99 | 8 | < 25mph | PG116 | 2.81 | 2019-01-31T07:00:00Z | 8.55 | 14 | < 25mph | MTZC1 | 6.33 | 2019-01-31T06:56:00Z | 10 | 16 | < 25mph
PG&E | 2015-08-16 07:35 | 2015-08-16 07:35 | 35.4572 | -120.6567 | Vegetation | Rural | < 3 meters | Utility: PG&E |  | 8932 SAN GABRIEL RD. SW C/O OF LOT, Atascadero | None | 0 – 750 | Conductor | Overhead | Yes | 42232.316 | 2015-08-16 07:35 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0534 | 2015 | 8 | 16 | 7 | 35 | 15-0055284 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.0129 | 215_99 | <25mph | <15mph | HFTD - Distribution | 2015-08-16 07:35:00 | 278 | 16.9932 | FALSE | <25mph | PG210 | 3.26 | 2019-06-16T15:40:00Z | 4.61 | 29 | < 25mph | PG119 | 6.68 | 2019-06-16T15:00:00Z | 7.45 | 85 | < 25mph | E2260 | 2.13 | 2019-06-16T16:14:00Z | 8.01 | 58 | < 25mph | PG142 | 5.29 | 2019-06-16T16:20:00Z | 8.12 | 167 | < 25mph
PG&E | 2018-06-30 | 11:14 | 39.3621 | -121.0809 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ENGINEER YUREK | 100091354 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 11:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1713 | 2018 | 6 | 30 | 11 | 14 | 18-0055945 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5724 | 3.7745 | 196_314 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 11:14:00 | 1454 | 12.1468 | FALSE | <25mph | E3651 | 2.44 | 2019-02-15T08:00:00Z | 15.99 | 12 | < 25mph | RRRC1 | 4.49 | 2019-02-15T07:13:00Z | 32.01 | 25 | 25-40mph | E3651 | 2.44 | 2019-02-15T08:05:00Z | 15.99 | 24 | < 25mph | RRRC1 | 4.49 | 2019-02-15T08:13:00Z | 35.99 | 50 | 25-40mph
PG&E | 2016-07-15 05:19 | 2016-07-15 05:19 | 35.1839 | -120.5018 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101846594 |  | 12000 | Conductor | Overhead | Yes | 42566.2215 | 2016-07-15 05:19 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0851 | 2016 | 7 | 15 | 5 | 19 | 16-0050086 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 62404 | 2.6454 | 222_84 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 05:19:00 | 594 | 14.1102 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D6295 | 5.2 | 2017-06-20T22:58:00Z | 11.01 | 21 | < 25mph |  |  |  | 0 | 0 | No data | D6295 | 5.2 | 2017-06-20T22:58:00Z | 11.01 | 39 | < 25mph
PG&E | 2015-06-28 02:50 | 42183.1181 | 35.491 | -120.731 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 13505 Santa Lucia Rd. Atascadero |  | 12000 | Conductor | Overhead | Yes | 42183.1181 | 42183.1181 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0418 | 2015 | 6 | 28 | 2 | 50 | 15-0043807 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 12323 | 9.9634 | 212_101 | <25mph | <15mph | HFTD - Distribution | 2015-06-28 02:50:00 | 163 | 24.8049 | FALSE | <25mph | PG210 | 3.25 | 2019-05-06T02:30:00Z | 29.37 | 34 | 25-40mph | PG210 | 3.25 | 2019-05-06T02:30:00Z | 29.37 | 65 | 25-40mph | PG210 | 3.25 | 2019-05-06T03:10:00Z | 34.85 | 65 | 25-40mph | PG210 | 3.25 | 2019-05-06T03:10:00Z | 34.85 | 127 | 25-40mph
PG&E | 2015-08-22 20:38 | 2015-08-22 20:38 | 38.7748 | -120.8564 | Vegetation | Rural | < 3 meters | Self Extinguished |  | at base of co pole 21721 - 720 Woodridge Rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42238.8597 | 2015-08-22 20:38 | Contact From Object | N.A. | Vegetation | Communication Facility | Unknown | tree hit phone lines | Fell into (Moderate-Severe defect) | 0549 | 2015 | 8 | 22 | 20 | 38 | 15-0056766 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26513 | 9.2929 | 206_282 | <25mph | <15mph | HFTD - Distribution | 2015-08-22 20:38:00 | 293 | 10.7008 | FALSE | <25mph | E5691 | 3.87 | 2016-01-31T09:37:00Z | 1.01 | 12 | < 25mph | E6490 | 6.16 | 2016-01-31T09:21:00Z | 4.99 | 59 | < 25mph | E5691 | 3.87 | 2016-01-31T09:37:00Z | 1.01 | 24 | < 25mph | E6490 | 6.16 | 2016-01-31T09:21:00Z | 4.99 | 117 | < 25mph
PG&E | 2019-06-03 | 14:31 | 40.6822 | -122.2806 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 101466598 |  | 12000 | Transformer | Overhead | Yes | 43619 | 14:31 | Equipment - Overloaded | Transformer |  |  |  |  | no-match | 2019-161 | 2019 | 6 | 3 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 6.522 | 146_387 | <25mph | <15mph | HFTD - Distribution | 2019-06-03 14:31:00 | 1798 | 12.4331 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C5599 | 6.05 | 2019-01-16T01:16:00Z | 4.99 | 8 | < 25mph |  |  |  | 0 | 0 | No data | C5599 | 6.05 | 2019-01-16T02:26:00Z | 4.99 | 16 | < 25mph
PG&E | 2015-08-17 20:57 | 2015-08-17 20:57 | 36.6867 | -119.0612 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46371 ORCHARD DRIVE |  | 12000 | Conductor | Overhead | Yes | 42233.8729 | 2015-08-17 20:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0540 | 2015 | 8 | 17 | 20 | 57 | 15-0055696 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 34398 | 8.6424 | 285_168 | <25mph | <15mph | HFTD - Distribution | 2015-08-17 20:57:00 | 284 | 13.6283 | FALSE | <25mph | PHRC1 | 2.47 | 2018-06-29T07:58:00Z | 11.01 | 1 | < 25mph | PHRC1 | 2.47 | 2018-06-29T07:58:00Z | 11.01 | 13 | < 25mph | PHRC1 | 2.47 | 2018-06-29T08:58:00Z | 11.01 | 2 | < 25mph | PHRC1 | 2.47 | 2018-06-29T08:58:00Z | 11.01 | 24 | < 25mph
PG&E | 2015-08-29 03:30 | 2015-08-29 03:30 | 38.6302 | -122.8327 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Dirt road across from 3204 Rio Lindo Rd, Healdsburg |  | 12000 | Conductor | Overhead | Yes | 42245.1458 | 2015-08-29 03:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0566 | 2015 | 8 | 29 | 3 | 30 | 15-0058127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4780 | 9.2134 | 120_274 | <25mph | <15mph | HFTD - Distribution | 2015-08-29 03:30:00 | 310 | 15.1029 | FALSE | <25mph | E3235 | 3.49 | 2016-01-11T21:28:00Z | 8.01 | 14 | < 25mph | HWKC1 | 7.25 | 2016-01-11T21:56:00Z | 18.01 | 34 | < 25mph | E3235 | 3.49 | 2016-01-11T22:43:00Z | 10 | 27 | < 25mph | HWKC1 | 7.25 | 2016-01-11T21:56:00Z | 18.01 | 66 | < 25mph
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 9:36 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 14.8685 | 222_261 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 09:36:00 | 925 | 23.4839 | FALSE | <25mph | AT450 | 2.61 | 2016-07-03T12:10:00Z | 3 | 12 | < 25mph | ESPC1 | 7.8 | 2016-07-03T12:13:00Z | 7 | 23 | < 25mph | AT450 | 2.61 | 2016-07-03T13:10:00Z | 3 | 24 | < 25mph | ESPC1 | 7.8 | 2016-07-03T12:13:00Z | 7 | 46 | < 25mph
PG&E | 2016-09-28 | 14:00 | 35.2145 | -118.5625 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire |  |  | 0 – 750 | Conductor | Overhead | Yes | 42641 | 14:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1008 | 2016 | 9 | 28 | 14 | 0 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.8467 | 310_87 | <25mph | <15mph | HFTD - Distribution | 2016-09-28 14:00:00 | 750 | 26.957 | FALSE | 25-40mph | HFLC1 | 3.31 | 2016-05-18T07:13:00Z | 11.01 | 7 | < 25mph | HFLC1 | 3.31 | 2016-05-18T07:13:00Z | 11.01 | 24 | < 25mph | HFLC1 | 3.31 | 2016-05-18T07:13:00Z | 11.01 | 19 | < 25mph | HFLC1 | 3.31 | 2016-05-18T07:13:00Z | 11.01 | 53 | < 25mph
PG&E | 2015-08-19 06:20 | 2015-08-19 06:20 | 39.2831 | -123.2931 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | MTR#50001225 | None | 12000 | Conductor | Overhead | Yes | 42235.2639 | 2015-08-19 06:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0545 | 2015 | 8 | 19 | 6 | 20 | 15-0055982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5403 | 1.4303 | 102_311 | <25mph | <15mph | HFTD - Distribution | 2015-08-19 06:20:00 | 289 | 19.8186 | FALSE | <25mph | AU552 | 3.69 | 2018-08-31T11:02:00Z | 13 | 2 | < 25mph | AU552 | 3.69 | 2018-08-31T11:02:00Z | 13 | 28 | < 25mph | AU552 | 3.69 | 2018-08-31T11:02:00Z | 13 | 2 | < 25mph | AU552 | 3.69 | 2018-08-31T11:02:00Z | 13 | 54 | < 25mph
PG&E | 2018-07-20 | 6:31 | 37.4318 | -119.9441 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ZACH RUTHERFORD 209-966-3621 | 103909942 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43301 | 6:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1771 | 2018 | 7 | 20 | 6 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2004 | 246_208 | <25mph | <15mph | HFTD - Distribution | 2018-07-20 06:31:00 | 1511 | 13.5994 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MPOC1 | 5.51 | 2018-03-12T09:07:00Z | 7 | 4 | < 25mph |  |  |  | 0 | 0 | No data | MPOC1 | 5.51 | 2018-03-12T10:07:00Z | 7 | 7 | < 25mph
PG&E | 2018-11-01 | 20:45 | 38.372 | -123.0507 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103852431 | AT&T | 12000 | Conductor | Overhead | Yes | 43405 | 20:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1958 | 2018 | 11 | 1 | 20 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.9426 | 111_260 | <25mph | <15mph | HFTD - Distribution | 2018-11-01 20:45:00 | 1697 | 13.8199 | FALSE | <25mph | BBYC1 | 3.77 | 2018-07-05T18:10:00Z | 7.02 | 1 | < 25mph | UCBM | 4.05 | 2018-07-05T17:50:00Z | 10.6 | 20 | < 25mph | BBYC1 | 3.77 | 2018-07-05T19:10:00Z | 7.4 | 2 | < 25mph | UCBM | 4.05 | 2018-07-05T18:40:00Z | 11.41 | 40 | < 25mph
PG&E | 2017-07-11 22:13 | 22:12 | 37.0122 | -121.9497 | Vegetation | Rural | < 3 Meters | Fire Agency | CAPT PHIL CRAMBLET 831-479-6842 | 101676689 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42927.9254 | 22:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1244 | 2017 | 7 | 11 | 22 | 12 | 17-0062198 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 714 | 7.2694 | 158_185 | <25mph | <15mph | HFTD - Distribution | 2017-07-11 22:12:00 | 983 | 9.7577 | FALSE | <25mph | E5038 | 3.28 | 2018-04-20T08:58:00Z | 4.99 | 42 | < 25mph | UCYL | 7.78 | 2018-04-20T08:50:00Z | 7 | 158 | < 25mph | E5038 | 3.28 | 2018-04-20T08:58:00Z | 4.99 | 82 | < 25mph | UCYL | 7.78 | 2018-04-20T08:50:00Z | 7 | 303 | < 25mph
PG&E | 2019-01-16 | 0:17 | 38.0621 | -120.1964 | Vegetation | Conifer Forest | Structure Only | Cal Fire |  | 163661701 |  | 17000 | Conductor | Overhead | Yes | 43481 | 0:17 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-01 | 2019 | 1 | 16 | 0 | 17 | 19-0010443 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1041827 | 14.8061 | 234_243 | <25mph | <15mph | HFTD - Distribution | 2019-01-16 00:17:00 | 1728 | 28.2081 | FALSE | 25-40mph | MOUC1 | 2.77 | 2016-07-15T12:02:00Z | 10 | 1 | < 25mph | MOUC1 | 2.77 | 2016-07-15T12:02:00Z | 10 | 1 | < 25mph | MOUC1 | 2.77 | 2016-07-15T13:02:00Z | 11.01 | 2 | < 25mph | MOUC1 | 2.77 | 2016-07-15T13:02:00Z | 11.01 | 2 | < 25mph
PG&E | 2018-06-11 | 17:49 | 34.7329 | -120.0861 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103015183 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43262 | 17:49 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1649 | 2018 | 6 | 11 | 17 | 49 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 16.7571 | 241_59 | <25mph | <15mph | HFTD - Distribution | 2018-06-11 17:49:00 | 1391 | 18.839 | FALSE | <25mph | UCSE | 3.69 | 2015-08-22T18:30:00Z | 11.79 | 6 | < 25mph | UCSE | 3.69 | 2015-08-22T18:30:00Z | 11.79 | 7 | < 25mph | UCSE | 3.69 | 2015-08-22T19:40:00Z | 13 | 12 | < 25mph | UCSE | 3.69 | 2015-08-22T19:40:00Z | 13 | 14 | < 25mph
PG&E | 2019-08-05 | 22:38 | 37.1869 | -119.7902 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Unknown |  | 322066125092 |  | 21000 | Transformer | Overhead | Yes | 43682 | 22:38 | Equipment - Overloaded | Transformer |  |  |  |  | Other/Unknown | 2019-134 | 2019 | 8 | 5 | 22 | 38 | 19-0084586 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 996 | 7.0886 | 253_195 | <25mph | <15mph | HFTD - Distribution | 2019-08-05 22:38:00 | 1952 | 12.3468 | FALSE | <25mph | E5766 | 3.69 | 2017-06-11T05:33:00Z | 2.01 | 9 | < 25mph | E5766 | 3.69 | 2017-06-11T05:33:00Z | 2.01 | 9 | < 25mph | E5766 | 3.69 | 2017-06-11T06:33:00Z | 2.01 | 18 | < 25mph | E5766 | 3.69 | 2017-06-11T06:33:00Z | 2.01 | 18 | < 25mph
PG&E | 2017-07-02 | 13:28 | 39.8605 | -121.6274 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 000/017c | Unknown | 60000 | Conductor | Overhead | Yes | 42918 | 13:28 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1216 | 2017 | 7 | 2 | 13 | 28 | INT-09794 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 10.1141 | 173_342 | <25mph | <15mph | HFTD - Transmission | 2017-07-02 13:28:00 | 956 | 11.4462 | FALSE | <25mph | E4833 | 3.87 | 2015-10-24T11:08:00Z | 2.01 | 25 | < 25mph | CSTC1 | 7.55 | 2015-10-24T10:51:00Z | 4.99 | 27 | < 25mph | C8878 | 1.44 | 2015-10-24T12:08:00Z | 3 | 47 | < 25mph | CSTC1 | 7.55 | 2015-10-24T11:51:00Z | 4.99 | 51 | < 25mph
PG&E | 2015-08-31 14:28 | 2015-08-31 14:28 | 36.5325 | -121.1462 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 29401 Hwy 25 |  | 21000 | Conductor | Overhead | Yes | 42247.6028 | 2015-08-31 14:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0568 | 2015 | 8 | 31 | 14 | 28 | 15-0058455 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25668 | 4.8975 | 193_158 | <25mph | <15mph | HFTD - Distribution | 2015-08-31 14:28:00 | 312 | 19.6836 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.27 | 2015-12-30T13:37:00Z | 4 | 1 | < 25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.27 | 2015-12-30T14:37:00Z | 5.99 | 2 | < 25mph
PG&E | 2018-06-10 | 17:19 | 38.4157 | -122.9184 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101978419 | AT&T | 12000 | Conductor | Overhead | Yes | 43261 | 17:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1647 | 2018 | 6 | 10 | 17 | 19 | 18-0049445 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2386 | 19.6716 | 117_263 | <25mph | <15mph | HFTD - Distribution | 2018-06-10 17:19:00 | 1389 | 23.7271 | FALSE | <25mph | E9070 | 3.67 | 2019-02-07T03:01:00Z | 4 | 44 | < 25mph | E9070 | 3.67 | 2019-02-07T03:01:00Z | 4 | 98 | < 25mph | E9070 | 3.67 | 2019-02-07T03:16:00Z | 5.99 | 83 | < 25mph | E9070 | 3.67 | 2019-02-07T03:16:00Z | 5.99 | 192 | < 25mph
PG&E | 2017-07-18 | 11:30 | 38.0484 | -120.5565 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 012/071 | Unknown | 115000 | Conductor | Overhead | Yes | 42934 | 11:30 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1265 | 2017 | 7 | 18 | 11 | 30 | INT-09873 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 55499 | 7.0574 | 219_242 | <25mph | <15mph | HFTD - Transmission | 2017-07-18 11:30:00 | 1005 | 15.7901 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F0305 | 5.89 | 2017-09-01T11:55:00Z | 3 | 62 | < 25mph |  |  |  | 0 | 0 | No data | F0305 | 5.89 | 2017-09-01T11:55:00Z | 3 | 122 | < 25mph
PG&E | 2017-10-16 | 12:10 | 36.5831 | -121.9368 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101781248 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43024 | 12:10 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | Other/Unknown | 1493 | 2017 | 10 | 16 | 12 | 10 | 17-0087767 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 6313 | 5.0415 | 158_161 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:10:00 | 1236 | 13.6905 | FALSE | <25mph | E4129 | 2.99 | 2018-09-16T22:45:00Z | 21 | 34 | < 25mph | E4129 | 2.99 | 2018-09-16T22:45:00Z | 21 | 39 | < 25mph | E4129 | 2.99 | 2018-09-16T22:45:00Z | 21 | 68 | < 25mph | E4129 | 2.99 | 2018-09-16T22:45:00Z | 21 | 78 | < 25mph
PG&E | 2015-09-10 18:39 | 2015-09-10 18:39 | 40.7569 | -123.7958 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 096/004 |  | 115000 | Conductor | Overhead | Yes | 42257.7771 | 2015-09-10 18:39 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0590 | 2015 | 9 | 10 | 18 | 39 | RM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 2.2423 | 82_393 | <25mph | <15mph | HFTD - Transmission | 2015-09-10 18:39:00 | 335 | 12.4043 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.39 | 2015-05-08T18:55:00Z | 11.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.39 | 2015-05-08T19:55:00Z | 12.01 | 2 | < 25mph
PG&E | 2018-07-30 | 14:36 | 38.1987 | -120.3638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NICK WEBB ( 209) 532-7424 | 103336176 | Unknown | 17000 | Conductor | Overhead | Yes | 43311 | 14:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1800 | 2018 | 7 | 30 | 14 | 36 | 18-0065131 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18530 | 10.5817 | 227_250 | <25mph | <15mph | HFTD - Distribution | 2018-07-30 14:36:00 | 1540 | 14.4256 | FALSE | <25mph | E8204 | 0 | 2018-03-16T23:17:00Z | 0 | 4 | < 25mph | E9838 | 7.59 | 2018-03-16T22:38:00Z | 1.01 | 19 | < 25mph | E8204 | 0 | 2018-03-17T00:17:00Z | 0 | 8 | < 25mph | E9838 | 7.59 | 2018-03-17T00:16:00Z | 2.01 | 39 | < 25mph
PG&E | 2018-06-05 | 10:13 | 40.6183 | -122.3173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JASON COLLINS 530-225-4628 | 101467801 | None | 12000 | Conductor | Overhead | Yes | 43256 | 10:13 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1631 | 2018 | 6 | 5 | 10 | 13 | 18-0047539 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 277 | 7.1547 | 144_384 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 10:13:00 | 1373 | 12.6046 | FALSE | <25mph | C5599 | 1.27 | 2016-12-15T03:47:00Z | 21 | 5 | < 25mph | KRDD | 7.24 | 2016-12-15T02:55:00Z | 33.38 | 8 | 25-40mph | C5599 | 1.27 | 2016-12-15T04:46:00Z | 28.99 | 9 | 25-40mph | KRDD | 7.24 | 2016-12-15T04:06:00Z | 35.68 | 23 | 25-40mph
PG&E | 2016-07-28 13:19 | 2016-07-28 13:19 | 39.7127 | -123.4973 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102195566 |  | 12000 | Conductor | Overhead | Yes | 42579.5549 | 2016-07-28 13:19 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0886 | 2016 | 7 | 28 | 13 | 19 | 16-0053369 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 4447 | 11.1949 | 93_335 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 13:19:00 | 629 | 12.238 | FALSE | <25mph | LAYC1 | 0.97 | 2016-02-19T22:29:00Z | 7 | 1 | < 25mph | LAYC1 | 0.97 | 2016-02-19T22:29:00Z | 7 | 1 | < 25mph | LAYC1 | 0.97 | 2016-02-19T22:29:00Z | 7 | 2 | < 25mph | LAYC1 | 0.97 | 2016-02-19T22:29:00Z | 7 | 2 | < 25mph
PG&E | 2017-06-13 | 14:30 | 37.8526 | -122.1853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Tower 005/035c | Unknown | 115000 | Conductor | Overhead | Yes | 42899 | 14:30 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1143 | 2017 | 6 | 13 | 14 | 30 | INT-09744 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | Balloons | 0 | 10.6352 | 148_231 | <25mph | <15mph | HFTD - Transmission | 2017-06-13 14:30:00 | 882 | 14.5193 | FALSE | <25mph | PG054 | 2.14 | 2018-07-21T19:00:00Z | 10.96 | 73 | < 25mph | LTRC1 | 6.59 | 2018-07-21T18:28:00Z | 22.01 | 181 | < 25mph | F2503 | 2.23 | 2018-07-21T19:47:00Z | 14.99 | 145 | < 25mph | PG064 | 7.68 | 2018-07-21T20:00:00Z | 22.15 | 358 | < 25mph
PG&E | 2017-06-15 04:31 | 2:58 | 40.299 | -122.4318 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101511631 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42901.1885 | 2:58 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | Other/Unknown | 1145 | 2017 | 6 | 15 | 2 | 58 | 17-0055359 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1762 | 9.755 | 139_366 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 02:58:00 | 884 | 19.4408 | FALSE | <25mph | E7114 | 1.68 | 2019-04-14T05:46:00Z | 5.99 | 4 | < 25mph | E7114 | 1.68 | 2019-04-14T05:46:00Z | 5.99 | 4 | < 25mph | E7114 | 1.68 | 2019-04-14T05:46:00Z | 5.99 | 8 | < 25mph | E7114 | 1.68 | 2019-04-14T05:46:00Z | 5.99 | 8 | < 25mph
PG&E | 2017-07-05 12:11 | 11:58 | 39.2105 | -121.2266 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVE ROBERTSON 530 906 4892 | 100010286 | Unknown | 21000 | Conductor | Overhead | Yes | 42921.5077 | 11:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1223 | 2017 | 7 | 5 | 11 | 58 | 17-0060605 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 10231 | 9.71 | 190_306 | <25mph | <15mph | HFTD - Distribution | 2017-07-05 11:58:00 | 962 | 14.0848 | FALSE | <25mph | E2572 | 2.49 | 2017-05-06T19:53:00Z | 3 | 11 | < 25mph | E6355 | 7.17 | 2017-05-06T19:05:00Z | 8.99 | 28 | < 25mph | E2572 | 2.49 | 2017-05-06T20:28:00Z | 4.99 | 19 | < 25mph | E1789 | 6.76 | 2017-05-06T20:24:00Z | 10 | 48 | < 25mph
PG&E | 2015-08-24 22:48 | 2015-08-24 22:48 | 37.896 | -122.6011 | Vegetation | Rural | < 3 meters | Fire Agency | marin county fire | 200' east of pan toll rd 50' north of panoramic hwy |  | 12000 | Unknown | Overhead | Yes | 42240.95 | 2015-08-24 22:48 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0552 | 2015 | 8 | 24 | 22 | 48 | 15-0057082 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 1128 | 8.5935 | 130_234 | <25mph | <15mph | HFTD - Distribution | 2015-08-24 22:48:00 | 296 | 14.2171 | FALSE | <25mph | MDEC1 | 2.32 | 2016-07-17T03:36:00Z | 13 | 9 | < 25mph | AU915 | 7.84 | 2016-07-17T03:31:00Z | 20 | 26 | < 25mph | MDEC1 | 2.32 | 2016-07-17T04:36:00Z | 14.99 | 18 | < 25mph | AU915 | 7.84 | 2016-07-17T04:45:00Z | 20 | 51 | < 25mph
PG&E | 2018-10-14 | 20:08 | 38.8935 | -120.8497 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103674516 | Unknown | 21000 | Conductor | Overhead | Yes | 43387 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1940 | 2018 | 10 | 14 | 20 | 8 | 18-0090299 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 48095 | 8.663 | 206_288 | <25mph | <15mph | HFTD - Distribution | 2018-10-14 20:08:00 | 1679 | 24.0259 | FALSE | <25mph | D5266 | 1.24 | 2016-11-21T01:51:00Z | 3 | 8 | < 25mph | BDMC1 | 7.81 | 2016-11-21T02:36:00Z | 13 | 9 | < 25mph | D5266 | 1.24 | 2016-11-21T01:51:00Z | 3 | 18 | < 25mph | BDMC1 | 7.81 | 2016-11-21T02:36:00Z | 13 | 20 | < 25mph
PG&E | 2015-07-04 01:14 | 2015-07-04 01:14 | 38.9566 | -121.0434 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100037226 |  | 12000 | Other | Overhead | Yes | 42189.0514 | 2015-07-04 01:14 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0441 | 2015 | 7 | 4 | 1 | 14 | 15-0045440 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 53865 | 7.3476 | 198_292 | <25mph | <15mph | HFTD - Distribution | 2015-07-04 01:14:00 | 186 | 12.3228 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8862 | 5.23 | 2017-11-28T16:00:00Z | 3 | 14 | < 25mph |  |  |  | 0 | 0 | No data | D8862 | 5.23 | 2017-11-28T16:46:00Z | 4 | 28 | < 25mph
PG&E | 2015-08-13 03:46 | 2015-08-13 03:46 | 37.2072 | -119.7343 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 44365 SAVAGE RD COARSEGOLD |  | 21000 | Conductor | Overhead | Yes | 42229.1569 | 2015-08-13 03:46 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0526 | 2015 | 8 | 13 | 3 | 46 | 15-0054655 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 7600 | 7.8941 | 255_196 | <25mph | <15mph | HFTD - Distribution | 2015-08-13 03:46:00 | 270 | 10.403 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5766 | 4.34 | 2015-01-19T22:12:00Z | 8.99 | 12 | < 25mph |  |  |  | 0 | 0 | No data | E5766 | 4.34 | 2015-01-19T22:12:00Z | 8.99 | 20 | < 25mph
PG&E | 2017-07-08 19:23 | 18:49 | 40.2935 | -122.4089 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | TOM STROING, RED BLUFF | 101526269 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42924.8076 | 18:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1234 | 2017 | 7 | 8 | 18 | 49 | 17-0061469 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 157484 | 8.2983 | 140_366 | <25mph | <15mph | HFTD - Distribution | 2017-07-08 18:49:00 | 973 | 15.6109 | FALSE | <25mph | E7114 | 0.65 | 2018-04-04T05:27:00Z | 8.01 | 4 | < 25mph | E7114 | 0.65 | 2018-04-04T05:27:00Z | 8.01 | 4 | < 25mph | E7114 | 0.65 | 2018-04-04T06:43:00Z | 8.99 | 8 | < 25mph | E7114 | 0.65 | 2018-04-04T06:43:00Z | 8.99 | 8 | < 25mph
PG&E | 2018-06-21 | 18:58 | 35.1224 | -120.3938 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101878933 | AT&T | 12000 | Conductor | Overhead | Yes | 43272 | 18:58 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1683 | 2018 | 6 | 21 | 18 | 58 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 13.9909 | 227_80 | <25mph | <15mph | HFTD - Distribution | 2018-06-21 18:58:00 | 1425 | 15.3983 | FALSE | <25mph | AU609 | 1.36 | 2017-08-12T09:05:00Z | 0 | 4 | < 25mph | F0412 | 7.22 | 2017-08-12T08:35:00Z | 4 | 8 | < 25mph | AU609 | 1.36 | 2017-08-12T10:05:00Z | 0 | 7 | < 25mph | F0412 | 7.22 | 2017-08-12T08:35:00Z | 4 | 16 | < 25mph
PG&E | 2019-06-17 | 10:25 | 38.511 | -122.2134 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 43051101 |  | 12000 | Conductor | Overhead | Yes | 43633 | 10:25 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-84 | 2019 | 6 | 17 | 10 | 25 | 19-0068579 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 306900 | 10.2943 | 147_267 | <25mph | <15mph | HFTD - Distribution | 2019-06-17 10:25:00 | 1843 | 15.8677 | FALSE | <25mph | ATLC1 | 3.74 | 2018-10-11T16:29:00Z | 10 | 7 | < 25mph | PG044 | 5.51 | 2018-10-11T16:40:00Z | 12.93 | 25 | < 25mph | ATLC1 | 3.74 | 2018-10-11T17:29:00Z | 11.01 | 14 | < 25mph | PG044 | 5.51 | 2018-10-11T16:40:00Z | 12.93 | 50 | < 25mph
PG&E | 2018-09-02 | 15:36 | 37.4714 | -122.4248 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Arie Delay 659-740-4636 | 103808872 | Unknown | 12000 | Capacitor Bank | Overhead | Yes | 43345 | 15:36 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1876 | 2018 | 9 | 2 | 15 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 11.73 | 137_210 | <25mph | <15mph | HFTD - Distribution | 2018-09-02 15:36:00 | 1615 | 13.6047 | FALSE | <25mph | D9259 | 3.46 | 2019-02-15T10:18:00Z | 13 | 4 | < 25mph | HSPC1 | 6.33 | 2019-02-15T10:18:00Z | 28.01 | 54 | 25-40mph | D9259 | 3.46 | 2019-02-15T10:18:00Z | 13 | 8 | < 25mph | HSPC1 | 6.33 | 2019-02-15T11:18:00Z | 34.99 | 106 | 25-40mph
PG&E | 2016-08-13 | 2016-08-13 14:00 | 39.2009 | -121.213 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100011376 | PACIFIC BELL | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0924 | 2016 | 8 | 13 | 14 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 9.674 | 190_305 | <25mph | <15mph | HFTD - Distribution | 2016-08-13 14:00:00 | 666 | 11.9455 | FALSE | <25mph | E2572 | 2.38 | 2015-09-01T10:33:00Z | 1.01 | 12 | < 25mph | E1789 | 5.78 | 2015-09-01T11:12:00Z | 7 | 39 | < 25mph | E2572 | 2.38 | 2015-09-01T12:13:00Z | 1.01 | 24 | < 25mph | E1789 | 5.78 | 2015-09-01T11:48:00Z | 7 | 74 | < 25mph
PG&E | 2017-10-20 | 6:18 | 39.2922 | -121.0157 | Vegetation | Rural | < 3 Meters | Fire Agency | PHILLIP NUNNINK INCIDENT # 27272 | 100087647 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43028 | 6:18 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1499 | 2017 | 10 | 20 | 6 | 18 | 17-0088957 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 102410 | 6.1464 | 199_310 | <25mph | <15mph | HFTD - Distribution | 2017-10-20 06:18:00 | 1242 | 23.0997 | FALSE | <25mph | E3651 | 3.59 | 2017-05-30T22:35:00Z | 5.99 | 19 | < 25mph | E5439 | 4.03 | 2017-05-30T22:35:00Z | 10 | 56 | < 25mph | E3651 | 3.59 | 2017-05-30T23:10:00Z | 7 | 36 | < 25mph | RRRC1 | 5.48 | 2017-05-30T23:13:00Z | 12.01 | 105 | < 25mph
PG&E | 2017-06-24 15:06 | 14:51 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 42910.6292 | 14:51 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1194 | 2017 | 6 | 24 | 14 | 51 | 17-0058332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 21296 | 10.4286 | 210_259 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 14:51:00 | 933 | 10.7263 | FALSE | <25mph | KJAQ | 1.92 | 2015-04-01T01:25:00Z | 16.11 | 2 | < 25mph | KJAQ | 1.92 | 2015-04-01T01:25:00Z | 16.11 | 3 | < 25mph | KJAQ | 1.92 | 2015-04-01T02:20:00Z | 18.41 | 9 | < 25mph | KJAQ | 1.92 | 2015-04-01T02:20:00Z | 18.41 | 11 | < 25mph
PG&E | 2017-09-15 | 14:55 | 39.7461 | -121.4885 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100335239 | Unknown | 12000 | Conductor | Overhead | Yes | 42993 | 14:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1415 | 2017 | 9 | 15 | 14 | 55 | 17-0079388 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 8834 | 10.5756 | 179_335 | <25mph | <15mph | HFTD - Distribution | 2017-09-15 14:55:00 | 1153 | 16.2937 | FALSE | <25mph | JBGC1 | 0.7 | 2018-04-03T08:13:00Z | 24.99 | 1 | < 25mph | JBGC1 | 0.7 | 2018-04-03T08:13:00Z | 24.99 | 2 | < 25mph | JBGC1 | 0.7 | 2018-04-03T09:13:00Z | 27 | 2 | 25-40mph | JBGC1 | 0.7 | 2018-04-03T09:13:00Z | 27 | 4 | 25-40mph
PG&E | 2015-06-21 13:31 | 2015-06-21 13:31 | 37.375 | -119.6116 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103204866 |  | 0 – 750 | Conductor | Overhead | No |  |  | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0399 | 2015 | 6 | 21 | 13 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 11.8124 | 260_205 | <25mph | <15mph | HFTD - Distribution | 2015-06-21 13:31:00 | 145 | 12.2407 | FALSE | <25mph | AT301 | 3.85 | 2016-10-31T07:23:00Z | 5.99 | 18 | < 25mph | MIAC1 | 7.96 | 2016-10-31T06:59:00Z | 11.01 | 58 | < 25mph | BSNC1 | 1.01 | 2016-10-31T07:48:00Z | 7 | 34 | < 25mph | MIAC1 | 7.96 | 2016-10-31T06:59:00Z | 11.01 | 124 | < 25mph
PG&E | 2015-08-19 06:20 | 2015-08-19 06:20 | 39.2831 | -123.2931 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | MTR#50001225 | None | 12000 | Conductor | Overhead | Yes | 42235.2639 | 2015-08-19 06:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0545 | 2015 | 8 | 19 | 6 | 20 | 15-0055982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5403 | 1.4303 | 102_311 | <25mph | <15mph | HFTD - Distribution | 2015-08-19 06:20:00 | 289 | 19.8186 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7513 | 7.43 | 2018-06-04T03:48:00Z | 4 | 12 | < 25mph |  |  |  | 0 | 0 | No data | E7513 | 7.43 | 2018-06-04T03:48:00Z | 4 | 24 | < 25mph
PG&E | 2016-10-11 23:17 | 23:16 | 39.0201 | -120.8294 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire.foresthill fire | 100025501 |  | 60000 | Conductor | Overhead | Yes | 42654.9701 | 23:16 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error |  | no-match | 1028 | 2016 | 10 | 11 | 23 | 16 | INT-08640 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 0 | 7.6312 | 207_295 | <25mph | <15mph | HFTD - Transmission | 2016-10-11 23:16:00 | 769 | 11.1078 | FALSE | <25mph | PG032 | 2.4 | 2018-10-22T23:20:00Z | 7.67 | 9 | < 25mph | FSHC1 | 7.19 | 2018-10-22T23:33:00Z | 17 | 22 | < 25mph | PG032 | 2.4 | 2018-10-22T23:20:00Z | 7.67 | 20 | < 25mph | FSHC1 | 7.19 | 2018-10-22T23:33:00Z | 17 | 46 | < 25mph
PG&E | 2018-09-29 | 16:16 | 41.0219 | -123.655 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Hoopa Fire Dept | 100962165 | Unknown | 12000 | Conductor | Overhead | Yes | 43372 | 16:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1923 | 2018 | 9 | 29 | 16 | 16 | 18-0084877 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 16028 | 7.8421 | 89_407 | <25mph | <15mph | HFTD - Distribution | 2018-09-29 16:16:00 | 1662 | 11.5265 | FALSE | <25mph | HOAC1 | 1.98 | 2018-03-05T16:40:00Z | 11.01 | 1 | < 25mph | BHTC1 | 7.5 | 2018-03-05T16:46:00Z | 13 | 7 | < 25mph | HOAC1 | 1.98 | 2018-03-05T16:40:00Z | 11.01 | 2 | < 25mph | BHTC1 | 7.5 | 2018-03-05T16:46:00Z | 13 | 14 | < 25mph
PG&E | 2016-11-15 | 17:27 | 39.7275 | -121.6557 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100327525 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42689 | 17:27 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 1049 | 2016 | 11 | 15 | 17 | 27 | 16-0080083 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 69231 | 9.6883 | 172_334 | <25mph | <15mph | HFTD - Distribution | 2016-11-15 17:27:00 | 790 | 16.6369 | FALSE | <25mph | PDEC1 | 2.44 | 2017-07-27T09:00:00Z | 3 | 1 | < 25mph | PDEC1 | 2.44 | 2017-07-27T09:00:00Z | 3 | 1 | < 25mph | PDEC1 | 2.44 | 2017-07-27T09:00:00Z | 3 | 1 | < 25mph | PDEC1 | 2.44 | 2017-07-27T09:00:00Z | 3 | 1 | < 25mph
PG&E | 2017-05-24 16:25 | 16:24 | 38.834 | -121.1197 | Vegetation | Rural | < 3 Meters | Fire Agency | Fire Capt | 103838109 | None | 12000 | Conductor | Overhead | Yes | 42879.6837 | 16:24 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | no-match | 1111 | 2017 | 5 | 24 | 16 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 20.975 | 194_285 | <25mph | <15mph | HFTD - Distribution | 2017-05-24 16:24:00 | 851 | 20.975 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG366 | 4.2 | 2019-12-03T02:10:00Z | 5.91 | 33 | < 25mph |  |  |  | 0 | 0 | No data | E9372 | 6.24 | 2019-12-03T03:31:00Z | 10 | 67 | < 25mph
PG&E | 2017-07-19 | 5:52 | 37.0905 | -119.6047 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Tower 003/001 | Unknown | 115000 | Conductor | Overhead | Yes | 42935 | 5:52 | Contact From Object | N.A. | Other | Electric Facility | Unknown |  | no-match | 1269 | 2017 | 7 | 19 | 5 | 52 | INT-09877 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 0 | 0.36815 | 261_189 | <25mph | <15mph | HFTD - Transmission | 2017-07-19 05:52:00 | 1008 | 14.3689 | FALSE | <25mph | PG484 | 0.44 | 2019-10-28T13:20:00Z | 14.76 | 12 | < 25mph | PG467 | 7.7 | 2019-10-28T13:10:00Z | 16.6 | 79 | < 25mph | PG484 | 0.44 | 2019-10-28T13:20:00Z | 14.76 | 24 | < 25mph | PG467 | 7.7 | 2019-10-28T13:10:00Z | 16.6 | 158 | < 25mph
PG&E | 2019-05-29 | 16:54 | 37.0371 | -119.5209 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 100680674 |  | 12000 | Pole | Overhead | Yes | 43614 | 16:54 | Vegetation |  | Veg. contact | Pole |  |  | Dead | 2019-202 | 2019 | 5 | 29 | 16 | 54 | 19-0059237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 6780 | 6.6167 | 265_186 | <25mph | <15mph | HFTD - Distribution | 2019-05-29 16:54:00 | 1787 | 9.3593 | FALSE | <25mph | PRHC1 | 3 | 2019-02-19T20:27:00Z | 14 | 1 | < 25mph | PRHC1 | 3 | 2019-02-19T20:27:00Z | 14 | 7 | < 25mph | PRHC1 | 3 | 2019-02-19T20:27:00Z | 14 | 2 | < 25mph | PRHC1 | 3 | 2019-02-19T20:27:00Z | 14 | 14 | < 25mph
PG&E | 2017-09-11 | 7:18 | 37.0008 | -121.6667 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100621936 | VERIZON CALIFORNIA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1407 | 2017 | 9 | 11 | 7 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.0313 | 170_184 | <25mph | <15mph | HFTD - Distribution | 2017-09-11 07:18:00 | 1145 | 32.6801 | FALSE | 25-40mph | AU710 | 3.82 | 2017-01-29T08:21:00Z | 3 | 4 | < 25mph | CTOC1 | 7.65 | 2017-01-29T08:27:00Z | 4 | 37 | < 25mph | AU710 | 3.82 | 2017-01-29T08:21:00Z | 3 | 8 | < 25mph | CTOC1 | 7.65 | 2017-01-29T09:27:00Z | 4.99 | 72 | < 25mph
PG&E | 2016-08-05 | 2016-08-05 12:42 | 38.4048 | -120.5292 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101244628 |  | 12000 | Conductor | Overhead | Yes | 42587 | 2016-08-05 12:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0906 | 2016 | 8 | 5 | 12 | 42 | 16-0055368 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 363 | 12.0247 | 220_261 | <25mph | <15mph | HFTD - Distribution | 2016-08-05 12:42:00 | 649 | 12.7612 | FALSE | <25mph | PG261 | 1.78 | 2019-09-27T07:10:00Z | 5.55 | 24 | < 25mph | PG263 | 6.73 | 2019-09-27T06:50:00Z | 7.16 | 71 | < 25mph | PG261 | 1.78 | 2019-09-27T07:10:00Z | 5.55 | 48 | < 25mph | PG263 | 6.73 | 2019-09-27T06:50:00Z | 7.16 | 142 | < 25mph
PG&E | 2016-05-31 04:02 | 2016-05-31 04:02 | 35.7984 | -120.9743 | Vegetation | RURAL | < 0.25 Acres | Utility: PG&E | N.A. | 101863413 |  | 12000 | Conductor | Overhead | Yes | 42521.1681 | 2016-05-31 04:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0754 | 2016 | 5 | 31 | 4 | 2 | 16-0039748 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 51888 | 1.5922 | 201_118 | <25mph | <15mph | HFTD - Distribution | 2016-05-31 04:02:00 | 497 | 16.9662 | FALSE | <25mph | E9175 | 3.45 | 2018-05-06T08:05:00Z | 4.99 | 13 | < 25mph | E9175 | 3.45 | 2018-05-06T08:05:00Z | 4.99 | 17 | < 25mph | E9175 | 3.45 | 2018-05-06T09:10:00Z | 4.99 | 25 | < 25mph | E9175 | 3.45 | 2018-05-06T09:10:00Z | 4.99 | 33 | < 25mph
PG&E | 2015-11-21 10:36 | 2015-11-21 10:36 | 38.0679 | -120.1872 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101045952 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42329.4417 | 2015-11-21 10:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0677 | 2015 | 11 | 21 | 10 | 36 | 15-0079868 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18350 | 7.816 | 235_243 | <25mph | <15mph | HFTD - Distribution | 2015-11-21 10:36:00 | 421 | 16.6927 | FALSE | <25mph | MOUC1 | 3.29 | 2017-07-18T21:02:00Z | 14 | 1 | < 25mph | MOUC1 | 3.29 | 2017-07-18T21:02:00Z | 14 | 1 | < 25mph | MOUC1 | 3.29 | 2017-07-18T22:02:00Z | 18.99 | 2 | < 25mph | MOUC1 | 3.29 | 2017-07-18T22:02:00Z | 18.99 | 2 | < 25mph
PG&E | 2017-07-22 12:26 | 12:25 | 40.8795 | -123.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Josh , comander chief of forest service. | 100980577 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.518 | 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1279 | 2017 | 7 | 22 | 12 | 25 | 17-0064721 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 23227 | 10.7493 | 84_399 | <25mph | <15mph | HFTD - Distribution | 2017-07-22 12:25:00 | 1018 | 13.5476 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BHTC1 | 5.5 | 2018-10-12T16:46:00Z | 20 | 1 | < 25mph |  |  |  | 0 | 0 | No data | BHTC1 | 5.5 | 2018-10-12T16:46:00Z | 20 | 2 | < 25mph
PG&E | 2018-09-05 | 16:55 | 37.4655 | -119.9005 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JON BERRY 209-966-4700 | 101087053 | Unknown | 21000 | Conductor | Overhead | Yes | 43348 | 16:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1882 | 2018 | 9 | 5 | 16 | 55 | 18-0076909 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 4017 | 13.8551 | 248_210 | <25mph | <15mph | HFTD - Distribution | 2018-09-05 16:55:00 | 1621 | 17.3022 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MPOC1 | 5.43 | 2017-08-05T13:07:00Z | 8.01 | 10 | < 25mph |  |  |  | 0 | 0 | No data | MPOC1 | 5.43 | 2017-08-05T14:07:00Z | 8.01 | 20 | < 25mph
PG&E | 2017-11-29 17:35 | 17:34 | 38.6841 | -120.6546 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 101419450 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 43068.7326 | 17:34 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1533 | 2017 | 11 | 29 | 17 | 34 | 17-0098456 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 582825 | 2.2539 | 214_277 | <25mph | <15mph | HFTD - Distribution | 2017-11-29 17:34:00 | 1275 | 13.1335 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GZFC1 | 7.93 | 2015-08-02T04:17:00Z | 4.99 | 8 | < 25mph |  |  |  | 0 | 0 | No data | GZFC1 | 7.93 | 2015-08-02T04:17:00Z | 4.99 | 13 | < 25mph
PG&E | 2019-08-14 | 10:16 | 35.379 | -120.4232 | Vegetation | Hardwood Woodland | < 1 meter | Cal Fire |  | 512769069280 |  | 21000 | Conductor | Overhead | Yes | 43691 | 10:16 | Vegetation | [5 empty] | no-match |  | 2019 | 8 | 14 | 10 | 16 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.0314 | 226_94 | <25mph | <15mph | HFTD - Distribution | 2019-08-14 10:16:00 | 1976 | 14.3934 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-02-12 | 20:20 | 39.9395 | -121.6494 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430947 | Unknown | 12000 | Conductor | Overhead | Yes | 43143 | 20:20 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1561 | 2018 | 2 | 12 | 20 | 20 | 18-0013604 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 149212 | 10.1876 | 172_346 | <25mph | <15mph | HFTD - Distribution | 2018-02-12 20:20:00 | 1303 | 14.6044 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CSTC1 | 7.88 | 2015-11-02T11:51:00Z | 8.01 | 18 | < 25mph |  |  |  | 0 | 0 | No data | CSTC1 | 7.88 | 2015-11-02T12:51:00Z | 8.01 | 35 | < 25mph
PG&E | 2018-10-16 | 10:44 | 40.5097 | -124.1624 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101004106 | Unknown | 12000 | Conductor | Overhead | Yes | 43389 | 10:44 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1942 | 2018 | 10 | 16 | 10 | 44 | 18-0090952 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 2081 | 4.5851 | 67_380 | <25mph | <15mph | HFTD - Distribution | 2018-10-16 10:44:00 | 1681 | 13.3626 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AT493 | 4.22 | 2019-01-29T02:20:00Z | 8.99 | 19 | < 25mph |  |  |  | 0 | 0 | No data | AT493 | 4.22 | 2019-01-29T02:20:00Z | 8.99 | 39 | < 25mph
PG&E | 2017-07-15 14:35 | 14:34 | 39.6231 | -121.5328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | russ fowler | 100404385 | Unknown | 12000 | Conductor | Overhead | Yes | 42931.6076 | 14:34 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1254 | 2017 | 7 | 15 | 14 | 34 | 17-0063126 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 54372 | 7.6156 | 177_329 | <25mph | <15mph | HFTD - Distribution | 2017-07-15 14:34:00 | 993 | 11.3229 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CICC1 | 5.91 | 2015-04-14T09:54:00Z | 30 | 1 | 25-40mph |  |  |  | 0 | 0 | No data | CICC1 | 5.91 | 2015-04-14T09:54:00Z | 30 | 2 | 25-40mph
PG&E | 2017-07-07 20:49 | 14:31 | 37.499 | -119.799 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVEN WARD OFFICE 209-966-3542 CELL559-706-8811 | 103855637 | Unknown | 21000 | Conductor | Overhead | Yes | 42923.8675 | 14:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1230 | 2017 | 7 | 7 | 14 | 31 | 17-0061288 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 554306 | 11.2535 | 252_212 | <25mph | <15mph | HFTD - Distribution | 2017-07-07 14:31:00 | 968 | 22.3608 | FALSE | <25mph | JSDC1 | 3.81 | 2017-09-07T09:47:00Z | 3 | 1 | < 25mph | MIAC1 | 6.24 | 2017-09-07T09:59:00Z | 14 | 12 | < 25mph | JSDC1 | 3.81 | 2017-09-07T09:47:00Z | 3 | 2 | < 25mph | MIAC1 | 6.24 | 2017-09-07T10:59:00Z | 14.99 | 21 | < 25mph
PG&E | 2016-07-29 01:31 | 2016-07-29 01:31 | 41.0396 | -123.674 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Hoopa FD | 100962351 |  | 12000 | Conductor | Overhead | Yes | 42580.0632 | 2016-07-29 01:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0891 | 2016 | 7 | 29 | 1 | 31 | 16-0053478 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1418 | 4.1421 | 88_408 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 01:31:00 | 633 | 13.6696 | FALSE | <25mph | HOAC1 | 0.58 | 2019-01-27T15:40:00Z | 0 | 1 | < 25mph | BIIC1 | 4.46 | 2019-01-27T15:40:00Z | 12.01 | 2 | < 25mph | HOAC1 | 0.58 | 2019-01-27T16:40:00Z | 0 | 2 | < 25mph | BIIC1 | 4.46 | 2019-01-27T15:40:00Z | 12.01 | 4 | < 25mph
PG&E | 2017-08-31 | 11:33 | 37.1379 | -121.9966 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100519201 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 11:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1373 | 2017 | 8 | 31 | 11 | 33 | 17-0074457 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 99153 | 14.3205 | 156_192 | <25mph | <15mph | HFTD - Distribution | 2017-08-31 11:33:00 | 1111 | 14.3569 | FALSE | <25mph | PG057 | 3.89 | 2018-07-05T11:30:00Z | 2.86 | 27 | < 25mph | PG050 | 5.43 | 2018-07-05T10:50:00Z | 7.9 | 130 | < 25mph | PG057 | 3.89 | 2018-07-05T12:40:00Z | 3.94 | 54 | < 25mph | PG050 | 5.43 | 2018-07-05T10:50:00Z | 7.9 | 260 | < 25mph
PG&E | 2018-05-09 | 14:00 | 38.5908 | -123.3423 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CASE# 18CALNU 005865 | 101998286 | Unknown | 12000 | Conductor | Overhead | Yes | 43229 | 14:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1584 | 2018 | 5 | 9 | 14 | 0 | 18-0039683 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 29522 | 27.1689 | 98_273 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-05-09 14:00:00 | 1326 | 27.3091 | FALSE | 25-40mph | E7021 | 3.81 | 2017-04-07T13:19:00Z | 10 | 6 | < 25mph | E7021 | 3.81 | 2017-04-07T13:19:00Z | 10 | 6 | < 25mph | E7021 | 3.81 | 2017-04-07T13:19:00Z | 10 | 10 | < 25mph | E7021 | 3.81 | 2017-04-07T13:19:00Z | 10 | 10 | < 25mph
PG&E | 2015-07-31 22:45 | 2015-07-31 22:45 | 38.3805 | -120.5628 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS FROM 1958 QUAIL LN WEST POINT | None | 12000 | Conductor | Overhead | Yes | 42216.9479 | 2015-07-31 22:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0503 | 2015 | 7 | 31 | 22 | 45 | 15-0052033 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 33559 | 6.4734 | 218_260 | <25mph | <15mph | HFTD - Distribution | 2015-07-31 22:45:00 | 248 | 15.0324 | FALSE | <25mph | AT450 | 2.7 | 2015-08-22T13:49:00Z | 3 | 1 | < 25mph | C9148 | 7.8 | 2015-08-22T13:48:00Z | 8.99 | 17 | < 25mph | AT450 | 2.7 | 2015-08-22T13:54:00Z | 3 | 2 | < 25mph | MTZC1 | 4.9 | 2015-08-22T13:56:00Z | 10 | 34 | < 25mph
PG&E | 2015-06-06 15:38 | 2015-06-06 15:38 | 39.0409 | -123.4019 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 11480 ANDERSON VALLEY WAY @ BRIDGE |  | 12000 | Conductor | Overhead | Yes | 42161.6514 | 2015-06-06 15:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0355 | 2015 | 6 | 6 | 15 | 38 | 15-0039056 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 1748 | 19.2204 | 97_298 | <25mph | <15mph | HFTD - Distribution | 2015-06-06 15:38:00 | 101 | 19.2204 | FALSE | <25mph | PG252 | 2.47 | 2019-09-22T06:00:00Z | 1.45 | 9 | < 25mph | BNVC1 | 4.68 | 2019-09-22T05:50:00Z | 5.99 | 24 | < 25mph | PG252 | 2.47 | 2019-09-22T07:00:00Z | 1.9 | 18 | < 25mph | BNVC1 | 4.68 | 2019-09-22T05:50:00Z | 5.99 | 48 | < 25mph
PG&E | 2016-07-15 14:26 | 2016-07-15 14:26 | 38.1366 | -122.7092 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | NOVATO FIRE AND OTHERS | 102013570 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.6014 | 2016-07-15 14:26 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0853 | 2016 | 7 | 15 | 14 | 26 | 16-0050269 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 758 | 13.1533 | 125_247 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 14:26:00 | 596 | 15.659 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E0433 | 5.38 | 2015-02-17T02:51:00Z | 15.99 | 20 | < 25mph |  |  |  | 0 | 0 | No data | E0433 | 5.38 | 2015-02-17T04:01:00Z | 16.98 | 39 | < 25mph
PG&E | 2018-08-08 | 10:03 | 40.7933 | -124.0242 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CHIEF | 100983089 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 10:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1829 | 2018 | 8 | 8 | 10 | 3 | 18-0067921 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 27379 | 3.1403 | 73_395 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 10:03:00 | 1568 | 7.3376 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.13 | 2019-08-03T04:55:00Z | 5.99 | 33 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.13 | 2019-08-03T05:55:00Z | 5.99 | 68 | < 25mph
PG&E | 2019-05-29 | 16:54 | 37.0371 | -119.5209 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 100680674 |  | 12000 | Pole | Overhead | Yes | 43614 | 16:54 | Vegetation |  | Veg. contact | Pole |  |  | Dead | 2019-202 | 2019 | 5 | 29 | 16 | 54 | 19-0059237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 6780 | 6.6167 | 265_186 | <25mph | <15mph | HFTD - Distribution | 2019-05-29 16:54:00 | 1787 | 9.3593 | FALSE | <25mph | PRHC1 | 3 | 2016-07-12T10:27:00Z | 3 | 1 | < 25mph | PRHC1 | 3 | 2016-07-12T10:27:00Z | 3 | 1 | < 25mph | PRHC1 | 3 | 2016-07-12T11:27:00Z | 3 | 2 | < 25mph | PRHC1 | 3 | 2016-07-12T11:27:00Z | 3 | 2 | < 25mph
PG&E | 2019-06-18 | 19:49 | 35.8876 | -120.9217 | Bird Found | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Pole | Overhead | Yes | 43634 | 19:49 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | no-match | 2019-55 | 2019 | 6 | 18 | 19 | 49 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 15.5935 | 203_122 | <25mph | <15mph | HFTD - Distribution | 2019-06-18 19:49:00 | 1852 | 21.7258 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RBYC1 | 6.84 | 2017-06-12T11:12:00Z | 4 | 1 | < 25mph |  |  |  | 0 | 0 | No data | RBYC1 | 6.84 | 2017-06-12T11:12:00Z | 4 | 2 | < 25mph
PG&E | 2018-07-27 | 23:12 | 37.18 | -122.029 | Vegetation | Rural | < 3 meters | Fire Agency | Jeremy Wise 408-378-4010 Incident # C182080066 | 100518365 | Unknown | 12000 | Conductor | Overhead | Yes | 43308 | 23:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1793 | 2018 | 7 | 27 | 23 | 12 | 18-0064525 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 30475 | 3.2895 | 154_194 | <25mph | <15mph | HFTD - Distribution | 2018-07-27 23:12:00 | 1533 | 9.1823 | FALSE | <25mph | AV005 | 3.55 | 2015-06-19T14:56:00Z | 3 | 10 | < 25mph | D3546 | 4.14 | 2015-06-19T14:15:00Z | 7 | 104 | < 25mph | AV005 | 3.55 | 2015-06-19T15:56:00Z | 4 | 20 | < 25mph | D3546 | 4.14 | 2015-06-19T14:15:00Z | 7 | 210 | < 25mph
PG&E | 2018-06-30 | 11:14 | 39.3621 | -121.0809 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ENGINEER YUREK | 100091354 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 11:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1713 | 2018 | 6 | 30 | 11 | 14 | 18-0055945 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5724 | 3.7745 | 196_314 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 11:14:00 | 1454 | 12.1468 | FALSE | <25mph | PG350 | 3.87 | 2019-05-12T08:10:00Z | 0.65 | 18 | < 25mph | RRRC1 | 4.49 | 2019-05-12T07:13:00Z | 5.99 | 38 | < 25mph | E3651 | 2.44 | 2019-05-12T08:30:00Z | 2.01 | 36 | < 25mph | RRRC1 | 4.49 | 2019-05-12T09:13:00Z | 5.99 | 75 | < 25mph
PG&E | 2016-06-12 | 2016-06-12 13:14 | 37.5096 | -120.0462 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101083986 |  | 0 – 750 | Conductor | Overhead | Yes | 42533 | 2016-06-12 13:14 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0795 | 2016 | 6 | 12 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.8806 | 241_212 | <25mph | <15mph | HFTD - Distribution | 2016-06-12 13:14:00 | 539 | 13.4596 | FALSE | <25mph | MPOC1 | 3.28 | 2017-12-18T10:07:00Z | 11.01 | 1 | < 25mph | MPOC1 | 3.28 | 2017-12-18T10:07:00Z | 11.01 | 1 | < 25mph | MPOC1 | 3.28 | 2017-12-18T10:07:00Z | 11.01 | 2 | < 25mph | MPOC1 | 3.28 | 2017-12-18T10:07:00Z | 11.01 | 2 | < 25mph
PG&E | 2016-09-25 10:35 | 2016-09-25 10:35 | 38.8019 | -122.8176 | Vegetation | RURAL | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103613996 |  | 115000 | Other | Overhead | Yes | 2016-09-25 10:35 | 2016-09-25 10:35 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1004 | 2016 | 9 | 25 | 10 | 35 | INT-08572 | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Equip Failure - Other | 0 | 28.1055 | 121_284 | 25-40mph | 15-30mph | HFTD - Transmission | 2016-09-25 10:35:00 | 743 | 28.9174 | FALSE | 25-40mph | PG125 | 1.13 | 2019-02-25T09:40:00Z | 34.63 | 6 | 25-40mph | PG125 | 1.13 | 2019-02-25T09:40:00Z | 34.63 | 36 | 25-40mph | PG125 | 1.13 | 2019-02-25T09:40:00Z | 34.63 | 12 | 25-40mph | PG125 | 1.13 | 2019-02-25T09:40:00Z | 34.63 | 68 | 25-40mph
PG&E | 2015-03-14 02:30 | 2015-03-14 02:30 | 38.9038 | -122.7579 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 9210 Wildcat Road, Kelseyville |  | 12000 | Conductor | Overhead | Yes | 42077.1042 | 2015-03-14 02:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0274 | 2015 | 3 | 14 | 2 | 30 | 15-0019556 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2280 | 8.9688 | 124_289 | <25mph | <15mph | HFTD - Distribution | 2015-03-14 02:30:00 | 20 | 8.9688 | FALSE | <25mph | KELC1 | 2.83 | 2015-09-25T18:57:00Z | 14 | 1 | < 25mph | KELC1 | 2.83 | 2015-09-25T18:57:00Z | 14 | 5 | < 25mph | KELC1 | 2.83 | 2015-09-25T19:57:00Z | 15.99 | 2 | < 25mph | KELC1 | 2.83 | 2015-09-25T19:57:00Z | 15.99 | 10 | < 25mph
PG&E | 2017-11-11 12:17 | 11:57 | 35.1191 | -120.3936 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Jordan Dayley ph#929-3911,engine#3467 | 101931190 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43050.5115 | 11:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1518 | 2017 | 11 | 11 | 11 | 57 | 17-0094408 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29093 | 8.6182 | 227_80 | <25mph | <15mph | HFTD - Distribution | 2017-11-11 11:57:00 | 1260 | 14.1707 | FALSE | <25mph | AU609 | 1.13 | 2016-06-29T00:53:00Z | 8.99 | 4 | < 25mph | AU609 | 1.13 | 2016-06-29T00:53:00Z | 8.99 | 4 | < 25mph | AU609 | 1.13 | 2016-06-29T01:08:00Z | 11.01 | 8 | < 25mph | AU609 | 1.13 | 2016-06-29T01:08:00Z | 11.01 | 8 | < 25mph
PG&E | 2015-07-01 12:57 | 2015-07-01 12:57 | 39.4146 | -121.379 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42186.5396 | 2015-07-01 12:57 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0434 | 2015 | 7 | 1 | 12 | 57 | 15-0044609 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 12.6482 | 183_317 | <25mph | <15mph | HFTD - Distribution | 2015-07-01 12:57:00 | 179 | 18.7031 | FALSE | <25mph | BNGC1 | 2.37 | 2017-07-12T10:51:00Z | 1.01 | 1 | < 25mph | TT309 | 4.14 | 2017-07-12T10:45:00Z | 5.99 | 2 | < 25mph | BNGC1 | 2.37 | 2017-07-12T11:51:00Z | 2.01 | 2 | < 25mph | TT309 | 4.14 | 2017-07-12T10:45:00Z | 5.99 | 4 | < 25mph
PG&E | 2016-08-08 | 2016-08-08 15:44 | 37.1382 | -121.9672 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100519919 |  | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0912 | 2016 | 8 | 8 | 15 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 8.8992 | 157_192 | <25mph | <15mph | HFTD - Distribution | 2016-08-08 15:44:00 | 655 | 10.1741 | FALSE | <25mph | D9791 | 1.67 | 2019-01-31T20:41:00Z | 4 | 29 | < 25mph | LSGC1 | 4.65 | 2019-01-31T20:32:00Z | 14 | 144 | < 25mph | PG057 | 2.38 | 2019-01-31T22:00:00Z | 6.13 | 61 | < 25mph | LSGC1 | 4.65 | 2019-01-31T20:32:00Z | 14 | 294 | < 25mph
PG&E | 2015-06-04 20:00 | 2015-06-04 20:00 | 38.6916 | -120.8606 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101412760 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42159.8333 | 2015-06-04 20:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0347 | 2015 | 6 | 4 | 20 | 0 | 15-0038597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 9640 | 2.0731 | 205_277 | <25mph | <15mph | HFTD - Distribution | 2015-06-04 20:00:00 | 93 | 11.0268 | FALSE | <25mph | E6490 | 1.72 | 2016-07-27T20:41:00Z | 12.01 | 30 | < 25mph | BENC1 | 8 | 2016-07-27T20:59:00Z | 13 | 66 | < 25mph | C6129 | 0.68 | 2016-07-27T21:39:00Z | 14.99 | 59 | < 25mph | C6129 | 0.68 | 2016-07-27T21:39:00Z | 14.99 | 129 | < 25mph
PG&E | 2018-06-15 | 9:51 | 37.1986 | -119.4709 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RANCHARIA ENGINE 4255 USFS ENG 52 | 101058060 | Unknown | 12000 | Conductor | Overhead | Yes | 43266 | 9:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1660 | 2018 | 6 | 15 | 9 | 51 | 18-0051354 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 35146 | 7.0865 | 267_195 | <25mph | <15mph | HFTD - Distribution | 2018-06-15 09:51:00 | 1402 | 16.2916 | FALSE | <25mph | NFRC1 | 3.06 | 2018-07-11T06:55:00Z | 8.01 | 1 | < 25mph | NFRC1 | 3.06 | 2018-07-11T06:55:00Z | 8.01 | 1 | < 25mph | NFRC1 | 3.06 | 2018-07-11T06:55:00Z | 8.01 | 2 | < 25mph | NFRC1 | 3.06 | 2018-07-11T06:55:00Z | 8.01 | 2 | < 25mph
PG&E | 2015-07-15 09:00 | 2015-07-15 09:00 | 36.997 | -121.7381 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101795728 |  | 21000 | Conductor | Overhead | Yes | 42200.375 | 2015-07-15 09:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0463 | 2015 | 7 | 15 | 9 | 0 | 15-0047650 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3800 | 8.5113 | 167_184 | <25mph | <15mph | HFTD - Distribution | 2015-07-15 09:00:00 | 208 | 13.379 | FALSE | <25mph | CTOC1 | 3.71 | 2015-03-13T19:27:00Z | 4 | 1 | < 25mph | C4503 | 7.38 | 2015-03-13T20:15:00Z | 10 | 29 | < 25mph | CTOC1 | 3.71 | 2015-03-13T19:27:00Z | 4 | 2 | < 25mph | C4503 | 7.38 | 2015-03-13T20:15:00Z | 10 | 56 | < 25mph
PG&E | 2015-07-15 09:00 | 2015-07-15 09:00 | 36.997 | -121.7381 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101795728 |  | 21000 | Conductor | Overhead | Yes | 42200.375 | 2015-07-15 09:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0463 | 2015 | 7 | 15 | 9 | 0 | 15-0047650 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3800 | 8.5113 | 167_184 | <25mph | <15mph | HFTD - Distribution | 2015-07-15 09:00:00 | 208 | 13.379 | FALSE | <25mph | PG399 | 1.65 | 2019-11-09T17:30:00Z | 6.93 | 13 | < 25mph | PG399 | 1.65 | 2019-11-09T17:30:00Z | 6.93 | 43 | < 25mph | PG399 | 1.65 | 2019-11-09T18:20:00Z | 7.74 | 26 | < 25mph | D2539 | 7.29 | 2019-11-09T18:15:00Z | 122 | 86 | 55mph+
PG&E | 2016-08-03 | 2016-08-03 12:41 | 39.3269 | -120.6033 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100001032 |  | 12000 | Conductor | Overhead | Yes | 42585 | 2016-08-03 12:41 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0902 | 2016 | 8 | 3 | 12 | 41 | 16-0054769 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 20554 | 9.0542 | 216_312 | <25mph | <15mph | HFTD - Distribution | 2016-08-03 12:41:00 | 645 | 12.3394 | FALSE | <25mph | CISCO | 2.6 | 2015-10-31T12:30:00Z | 8.81 | 12 | < 25mph | CISCO | 2.6 | 2015-10-31T12:30:00Z | 8.81 | 16 | < 25mph | CISCO | 2.6 | 2015-10-31T12:30:00Z | 8.81 | 22 | < 25mph | CISCO | 2.6 | 2015-10-31T12:30:00Z | 8.81 | 30 | < 25mph
PG&E | 2015-02-06 06:01 | 2015-02-06 06:01 | 38.6059 | -121.0221 | Vegetation | Rural | < 3 meters | Fire Agency |  | 6661 Ryan Ranch Road, El Dorado Hills |  | 21000 | Conductor | Overhead | Yes | 42041.2507 | 2015-02-06 06:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0259 | 2015 | 2 | 6 | 6 | 1 | 15-0009876 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 51996 | 16.7927 | 199_272 | <25mph | <15mph | HFTD - Distribution | 2015-02-06 06:01:00 | 6 | 30.3484 | FALSE | 25-40mph | E8856 | 3.45 | 2018-02-04T09:35:00Z | 0 | 12 | < 25mph | BENC1 | 4.89 | 2018-02-04T08:59:00Z | 7 | 52 | < 25mph | E8856 | 3.45 | 2018-02-04T10:35:00Z | 0 | 24 | < 25mph | BENC1 | 4.89 | 2018-02-04T09:59:00Z | 8.99 | 105 | < 25mph
PG&E | 2016-07-21 21:45 | 2016-07-21 21:45 | 40.8566 | -122.3387 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101455670 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0870 | 2016 | 7 | 21 | 21 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.7351 | 143_397 | <25mph | <15mph | HFTD - Distribution | 2016-07-21 21:45:00 | 613 | 15.1303 | FALSE | <25mph | CTANT | 1.58 | 2018-12-20T21:30:00Z | 4.97 | 4 | < 25mph | PG138 | 6.77 | 2018-12-20T21:20:00Z | 10.74 | 15 | < 25mph | CTANT | 1.58 | 2018-12-20T21:30:00Z | 4.97 | 8 | < 25mph | PG138 | 6.77 | 2018-12-20T22:40:00Z | 12.28 | 30 | < 25mph
PG&E | 2015-03-14 02:30 | 2015-03-14 02:30 | 38.9038 | -122.7579 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 9210 Wildcat Road, Kelseyville |  | 12000 | Conductor | Overhead | Yes | 42077.1042 | 2015-03-14 02:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0274 | 2015 | 3 | 14 | 2 | 30 | 15-0019556 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2280 | 8.9688 | 124_289 | <25mph | <15mph | HFTD - Distribution | 2015-03-14 02:30:00 | 20 | 8.9688 | FALSE | <25mph | KELC1 | 2.83 | 2018-03-24T05:57:00Z | 32.99 | 1 | 25-40mph | KELC1 | 2.83 | 2018-03-24T05:57:00Z | 32.99 | 5 | 25-40mph | KELC1 | 2.83 | 2018-03-24T05:57:00Z | 32.99 | 2 | 25-40mph | KELC1 | 2.83 | 2018-03-24T05:57:00Z | 32.99 | 10 | 25-40mph
PG&E | 2016-08-09 | 2016-08-09 19:21 | 38.9187 | -120.9525 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | El Dorado County FD | 100038028 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0915 | 2016 | 8 | 9 | 19 | 21 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.2678 | 201_290 | <25mph | <15mph | HFTD - Distribution | 2016-08-09 19:21:00 | 658 | 10.7446 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 6.74 | 2016-07-10T16:56:00Z | 8.99 | 17 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 6.74 | 2016-07-10T17:56:00Z | 11.01 | 34 | < 25mph
PG&E | 2017-11-11 12:17 | 11:57 | 35.1191 | -120.3936 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Jordan Dayley ph#929-3911,engine#3467 | 101931190 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43050.5115 | 11:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1518 | 2017 | 11 | 11 | 11 | 57 | 17-0094408 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29093 | 8.6182 | 227_80 | <25mph | <15mph | HFTD - Distribution | 2017-11-11 11:57:00 | 1260 | 14.1707 | FALSE | <25mph | AU609 | 1.13 | 2019-10-18T07:30:00Z | 8.99 | 4 | < 25mph | PG496 | 7.78 | 2019-10-18T08:00:00Z | 25.86 | 22 | 25-40mph | AU609 | 1.13 | 2019-10-18T07:30:00Z | 8.99 | 8 | < 25mph | PG496 | 7.78 | 2019-10-18T08:10:00Z | 26.02 | 44 | 25-40mph
PG&E | 2017-05-05 15:52 | 15:52 | 40.3776 | -123.0019 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101501566 | None | 12000 | Conductor | Overhead | Yes | 42860.6614 | 15:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1084 | 2017 | 5 | 5 | 15 | 52 | 17-0045707 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 56893 | 24.5621 | 115_371 | <25mph | <15mph | HFTD - Distribution | 2017-05-05 15:52:00 | 824 | 35.0644 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | YOBC1 | 4.35 | 2016-05-21T04:35:00Z | 4.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | YOBC1 | 4.35 | 2016-05-21T04:35:00Z | 4.99 | 2 | < 25mph
PG&E | 2015-08-04 16:05 | 2015-08-04 16:05 | 40.0822 | -121.1538 | Vegetation | Rural | < 0.25 Acres | Fire Agency | USFS | 100441220 | None | 0 – 750 | Fuse | Overhead | Yes | 42220.6701 | 2015-08-04 16:05 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0511 | 2015 | 8 | 4 | 16 | 5 | 15-0052743 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 4591 | 11.3093 | 193_354 | <25mph | <15mph | HFTD - Distribution | 2015-08-04 16:05:00 | 256 | 18.1222 | FALSE | <25mph | PG129 | 3.58 | 2019-07-25T22:10:00Z | 11.41 | 6 | < 25mph | PG292 | 6.36 | 2019-07-25T22:50:00Z | 12.48 | 13 | < 25mph | PG129 | 3.58 | 2019-07-25T23:50:00Z | 12.71 | 12 | < 25mph | PG292 | 6.36 | 2019-07-25T23:20:00Z | 14.47 | 26 | < 25mph
PG&E | 2017-07-05 12:11 | 11:58 | 39.2105 | -121.2266 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVE ROBERTSON 530 906 4892 | 100010286 | Unknown | 21000 | Conductor | Overhead | Yes | 42921.5077 | 11:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1223 | 2017 | 7 | 5 | 11 | 58 | 17-0060605 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 10231 | 9.71 | 190_306 | <25mph | <15mph | HFTD - Distribution | 2017-07-05 11:58:00 | 962 | 14.0848 | FALSE | <25mph | E2572 | 2.49 | 2016-06-08T13:23:00Z | 1.01 | 12 | < 25mph | E1789 | 6.76 | 2016-06-08T13:06:00Z | 4.99 | 29 | < 25mph | E2572 | 2.49 | 2016-06-08T13:23:00Z | 1.01 | 24 | < 25mph | E1789 | 6.76 | 2016-06-08T13:06:00Z | 4.99 | 57 | < 25mph
PG&E | 2016-06-21 | 2016-06-21 16:53 | 38.4233 | -122.5448 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | KENWOOD FIRE XST | 102036904 | Yes | 0 – 750 | Conductor | Overhead | Yes | 42542 | 2016-06-21 16:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0814 | 2016 | 6 | 21 | 16 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 14.0146 | 133_263 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 16:53:00 | 556 | 14.0381 | FALSE | <25mph | KENWW | 1.1 | 2018-06-27T22:00:00Z | 9.8 | 1 | < 25mph | C3628 | 7.94 | 2018-06-27T22:16:00Z | 17 | 17 | < 25mph | KENWW | 1.1 | 2018-06-27T23:00:00Z | 12.41 | 2 | < 25mph | C3628 | 7.94 | 2018-06-27T23:16:00Z | 17 | 34 | < 25mph
PG&E | 2018-07-30 | 14:36 | 38.1987 | -120.3638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NICK WEBB ( 209) 532-7424 | 103336176 | Unknown | 17000 | Conductor | Overhead | Yes | 43311 | 14:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1800 | 2018 | 7 | 30 | 14 | 36 | 18-0065131 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18530 | 10.5817 | 227_250 | <25mph | <15mph | HFTD - Distribution | 2018-07-30 14:36:00 | 1540 | 14.4256 | FALSE | <25mph | E8204 | 0 | 2017-12-23T11:08:00Z | 0 | 8 | < 25mph | E1869 | 7.47 | 2017-12-23T10:29:00Z | 2.01 | 24 | < 25mph | E8204 | 0 | 2017-12-23T12:08:00Z | 0 | 15 | < 25mph | E1869 | 7.47 | 2017-12-23T10:29:00Z | 2.01 | 45 | < 25mph
PG&E | 2017-09-01 | 17:48 | 36.6518 | -121.7249 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MCFD | 103155761 | Unknown | 12000 | Conductor | Overhead | Yes | 42979 | 17:48 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1382 | 2017 | 9 | 1 | 17 | 48 | 17-0074898 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 8152 | 14.5474 | 167_165 | <25mph | <15mph | HFTD - Distribution | 2017-09-01 17:48:00 | 1120 | 19.9505 | FALSE | <25mph | E6666 | 3.59 | 2017-04-16T16:55:00Z | 4.99 | 4 | < 25mph | E8875 | 7.26 | 2017-04-16T17:10:00Z | 8.01 | 14 | < 25mph | E6666 | 3.59 | 2017-04-16T18:25:00Z | 8.01 | 8 | < 25mph | E8875 | 7.26 | 2017-04-16T18:25:00Z | 8.01 | 27 | < 25mph
PG&E | 2018-08-31 | 18:04 | 39.5785 | -123.3842 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102196393 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 18:04 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1873 | 2018 | 8 | 31 | 18 | 4 | 18-0075741 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18540 | 15.395 | 98_327 | <25mph | <15mph | HFTD - Distribution | 2018-08-31 18:04:00 | 1612 | 16.0884 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RDVC1 | 7.03 | 2017-05-20T13:28:00Z | 8.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | RDVC1 | 7.03 | 2017-05-20T14:28:00Z | 8.01 | 2 | < 25mph
PG&E | 2019-07-15 | 7:51 | 38.3266 | -122.568 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 42721104 |  | 12000 | Conductor | Overhead | Yes | 43661 | 7:51 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-343 | 2019 | 7 | 15 | 7 | 51 | 19-0077351 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2348 | 31.0114 | 132_257 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-07-15 07:51:00 | 1903 | 35.3209 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data | E9543 | 3.79 | 2017-04-06T20:54:00Z | 3 | 2 | < 25mph | E8654 | 7.85 | 2017-04-06T21:01:00Z | 12.01 | 21 | < 25mph
PG&E | 2015-03-04 18:44 | 2015-03-04 18:44 | 38.9995 | -122.7545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kelseyville FD | 102156367 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42067.7806 | 2015-03-04 18:44 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0271 | 2015 | 3 | 4 | 18 | 44 | 15-0017374 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29532 | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2015-03-04 18:44:00 | NA | 0 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG060 | 7.6 | 2018-09-06T05:50:00Z | 9.64 | 10 | < 25mph |  |  |  | 0 | 0 | No data | PG060 | 7.6 | 2018-09-06T05:50:00Z | 9.64 | 20 | < 25mph
PG&E | 2019-09-10 | 7:13 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 82841102 |  | 12000 | Conductor | Overhead | Yes | 43718 | 7:13 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-369 | 2019 | 9 | 10 | 7 | 13 | 19-0097264 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 23500 | 14.6244 | 147_193 | <25mph | <15mph | HFTD - Distribution | 2019-09-10 07:13:00 | 2029 | 17.7422 | FALSE | <25mph | BNDC1 | 2.84 | 2019-09-23T17:50:00Z | 15.99 | 13 | < 25mph | BNDC1 | 2.84 | 2019-09-23T17:50:00Z | 15.99 | 66 | < 25mph | BNDC1 | 2.84 | 2019-09-23T17:50:00Z | 15.99 | 26 | < 25mph | BNDC1 | 2.84 | 2019-09-23T17:50:00Z | 15.99 | 128 | < 25mph
PG&E | 2017-10-20 | 6:18 | 39.2922 | -121.0157 | Vegetation | Rural | < 3 Meters | Fire Agency | PHILLIP NUNNINK INCIDENT # 27272 | 100087647 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43028 | 6:18 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1499 | 2017 | 10 | 20 | 6 | 18 | 17-0088957 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 102410 | 6.1464 | 199_310 | <25mph | <15mph | HFTD - Distribution | 2017-10-20 06:18:00 | 1242 | 23.0997 | FALSE | <25mph | E3651 | 3.59 | 2018-09-18T18:10:00Z | 10 | 32 | < 25mph | E3651 | 3.59 | 2018-09-18T18:10:00Z | 10 | 77 | < 25mph | PG026 | 3.98 | 2018-09-18T19:10:00Z | 11.18 | 64 | < 25mph | PG026 | 3.98 | 2018-09-18T19:10:00Z | 11.18 | 151 | < 25mph
PG&E | 2017-12-14 | 17:16 | 34.5878 | -120.3566 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101911004 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 43083 | 17:16 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1538 | 2017 | 12 | 14 | 17 | 16 | 17-0101672 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2896 | 2.7073 | 229_51 | <25mph | <15mph | HFTD - Distribution | 2017-12-14 17:16:00 | 1280 | 11.3138 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2332 | 7.61 | 2016-04-07T05:34:00Z | 24.99 | 18 | < 25mph |  |  |  | 0 | 0 | No data | E2332 | 7.61 | 2016-04-07T05:34:00Z | 24.99 | 32 | < 25mph
PG&E | 2016-09-25 | 19:19 | 37.0993 | -122.1155 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire ben lomond fire | 101670837 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42638 | 19:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1003 | 2016 | 9 | 25 | 19 | 19 | 16-0067346 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1497 | 2.1111 | 150_190 | <25mph | <15mph | HFTD - Distribution | 2016-09-25 19:19:00 | 746 | 9.8702 | FALSE | <25mph | BNDC1 | 3.83 | 2018-12-06T11:50:00Z | 14 | 33 | < 25mph | BNDC1 | 3.83 | 2018-12-06T11:50:00Z | 14 | 60 | < 25mph | BNDC1 | 3.83 | 2018-12-06T11:50:00Z | 14 | 66 | < 25mph | BNDC1 | 3.83 | 2018-12-06T11:50:00Z | 14 | 122 | < 25mph
PG&E | 2016-07-15 14:09 | 2016-07-15 14:09 | 38.6965 | -120.8598 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412774 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.5896 | 2016-07-15 14:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0852 | 2016 | 7 | 15 | 14 | 9 | 16-0050274 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 11253 | 10.7453 | 205_277 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 14:09:00 | 595 | 14.2057 | FALSE | <25mph | C6129 | 0.59 | 2018-03-16T08:09:00Z | 37 | 36 | 25-40mph | C6129 | 0.59 | 2018-03-16T08:09:00Z | 37 | 75 | 25-40mph | C6129 | 0.59 | 2018-03-16T08:09:00Z | 37 | 72 | 25-40mph | C6129 | 0.59 | 2018-03-16T08:09:00Z | 37 | 148 | 25-40mph
PG&E | 2015-07-16 19:11 | 2015-07-16 19:11 | 37.1989 | -119.7712 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 20334 ROAD 400 |  | 12000 | Conductor | Overhead | Yes | 42201.7993 | 2015-07-16 19:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0465 | 2015 | 7 | 16 | 19 | 11 | 15-0048064 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 8.6422 | 254_195 | <25mph | <15mph | HFTD - Distribution | 2015-07-16 19:11:00 | 210 | 13.1745 | FALSE | <25mph | D7022 | 1.32 | 2016-05-29T03:57:00Z | 4 | 18 | < 25mph | D7022 | 1.32 | 2016-05-29T03:57:00Z | 4 | 18 | < 25mph | D7022 | 1.32 | 2016-05-29T03:57:00Z | 4 | 36 | < 25mph | D7022 | 1.32 | 2016-05-29T03:57:00Z | 4 | 36 | < 25mph
PG&E | 2015-09-10 18:39 | 2015-09-10 18:39 | 40.7569 | -123.7958 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 096/004 |  | 115000 | Conductor | Overhead | Yes | 42257.7771 | 2015-09-10 18:39 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0590 | 2015 | 9 | 10 | 18 | 39 | RM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 2.2423 | 82_393 | <25mph | <15mph | HFTD - Transmission | 2015-09-10 18:39:00 | 335 | 12.4043 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.39 | 2017-06-07T02:55:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.39 | 2017-06-07T03:55:00Z | 8.01 | 2 | < 25mph
PG&E | 2017-09-18 | 23:50 | 37.9088 | -120.4865 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | incident comander geoff marshall 209-419-4407 | 101040882 | Unknown | 17000 | Conductor | Overhead | Yes | 42996 | 23:50 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1422 | 2017 | 9 | 18 | 23 | 50 | 17-0079858 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 382303 | 9.0814 | 222_234 | <25mph | <15mph | HFTD - Distribution | 2017-09-18 23:50:00 | 1160 | 16.9339 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.23 | 2015-10-17T08:03:00Z | 4.99 | 7 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.23 | 2015-10-17T08:03:00Z | 4.99 | 15 | < 25mph
PG&E | 2017-08-27 | 20:04 | 38.9165 | -121.151 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-477-0641 x7, log 22629 | 100077184 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42974 | 20:04 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1352 | 2017 | 8 | 27 | 20 | 4 | 17-0073228 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 905 | 9.7822 | 193_290 | <25mph | <15mph | HFTD - Distribution | 2017-08-27 20:04:00 | 1090 | 16.757 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LICC1 | 6.69 | 2015-01-28T21:13:00Z | 8.99 | 22 | < 25mph |  |  |  | 0 | 0 | No data | LICC1 | 6.69 | 2015-01-28T21:13:00Z | 8.99 | 52 | < 25mph
PG&E | 2017-09-04 | 3:29 | 39.8317 | -121.8444 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102300100 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1392 | 2017 | 9 | 4 | 3 | 29 | 17-0075723 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 214974 | 9.8341 | 164_340 | <25mph | <15mph | HFTD - Distribution | 2017-09-04 03:29:00 | 1130 | 13.8789 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E3006 | 4.05 | 2018-12-25T23:30:00Z | 18.01 | 10 | < 25mph |  |  |  | 0 | 0 | No data | E3006 | 4.05 | 2018-12-25T23:30:00Z | 18.01 | 21 | < 25mph
PG&E | 2019-06-10 | 16:34 | 38.821 | -120.846 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Garden Valley FD | 153082106 |  | 21000 | Conductor | Overhead | Yes | 43626 | 16:34 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-372 | 2019 | 6 | 10 | 16 | 34 | 19-0065481 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14169 | 8.5329 | 206_284 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 16:34:00 | 1827 | 15.7607 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5691 | 5.53 | 2015-01-15T02:36:00Z | 2.01 | 36 | < 25mph |  |  |  | 0 | 0 | No data | E5691 | 5.53 | 2015-01-15T04:06:00Z | 8.01 | 72 | < 25mph
PG&E | 2017-08-31 | 11:33 | 37.1379 | -121.9966 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100519201 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 11:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1373 | 2017 | 8 | 31 | 11 | 33 | 17-0074457 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 99153 | 14.3205 | 156_192 | <25mph | <15mph | HFTD - Distribution | 2017-08-31 11:33:00 | 1111 | 14.3569 | FALSE | <25mph | D8979 | 2.5 | 2018-03-27T04:28:00Z | 8.99 | 26 | < 25mph | LSGC1 | 5.23 | 2018-03-27T04:32:00Z | 12.01 | 92 | < 25mph | D8979 | 2.5 | 2018-03-27T04:28:00Z | 8.99 | 52 | < 25mph | LSGC1 | 5.23 | 2018-03-27T05:32:00Z | 12.01 | 182 | < 25mph
PG&E | 2017-10-31 | 21:02 | 39.1119 | -122.9163 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Structure 020/003 | Unknown | 60000 | Conductor | Overhead | Yes | 43039 | 21:02 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | no-match | 1513 | 2017 | 10 | 31 | 21 | 2 | INT-10325 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | 50730 | 1.8727 | 117_301 | <25mph | <15mph | HFTD - Transmission | 2017-10-31 21:02:00 | 1255 | 9.8895 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5780 | 6.35 | 2018-09-23T05:01:00Z | 3 | 13 | < 25mph |  |  |  | 0 | 0 | No data | E5780 | 6.35 | 2018-09-23T06:16:00Z | 3 | 25 | < 25mph
PG&E | 2016-07-25 15:32 | 2016-07-25 15:32 | 38.3522 | -120.7107 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42576.6472 | 2016-07-25 15:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0878 | 2016 | 7 | 25 | 15 | 32 | 16-0052398 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 19951 | 10.4912 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-25 15:32:00 | 621 | 14.4675 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2016-01-04T12:56:00Z | 11.01 | 2 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2016-01-04T13:56:00Z | 11.01 | 4 | < 25mph
PG&E | 2015-05-06 17:17 | 2015-05-06 17:17 | 37.4273 | -119.8803 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | BOOSTER 8179 INDIAN PEEK N/O MIWUK | None | 21000 | Other | Overhead | Yes | 42130.7201 | 2015-05-06 17:17 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0307 | 2015 | 5 | 6 | 17 | 17 | 15-0032311 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 81600 | 12.4413 | 249_208 | <25mph | <15mph | HFTD - Distribution | 2015-05-06 17:17:00 | 53 | 13.2212 | FALSE | <25mph | C1522 | 2.85 | 2015-11-09T04:37:00Z | 13 | 5 | < 25mph | MPOC1 | 7.89 | 2015-11-09T05:07:00Z | 15.99 | 8 | < 25mph | C1522 | 2.85 | 2015-11-09T04:37:00Z | 13 | 6 | < 25mph | MIAC1 | 7.42 | 2015-11-09T05:59:00Z | 24.99 | 12 | < 25mph
PG&E | 2015-10-09 06:32 | 2015-10-09 06:32 | 38.364 | -122.9173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 320 Freestone St, Frestone | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0642 | 2015 | 10 | 9 | 6 | 32 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 2.6818 | 117_260 | <25mph | <15mph | HFTD - Distribution | 2015-10-09 06:32:00 | 386 | 15.5803 | FALSE | <25mph | E9690 | 2.76 | 2018-08-25T21:16:00Z | 13 | 23 | < 25mph | E9690 | 2.76 | 2018-08-25T21:16:00Z | 13 | 67 | < 25mph | E9690 | 2.76 | 2018-08-25T21:16:00Z | 13 | 45 | < 25mph | DUTWW | 4.4 | 2018-08-25T22:00:00Z | 13.2 | 133 | < 25mph
PG&E | 2018-06-23 | 9:31 | 40.8632 | -122.3962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | RYAN MEANS 530-238-2416 | 101472252 | AT&T | 12000 | Conductor | Overhead | Yes | 43274 | 9:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1688 | 2018 | 6 | 23 | 9 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2018-06-23 09:31:00 | NA | 0 | FALSE | <25mph | CTANT | 1.62 | 2018-04-03T03:30:00Z | 3.74 | 4 | < 25mph | SLFC1 | 4.17 | 2018-04-03T03:19:00Z | 20 | 9 | < 25mph | CTANT | 1.62 | 2018-04-03T05:15:00Z | 6.85 | 8 | < 25mph | SLFC1 | 4.17 | 2018-04-03T04:19:00Z | 23 | 18 | < 25mph
PG&E | 2018-06-15 | 10:05 | 38.6238 | -121.0221 | Vegetation | Rural | < 3 meters | Customer | N.A. | 101376538 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43266 | 10:05 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1661 | 2018 | 6 | 15 | 10 | 5 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 10.3423 | 199_273 | <25mph | <15mph | HFTD - Distribution | 2018-06-15 10:05:00 | 1403 | 17.1425 | FALSE | <25mph | D4314 | 3.9 | 2015-07-01T14:58:00Z | 0 | 12 | < 25mph | D7401 | 4.09 | 2015-07-01T14:18:00Z | 4.99 | 45 | < 25mph | D4314 | 3.9 | 2015-07-01T15:52:00Z | 5.99 | 24 | < 25mph | D4314 | 3.9 | 2015-07-01T15:52:00Z | 5.99 | 90 | < 25mph
PG&E | 2017-06-24 15:06 | 14:51 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 42910.6292 | 14:51 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1194 | 2017 | 6 | 24 | 14 | 51 | 17-0058332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 21296 | 10.4286 | 210_259 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 14:51:00 | 933 | 10.7263 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.33 | 2015-11-01T21:56:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.33 | 2015-11-01T21:56:00Z | 7 | 2 | < 25mph
PG&E | 2016-06-15 | 2016-06-15 13:09 | 38.4433 | -120.7568 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103169620 |  | 12000 | Conductor | Overhead | Yes | 42536 | 2016-06-15 13:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0801 | 2016 | 6 | 15 | 13 | 9 | 16-0043476 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 23963 | 15.7348 | 210_263 | <25mph | <15mph | HFTD - Distribution | 2016-06-15 13:09:00 | 543 | 16.8625 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.74 | 2015-01-15T23:56:00Z | 5.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.74 | 2015-01-16T00:56:00Z | 5.99 | 2 | < 25mph
PG&E | 2015-08-03 17:53 | 2015-08-03 17:53 | 39.3361 | -121.1894 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Pole 000/008 |  | 60000 | Conductor | Overhead | Yes | 42219.7451 | 2015-08-03 17:53 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0510 | 2015 | 8 | 3 | 17 | 53 | TM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 11.0618 | 191_313 | <25mph | <15mph | HFTD - Transmission | 2015-08-03 17:53:00 | 255 | 11.5241 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RRRC1 | 4.47 | 2016-03-09T09:13:00Z | 5.99 | 31 | < 25mph |  |  |  | 0 | 0 | No data | RRRC1 | 4.47 | 2016-03-09T10:13:00Z | 7 | 60 | < 25mph
PG&E | 2017-07-23 09:22 | 09:22 | 40.642 | -122.2302 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT? | 101459708 | FRONTIER COMMUNICATI | 12000 | Conductor | Overhead | Yes | 42939.3906 | 09:22 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1282 | 2017 | 7 | 23 | 9 | 22 | 17-0064801 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 184712 | 3.9314 | 148_385 | <25mph | <15mph | HFTD - Distribution | 2017-07-23 09:22:00 | 1021 | 13.6933 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C5599 | 5.97 | 2016-03-12T11:31:00Z | 17 | 4 | < 25mph |  |  |  | 0 | 0 | No data | C5599 | 5.97 | 2016-03-12T12:16:00Z | 20 | 8 | < 25mph
PG&E | 2018-12-12 | 12:09 | 38.727 | -120.7947 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 101404403 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43446 | 12:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1984 | 2018 | 12 | 12 | 12 | 9 | No ILIS or TOTL available | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.1462 | 208_279 | <25mph | <15mph | HFTD - Distribution | 2018-12-12 12:09:00 | 1724 | 13.5134 | FALSE | <25mph | PG068 | 1.89 | 2019-04-19T17:30:00Z | 8.12 | 50 | < 25mph | PG077 | 6.29 | 2019-04-19T17:30:00Z | 9.64 | 93 | < 25mph | C6129 | 3.65 | 2019-04-19T18:34:00Z | 12.01 | 99 | < 25mph | C6129 | 3.65 | 2019-04-19T18:34:00Z | 12.01 | 185 | < 25mph
PG&E | 2015-12-31 19:12 | 2015-12-31 19:12 | 37.1568 | -121.9868 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LOS GATOS MONTE SERENO SARATOGA | 100518215 | Verizon | 21000 | Conductor | Overhead | Yes | 42369.8 | 2015-12-31 19:12 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0689 | 2015 | 12 | 31 | 19 | 12 | 15-0087962 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7979 | 7.4149 | 156_193 | <25mph | <15mph | HFTD - Distribution | 2015-12-31 19:12:00 | 433 | 10.9251 | FALSE | <25mph | LSGC1 | 3.83 | 2019-11-06T15:32:00Z | 4 | 33 | < 25mph | SJS04 | 5.6 | 2019-11-06T15:35:00Z | 8.99 | 220 | < 25mph | LSGC1 | 3.83 | 2019-11-06T15:32:00Z | 4 | 63 | < 25mph | SJS04 | 5.6 | 2019-11-06T15:35:00Z | 8.99 | 440 | < 25mph
PG&E | 2016-09-12 | 12:38 | 38.7832 | -120.6006 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101421708 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42625 | 12:38 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0974 | 2016 | 9 | 12 | 12 | 38 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 15.5165 | 217_282 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 12:38:00 | 716 | 15.5342 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E3165 | 7.91 | 2018-03-08T07:33:00Z | 5.99 | 8 | < 25mph |  |  |  | 0 | 0 | No data | E3165 | 7.91 | 2018-03-08T07:33:00Z | 5.99 | 15 | < 25mph
PG&E | 2017-07-24 21:45 | 21:45 | 35.6024 | -120.9211 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101860186 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.9063 | 21:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1289 | 2017 | 7 | 24 | 21 | 45 | 17-0065191 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 21231 | 19.4445 | 203_107 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 21:45:00 | 1028 | 30.0108 | FALSE | 25-40mph | TABC1 | 3.74 | 2015-03-12T02:07:00Z | 5.99 | 1 | < 25mph | TABC1 | 3.74 | 2015-03-12T02:07:00Z | 5.99 | 1 | < 25mph | TABC1 | 3.74 | 2015-03-12T02:07:00Z | 5.99 | 2 | < 25mph | TABC1 | 3.74 | 2015-03-12T02:07:00Z | 5.99 | 2 | < 25mph
PG&E | 2019-08-05 | 22:38 | 37.1869 | -119.7902 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Unknown |  | 322066125092 |  | 21000 | Transformer | Overhead | Yes | 43682 | 22:38 | Equipment - Overloaded | Transformer |  |  |  |  | Other/Unknown | 2019-134 | 2019 | 8 | 5 | 22 | 38 | 19-0084586 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 996 | 7.0886 | 253_195 | <25mph | <15mph | HFTD - Distribution | 2019-08-05 22:38:00 | 1952 | 12.3468 | FALSE | <25mph | E5766 | 3.69 | 2019-02-12T01:10:00Z | 8.01 | 18 | < 25mph | E5766 | 3.69 | 2019-02-12T01:10:00Z | 8.01 | 18 | < 25mph | E5766 | 3.69 | 2019-02-12T01:10:00Z | 8.01 | 36 | < 25mph | E5766 | 3.69 | 2019-02-12T01:10:00Z | 8.01 | 36 | < 25mph
PG&E | 2015-07-26 12:25 | 2015-07-26 12:25 | 39.1586 | -121.0634 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 15499 ALLISON RANCH RD |  | 12000 | Conductor | Overhead | Yes | 42211.5174 | 2015-07-26 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0485 | 2015 | 7 | 26 | 12 | 25 | 15-0050558 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2224 | 13.0644 | 197_303 | <25mph | <15mph | HFTD - Distribution | 2015-07-26 12:25:00 | 230 | 13.6917 | FALSE | <25mph | E1789 | 3.9 | 2019-08-12T14:24:00Z | 4.99 | 10 | < 25mph | PG059 | 7.97 | 2019-08-12T14:00:00Z | 7.9 | 99 | < 25mph | E1789 | 3.9 | 2019-08-12T14:24:00Z | 4.99 | 20 | < 25mph | PG059 | 7.97 | 2019-08-12T14:00:00Z | 7.9 | 186 | < 25mph
PG&E | 2016-07-16 08:19 | 2016-07-16 08:19 | 37.4828 | -119.87 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101079104 | None | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0856 | 2016 | 7 | 16 | 8 | 19 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 2.1905 | 249_211 | <25mph | <15mph | HFTD - Distribution | 2016-07-16 08:19:00 | 599 | 13.487 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JSDC1 | 4.53 | 2017-07-01T14:47:00Z | 5.99 | 8 | < 25mph |  |  |  | 0 | 0 | No data | MPOC1 | 6.57 | 2017-07-01T16:07:00Z | 8.01 | 18 | < 25mph
PG&E | 2017-05-09 18:41 | 18:26 | 40.8689 | -123.5156 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | todd wright fire chief. 5307392493 | 103796045 | Unknown | 12000 | Conductor | Overhead | Yes | 42864.7782 | 18:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1092 | 2017 | 5 | 9 | 18 | 26 | 17-0046642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 108117 | 15.9566 | 94_399 | <25mph | <15mph | HFTD - Distribution | 2017-05-09 18:26:00 | 832 | 17.9691 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8984 | 6.51 | 2018-11-28T05:16:00Z | 0 | 4 | < 25mph |  |  |  | 0 | 0 | No data | D8984 | 6.51 | 2018-11-28T06:17:00Z | 0 | 8 | < 25mph
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 9:36 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 14.8685 | 222_261 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 09:36:00 | 925 | 23.4839 | FALSE | <25mph | PG178 | 3.94 | 2019-12-29T11:00:00Z | 8.84 | 10 | < 25mph | ULBC1 | 6.95 | 2019-12-29T10:33:00Z | 10 | 58 | < 25mph | PG178 | 3.94 | 2019-12-29T11:10:00Z | 10.29 | 20 | < 25mph | PG178 | 3.94 | 2019-12-29T11:10:00Z | 10.29 | 118 | < 25mph
PG&E | 2018-02-07 | 9:16 | 38.0369 | -120.2096 | Vegetation | Rural | < 3 meters | Fire Agency | Jason Podesta 209-586-3362 | 101038120 | AT&T | 17000 | Conductor | Overhead | Yes | 43138 | 9:16 | Contact From Object | N.A. | Other | Electric Facility | Human Error | third-party caused | Other/Unknown | 1559 | 2018 | 2 | 7 | 9 | 16 | 18-0012146 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 78738 | 9.6764 | 234_241 | <25mph | <15mph | HFTD - Distribution | 2018-02-07 09:16:00 | 1301 | 13.44 | FALSE | <25mph | MOUC1 | 2.73 | 2015-02-06T06:02:00Z | 21 | 1 | < 25mph | MOUC1 | 2.73 | 2015-02-06T06:02:00Z | 21 | 1 | < 25mph | MOUC1 | 2.73 | 2015-02-06T07:02:00Z | 27 | 2 | 25-40mph | MOUC1 | 2.73 | 2015-02-06T07:02:00Z | 27 | 2 | 25-40mph
PG&E | 2016-06-03 | 2016-06-03 12:16 | 38.6435 | -120.6959 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | cal-fire and usfs | 103119737 |  | 21000 | Conductor | Overhead | Yes | 42524 | 2016-06-03 12:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0764 | 2016 | 6 | 3 | 12 | 16 | 16-0040808 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 101354 | 7.6436 | 213_274 | <25mph | <15mph | HFTD - Distribution | 2016-06-03 12:16:00 | 507 | 11.74 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6490 | 7.82 | 2017-06-14T20:08:00Z | 10 | 16 | < 25mph |  |  |  | 0 | 0 | No data | E6490 | 7.82 | 2017-06-14T21:04:00Z | 12.01 | 32 | < 25mph
PG&E | 2017-08-31 | 11:33 | 37.1379 | -121.9966 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100519201 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 11:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1373 | 2017 | 8 | 31 | 11 | 33 | 17-0074457 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 99153 | 14.3205 | 156_192 | <25mph | <15mph | HFTD - Distribution | 2017-08-31 11:33:00 | 1111 | 14.3569 | FALSE | <25mph | AP191 | 3.71 | 2015-01-14T01:34:00Z | 10 | 20 | < 25mph | D3546 | 7.44 | 2015-01-14T02:20:00Z | 10 | 97 | < 25mph | D8979 | 2.5 | 2015-01-14T03:27:00Z | 11.99 | 43 | < 25mph | D8979 | 2.5 | 2015-01-14T03:27:00Z | 11.99 | 203 | < 25mph
PG&E | 2018-10-21 | 0:32 | 35.5035 | -120.6025 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101886776 | Unknown | 21000 | Conductor | Overhead | Yes | 43394 | 0:32 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1948 | 2018 | 10 | 21 | 0 | 32 | 18-0092526 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 302559 | 9.0366 | 217_101 | <25mph | <15mph | HFTD - Distribution | 2018-10-21 00:32:00 | 1687 | 16.4549 | FALSE | <25mph | PG238 | 2.34 | 2019-04-02T12:50:00Z | 17.54 | 18 | < 25mph | PG210 | 7.37 | 2019-04-02T12:20:00Z | 26.31 | 55 | 25-40mph | PG238 | 2.34 | 2019-04-02T12:50:00Z | 17.54 | 36 | < 25mph | PG210 | 7.37 | 2019-04-02T12:20:00Z | 26.31 | 112 | 25-40mph
PG&E | 2018-07-29 | 17:29 | 38.5777 | -120.8556 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101383255 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43310 | 17:29 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1797 | 2018 | 7 | 29 | 17 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.882 | 206_271 | <25mph | <15mph | HFTD - Distribution | 2018-07-29 17:29:00 | 1537 | 11.0812 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BENC1 | 4.31 | 2016-09-22T10:59:00Z | 4.99 | 25 | < 25mph |  |  |  | 0 | 0 | No data | BENC1 | 4.31 | 2016-09-22T11:59:00Z | 8.99 | 50 | < 25mph
PG&E | 2015-02-23 02:05 | 2015-02-23 02:05 | 39.3027 | -121.0175 | Vegetation | Rural | < 3 meters | Fire Agency | NEVADA CITY FIRE | 100086316 |  | 12000 | Conductor | Overhead | Yes | 42058.0868 | 2015-02-23 02:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0267 | 2015 | 2 | 23 | 2 | 5 | 15-0014910 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 93279 | 24.5459 | 199_311 | <25mph | <15mph | HFTD - Distribution | 2015-02-23 02:05:00 | 14 | 25.6662 | FALSE | 25-40mph | E3651 | 2.92 | 2017-12-26T04:05:00Z | 0 | 12 | < 25mph | RRRC1 | 5.33 | 2017-12-26T03:13:00Z | 4.99 | 69 | < 25mph | E3651 | 2.92 | 2017-12-26T05:05:00Z | 0 | 24 | < 25mph | RRRC1 | 5.33 | 2017-12-26T04:13:00Z | 4.99 | 138 | < 25mph
PG&E | 2019-10-04 | 19:07 | 40.4964 | -122.0448 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | Yes | 43742 | 19:07 | Equipment - Overloaded | Other |  |  |  |  | no-match | 2019-257 | 2019 | 10 | 4 | 19 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 6.2955 | 155_377 | <25mph | <15mph | HFTD - Distribution | 2019-10-04 19:07:00 | 2076 | 10.3362 | FALSE | <25mph | PG107 | 2.58 | 2019-02-02T02:20:00Z | 12.28 | 6 | < 25mph | PG107 | 2.58 | 2019-02-02T02:20:00Z | 12.28 | 6 | < 25mph | PG107 | 2.58 | 2019-02-02T04:00:00Z | 12.48 | 12 | < 25mph | PG107 | 2.58 | 2019-02-02T04:00:00Z | 12.48 | 12 | < 25mph
PG&E | 2017-09-11 | 8:50 | 36.9515 | -121.842 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101790954 | PACIFIC BELL | 21000 | Fuse | Overhead | Yes | 42989 | 8:50 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | no-match | 1408 | 2017 | 9 | 11 | 8 | 50 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | N.A. | 9.6414 | 162_181 | <25mph | <15mph | HFTD - Distribution | 2017-09-11 08:50:00 | 1146 | 17.9559 | FALSE | <25mph | E7291 | 2.85 | 2017-11-16T02:55:00Z | 4.99 | 33 | < 25mph | E7291 | 2.85 | 2017-11-16T02:55:00Z | 4.99 | 59 | < 25mph | E7291 | 2.85 | 2017-11-16T03:54:00Z | 5.99 | 66 | < 25mph | E7291 | 2.85 | 2017-11-16T03:54:00Z | 5.99 | 119 | < 25mph
PG&E | 2018-09-16 | 8:26 | 35.3046 | -120.6389 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | Pole 4/23A | None | 70000 | Conductor | Overhead | Yes | 43359 | 8:26 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1903 | 2018 | 9 | 16 | 8 | 26 | INT-11371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 29925 | 32.6873 | 216_90 | 25-40mph | 30-45mph | HFTD - Transmission | 2018-09-16 08:26:00 | 1642 | 35.3808 | FALSE | 25-40mph | ARGC1 | 2.25 | 2017-12-20T14:54:00Z | 2.01 | 1 | < 25mph | ARGC1 | 2.25 | 2017-12-20T14:54:00Z | 2.01 | 4 | < 25mph | ARGC1 | 2.25 | 2017-12-20T15:54:00Z | 3 | 2 | < 25mph | ARGC1 | 2.25 | 2017-12-20T15:54:00Z | 3 | 6 | < 25mph
PG&E | 2018-09-14 | 15:08 | 35.328 | -120.6982 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Sean Hernandez Cell # 805 903 3423 | 103400199 | Unknown | 12000 | Conductor | Overhead | Yes | 43357 | 15:08 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1898 | 2018 | 9 | 14 | 15 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 24.1105 | 213_92 | <25mph | <15mph | HFTD - Distribution | 2018-09-14 15:08:00 | 1637 | 24.1304 | FALSE | <25mph | ARGC1 | 2.05 | 2016-08-11T06:54:00Z | 0 | 1 | < 25mph | E6113 | 7.29 | 2016-08-11T07:12:00Z | 3 | 5 | < 25mph | ARGC1 | 2.05 | 2016-08-11T07:54:00Z | 2.01 | 2 | < 25mph | E6113 | 7.29 | 2016-08-11T08:13:00Z | 4 | 10 | < 25mph
PG&E | 2016-04-21 09:25 | 2016-04-21 09:25 | 39.293 | -123.769 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 103312287 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0711 | 2016 | 4 | 21 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 8.8774 | 81_312 | <25mph | <15mph | HFTD - Distribution | 2016-04-21 09:25:00 | 455 | 20.2474 | FALSE | <25mph | E6025 | 0.21 | 2016-03-27T16:45:00Z | 12.01 | 4 | < 25mph | E6025 | 0.21 | 2016-03-27T16:45:00Z | 12.01 | 4 | < 25mph | E6025 | 0.21 | 2016-03-27T18:00:00Z | 12.01 | 8 | < 25mph | E6025 | 0.21 | 2016-03-27T18:00:00Z | 12.01 | 8 | < 25mph
PG&E | 2018-07-24 | 13:47 | 39.0606 | -123.4456 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102212216 | Unknown | 12000 | Conductor | Overhead | Yes | 43305 | 13:47 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1786 | 2018 | 7 | 24 | 13 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 16.5971 | 95_299 | <25mph | <15mph | HFTD - Distribution | 2018-07-24 13:47:00 | 1526 | 19.7448 | FALSE | <25mph | E1763 | 3.79 | 2016-12-30T04:47:00Z | 4.99 | 4 | < 25mph | BNVC1 | 7.27 | 2016-12-30T03:50:00Z | 5.99 | 5 | < 25mph | E1763 | 3.79 | 2016-12-30T04:47:00Z | 4.99 | 8 | < 25mph | BNVC1 | 7.27 | 2016-12-30T04:50:00Z | 14 | 10 | < 25mph
PG&E | 2018-06-05 | 10:13 | 40.6183 | -122.3173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JASON COLLINS 530-225-4628 | 101467801 | None | 12000 | Conductor | Overhead | Yes | 43256 | 10:13 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1631 | 2018 | 6 | 5 | 10 | 13 | 18-0047539 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 277 | 7.1547 | 144_384 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 10:13:00 | 1373 | 12.6046 | FALSE | <25mph | PG516 | 2.82 | 2019-08-15T07:40:00Z | 4.38 | 18 | < 25mph | RRAC1 | 7.21 | 2019-08-15T07:24:00Z | 10 | 55 | < 25mph | PG516 | 2.82 | 2019-08-15T08:00:00Z | 5.03 | 36 | < 25mph | RRAC1 | 7.21 | 2019-08-15T07:24:00Z | 10 | 110 | < 25mph
PG&E | 2018-07-09 | 7:27 | 35.0785 | -120.3948 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101861366 | Unknown | 12000 | Conductor | Overhead | Yes | 43290 | 7:27 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1735 | 2018 | 7 | 9 | 7 | 27 | 18-0057904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 21045 | 9.782 | 227_78 | <25mph | <15mph | HFTD - Distribution | 2018-07-09 07:27:00 | 1475 | 17.5911 | FALSE | <25mph | AU609 | 1.69 | 2017-06-30T21:19:00Z | 12.01 | 4 | < 25mph | AU609 | 1.69 | 2017-06-30T21:19:00Z | 12.01 | 10 | < 25mph | AU609 | 1.69 | 2017-06-30T22:34:00Z | 12.01 | 8 | < 25mph | AU609 | 1.69 | 2017-06-30T22:34:00Z | 12.01 | 20 | < 25mph
PG&E | 2019-06-10 | 16:18 | 38.1107 | -122.9025 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 42291101 |  | 12000 | Conductor | Overhead | Yes | 43626 | 16:18 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-401 | 2019 | 6 | 10 | 16 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.6937 | 117_246 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 16:18:00 | 1826 | 12.047 | FALSE | <25mph | PG046 | 2.87 | 2018-12-03T06:10:00Z | 16.67 | 18 | < 25mph | PG046 | 2.87 | 2018-12-03T06:10:00Z | 16.67 | 18 | < 25mph | PG046 | 2.87 | 2018-12-03T07:50:00Z | 20.18 | 36 | < 25mph | PG046 | 2.87 | 2018-12-03T07:50:00Z | 20.18 | 36 | < 25mph
PG&E | 2018-10-24 | 14:18 | 36.7265 | -119.1086 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CHRIS CHRISTOPHERSON (559)493-4320 I.C #18CAFKUO15649 | 100691946 | None | 12000 | Conductor | Overhead | Yes | 43397 | 14:18 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1950 | 2018 | 10 | 24 | 14 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 7.8375 | 283_170 | <25mph | <15mph | HFTD - Distribution | 2018-10-24 14:18:00 | 1689 | 7.8887 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AV176 | 5.39 | 2019-03-23T06:36:00Z | 4.99 | 16 | < 25mph |  |  |  | 0 | 0 | No data | AV176 | 5.39 | 2019-03-23T07:41:00Z | 8.01 | 32 | < 25mph
PG&E | 2017-12-07 12:26 | 12:25 | 34.7115 | -120.1772 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 015/220 | Unknown | 115000 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1534 | 2017 | 12 | 7 | 12 | 25 | 17-0097211 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 4.373 | 237_58 | <25mph | <15mph | HFTD - Transmission | 2017-12-07 12:25:00 | 1276 | 13.3077 | FALSE | <25mph |  |  |  | 0 | 0 | No data | SXWC1 | 7.67 | 2018-04-30T13:09:00Z | 4.99 | 7 | < 25mph |  |  |  | 0 | 0 | No data | SXWC1 | 7.67 | 2018-04-30T14:09:00Z | 4.99 | 14 | < 25mph
PG&E | 2017-09-06 | 20:08 | 37.2925 | -122.294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100256917 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1400 | 2017 | 9 | 6 | 20 | 8 | 17-0076502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4914 | 6.7999 | 143_200 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 20:08:00 | 1138 | 13.6021 | FALSE | <25mph | LAHC1 | 2.3 | 2016-02-25T13:07:00Z | 5.99 | 1 | < 25mph | LAHC1 | 2.3 | 2016-02-25T13:07:00Z | 5.99 | 14 | < 25mph | LAHC1 | 2.3 | 2016-02-25T14:07:00Z | 5.99 | 2 | < 25mph | LAHC1 | 2.3 | 2016-02-25T14:07:00Z | 5.99 | 27 | < 25mph
PG&E | 2017-08-30 | 18:21 | 40.6243 | -122.3039 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CASHU008896 | 103151338 | YES | 12000 | Conductor | Overhead | Yes | 42977 | 18:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1369 | 2017 | 8 | 30 | 18 | 21 | 17-0074287 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 76344 | 5.8461 | 145_384 | <25mph | <15mph | HFTD - Distribution | 2017-08-30 18:21:00 | 1107 | 16.2636 | FALSE | <25mph | C5599 | 2.06 | 2019-04-30T12:26:00Z | 8.99 | 12 | < 25mph | RRAC1 | 7.52 | 2019-04-30T12:24:00Z | 14.99 | 25 | < 25mph | C5599 | 2.06 | 2019-04-30T13:56:00Z | 10 | 20 | < 25mph | RRAC1 | 7.52 | 2019-04-30T12:24:00Z | 14.99 | 46 | < 25mph
PG&E | 2019-07-06 | 14:22 | 34.6388 | -119.9695 |  | Herbaceous | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | 182721104 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43652 | 14:22 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-153 | 2019 | 7 | 6 | 14 | 22 | 19-0074960 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 14213 | 21.2189 | 246_54 | <25mph | <15mph | HFTD - Distribution | 2019-07-06 14:22:00 | 1888 | 23.8361 | FALSE | <25mph |  |  |  | 0 | 0 | No data | UCSE | 5.59 | 2017-09-03T18:00:00Z | 14.2 | 12 | < 25mph |  |  |  | 0 | 0 | No data | UCSE | 5.59 | 2017-09-03T19:00:00Z | 17 | 22 | < 25mph
PG&E | 2015-05-21 09:23 | 2015-05-21 09:23 | 38.5996 | -122.9935 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 4 SPANS LOAD SIDE 2993 |  | 12000 | Conductor | Overhead | Yes | 42145.391 | 2015-05-21 09:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0324 | 2015 | 5 | 21 | 9 | 23 | 15-0035686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2850 | 1.6525 | 114_273 | <25mph | <15mph | HFTD - Distribution | 2015-05-21 09:23:00 | 70 | 15.124 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AR798 | 6.08 | 2019-02-04T12:08:00Z | 7 | 38 | < 25mph |  |  |  | 0 | 0 | No data | AR798 | 6.08 | 2019-02-04T12:25:00Z | 7 | 73 | < 25mph
PG&E | 2019-07-13 | 13:13 | 34.7273 | -120.4357 |  | Shrub | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | Y44 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43659 | 13:13 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-154 | 2019 | 7 | 13 | 13 | 13 | 19-0077070 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 18256 | 12.2026 | 225_58 | <25mph | <15mph | HFTD - Distribution | 2019-07-13 13:13:00 | 1900 | 12.8932 | FALSE | <25mph | D4531 | 2.22 | 2015-03-01T22:52:00Z | 14.99 | 5 | < 25mph | D4531 | 2.22 | 2015-03-01T22:52:00Z | 14.99 | 17 | < 25mph | VDBC1 | 3.58 | 2015-03-01T23:22:00Z | 15.99 | 10 | < 25mph | VDBC1 | 3.58 | 2015-03-01T23:22:00Z | 15.99 | 34 | < 25mph
PG&E | 2019-08-16 | 8:19 | 40.1235 | -123.8758 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Self Extinguished |  | 192221102-2101118022{5563} |  | 12000 | Conductor | Overhead | Yes | 43693 | 8:19 | Vegetation | [5 empty] | Other/Unknown |  | 2019 | 8 | 16 | 8 | 19 | 19-0088744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 2979 | 5.7689 | 78_358 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 08:19:00 | 1983 | 18.468 | FALSE | <25mph | ERCC1 | 2.93 | 2016-04-06T06:28:00Z | 4 | 1 | < 25mph | AV037 | 6 | 2016-04-06T06:43:00Z | 4 | 4 | < 25mph | ERCC1 | 2.93 | 2016-04-06T07:28:00Z | 4 | 2 | < 25mph | AV037 | 6 | 2016-04-06T06:43:00Z | 4 | 8 | < 25mph
PG&E | 2019-07-27 | 4:51 | 37.9486 | -120.4656 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 163781705 |  | 17000 | Conductor | Overhead | Yes | 43673 | 4:51 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-385 | 2019 | 7 | 27 | 4 | 51 | 19-0081744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 1364 | 13.5826 | 223_236 | <25mph | <15mph | HFTD - Distribution | 2019-07-27 04:51:00 | 1934 | 16.9934 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F0305 | 5.84 | 2017-03-04T06:25:00Z | 0 | 12 | < 25mph |  |  |  | 0 | 0 | No data | F0305 | 5.84 | 2017-03-04T07:25:00Z | 0 | 24 | < 25mph
PG&E | 2016-11-09 | 9:06 | 37.4532 | -119.6413 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | US FOREST SERVICE | 101017062 |  | 12000 | Conductor | Overhead | Yes | 42683 | 9:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1046 | 2016 | 11 | 9 | 9 | 6 | 16-0078863 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1586 | 6.3162 | 259_209 | <25mph | <15mph | HFTD - Distribution | 2016-11-09 09:06:00 | 787 | 14.6769 | FALSE | <25mph | D0826 | 0.25 | 2015-06-28T17:31:00Z | 4 | 2 | < 25mph | AT301 | 7.85 | 2015-06-28T17:37:00Z | 11.01 | 26 | < 25mph | D0826 | 0.25 | 2015-06-28T18:01:00Z | 4.99 | 4 | < 25mph | D7171 | 6.85 | 2015-06-28T18:15:00Z | 15.99 | 53 | < 25mph
PG&E | 2019-08-05 | 22:38 | 37.1869 | -119.7902 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Unknown |  | 322066125092 |  | 21000 | Transformer | Overhead | Yes | 43682 | 22:38 | Equipment - Overloaded | Transformer |  |  |  |  | Other/Unknown | 2019-134 | 2019 | 8 | 5 | 22 | 38 | 19-0084586 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 996 | 7.0886 | 253_195 | <25mph | <15mph | HFTD - Distribution | 2019-08-05 22:38:00 | 1952 | 12.3468 | FALSE | <25mph | D7022 | 1.42 | 2015-09-08T12:51:00Z | 1.01 | 18 | < 25mph | D7022 | 1.42 | 2015-09-08T12:51:00Z | 1.01 | 18 | < 25mph | D7022 | 1.42 | 2015-09-08T13:41:00Z | 1.01 | 36 | < 25mph | D7022 | 1.42 | 2015-09-08T13:41:00Z | 1.01 | 36 | < 25mph
PG&E | 2017-09-18 | 13:01 | 39.3889 | -121.4054 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 103795057 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42996 | 13:01 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1418 | 2017 | 9 | 18 | 13 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 17.7047 | 182_316 | <25mph | <15mph | HFTD - Distribution | 2017-09-18 13:01:00 | 1156 | 19.5678 | FALSE | <25mph | PG290 | 0.32 | 2019-10-26T16:10:00Z | 4.09 | 7 | < 25mph | PG309 | 7.97 | 2019-10-26T16:00:00Z | 9.73 | 49 | < 25mph | PG290 | 0.32 | 2019-10-26T17:20:00Z | 6.35 | 14 | < 25mph | PG309 | 7.97 | 2019-10-26T16:50:00Z | 9.93 | 98 | < 25mph
PG&E | 2019-04-09 | 14:07 | 34.6311 | -119.9813 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Fire Dept | Santa Barbra County FD | 101863014 |  | 12000 | Conductor | Overhead | Yes | 43564 | 14:07 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-263 | 2019 | 4 | 9 | 14 | 7 | 19-0040969 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 70756 | 38.5369 | 246_53 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-09 14:07:00 | 1737 | 43.1384 | FALSE | 40-55mph |  |  |  | 0 | 0 | No data | SXWC1 | 5.08 | 2018-03-23T07:09:00Z | 17 | 13 | < 25mph |  |  |  | 0 | 0 | No data | SXWC1 | 5.08 | 2018-03-23T07:09:00Z | 17 | 25 | < 25mph
PG&E | 2016-06-21 | 2016-06-21 10:09 | 39.0294 | -121.2927 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100024816 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | no-match | 0813 | 2016 | 6 | 21 | 10 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 5.0939 | 187_296 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 10:09:00 | 555 | 12.3682 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5440 | 6.7 | 2015-05-16T18:55:00Z | 14.99 | 16 | < 25mph |  |  |  | 0 | 0 | No data | E5440 | 6.7 | 2015-05-16T18:55:00Z | 14.99 | 31 | < 25mph
PG&E | 2019-03-19 | 12:52 | 37.9956 | -120.3244 | Tree - cutting, 3rd party | Hardwood Forest | 1 meter - < 3 meters | Self Extinguished |  | 101045032 |  | 17000 | Conductor | Overhead | Yes | 43543 | 12:52 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-187 | 2019 | 3 | 19 | 12 | 52 | 19-0035101 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 70602 | 12.9023 | 229_239 | <25mph | <15mph | HFTD - Distribution | 2019-03-19 12:52:00 | 1736 | 14.3226 | FALSE | <25mph | PG058 | 1.64 | 2019-01-02T21:50:00Z | 8.99 | 18 | < 25mph | PG167 | 5.03 | 2019-01-02T21:50:00Z | 10.29 | 59 | < 25mph | PG058 | 1.64 | 2019-01-02T21:50:00Z | 8.99 | 36 | < 25mph | PG157 | 7.1 | 2019-01-02T23:20:00Z | 10.29 | 118 | < 25mph
PG&E | 2015-06-08 14:18 | 2015-06-08 14:18 | 38.1796 | -120.959 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 102048579 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42163.5958 | 2015-06-08 14:18 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0360 | 2015 | 6 | 8 | 14 | 18 | 15-0039368 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 65168 | 7.0021 | 201_249 | <25mph | <15mph | HFTD - Distribution | 2015-06-08 14:18:00 | 106 | 9.7763 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CMAC1 | 5.88 | 2018-12-22T17:59:00Z | 4 | 2 | < 25mph |  |  |  | 0 | 0 | No data | CMAC1 | 5.88 | 2018-12-22T18:59:00Z | 8.01 | 3 | < 25mph
PG&E | 2015-08-03 17:53 | 2015-08-03 17:53 | 39.3361 | -121.1894 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Pole 000/008 |  | 60000 | Conductor | Overhead | Yes | 42219.7451 | 2015-08-03 17:53 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0510 | 2015 | 8 | 3 | 17 | 53 | TM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 11.0618 | 191_313 | <25mph | <15mph | HFTD - Transmission | 2015-08-03 17:53:00 | 255 | 11.5241 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RRRC1 | 4.47 | 2016-08-10T05:13:00Z | 7 | 31 | < 25mph |  |  |  | 0 | 0 | No data | RRRC1 | 4.47 | 2016-08-10T05:13:00Z | 7 | 61 | < 25mph
PG&E | 2018-10-14 | 20:08 | 38.8935 | -120.8497 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103674516 | Unknown | 21000 | Conductor | Overhead | Yes | 43387 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1940 | 2018 | 10 | 14 | 20 | 8 | 18-0090299 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 48095 | 8.663 | 206_288 | <25mph | <15mph | HFTD - Distribution | 2018-10-14 20:08:00 | 1679 | 24.0259 | FALSE | <25mph | PG180 | 3.73 | 2019-12-06T05:10:00Z | 5.35 | 24 | < 25mph | BDMC1 | 7.81 | 2019-12-06T04:36:00Z | 14 | 37 | < 25mph | PG180 | 3.73 | 2019-12-06T05:20:00Z | 5.7 | 48 | < 25mph | BDMC1 | 7.81 | 2019-12-06T04:36:00Z | 14 | 74 | < 25mph
PG&E | 2016-07-15 14:09 | 2016-07-15 14:09 | 38.6965 | -120.8598 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412774 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.5896 | 2016-07-15 14:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0852 | 2016 | 7 | 15 | 14 | 9 | 16-0050274 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 11253 | 10.7453 | 205_277 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 14:09:00 | 595 | 14.2057 | FALSE | <25mph | PG027 | 3.79 | 2019-01-19T08:40:00Z | 9.22 | 48 | < 25mph | PG181 | 5.82 | 2019-01-19T08:50:00Z | 9.22 | 111 | < 25mph | PG027 | 3.79 | 2019-01-19T09:20:00Z | 9.22 | 96 | < 25mph | PG068 | 5.97 | 2019-01-19T09:20:00Z | 12.06 | 222 | < 25mph
PG&E | 2015-09-25 17:28 | 2015-09-25 17:28 | 38.7169 | -120.7693 | Vegetation | Rural | < 0.25 Acres | Fire Agency | el dorado F D | 101405928 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42272.7278 | 2015-09-25 17:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0616 | 2015 | 9 | 25 | 17 | 28 | 15-0063666 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 111180 | 8.3925 | 209_279 | <25mph | <15mph | HFTD - Distribution | 2015-09-25 17:28:00 | 361 | 11.4196 | FALSE | <25mph | E6490 | 3.78 | 2015-02-15T22:53:00Z | 5.99 | 22 | < 25mph | C6129 | 4.54 | 2015-02-15T23:19:00Z | 8.01 | 45 | < 25mph | E6490 | 3.78 | 2015-02-15T22:53:00Z | 5.99 | 46 | < 25mph | C6129 | 4.54 | 2015-02-15T23:19:00Z | 8.01 | 93 | < 25mph
PG&E | 2015-09-18 17:05 | 2015-09-18 17:05 | 37.8992 | -120.4551 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101019893 |  | 17000 | Conductor | Overhead | Yes | 42265.7118 | 2015-09-18 17:05 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0602 | 2015 | 9 | 18 | 17 | 5 | 15-0062207 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 35222 | 9.055 | 223_234 | <25mph | <15mph | HFTD - Distribution | 2015-09-18 17:05:00 | 347 | 11.0018 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.2 | 2017-11-11T18:03:00Z | 4.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.2 | 2017-11-11T19:03:00Z | 7 | 2 | < 25mph
PG&E | 2018-08-31 | 18:04 | 39.5785 | -123.3842 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102196393 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 18:04 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1873 | 2018 | 8 | 31 | 18 | 4 | 18-0075741 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18540 | 15.395 | 98_327 | <25mph | <15mph | HFTD - Distribution | 2018-08-31 18:04:00 | 1612 | 16.0884 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RDVC1 | 7.03 | 2015-11-06T21:28:00Z | 8.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | RDVC1 | 7.03 | 2015-11-06T22:28:00Z | 8.01 | 2 | < 25mph
PG&E | 2018-06-22 | 17:44 | 37.2485 | -119.5625 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Madera County | 101117749 | None | 0 – 750 | Conductor | Overhead | Yes | 43273 | 17:44 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1686 | 2018 | 6 | 22 | 17 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 10.123 | 263_198 | <25mph | <15mph | HFTD - Distribution | 2018-06-22 17:44:00 | 1428 | 12.3323 | FALSE | <25mph | NFRC1 | 3.29 | 2018-08-27T00:55:00Z | 11.01 | 1 | < 25mph | NFRC1 | 3.29 | 2018-08-27T00:55:00Z | 11.01 | 38 | < 25mph | NFRC1 | 3.29 | 2018-08-27T00:55:00Z | 11.01 | 2 | < 25mph | NFRC1 | 3.29 | 2018-08-27T00:55:00Z | 11.01 | 64 | < 25mph
PG&E | 2016-06-21 | 2016-06-21 10:09 | 39.0294 | -121.2927 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100024816 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | no-match | 0813 | 2016 | 6 | 21 | 10 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 5.0939 | 187_296 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 10:09:00 | 555 | 12.3682 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D7902 | 7.03 | 2017-07-02T15:35:00Z | 8.99 | 16 | < 25mph |  |  |  | 0 | 0 | No data | D7902 | 7.03 | 2017-07-02T15:35:00Z | 8.99 | 32 | < 25mph
PG&E | 2016-09-12 | 12:38 | 38.7832 | -120.6006 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101421708 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42625 | 12:38 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0974 | 2016 | 9 | 12 | 12 | 38 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 15.5165 | 217_282 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 12:38:00 | 716 | 15.5342 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TT260 | 7.42 | 2015-07-24T08:25:00Z | 4.99 | 7 | < 25mph |  |  |  | 0 | 0 | No data | TT260 | 7.42 | 2015-07-24T08:25:00Z | 4.99 | 14 | < 25mph
PG&E | 2016-09-20 | 8:25 | 40.0044 | -123.7871 | Vegetation | RURAL | < 3 meters | Self Extinguished | N.A. | 100992643 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42633 | 8:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0990 | 2016 | 9 | 20 | 8 | 25 | 16-0065910 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 798 | 11.2567 | 82_351 | <25mph | <15mph | HFTD - Distribution | 2016-09-20 08:25:00 | 732 | 20.9022 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AV037 | 4.73 | 2016-01-22T14:23:00Z | 2.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | AV037 | 4.73 | 2016-01-22T14:23:00Z | 2.01 | 6 | < 25mph
PG&E | 2015-06-12 23:32 | 2015-06-12 23:32 | 39.2308 | -121.1559 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 10903 PROSPECTOR RD ROUGH AND READY | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42167.9806 | 2015-06-12 23:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0380 | 2015 | 6 | 12 | 23 | 32 | 15-0040789 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 20 | 12.2901 | 193_307 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 23:32:00 | 126 | 14.4252 | FALSE | <25mph | E6355 | 3.14 | 2018-08-25T22:02:00Z | 13 | 12 | < 25mph | E6355 | 3.14 | 2018-08-25T22:02:00Z | 13 | 52 | < 25mph | E6355 | 3.14 | 2018-08-25T22:02:00Z | 13 | 24 | < 25mph | RRRC1 | 5.44 | 2018-08-25T23:13:00Z | 17 | 104 | < 25mph
PG&E | 2015-10-30 17:13 | 2015-10-30 17:13 | 38.3166 | -120.7226 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 7600 HWY 49, Jackson | None | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0662 | 2015 | 10 | 30 | 17 | 13 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 8.0122 | 211_256 | <25mph | <15mph | HFTD - Distribution | 2015-10-30 17:13:00 | 406 | 12.822 | FALSE | <25mph | PG372 | 2.84 | 2019-09-07T04:50:00Z | 11.25 | 7 | < 25mph | PG372 | 2.84 | 2019-09-07T04:50:00Z | 11.25 | 52 | < 25mph | PG372 | 2.84 | 2019-09-07T04:50:00Z | 11.25 | 13 | < 25mph | PG372 | 2.84 | 2019-09-07T04:50:00Z | 11.25 | 97 | < 25mph
PG&E | 2019-09-12 | 14:25 | 37.3144 | -122.1865 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 024131103 |  | 12000 | Conductor | Overhead | Yes | 43720 | 14:25 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-217 | 2019 | 9 | 12 | 14 | 25 | 19-0098386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 89097 | 5.2412 | 147_201 | <25mph | <15mph | HFTD - Distribution | 2019-09-12 14:25:00 | 2036 | 15.0249 | FALSE | <25mph | AU836 | 3.83 | 2019-01-31T09:00:00Z | 10 | 39 | < 25mph | AU836 | 3.83 | 2019-01-31T09:00:00Z | 10 | 119 | < 25mph | PG152 | 1.17 | 2019-01-31T10:50:00Z | 15.77 | 80 | < 25mph | PG152 | 1.17 | 2019-01-31T10:50:00Z | 15.77 | 238 | < 25mph
PG&E | 2016-07-16 00:58 | 2016-07-16 00:58 | 36.4379 | -121.9198 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101669758 |  | 12000 | Other | Overhead | Yes | 42567.0403 | 2016-07-16 00:58 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0855 | 2016 | 7 | 16 | 0 | 58 | 16-0050335 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 8976 | 11.1025 | 159_153 | <25mph | <15mph | HFTD - Distribution | 2016-07-16 00:58:00 | 598 | 18.5622 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6019 | 7.86 | 2018-09-09T21:30:00Z | 7 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6019 | 7.86 | 2018-09-09T23:01:00Z | 7 | 8 | < 25mph
PG&E | 2015-09-19 09:51 | 2015-09-19 09:51 | 38.4755 | -122.9069 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FORESTVILLE | 103334444 |  | 12000 | Conductor | Overhead | Yes | 42266.4104 | 2015-09-19 09:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0603 | 2015 | 9 | 19 | 9 | 51 | 15-0062267 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 488 | 1.1332 | 117_266 | <25mph | <15mph | HFTD - Distribution | 2015-09-19 09:51:00 | 348 | 13.7107 | FALSE | <25mph | AU415 | 3.15 | 2016-05-05T13:30:00Z | 0 | 6 | < 25mph | E9070 | 4.38 | 2016-05-05T13:00:00Z | 7 | 114 | < 25mph | AU415 | 3.15 | 2016-05-05T14:20:00Z | 0 | 13 | < 25mph | E9070 | 4.38 | 2016-05-05T13:00:00Z | 7 | 225 | < 25mph
PG&E | 2019-09-11 | 21:03 | 38.3132 | -120.9809 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 163341103 |  | 12000 | Conductor | Overhead | Yes | 43719 | 21:03 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-370 | 2019 | 9 | 11 | 21 | 3 | 19-0098003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25994 | 11.7888 | 200_256 | <25mph | <15mph | HFTD - Distribution | 2019-09-11 21:03:00 | 2035 | 13.1911 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 5.36 | 2017-04-29T19:05:00Z | 10 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 5.36 | 2017-04-29T20:05:00Z | 10 | 2 | < 25mph
PG&E | 2015-03-15 22:47 | 2015-03-15 22:47 | 38.3346 | -120.5325 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 103106530 |  | 12000 | Conductor | Overhead | Yes | 42078.9493 | 2015-03-15 22:47 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0279 | 2015 | 3 | 15 | 22 | 47 | 15-0019709 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 14520 | 7.4897 | 220_257 | <25mph | <15mph | HFTD - Distribution | 2015-03-15 22:47:00 | 25 | 18.5478 | FALSE | <25mph | D9396 | 3.65 | 2018-07-06T03:38:00Z | 2.01 | 16 | < 25mph | ESPC1 | 4.17 | 2018-07-06T03:13:00Z | 8.99 | 30 | < 25mph | D9396 | 3.65 | 2018-07-06T05:08:00Z | 2.01 | 32 | < 25mph | ESPC1 | 4.17 | 2018-07-06T03:13:00Z | 8.99 | 59 | < 25mph
PG&E | 2017-08-12 09:09 | 09:08 | 34.6689 | -120.0286 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103391912 | Unknown | 12000 | Conductor | Overhead | Yes | 42959.3812 | 09:08 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | wire cut | Other/Unknown | 1330 | 2017 | 8 | 12 | 9 | 8 | 17-0069829 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 26070 | 3.5662 | 244_55 | <25mph | <15mph | HFTD - Distribution | 2017-08-12 09:08:00 | 1068 | 23.4799 | FALSE | <25mph | SXWC1 | 1.34 | 2018-12-26T07:09:00Z | 24.99 | 7 | < 25mph | FGMC1 | 4.7 | 2018-12-26T06:35:00Z | 25.99 | 24 | 25-40mph | SXWC1 | 1.34 | 2018-12-26T07:09:00Z | 24.99 | 14 | < 25mph | FGMC1 | 4.7 | 2018-12-26T07:35:00Z | 28.01 | 47 | 25-40mph
PG&E | 2019-09-13 | 6:30 | 37.3348 | -121.7716 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 83392110 |  | 21000 | Splice/Clamp/Connector | Overhead | Yes | 43721 | 6:30 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-444 | 2019 | 9 | 13 | 6 | 30 | 19-0098560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 35534 | 3.3882 | 166_202 | <25mph | <15mph | HFTD - Distribution | 2019-09-13 06:30:00 | 2037 | 14.1926 | FALSE | <25mph | E8563 | 3.34 | 2018-06-29T03:21:00Z | 10 | 25 | < 25mph | SJS01 | 6.07 | 2018-06-29T03:25:00Z | 16.67 | 97 | < 25mph | E8563 | 3.34 | 2018-06-29T03:21:00Z | 10 | 49 | < 25mph | SJS01 | 6.07 | 2018-06-29T03:25:00Z | 16.67 | 193 | < 25mph
PG&E | 2018-10-16 | 16:30 | 38.7754 | -122.8976 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MARK GRADEK (707) 889-4303 | 101962692 | AT&T | 12000 | Conductor | Overhead | Yes | 43389 | 16:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1943 | 2018 | 10 | 16 | 16 | 30 | 18-0091127 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 744 | 10.3513 | 118_282 | <25mph | <15mph | HFTD - Distribution | 2018-10-16 16:30:00 | 1682 | 19.9126 | FALSE | <25mph |  |  |  | 0 | 0 | No data | R38WW | 4.61 | 2018-04-09T12:00:00Z | 26.6 | 16 | 25-40mph |  |  |  | 0 | 0 | No data | R38WW | 4.61 | 2018-04-09T12:00:00Z | 26.6 | 31 | 25-40mph
1. Butte | 2015-09-09 | 14:26 | 38.3297 | -120.7042 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1987 | 2015 | 9 | 9 | 14 | 26 |  | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 1353755 | 12.0917 | 212_257 | <25mph | <15mph | HFTD - Distribution | 2015-09-09 14:26:00 | 332 | 14.8248 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 5.02 | 2015-01-09T02:56:00Z | 4.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 5.02 | 2015-01-09T03:56:00Z | 8.01 | 2 | < 25mph
PG&E | 2017-07-12 | 16:04 | 40.6531 | -122.3343 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 000/001 | Unknown | 60000 | Conductor | Overhead | Yes | 42928 | 16:04 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1245 | 2017 | 7 | 12 | 16 | 4 | INT-09837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 13.5069 | 143_386 | <25mph | <15mph | HFTD - Transmission | 2017-07-12 16:04:00 | 987 | 13.828 | FALSE | <25mph | C5599 | 3.4 | 2017-03-16T08:31:00Z | 0 | 3 | < 25mph | C5599 | 3.4 | 2017-03-16T08:31:00Z | 0 | 3 | < 25mph | C5599 | 3.4 | 2017-03-16T09:16:00Z | 0 | 6 | < 25mph | C5599 | 3.4 | 2017-03-16T09:16:00Z | 0 | 6 | < 25mph
PG&E | 2016-10-02 16:41 | 16:41 | 39.8888 | -121.6648 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103358082 |  | 12000 | Other | Overhead | Yes | 42645.6954 | 16:41 | Other | N.A. | N.A. | N.A. | Weather | lightning strike | Other/Unknown | 1013 | 2016 | 10 | 2 | 16 | 41 | 16-0069050 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 339550 | 8.5152 | 171_343 | <25mph | <15mph | HFTD - Distribution | 2016-10-02 16:41:00 | 755 | 17.2989 | FALSE | <25mph | PG134 | 0.91 | 2018-11-05T08:00:00Z | 11.18 | 24 | < 25mph | PG134 | 0.91 | 2018-11-05T08:00:00Z | 11.18 | 37 | < 25mph | PG134 | 0.91 | 2018-11-05T08:00:00Z | 11.18 | 48 | < 25mph | PG134 | 0.91 | 2018-11-05T08:00:00Z | 11.18 | 74 | < 25mph
PG&E | 2015-07-07 15:27 | 2015-07-07 15:27 | 35.155 | -120.5442 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 303corraltos cyn rd | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42192.6438 | 2015-07-07 15:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0449 | 2015 | 7 | 7 | 15 | 27 | 15-0046127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 98566 | 24.1391 | 220_82 | <25mph | <15mph | HFTD - Distribution | 2015-07-07 15:27:00 | 194 | 24.1391 | FALSE | <25mph | F0194 | 3.06 | 2018-07-11T20:32:00Z | 8.99 | 20 | < 25mph | F0194 | 3.06 | 2018-07-11T20:32:00Z | 8.99 | 24 | < 25mph | F0194 | 3.06 | 2018-07-11T20:32:00Z | 8.99 | 40 | < 25mph | F0194 | 3.06 | 2018-07-11T20:32:00Z | 8.99 | 48 | < 25mph
PG&E | 2016-06-12 | 2016-06-12 13:14 | 37.5096 | -120.0462 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101083986 |  | 0 – 750 | Conductor | Overhead | Yes | 42533 | 2016-06-12 13:14 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0795 | 2016 | 6 | 12 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.8806 | 241_212 | <25mph | <15mph | HFTD - Distribution | 2016-06-12 13:14:00 | 539 | 13.4596 | FALSE | <25mph | MPOC1 | 3.28 | 2018-02-04T03:07:00Z | 5.99 | 1 | < 25mph | MPOC1 | 3.28 | 2018-02-04T03:07:00Z | 5.99 | 1 | < 25mph | MPOC1 | 3.28 | 2018-02-04T04:07:00Z | 7 | 2 | < 25mph | MPOC1 | 3.28 | 2018-02-04T04:07:00Z | 7 | 2 | < 25mph
PG&E | 2018-08-10 | 12:54 | 38.799 | -120.73 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101386272 | AT&T | 12000 | Conductor | Overhead | Yes | 43322 | 12:54 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1832 | 2018 | 8 | 10 | 12 | 54 | 18-0068798 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 26532 | 10.1607 | 211_283 | <25mph | <15mph | HFTD - Distribution | 2018-08-10 12:54:00 | 1571 | 17.3224 | FALSE | <25mph | E3165 | 0.86 | 2017-11-01T00:28:00Z | 4 | 7 | < 25mph | BDMC1 | 7.39 | 2017-11-01T00:36:00Z | 7 | 37 | < 25mph | E3165 | 0.86 | 2017-11-01T00:28:00Z | 4 | 14 | < 25mph | BDMC1 | 7.39 | 2017-11-01T00:36:00Z | 7 | 75 | < 25mph
PG&E | 2018-07-23 | 17:27 | 39.734 | -121.4965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103843963 | AT&T | 12000 | Conductor | Overhead | Yes | 43304 | 17:27 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1782 | 2018 | 7 | 23 | 17 | 27 | 18-0062874 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 183629 | 9.1915 | 178_335 | <25mph | <15mph | HFTD - Distribution | 2018-07-23 17:27:00 | 1522 | 13.4352 | FALSE | <25mph | JBGC1 | 0.42 | 2018-02-21T15:13:00Z | 21 | 1 | < 25mph | JBGC1 | 0.42 | 2018-02-21T15:13:00Z | 21 | 11 | < 25mph | JBGC1 | 0.42 | 2018-02-21T16:13:00Z | 24 | 2 | < 25mph | JBGC1 | 0.42 | 2018-02-21T16:13:00Z | 24 | 23 | < 25mph
PG&E | 2019-08-12 | 17:42 | 38.6618 | -120.7451 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 101415488, 101404439 |  | 12000 | Pole | Overhead | Yes | 43689 | 17:42 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (slight defect) | 2019-241 | 2019 | 8 | 12 | 17 | 42 | 19-0087080 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 54604 | 8.3029 | 210_275 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 17:42:00 | 1968 | 11.2889 | FALSE | <25mph | PG077 | 3.79 | 2018-12-03T15:40:00Z | 4.16 | 7 | < 25mph | PG068 | 5.78 | 2018-12-03T15:40:00Z | 8.99 | 50 | < 25mph | PG077 | 3.79 | 2018-12-03T17:20:00Z | 8.77 | 17 | < 25mph | C6129 | 6.06 | 2018-12-03T17:29:00Z | 12.01 | 103 | < 25mph
PG&E | 2018-05-11 | 17:43 | 38.8218 | -120.9295 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Douglas Ferro. cell-530-708-2715. office-530-677-6192 | 101388939 | AT&T | 21000 | Conductor | Overhead | Yes | 43231 | 17:43 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1588 | 2018 | 5 | 11 | 17 | 43 | 18-0040415 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 53784 | 23.6414 | 202_284 | <25mph | <15mph | HFTD - Distribution | 2018-05-11 17:43:00 | 1330 | 24.2639 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 4.34 | 2017-04-15T17:56:00Z | 5.99 | 19 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 4.34 | 2017-04-15T18:56:00Z | 11.01 | 38 | < 25mph
PG&E | 2017-09-11 | 8:50 | 36.9515 | -121.842 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101790954 | PACIFIC BELL | 21000 | Fuse | Overhead | Yes | 42989 | 8:50 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | no-match | 1408 | 2017 | 9 | 11 | 8 | 50 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | N.A. | 9.6414 | 162_181 | <25mph | <15mph | HFTD - Distribution | 2017-09-11 08:50:00 | 1146 | 17.9559 | FALSE | <25mph | E7291 | 2.85 | 2019-06-05T09:01:00Z | 4 | 17 | < 25mph | E7291 | 2.85 | 2019-06-05T09:01:00Z | 4 | 66 | < 25mph | E7291 | 2.85 | 2019-06-05T10:15:00Z | 4 | 34 | < 25mph | PG370 | 7.97 | 2019-06-05T10:10:00Z | 5.7 | 135 | < 25mph
PG&E | 2016-10-08 15:05 | 15:04 | 38.6686 | -120.9091 | Vegetation | RURAL | < 0.25 Acres | Customer | N.A. | 101380856 |  | 0 – 750 | Capacitor Bank | Overhead | Yes | 42651.6284 | 15:04 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1021 | 2016 | 10 | 8 | 15 | 4 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 10.4532 | 203_276 | <25mph | <15mph | HFTD - Distribution | 2016-10-08 15:04:00 | 762 | 14.8776 | FALSE | <25mph | D2736 | 2.92 | 2017-09-27T02:31:00Z | 4.99 | 73 | < 25mph | BENC1 | 5.53 | 2017-09-27T02:59:00Z | 20 | 131 | < 25mph | D2736 | 2.92 | 2017-09-27T02:31:00Z | 4.99 | 141 | < 25mph | BENC1 | 5.53 | 2017-09-27T02:59:00Z | 20 | 254 | < 25mph
PG&E | 2017-05-25 15:05 | 15:05 | 36.5217 | -121.8473 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Buddy Bloxham 831-236-5659 | 101778611 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42880.6288 | 15:05 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1113 | 2017 | 5 | 25 | 15 | 5 | 17-0050761 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 13965 | 25.8899 | 162_158 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-05-25 15:05:00 | 853 | 26.2648 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PG268 | 6.1 | 2019-12-29T19:00:00Z | 12.48 | 58 | < 25mph |  |  |  | 0 | 0 | No data | PG268 | 6.1 | 2019-12-29T19:00:00Z | 12.48 | 116 | < 25mph
PG&E | 2018-08-21 | 10:13 | 38.6972 | -120.889 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101385436 | Unknown | 12000 | Conductor | Overhead | Yes | 43333 | 10:13 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1852 | 2018 | 8 | 21 | 10 | 13 | 18-0072055 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4572 | 5.9109 | 204_277 | <25mph | <15mph | HFTD - Distribution | 2018-08-21 10:13:00 | 1591 | 12.0437 | FALSE | <25mph | PG027 | 2.89 | 2018-08-04T06:50:00Z | 8.12 | 43 | < 25mph | PG027 | 2.89 | 2018-08-04T06:50:00Z | 8.12 | 121 | < 25mph | PG027 | 2.89 | 2018-08-04T07:20:00Z | 8.55 | 85 | < 25mph | PG068 | 7.32 | 2018-08-04T07:40:00Z | 9.22 | 242 | < 25mph
PG&E | 2019-09-05 | 23:02 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire | California Department of Forestry | 101670112 |  | 12000 | Fuse | Overhead | Yes | 43713 | 23:02 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-388 | 2019 | 9 | 5 | 23 | 2 | 19-0095858 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 17920 | 6.8605 | 147_193 | <25mph | <15mph | HFTD - Distribution | 2019-09-05 23:02:00 | 2016 | 8.0768 | FALSE | <25mph | BNDC1 | 2.84 | 2017-06-06T02:50:00Z | 7 | 1 | < 25mph | BNDC1 | 2.84 | 2017-06-06T02:50:00Z | 7 | 31 | < 25mph | BNDC1 | 2.84 | 2017-06-06T02:50:00Z | 7 | 2 | < 25mph | C1844 | 4.46 | 2017-06-06T04:30:00Z | 7 | 60 | < 25mph
PG&E | 2016-10-02 16:41 | 16:41 | 39.8888 | -121.6648 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103358082 |  | 12000 | Other | Overhead | Yes | 42645.6954 | 16:41 | Other | N.A. | N.A. | N.A. | Weather | lightning strike | Other/Unknown | 1013 | 2016 | 10 | 2 | 16 | 41 | 16-0069050 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 339550 | 8.5152 | 171_343 | <25mph | <15mph | HFTD - Distribution | 2016-10-02 16:41:00 | 755 | 17.2989 | FALSE | <25mph | C8878 | 1.4 | 2018-06-30T18:08:00Z | 18.01 | 12 | < 25mph | C8878 | 1.4 | 2018-06-30T18:08:00Z | 18.01 | 19 | < 25mph | C8878 | 1.4 | 2018-06-30T18:08:00Z | 18.01 | 24 | < 25mph | C8878 | 1.4 | 2018-06-30T18:08:00Z | 18.01 | 38 | < 25mph
PG&E | 2018-08-31 | 18:04 | 39.5785 | -123.3842 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102196393 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 18:04 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1873 | 2018 | 8 | 31 | 18 | 4 | 18-0075741 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18540 | 15.395 | 98_327 | <25mph | <15mph | HFTD - Distribution | 2018-08-31 18:04:00 | 1612 | 16.0884 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RDVC1 | 7.03 | 2015-09-10T13:28:00Z | 4.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | RDVC1 | 7.03 | 2015-09-10T14:28:00Z | 4.99 | 2 | < 25mph
PG&E | 2015-04-30 00:26 | 2015-04-30 00:26 | 37.2401 | -122.2472 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 1145 VERDE R |  | 12000 | Conductor | Overhead | Yes | 42124.0181 | 2015-04-30 00:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0304 | 2015 | 4 | 30 | 0 | 26 | 15-0030607 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1256 | 5.7566 | 145_197 | <25mph | <15mph | HFTD - Distribution | 2015-04-30 00:26:00 | 50 | 15.5915 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.52 | 2016-06-11T19:07:00Z | 13 | 5 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.52 | 2016-06-11T19:07:00Z | 13 | 10 | < 25mph
PG&E | 2018-07-17 | 11:11 | 35.6986 | -120.9777 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | dennis byrnes 8055434244 inc # = 18ca-slu-007640 | 103886652 | Unknown | 21000 | Conductor | Overhead | Yes | 43298 | 11:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1755 | 2018 | 7 | 17 | 11 | 11 | 18-0060637 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 9121 | 4.768 | 201_112 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 11:11:00 | 1495 | 12.6145 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D4060 | 6.73 | 2015-01-12T11:30:00Z | 0 | 5 | < 25mph |  |  |  | 0 | 0 | No data | TABC1 | 4.19 | 2015-01-12T12:07:00Z | 4 | 10 | < 25mph
PG&E | 2018-09-14 | 15:08 | 35.328 | -120.6982 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Sean Hernandez Cell # 805 903 3423 | 103400199 | Unknown | 12000 | Conductor | Overhead | Yes | 43357 | 15:08 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1898 | 2018 | 9 | 14 | 15 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 24.1105 | 213_92 | <25mph | <15mph | HFTD - Distribution | 2018-09-14 15:08:00 | 1637 | 24.1304 | FALSE | <25mph | PG119 | 3.27 | 2019-12-11T02:40:00Z | 14.76 | 8 | < 25mph | PG223 | 4.41 | 2019-12-11T02:00:00Z | 19.8 | 62 | < 25mph | PG119 | 3.27 | 2019-12-11T02:50:00Z | 16.67 | 15 | < 25mph | PG223 | 4.41 | 2019-12-11T03:10:00Z | 19.8 | 117 | < 25mph
PG&E | 2016-08-15 | 2016-08-15 15:43 | 37.8784 | -120.4488 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101020079 |  | 17000 | Conductor | Overhead | Yes | 42597 | 2016-08-15 15:43 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0928 | 2016 | 8 | 15 | 15 | 43 | 16-0057465 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 122905 | 10.0906 | 223_232 | <25mph | <15mph | HFTD - Distribution | 2016-08-15 15:43:00 | 671 | 12.9875 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.26 | 2017-11-20T06:03:00Z | 3 | 1 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.26 | 2017-11-20T07:03:00Z | 7 | 2 | < 25mph
PG&E | 2015-02-06 06:01 | 2015-02-06 06:01 | 38.6059 | -121.0221 | Vegetation | Rural | < 3 meters | Fire Agency |  | 6661 Ryan Ranch Road, El Dorado Hills |  | 21000 | Conductor | Overhead | Yes | 42041.2507 | 2015-02-06 06:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0259 | 2015 | 2 | 6 | 6 | 1 | 15-0009876 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 51996 | 16.7927 | 199_272 | <25mph | <15mph | HFTD - Distribution | 2015-02-06 06:01:00 | 6 | 30.3484 | FALSE | 25-40mph | E8856 | 3.45 | 2018-09-16T07:20:00Z | 1.01 | 12 | < 25mph | E4740 | 5.63 | 2018-09-16T07:00:00Z | 7 | 78 | < 25mph | E8856 | 3.45 | 2018-09-16T08:00:00Z | 7 | 24 | < 25mph | E4740 | 5.63 | 2018-09-16T08:20:00Z | 8.01 | 152 | < 25mph
PG&E | 2015-07-05 09:42 | 2015-07-05 09:42 | 35.5323 | -120.7371 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 0 – 750 | Conductor | Overhead | No |  |  | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0444 | 2015 | 7 | 5 | 9 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 11.0729 | 211_103 | <25mph | <15mph | HFTD - Distribution | 2015-07-05 09:42:00 | 189 | 25.4306 | FALSE | 25-40mph | E6394 | 1.7 | 2016-02-09T22:19:00Z | 4.99 | 8 | < 25mph | E1179 | 5.63 | 2016-02-09T22:31:00Z | 5.99 | 12 | < 25mph | E6394 | 1.7 | 2016-02-09T22:19:00Z | 4.99 | 16 | < 25mph | E1179 | 5.63 | 2016-02-09T22:31:00Z | 5.99 | 24 | < 25mph
PG&E | 2019-09-12 | 14:25 | 37.3144 | -122.1865 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 024131103 |  | 12000 | Conductor | Overhead | Yes | 43720 | 14:25 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-217 | 2019 | 9 | 12 | 14 | 25 | 19-0098386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 89097 | 5.2412 | 147_201 | <25mph | <15mph | HFTD - Distribution | 2019-09-12 14:25:00 | 2036 | 15.0249 | FALSE | <25mph | LAHC1 | 3.83 | 2016-12-01T14:07:00Z | 5.99 | 20 | < 25mph | E0516 | 4.98 | 2016-12-01T14:00:00Z | 18.01 | 89 | < 25mph | LAHC1 | 3.83 | 2016-12-01T15:07:00Z | 5.99 | 40 | < 25mph | E0516 | 4.98 | 2016-12-01T14:00:00Z | 18.01 | 174 | < 25mph
PG&E | 2019-06-18 | 19:49 | 35.8876 | -120.9217 | Bird Found | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Pole | Overhead | Yes | 43634 | 19:49 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | no-match | 2019-55 | 2019 | 6 | 18 | 19 | 49 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 15.5935 | 203_122 | <25mph | <15mph | HFTD - Distribution | 2019-06-18 19:49:00 | 1852 | 21.7258 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG360 | 6.27 | 2019-07-18T09:50:00Z | 6.8 | 13 | < 25mph |  |  |  | 0 | 0 | No data | PG360 | 6.27 | 2019-07-18T09:50:00Z | 6.8 | 26 | < 25mph
PG&E | 2018-07-17 | 11:58 | 37.2217 | -121.6778 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Luis Morado state arson fire fighter | 100601345 | Unknown | 12000 | Conductor | Overhead | Yes | 43298 | 11:58 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1756 | 2018 | 7 | 17 | 11 | 58 | 18-0060617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 5865 | 5.1834 | 170_196 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 11:58:00 | 1496 | 14.408 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C7794 | 7.07 | 2019-02-26T11:05:00Z | 14 | 22 | < 25mph |  |  |  | 0 | 0 | No data | C7794 | 7.07 | 2019-02-26T12:15:00Z | 18.99 | 44 | < 25mph
PG&E | 2017-05-15 16:14 | 16:00 | 37.1766 | -119.8189 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SHAUN FAIRBANKS 559-683-4823 | 101108423 | SIERRA | 21000 | Conductor | Overhead | Yes | 42870.6767 | 16:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1099 | 2017 | 5 | 15 | 16 | 0 | 17-0048096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20007 | 15.7465 | 251_194 | <25mph | <15mph | HFTD - Distribution | 2017-05-15 16:00:00 | 839 | 20.7849 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5766 | 4.44 | 2015-02-08T19:48:00Z | 10 | 12 | < 25mph |  |  |  | 0 | 0 | No data | E5766 | 4.44 | 2015-02-08T20:48:00Z | 15.99 | 24 | < 25mph
PG&E | 2015-07-15 09:00 | 2015-07-15 09:00 | 36.997 | -121.7381 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101795728 |  | 21000 | Conductor | Overhead | Yes | 42200.375 | 2015-07-15 09:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0463 | 2015 | 7 | 15 | 9 | 0 | 15-0047650 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3800 | 8.5113 | 167_184 | <25mph | <15mph | HFTD - Distribution | 2015-07-15 09:00:00 | 208 | 13.379 | FALSE | <25mph | CTOC1 | 3.71 | 2018-04-16T06:27:00Z | 2.01 | 1 | < 25mph | AU710 | 7.72 | 2018-04-16T06:42:00Z | 3 | 21 | < 25mph | CTOC1 | 3.71 | 2018-04-16T07:27:00Z | 2.01 | 2 | < 25mph | AU710 | 7.72 | 2018-04-16T07:57:00Z | 3 | 42 | < 25mph
PG&E | 2018-06-16 | 19:58 | 37.907 | -121.8063 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100483910 | Unknown | 21000 | Conductor | Overhead | Yes | 43267 | 19:58 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1670 | 2018 | 6 | 16 | 19 | 58 | 18-0051687 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 3322 | 40.9858 | 164_234 | 40-55mph | 30-45mph | HFTD - Distribution | 2018-06-16 19:58:00 | 1412 | 43.1884 | FALSE | 40-55mph | D2814 | 3.84 | 2015-02-05T00:38:00Z | 8.01 | 4 | < 25mph | SJS02 | 6.13 | 2015-02-05T00:55:00Z | 33.53 | 20 | 25-40mph | D2814 | 3.84 | 2015-02-05T00:38:00Z | 8.01 | 7 | < 25mph | SJS02 | 6.13 | 2015-02-05T01:55:00Z | 34.85 | 39 | 25-40mph
PG&E | 2015-11-15 16:30 | 2015-11-15 16:30 | 37.0007 | -121.885 | Vegetation | Rural | < 3 meters | Customer |  | 101691004 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42323.6875 | 2015-11-15 16:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0676 | 2015 | 11 | 15 | 16 | 30 | 15-0077978 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 25920 | 24.6094 | 161_184 | <25mph | <15mph | HFTD - Distribution | 2015-11-15 16:30:00 | 420 | 25.3186 | FALSE | 25-40mph | E7291 | 2.82 | 2019-09-30T07:02:00Z | 7 | 38 | < 25mph | PG004 | 6.94 | 2019-09-30T06:20:00Z | 11.99 | 161 | < 25mph | E7291 | 2.82 | 2019-09-30T07:47:00Z | 8.01 | 74 | < 25mph | PG004 | 6.94 | 2019-09-30T08:00:00Z | 12.8 | 318 | < 25mph
PG&E | 2015-08-29 03:30 | 2015-08-29 03:30 | 38.6302 | -122.8327 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Dirt road across from 3204 Rio Lindo Rd, Healdsburg |  | 12000 | Conductor | Overhead | Yes | 42245.1458 | 2015-08-29 03:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0566 | 2015 | 8 | 29 | 3 | 30 | 15-0058127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4780 | 9.2134 | 120_274 | <25mph | <15mph | HFTD - Distribution | 2015-08-29 03:30:00 | 310 | 15.1029 | FALSE | <25mph | E3235 | 3.49 | 2015-12-17T07:46:00Z | 0 | 21 | < 25mph | HWKC1 | 7.25 | 2015-12-17T07:56:00Z | 4 | 40 | < 25mph | E3235 | 3.49 | 2015-12-17T08:48:00Z | 0 | 41 | < 25mph | HWKC1 | 7.25 | 2015-12-17T08:56:00Z | 5.99 | 79 | < 25mph
PG&E | 2018-10-14 | 19:39 | 38.446 | -120.5147 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | IC- Dillon Gissell- 209-295-7735 | 103384485 | Unknown | 12000 | Conductor | Overhead | Yes | 43387 | 19:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1939 | 2018 | 10 | 14 | 19 | 39 | 18-0090288 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3497327 | 25.4932 | 220_264 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-14 19:39:00 | 1678 | 30.9108 | FALSE | 25-40mph | C9148 | 3.52 | 2018-05-15T00:34:00Z | 11.01 | 4 | < 25mph | C9148 | 3.52 | 2018-05-15T00:34:00Z | 11.01 | 8 | < 25mph | C9148 | 3.52 | 2018-05-15T00:34:00Z | 11.01 | 8 | < 25mph | C9148 | 3.52 | 2018-05-15T00:34:00Z | 11.01 | 16 | < 25mph
PG&E | 2017-08-05 08:33 | 08:33 | 38.4583 | -120.8695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JEFF MICHEL- 530 409 2223 | 101236223 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42952.3565 | 08:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1317 | 2017 | 8 | 5 | 8 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 6.5905 | 205_264 | <25mph | <15mph | HFTD - Distribution | 2017-08-05 08:33:00 | 1055 | 14.6063 | FALSE | <25mph | E8452 | 3.31 | 2016-08-08T13:49:00Z | 2.01 | 7 | < 25mph | CFAC1 | 6.33 | 2016-08-08T14:05:00Z | 11.01 | 8 | < 25mph | E8452 | 3.31 | 2016-08-08T14:34:00Z | 3 | 13 | < 25mph | CFAC1 | 6.33 | 2016-08-08T14:05:00Z | 11.01 | 15 | < 25mph
PG&E | 2016-08-07 | 2016-08-07 14:20 | 37.2316 | -122.1552 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire/woodside fire | 103413747 |  | 12000 | Conductor | Overhead | Yes | 42589 | 2016-08-07 14:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0910 | 2016 | 8 | 7 | 14 | 20 | 16-0055597 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29869 | 12.3369 | 149_197 | <25mph | <15mph | HFTD - Distribution | 2016-08-07 14:20:00 | 653 | 12.9748 | FALSE | <25mph | F0333 | 3.9 | 2019-07-04T19:35:00Z | 7 | 25 | < 25mph | PG455 | 5.13 | 2019-07-04T19:30:00Z | 11.41 | 116 | < 25mph | F0333 | 3.9 | 2019-07-04T20:41:00Z | 7 | 48 | < 25mph | PG455 | 5.13 | 2019-07-04T20:30:00Z | 12.71 | 227 | < 25mph
PG&E | 2019-07-13 | 13:13 | 34.7273 | -120.4357 |  | Shrub | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | Y44 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43659 | 13:13 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-154 | 2019 | 7 | 13 | 13 | 13 | 19-0077070 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 18256 | 12.2026 | 225_58 | <25mph | <15mph | HFTD - Distribution | 2019-07-13 13:13:00 | 1900 | 12.8932 | FALSE | <25mph | D4531 | 2.22 | 2017-03-17T09:14:00Z | 5.99 | 5 | < 25mph | D4531 | 2.22 | 2017-03-17T09:14:00Z | 5.99 | 23 | < 25mph | D4531 | 2.22 | 2017-03-17T09:44:00Z | 7 | 10 | < 25mph | E7619 | 6.24 | 2017-03-17T10:15:00Z | 11.01 | 46 | < 25mph
PG&E | 2015-07-31 22:45 | 2015-07-31 22:45 | 38.3805 | -120.5628 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS FROM 1958 QUAIL LN WEST POINT | None | 12000 | Conductor | Overhead | Yes | 42216.9479 | 2015-07-31 22:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0503 | 2015 | 7 | 31 | 22 | 45 | 15-0052033 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 33559 | 6.4734 | 218_260 | <25mph | <15mph | HFTD - Distribution | 2015-07-31 22:45:00 | 248 | 15.0324 | FALSE | <25mph | PG095 | 2.08 | 2019-12-21T00:20:00Z | 9.51 | 12 | < 25mph | ESPC1 | 7.73 | 2019-12-21T00:13:00Z | 12.01 | 78 | < 25mph | PG095 | 2.08 | 2019-12-21T00:20:00Z | 9.51 | 24 | < 25mph | ESPC1 | 7.73 | 2019-12-21T00:13:00Z | 12.01 | 156 | < 25mph
PG&E | 2018-07-28 | 6:51 | 38.7473 | -120.7866 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101418155 | AT&T | 21000 | Conductor | Overhead | Yes | 43309 | 6:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1794 | 2018 | 7 | 28 | 6 | 51 | 18-0064545 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 15429 | 14.6813 | 209_280 | <25mph | <15mph | HFTD - Distribution | 2018-07-28 06:51:00 | 1534 | 14.6813 | FALSE | <25mph | C5121 | 2.7 | 2018-02-04T18:44:00Z | 1.01 | 20 | < 25mph | C6129 | 4.92 | 2018-02-04T18:49:00Z | 5.99 | 107 | < 25mph | AV185 | 2.88 | 2018-02-04T19:30:00Z | 3 | 39 | < 25mph | C6129 | 4.92 | 2018-02-04T19:14:00Z | 5.99 | 217 | < 25mph
PG&E | 2017-08-08 20:35 | 20:35 | 37.2637 | -119.7103 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TROY CHEEK1-209-966-3621 | 103793352 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42955.8578 | 20:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1327 | 2017 | 8 | 8 | 20 | 35 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.9357 | 256_199 | <25mph | <15mph | HFTD - Distribution | 2017-08-08 20:35:00 | 1065 | 11.9714 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D7171 | 6.79 | 2015-08-17T12:05:00Z | 4 | 33 | < 25mph |  |  |  | 0 | 0 | No data | D7171 | 6.79 | 2015-08-17T12:05:00Z | 4 | 67 | < 25mph
PG&E | 2015-01-26 03:51 | 2015-01-26 03:51 | 37.0539 | -122.1587 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42030.1604 | 2015-01-26 03:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0258 | 2015 | 1 | 26 | 3 | 51 | 15-0007000 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7602 | 14.3078 | 149_187 | <25mph | <15mph | HFTD - Distribution | 2015-01-26 03:51:00 | 5 | 14.9656 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BNDC1 | 5.38 | 2018-04-28T04:50:00Z | 8.99 | 48 | < 25mph |  |  |  | 0 | 0 | No data | BNDC1 | 5.38 | 2018-04-28T04:50:00Z | 8.99 | 95 | < 25mph
PG&E | 2018-05-19 | 19:44 | 40.2665 | -122.2727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103899310 | Unknown | 12000 | Conductor | Overhead | Yes | 43239 | 19:44 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1599 | 2018 | 5 | 19 | 19 | 44 | 18-0042559 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 31980 | 15.59 | 146_364 | <25mph | <15mph | HFTD - Distribution | 2018-05-19 19:44:00 | 1341 | 18.253 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 7.1 | 2015-11-13T02:46:00Z | 3 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 7.1 | 2015-11-13T03:02:00Z | 4.99 | 7 | < 25mph
PG&E | 2018-06-09 | 0:46 | 35.0745 | -120.5167 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101927520 | Unknown | 12000 | Conductor | Overhead | Yes | 43260 | 0:46 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1645 | 2018 | 6 | 9 | 0 | 46 | 18-0049171 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 16825 | 5.84 | 221_78 | <25mph | <15mph | HFTD - Distribution | 2018-06-09 00:46:00 | 1387 | 22.9582 | FALSE | <25mph | F0412 | 2.71 | 2017-07-10T06:45:00Z | 3 | 17 | < 25mph | F0412 | 2.71 | 2017-07-10T06:45:00Z | 3 | 33 | < 25mph | F0412 | 2.71 | 2017-07-10T07:05:00Z | 3 | 33 | < 25mph | F0412 | 2.71 | 2017-07-10T07:05:00Z | 3 | 66 | < 25mph
PG&E | 2018-06-27 | 18:46 | 40.218 | -123.7989 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TJ alderpoint fire | 100990381 | Unknown | 12000 | Conductor | Overhead | Yes | 43278 | 18:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1700 | 2018 | 6 | 27 | 18 | 46 | 18-0055205 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 21357 | 17.7599 | 81_363 | <25mph | <15mph | HFTD - Distribution | 2018-06-27 18:46:00 | 1441 | 20.5507 | FALSE | <25mph | PG273 | 3.19 | 2019-06-19T05:10:00Z | 7.9 | 12 | < 25mph | ERCC1 | 5.65 | 2019-06-19T05:28:00Z | 14 | 13 | < 25mph | PG273 | 3.19 | 2019-06-19T05:10:00Z | 7.9 | 24 | < 25mph | ERCC1 | 5.65 | 2019-06-19T05:28:00Z | 14 | 26 | < 25mph
PG&E | 2018-10-14 | 19:39 | 38.446 | -120.5147 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | IC- Dillon Gissell- 209-295-7735 | 103384485 | Unknown | 12000 | Conductor | Overhead | Yes | 43387 | 19:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1939 | 2018 | 10 | 14 | 19 | 39 | 18-0090288 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3497327 | 25.4932 | 220_264 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-14 19:39:00 | 1678 | 30.9108 | FALSE | 25-40mph | C9148 | 3.52 | 2016-08-10T17:34:00Z | 13 | 16 | < 25mph | C9148 | 3.52 | 2016-08-10T17:34:00Z | 13 | 20 | < 25mph | AT450 | 3.11 | 2016-08-10T18:20:00Z | 13 | 32 | < 25mph | AT450 | 3.11 | 2016-08-10T18:20:00Z | 13 | 40 | < 25mph
PG&E | 2017-07-12 15:09 | 15:09 | 37.1491 | -122.0037 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 103565794 | Unknown | 21000 | Conductor | Overhead | Yes | 42928.6313 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1248 | 2017 | 7 | 12 | 15 | 9 | 17-0062439 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24690 | 9.5326 | 155_192 | <25mph | <15mph | HFTD - Distribution | 2017-07-12 15:09:00 | 986 | 9.5326 | FALSE | <25mph | D9791 | 1 | 2017-07-05T06:10:00Z | 0 | 26 | < 25mph | C1844 | 6.81 | 2017-07-05T06:10:00Z | 4 | 135 | < 25mph | D8979 | 3.17 | 2017-07-05T06:53:00Z | 2.01 | 52 | < 25mph | C5272 | 4.53 | 2017-07-05T06:52:00Z | 5.99 | 266 | < 25mph
PG&E | 2018-11-13 | 15:41 | 37.0644 | -121.9578 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101680441 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43417 | 15:41 | Other | N.A. | N.A. | N.A. | Human Error | Grow house | Other/Unknown | 1973 | 2018 | 11 | 13 | 15 | 41 | 18-0099492 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 21484 | 1.9347 | 157_188 | <25mph | <15mph | HFTD - Distribution | 2018-11-13 15:41:00 | 1713 | 13.1257 | FALSE | <25mph | AR778 | 3.96 | 2018-05-08T13:26:00Z | 4.99 | 36 | < 25mph | D8979 | 4.33 | 2018-05-08T13:29:00Z | 8.01 | 151 | < 25mph | E5965 | 0.43 | 2018-05-08T15:15:00Z | 4.99 | 72 | < 25mph | D8979 | 4.33 | 2018-05-08T13:29:00Z | 8.01 | 297 | < 25mph
PG&E | 2017-06-15 04:31 | 2:58 | 40.299 | -122.4318 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101511631 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42901.1885 | 2:58 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | Other/Unknown | 1145 | 2017 | 6 | 15 | 2 | 58 | 17-0055359 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1762 | 9.755 | 139_366 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 02:58:00 | 884 | 19.4408 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-08-24 | 5:03 | 39.1184 | -121.0154 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JIM SMITH BATT CHIEF 3 | 100097647 | Unknown | 12000 | Conductor | Overhead | Yes | 43336 | 5:03 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1858 | 2018 | 8 | 24 | 5 | 3 | 18-0073024 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 4048 | 6.5682 | 199_301 | <25mph | <15mph | HFTD - Distribution | 2018-08-24 05:03:00 | 1597 | 12.3049 | FALSE | <25mph | AT999 | 2.07 | 2016-10-28T04:44:00Z | 3 | 35 | < 25mph | E1789 | 6.59 | 2016-10-28T04:42:00Z | 10 | 82 | < 25mph | AT999 | 2.07 | 2016-10-28T05:03:00Z | 4.99 | 68 | < 25mph | E1789 | 6.59 | 2016-10-28T05:00:00Z | 12.01 | 163 | < 25mph
PG&E | 2019-08-11 | 1:19 | 39.1152 | -121.001 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100097796 |  | 12000 | Other | Overhead | Yes | 43688 | 1:19 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-387 | 2019 | 8 | 11 | 1 | 19 | 19-0086613 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6200 | 9.9563 | 199_300 | <25mph | <15mph | HFTD - Distribution | 2019-08-11 01:19:00 | 1965 | 18.5914 | FALSE | <25mph | C5488 | 3.22 | 2019-05-11T16:33:00Z | 2.01 | 10 | < 25mph | AV504 | 7.68 | 2019-05-11T16:15:00Z | 11.01 | 67 | < 25mph | C5488 | 3.22 | 2019-05-11T18:04:00Z | 7 | 20 | < 25mph | AV504 | 7.68 | 2019-05-11T17:40:00Z | 11.01 | 136 | < 25mph
PG&E | 2018-11-15 | 6:09 | 38.3599 | -122.3682 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102241814 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43419 | 6:09 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1974 | 2018 | 11 | 15 | 6 | 9 | 18-0099862 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 441 | 10.2454 | 140_259 | <25mph | <15mph | HFTD - Distribution | 2018-11-15 06:09:00 | 1714 | 12.9788 | FALSE | <25mph | AS725 | 3.41 | 2015-10-11T04:12:00Z | 1.01 | 7 | < 25mph | E6860 | 7.62 | 2015-10-11T04:30:00Z | 5.99 | 11 | < 25mph | AS725 | 3.41 | 2015-10-11T04:12:00Z | 1.01 | 15 | < 25mph | E6860 | 7.62 | 2015-10-11T04:30:00Z | 5.99 | 24 | < 25mph
PG&E | 2016-07-15 05:19 | 2016-07-15 05:19 | 35.1839 | -120.5018 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101846594 |  | 12000 | Conductor | Overhead | Yes | 42566.2215 | 2016-07-15 05:19 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0851 | 2016 | 7 | 15 | 5 | 19 | 16-0050086 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 62404 | 2.6454 | 222_84 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 05:19:00 | 594 | 14.1102 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG168 | 6.85 | 2019-10-05T19:50:00Z | 16.15 | 41 | < 25mph |  |  |  | 0 | 0 | No data | PG513 | 6.4 | 2019-10-05T20:30:00Z | 16.6 | 82 | < 25mph
PG&E | 2017-08-30 | 22:37 | 38.9993 | -120.9887 | Vegetation | Rural | < 3 Meters | Fire Agency | Andy 530-889-0111 | 100026238 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42977 | 22:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1370 | 2017 | 8 | 30 | 22 | 37 | 17-0074333 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 3750 | 7.3126 | 200_294 | <25mph | <15mph | HFTD - Distribution | 2017-08-30 22:37:00 | 1108 | 12.9461 | FALSE | <25mph | C0713 | 3.13 | 2017-05-24T08:00:00Z | 1.01 | 13 | < 25mph | AU268 | 7.79 | 2017-05-24T07:52:00Z | 4.99 | 26 | < 25mph | C0713 | 3.13 | 2017-05-24T08:00:00Z | 1.01 | 25 | < 25mph | AU268 | 7.79 | 2017-05-24T07:52:00Z | 4.99 | 53 | < 25mph
PG&E | 2017-10-31 | 21:02 | 39.1119 | -122.9163 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Structure 020/003 | Unknown | 60000 | Conductor | Overhead | Yes | 43039 | 21:02 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | no-match | 1513 | 2017 | 10 | 31 | 21 | 2 | INT-10325 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | 50730 | 1.8727 | 117_301 | <25mph | <15mph | HFTD - Transmission | 2017-10-31 21:02:00 | 1255 | 9.8895 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5780 | 6.35 | 2016-05-23T20:51:00Z | 4.99 | 12 | < 25mph |  |  |  | 0 | 0 | No data | E5780 | 6.35 | 2016-05-23T22:12:00Z | 7 | 24 | < 25mph
PG&E | 2018-07-01 | 0:45 | 38.8842 | -120.847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Brian Mackwood (530)708-2711 | 100109003 | None | 21000 | Conductor | Overhead | Yes | 43282 | 0:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1719 | 2018 | 7 | 1 | 0 | 45 | 18-0056045 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5760 | 9.2878 | 206_288 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 00:45:00 | 1460 | 12.1055 | FALSE | <25mph | C6662 | 3.44 | 2015-03-16T20:24:00Z | 7 | 15 | < 25mph | BDMC1 | 7.75 | 2015-03-16T20:36:00Z | 12.01 | 22 | < 25mph | C6662 | 3.44 | 2015-03-16T21:34:00Z | 7 | 31 | < 25mph | BDMC1 | 7.75 | 2015-03-16T21:36:00Z | 13 | 45 | < 25mph
PG&E | 2018-09-27 | 12:43 | 38.5148 | -122.4463 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Twr 000/010 | None | 60000 | Conductor | Overhead | Yes | 43370 | 12:43 | Contact From Object | N.A. | Other | Electric Facility | Human Error | helicopter | no-match | 1917 | 2018 | 9 | 27 | 12 | 43 | INT-11394 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1488992 | 4.4433 | 137_268 | <25mph | <15mph | HFTD - Transmission | 2018-09-27 12:43:00 | 1656 | 10.4879 | FALSE | <25mph | F0315 | 4 | 2019-06-22T01:10:00Z | 5.99 | 12 | < 25mph | PG199 | 6.16 | 2019-06-22T00:30:00Z | 19.28 | 76 | < 25mph | F0315 | 4 | 2019-06-22T01:35:00Z | 7 | 24 | < 25mph | PG199 | 6.16 | 2019-06-22T00:30:00Z | 19.28 | 156 | < 25mph
PG&E | 2016-10-11 23:17 | 23:16 | 39.0201 | -120.8294 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire.foresthill fire | 100025501 |  | 60000 | Conductor | Overhead | Yes | 42654.9701 | 23:16 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error |  | no-match | 1028 | 2016 | 10 | 11 | 23 | 16 | INT-08640 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 0 | 7.6312 | 207_295 | <25mph | <15mph | HFTD - Transmission | 2016-10-11 23:16:00 | 769 | 11.1078 | FALSE | <25mph | PG032 | 2.4 | 2019-04-23T14:20:00Z | 10.74 | 10 | < 25mph | PG032 | 2.4 | 2019-04-23T14:20:00Z | 10.74 | 23 | < 25mph | PG032 | 2.4 | 2019-04-23T14:20:00Z | 10.74 | 19 | < 25mph | PG023 | 4.28 | 2019-04-23T15:10:00Z | 12.48 | 45 | < 25mph
PG&E | 2017-04-28 16:21 | 15:49 | 38.7679 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chris paper fire investigator, 530/677-1868. incident #caaeuo11821 | 101409833 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42853.6815 | 15:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1077 | 2017 | 4 | 28 | 15 | 49 | 17-0043771 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 82614 | 19.7837 | 201_281 | <25mph | <15mph | HFTD - Distribution | 2017-04-28 15:49:00 | 817 | 25.4223 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PLTC1 | 5.08 | 2015-06-07T23:56:00Z | 14 | 52 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 5.08 | 2015-06-07T23:56:00Z | 14 | 103 | < 25mph
PG&E | 2018-08-31 | 18:04 | 39.5785 | -123.3842 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102196393 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 18:04 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1873 | 2018 | 8 | 31 | 18 | 4 | 18-0075741 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18540 | 15.395 | 98_327 | <25mph | <15mph | HFTD - Distribution | 2018-08-31 18:04:00 | 1612 | 16.0884 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RDVC1 | 7.03 | 2017-06-28T01:28:00Z | 14.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | RDVC1 | 7.03 | 2017-06-28T02:28:00Z | 14.99 | 2 | < 25mph
PG&E | 2016-09-12 | 12:38 | 38.7832 | -120.6006 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101421708 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42625 | 12:38 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0974 | 2016 | 9 | 12 | 12 | 38 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 15.5165 | 217_282 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 12:38:00 | 716 | 15.5342 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TT260 | 7.42 | 2017-12-28T14:29:00Z | 7 | 8 | < 25mph |  |  |  | 0 | 0 | No data | TT260 | 7.42 | 2017-12-28T14:29:00Z | 7 | 16 | < 25mph
PG&E | 2016-07-25 15:32 | 2016-07-25 15:32 | 38.3522 | -120.7107 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42576.6472 | 2016-07-25 15:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0878 | 2016 | 7 | 25 | 15 | 32 | 16-0052398 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 19951 | 10.4912 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-25 15:32:00 | 621 | 14.4675 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2017-01-06T05:56:00Z | 8.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2017-01-06T06:56:00Z | 11.01 | 8 | < 25mph
PG&E | 2019-06-19 | 11:44 | 39.8612 | -121.6907 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100400933 |  | 12000 | Conductor | Overhead | Yes | 43635 | 11:44 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-224 | 2019 | 6 | 19 | 11 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.9144 | 170_342 | <25mph | <15mph | HFTD - Distribution | 2019-06-19 11:44:00 | 1855 | 12.1329 | FALSE | <25mph | C8878 | 2.27 | 2016-10-24T05:13:00Z | 7 | 13 | < 25mph | CSTC1 | 4.21 | 2016-10-24T05:51:00Z | 14 | 21 | < 25mph | C8878 | 2.27 | 2016-10-24T05:13:00Z | 7 | 25 | < 25mph | CSTC1 | 4.21 | 2016-10-24T06:51:00Z | 15.99 | 40 | < 25mph
PG&E | 2018-09-11 | 5:23 | 37.376 | -119.6304 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | TROY CHEEK 209-966-3621 | 101023184 | Unknown | 12000 | Conductor | Overhead | Yes | 43354 | 5:23 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1891 | 2018 | 9 | 11 | 5 | 23 | 18-0078387 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 288 | 4.3046 | 260_205 | <25mph | <15mph | HFTD - Distribution | 2018-09-11 05:23:00 | 1630 | 11.3584 | FALSE | <25mph | BSNC1 | 0.17 | 2018-08-14T04:48:00Z | 4.99 | 17 | < 25mph | MIAC1 | 6.99 | 2018-08-14T04:59:00Z | 11.01 | 55 | < 25mph | BSNC1 | 0.17 | 2018-08-14T05:48:00Z | 7 | 34 | < 25mph | MIAC1 | 6.99 | 2018-08-14T04:59:00Z | 11.01 | 108 | < 25mph
PG&E | 2015-06-27 21:15 | 2015-06-27 21:15 | 39.2699 | -121.0403 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 16151 INDAIN FLAT RD |  | 12000 | Conductor | Overhead | Yes | 42182.8854 | 2015-06-27 21:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0416 | 2015 | 6 | 27 | 21 | 15 | 15-0043789 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4210 | 5.8168 | 198_309 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 21:15:00 | 161 | 11.6482 | FALSE | <25mph | PG030 | 0.94 | 2018-07-12T12:40:00Z | 2.42 | 41 | < 25mph | RRRC1 | 4.73 | 2018-07-12T13:13:00Z | 8.01 | 75 | < 25mph | PG030 | 0.94 | 2018-07-12T12:40:00Z | 2.42 | 80 | < 25mph | RRRC1 | 4.73 | 2018-07-12T13:13:00Z | 8.01 | 145 | < 25mph
PG&E | 2016-04-30 | 17:59 | 38.3142 | -120.9015 | Vegetation | RURAL | < 3 meters | Fire Agency | Kern County FD |  |  | 12000 | Conductor | Overhead | Yes | 42490 | 17:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0719 | 2016 | 4 | 30 | 17 | 59 | 16-0032910 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 722 | 19.7396 | 204_256 | <25mph | <15mph | HFTD - Distribution | 2016-04-30 17:59:00 | 465 | 19.7396 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TS389 | 6.75 | 2018-02-20T16:53:00Z | 8.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | CMAC1 | 6.54 | 2018-02-20T17:59:00Z | 10 | 8 | < 25mph
PG&E | 2017-12-14 | 17:16 | 34.5878 | -120.3566 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101911004 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 43083 | 17:16 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1538 | 2017 | 12 | 14 | 17 | 16 | 17-0101672 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2896 | 2.7073 | 229_51 | <25mph | <15mph | HFTD - Distribution | 2017-12-14 17:16:00 | 1280 | 11.3138 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7619 | 5.74 | 2016-07-20T03:20:00Z | 13 | 6 | < 25mph |  |  |  | 0 | 0 | No data | E7619 | 5.74 | 2016-07-20T03:20:00Z | 13 | 12 | < 25mph
PG&E | 2017-07-20 13:46 | 13:45 | 35.0804 | -120.5538 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | PAUL LEE 805 903-3416 INC # 8291 | 101941116 | Unknown | 12000 | Conductor | Overhead | Yes | 42936.5736 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1275 | 2017 | 7 | 20 | 13 | 45 | 17-0064321 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 45999 | 13.843 | 220_78 | <25mph | <15mph | HFTD - Distribution | 2017-07-20 13:45:00 | 1013 | 14.6968 | FALSE | <25mph | E8214 | 1.41 | 2018-06-18T11:03:00Z | 0 | 6 | < 25mph | F0194 | 4.03 | 2018-06-18T10:15:00Z | 4 | 28 | < 25mph | E8214 | 1.41 | 2018-06-18T12:03:00Z | 0 | 16 | < 25mph | F0194 | 4.03 | 2018-06-18T10:15:00Z | 4 | 60 | < 25mph
PG&E | 2016-06-24 | 2016-06-24 14:38 | 40.22 | -122.283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101526647 | PACIFIC BELL | 0 – 750 | Unknown | Overhead | Yes | 42545 | 2016-06-24 14:38 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0821 | 2016 | 6 | 24 | 14 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 11.9685 | 145_362 | <25mph | <15mph | HFTD - Distribution | 2016-06-24 14:38:00 | 564 | 17.4582 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2015-03-04 18:44 | 2015-03-04 18:44 | 38.9995 | -122.7545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kelseyville FD | 102156367 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42067.7806 | 2015-03-04 18:44 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0271 | 2015 | 3 | 4 | 18 | 44 | 15-0017374 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29532 | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2015-03-04 18:44:00 | NA | 0 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.58 | 2019-05-11T17:57:00Z | 12.01 | 23 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.58 | 2019-05-11T18:57:00Z | 12.01 | 46 | < 25mph
PG&E | 2015-08-30 17:05 | 2015-08-30 17:05 | 38.4039 | -120.5559 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | centennial mine rd |  | 12000 | Conductor | Overhead | Yes | 42246.7118 | 2015-08-30 17:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0567 | 2015 | 8 | 30 | 17 | 5 | 15-0058273 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 40298 | 10.8566 | 219_261 | <25mph | <15mph | HFTD - Distribution | 2015-08-30 17:05:00 | 311 | 12.2451 | FALSE | <25mph | PG108 | 2.75 | 2019-03-28T03:50:00Z | 8.55 | 18 | < 25mph | C9148 | 6.15 | 2019-03-28T03:49:00Z | 14 | 51 | < 25mph | PG108 | 2.75 | 2019-03-28T03:50:00Z | 8.55 | 36 | < 25mph | C9148 | 6.15 | 2019-03-28T04:49:00Z | 20 | 101 | < 25mph
PG&E | 2018-08-12 | 14:46 | 38.6443 | -120.9211 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101410516 | Unknown | 21000 | Conductor | Overhead | Yes | 43324 | 14:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1838 | 2018 | 8 | 12 | 14 | 46 | 18-0069084 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4032 | 11.2318 | 203_274 | <25mph | <15mph | HFTD - Distribution | 2018-08-12 14:46:00 | 1577 | 12.412 | FALSE | <25mph | PG359 | 2.38 | 2019-05-14T09:20:00Z | 8.55 | 31 | < 25mph | PG073 | 7.47 | 2019-05-14T09:20:00Z | 12.71 | 141 | < 25mph | PG359 | 2.38 | 2019-05-14T09:50:00Z | 10.74 | 62 | < 25mph | PG073 | 7.47 | 2019-05-14T10:20:00Z | 12.71 | 283 | < 25mph
PG&E | 2015-08-13 03:46 | 2015-08-13 03:46 | 37.2072 | -119.7343 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 44365 SAVAGE RD COARSEGOLD |  | 21000 | Conductor | Overhead | Yes | 42229.1569 | 2015-08-13 03:46 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0526 | 2015 | 8 | 13 | 3 | 46 | 15-0054655 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 7600 | 7.8941 | 255_196 | <25mph | <15mph | HFTD - Distribution | 2015-08-13 03:46:00 | 270 | 10.403 | FALSE | <25mph | D7022 | 2.54 | 2018-01-19T20:28:00Z | 4.99 | 6 | < 25mph | E5766 | 4.34 | 2018-01-19T20:36:00Z | 7 | 17 | < 25mph | D7022 | 2.54 | 2018-01-19T20:58:00Z | 7 | 12 | < 25mph | E5766 | 4.34 | 2018-01-19T21:41:00Z | 8.99 | 34 | < 25mph
PG&E | 2017-09-23 | 14:17 | 40.6509 | -122.2974 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DARREN STEWART 448-2421 | 101467221 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43001 | 14:17 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1429 | 2017 | 9 | 23 | 14 | 17 | 17-0081216 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 98820 | 17.9072 | 145_386 | <25mph | <15mph | HFTD - Distribution | 2017-09-23 14:17:00 | 1167 | 24.6958 | FALSE | <25mph | C5599 | 3.73 | 2018-04-22T18:17:00Z | 14 | 3 | < 25mph | C5599 | 3.73 | 2018-04-22T18:17:00Z | 14 | 3 | < 25mph | C5599 | 3.73 | 2018-04-22T18:46:00Z | 14.99 | 6 | < 25mph | C5599 | 3.73 | 2018-04-22T18:46:00Z | 14.99 | 6 | < 25mph
PG&E | 2018-06-23 | 9:31 | 40.8632 | -122.3962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | RYAN MEANS 530-238-2416 | 101472252 | AT&T | 12000 | Conductor | Overhead | Yes | 43274 | 9:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1688 | 2018 | 6 | 23 | 9 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2018-06-23 09:31:00 | NA | 0 | FALSE | <25mph | CTANT | 1.62 | 2018-09-18T01:45:00Z | 4.97 | 3 | < 25mph | SLFC1 | 4.17 | 2018-09-18T01:19:00Z | 13 | 4 | < 25mph | CTANT | 1.62 | 2018-09-18T01:45:00Z | 4.97 | 6 | < 25mph | SLFC1 | 4.17 | 2018-09-18T01:19:00Z | 13 | 8 | < 25mph
PG&E | 2015-07-01 12:57 | 2015-07-01 12:57 | 39.4146 | -121.379 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42186.5396 | 2015-07-01 12:57 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0434 | 2015 | 7 | 1 | 12 | 57 | 15-0044609 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 12.6482 | 183_317 | <25mph | <15mph | HFTD - Distribution | 2015-07-01 12:57:00 | 179 | 18.7031 | FALSE | <25mph | BNGC1 | 2.37 | 2015-07-15T23:51:00Z | 12.01 | 1 | < 25mph | BNGC1 | 2.37 | 2015-07-15T23:51:00Z | 12.01 | 1 | < 25mph | BNGC1 | 2.37 | 2015-07-16T00:51:00Z | 12.01 | 2 | < 25mph | BNGC1 | 2.37 | 2015-07-16T00:51:00Z | 12.01 | 2 | < 25mph
PG&E | 2017-04-25 12:39 | 12:38 | 38.6583 | -120.9762 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101376746 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 42850.5271 | 12:38 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1072 | 2017 | 4 | 25 | 12 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 9.948 | 200_275 | <25mph | <15mph | HFTD - Distribution | 2017-04-25 12:38:00 | 812 | 10.5664 | FALSE | <25mph | PG072 | 3.57 | 2019-02-23T21:50:00Z | 12.93 | 26 | < 25mph | PG072 | 3.57 | 2019-02-23T21:50:00Z | 12.93 | 130 | < 25mph | PG072 | 3.57 | 2019-02-23T21:50:00Z | 12.93 | 52 | < 25mph | PG072 | 3.57 | 2019-02-23T21:50:00Z | 12.93 | 259 | < 25mph
PG&E | 2017-07-05 12:11 | 11:58 | 39.2105 | -121.2266 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVE ROBERTSON 530 906 4892 | 100010286 | Unknown | 21000 | Conductor | Overhead | Yes | 42921.5077 | 11:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1223 | 2017 | 7 | 5 | 11 | 58 | 17-0060605 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 10231 | 9.71 | 190_306 | <25mph | <15mph | HFTD - Distribution | 2017-07-05 11:58:00 | 962 | 14.0848 | FALSE | <25mph | E2572 | 2.49 | 2016-12-13T04:33:00Z | 0 | 10 | < 25mph | E1789 | 6.76 | 2016-12-13T04:30:00Z | 4.99 | 31 | < 25mph | E2572 | 2.49 | 2016-12-13T05:18:00Z | 1.01 | 22 | < 25mph | E1789 | 6.76 | 2016-12-13T04:30:00Z | 4.99 | 64 | < 25mph
PG&E | 2017-07-01 | 12:02 | 39.8209 | -121.6418 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 003/039 | Unknown | 60000 | Conductor | Overhead | Yes | 42917 | 12:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1212 | 2017 | 7 | 1 | 12 | 2 | INT-09792 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.6345 | 172_339 | <25mph | <15mph | HFTD - Transmission | 2017-07-01 12:02:00 | 954 | 9.664 | FALSE | <25mph | C4565 | 2.41 | 2017-07-27T00:43:00Z | 4 | 16 | < 25mph | CSTC1 | 7.61 | 2017-07-27T00:51:00Z | 12.01 | 18 | < 25mph | C4565 | 2.41 | 2017-07-27T00:43:00Z | 4 | 33 | < 25mph | CSTC1 | 7.61 | 2017-07-27T00:51:00Z | 12.01 | 37 | < 25mph
PG&E | 2017-07-02 | 13:28 | 39.8605 | -121.6274 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 000/017c | Unknown | 60000 | Conductor | Overhead | Yes | 42918 | 13:28 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1216 | 2017 | 7 | 2 | 13 | 28 | INT-09794 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 10.1141 | 173_342 | <25mph | <15mph | HFTD - Transmission | 2017-07-02 13:28:00 | 956 | 11.4462 | FALSE | <25mph | PG333 | 3.91 | 2019-07-21T14:30:00Z | 8.32 | 34 | < 25mph | PG333 | 3.91 | 2019-07-21T14:30:00Z | 8.32 | 60 | < 25mph | PG333 | 3.91 | 2019-07-21T14:30:00Z | 8.32 | 68 | < 25mph | PG333 | 3.91 | 2019-07-21T14:30:00Z | 8.32 | 120 | < 25mph
PG&E | 2016-07-16 00:58 | 2016-07-16 00:58 | 36.4379 | -121.9198 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101669758 |  | 12000 | Other | Overhead | Yes | 42567.0403 | 2016-07-16 00:58 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0855 | 2016 | 7 | 16 | 0 | 58 | 16-0050335 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 8976 | 11.1025 | 159_153 | <25mph | <15mph | HFTD - Distribution | 2016-07-16 00:58:00 | 598 | 18.5622 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6019 | 7.86 | 2015-09-06T09:05:00Z | 11.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6019 | 7.86 | 2015-09-06T09:05:00Z | 11.01 | 8 | < 25mph
PG&E | 2016-01-21 21:32 | 2016-01-21 21:32 | 40.553 | -124.1116 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100994021 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42390.8972 | 2016-01-21 21:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0690 | 2016 | 1 | 21 | 21 | 32 | 16-0007239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 6468 | 26.2481 | 69_382 | 25-40mph | 15-30mph | HFTD - Distribution | 2016-01-21 21:32:00 | 434 | 29.6828 | FALSE | 25-40mph | C5061 | 1.29 | 2016-03-17T15:57:00Z | 13 | 27 | < 25mph | C5061 | 1.29 | 2016-03-17T15:57:00Z | 13 | 27 | < 25mph | C5061 | 1.29 | 2016-03-17T17:22:00Z | 13 | 54 | < 25mph | C5061 | 1.29 | 2016-03-17T17:22:00Z | 13 | 54 | < 25mph
PG&E | 2018-07-30 | 14:36 | 38.1987 | -120.3638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NICK WEBB ( 209) 532-7424 | 103336176 | Unknown | 17000 | Conductor | Overhead | Yes | 43311 | 14:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1800 | 2018 | 7 | 30 | 14 | 36 | 18-0065131 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18530 | 10.5817 | 227_250 | <25mph | <15mph | HFTD - Distribution | 2018-07-30 14:36:00 | 1540 | 14.4256 | FALSE | <25mph | E1299 | 3.7 | 2015-01-18T15:40:00Z | 1.01 | 18 | < 25mph | E1299 | 3.7 | 2015-01-18T15:40:00Z | 1.01 | 18 | < 25mph | AR738 | 3.05 | 2015-01-18T16:50:00Z | 3 | 32 | < 25mph | AR738 | 3.05 | 2015-01-18T16:50:00Z | 3 | 32 | < 25mph
PG&E | 2016-07-29 | 18:16 | 38.5769 | -122.6187 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Selma Fire Department |  |  | 12000 | Conductor | Overhead | Yes | 42580 | 18:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0890 | 2016 | 7 | 29 | 18 | 16 | 16-0053726 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 177834 | 13.7145 | 130_271 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 18:16:00 | 635 | 15.1116 | FALSE | <25mph | PG229 | 2.9 | 2019-07-20T16:10:00Z | 9.64 | 38 | < 25mph | PG162 | 7.54 | 2019-07-20T15:20:00Z | 17.76 | 84 | < 25mph | PG229 | 2.9 | 2019-07-20T16:10:00Z | 9.64 | 72 | < 25mph | PG162 | 7.54 | 2019-07-20T15:20:00Z | 17.76 | 158 | < 25mph
PG&E | 2016-06-21 | 2016-06-21 16:53 | 38.4233 | -122.5448 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | KENWOOD FIRE XST | 102036904 | Yes | 0 – 750 | Conductor | Overhead | Yes | 42542 | 2016-06-21 16:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0814 | 2016 | 6 | 21 | 16 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 14.0146 | 133_263 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 16:53:00 | 556 | 14.0381 | FALSE | <25mph | E9543 | 3.01 | 2017-05-19T09:44:00Z | 4 | 5 | < 25mph | E1582 | 5.25 | 2017-05-19T10:00:00Z | 7 | 19 | < 25mph | E9543 | 3.01 | 2017-05-19T09:44:00Z | 4 | 10 | < 25mph | E1582 | 5.25 | 2017-05-19T10:30:00Z | 8.99 | 40 | < 25mph
PG&E | 2019-01-16 | 0:17 | 38.0621 | -120.1964 | Vegetation | Conifer Forest | Structure Only | Cal Fire |  | 163661701 |  | 17000 | Conductor | Overhead | Yes | 43481 | 0:17 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-01 | 2019 | 1 | 16 | 0 | 17 | 19-0010443 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1041827 | 14.8061 | 234_243 | <25mph | <15mph | HFTD - Distribution | 2019-01-16 00:17:00 | 1728 | 28.2081 | FALSE | 25-40mph | MOUC1 | 2.77 | 2019-07-24T09:02:00Z | 4.99 | 1 | < 25mph | PG067 | 4.95 | 2019-07-24T08:50:00Z | 7 | 19 | < 25mph | MOUC1 | 2.77 | 2019-07-24T10:02:00Z | 4.99 | 2 | < 25mph | PG067 | 4.95 | 2019-07-24T08:50:00Z | 7 | 38 | < 25mph
PG&E | 2016-08-03 | 2016-08-03 04:38 | 38.8474 | -120.812 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire garden valley fire | 103809676 |  | 21000 | Conductor | Overhead | Yes | 42585 | 2016-08-03 04:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0901 | 2016 | 8 | 3 | 4 | 38 | 16-0054597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2751 | 9.4989 | 208_286 | <25mph | <15mph | HFTD - Distribution | 2016-08-03 04:38:00 | 644 | 11.5219 | FALSE | <25mph | PG022 | 1.4 | 2018-08-25T17:50:00Z | 7 | 19 | < 25mph | BDMC1 | 6.95 | 2018-08-25T17:36:00Z | 12.01 | 57 | < 25mph | PG022 | 1.4 | 2018-08-25T18:30:00Z | 7.45 | 37 | < 25mph | BDMC1 | 6.95 | 2018-08-25T18:36:00Z | 14.99 | 112 | < 25mph
PG&E | 2018-11-09 | 8:59 | 37.2809 | -122.1214 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100546562 | AT&T | 12000 | Conductor | Overhead | Yes | 43413 | 8:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1964 | 2018 | 11 | 9 | 8 | 59 | 18-0098521 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 77077 | 5.2345 | 150_200 | <25mph | <15mph | HFTD - Distribution | 2018-11-09 08:59:00 | 1704 | 17.3931 | FALSE | <25mph | E0516 | 1.72 | 2016-08-09T21:37:00Z | 8.99 | 15 | < 25mph | E8945 | 6.54 | 2016-08-09T22:11:00Z | 13 | 121 | < 25mph | E0516 | 1.72 | 2016-08-09T22:52:00Z | 14.99 | 29 | < 25mph | E0516 | 1.72 | 2016-08-09T22:52:00Z | 14.99 | 239 | < 25mph
PG&E | 2015-02-23 13:25 | 2015-02-23 13:25 | 38.5046 | -122.7408 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RINCON VALLEY | BEHIND 4870 CARRIAGE LN SANTA ROSA |  | 12000 | Conductor | Overhead | Yes | 42058.559 | 2015-02-23 13:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0268 | 2015 | 2 | 23 | 13 | 25 | 15-0015168 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 85762 | 20.3218 | 124_267 | <25mph | <15mph | HFTD - Distribution | 2015-02-23 13:25:00 | 15 | 32.6885 | FALSE | 25-40mph | C0677 | 3.78 | 2016-05-01T22:37:00Z | 20 | 16 | < 25mph | C0677 | 3.78 | 2016-05-01T22:37:00Z | 20 | 88 | < 25mph | RSAC1 | 2.39 | 2016-05-01T23:29:00Z | 21 | 32 | < 25mph | RSAC1 | 2.39 | 2016-05-01T23:29:00Z | 21 | 176 | < 25mph
PG&E | 2017-10-02 | 14:56 | 38.9102 | -120.9185 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100110800 | None | 21000 | Other | Overhead | Yes | 43010 | 14:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1447 | 2017 | 10 | 2 | 14 | 56 | 17-0083516 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 160 | 17.2967 | 203_289 | <25mph | <15mph | HFTD - Distribution | 2017-10-02 14:56:00 | 1185 | 22.7009 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.3 | 2018-05-05T05:56:00Z | 3 | 13 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.3 | 2018-05-05T06:56:00Z | 3 | 26 | < 25mph
PG&E | 2019-06-10 | 16:34 | 38.821 | -120.846 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Garden Valley FD | 153082106 |  | 21000 | Conductor | Overhead | Yes | 43626 | 16:34 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-372 | 2019 | 6 | 10 | 16 | 34 | 19-0065481 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14169 | 8.5329 | 206_284 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 16:34:00 | 1827 | 15.7607 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E3165 | 5.57 | 2017-02-22T12:22:00Z | 8.01 | 30 | < 25mph |  |  |  | 0 | 0 | No data | E3165 | 5.57 | 2017-02-22T12:22:00Z | 8.01 | 60 | < 25mph
PG&E | 2017-04-25 12:39 | 12:38 | 38.6583 | -120.9762 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101376746 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 42850.5271 | 12:38 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1072 | 2017 | 4 | 25 | 12 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 9.948 | 200_275 | <25mph | <15mph | HFTD - Distribution | 2017-04-25 12:38:00 | 812 | 10.5664 | FALSE | <25mph | PG357 | 3.05 | 2019-11-12T10:00:00Z | 4.61 | 38 | < 25mph | PG106 | 5.51 | 2019-11-12T10:00:00Z | 7.09 | 137 | < 25mph | PG357 | 3.05 | 2019-11-12T11:30:00Z | 5.35 | 76 | < 25mph | PG111 | 6.53 | 2019-11-12T11:50:00Z | 7.31 | 272 | < 25mph
PG&E | 2018-10-24 | 7:08 | 37.9475 | -120.2671 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SCOTT PITTMAN 209-768-8182 TCU INCIDENT# 012528 | 101047865 | Unknown | 17000 | Conductor | Overhead | Yes | 43397 | 7:08 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1949 | 2018 | 10 | 24 | 7 | 8 | 18-0093599 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 13433 | 8.6394 | 231_236 | <25mph | <15mph | HFTD - Distribution | 2018-10-24 07:08:00 | 1688 | 12.0171 | FALSE | <25mph | C3161 | 2.32 | 2017-08-02T03:41:00Z | 4.99 | 3 | < 25mph | C3161 | 2.32 | 2017-08-02T03:41:00Z | 4.99 | 3 | < 25mph | C3161 | 2.32 | 2017-08-02T03:41:00Z | 4.99 | 7 | < 25mph | C3161 | 2.32 | 2017-08-02T03:41:00Z | 4.99 | 7 | < 25mph
PG&E | 2015-12-03 12:10 | 2015-12-03 12:10 | 40.0277 | -120.9652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | usfs | spanish creek campground |  | 12000 | Conductor | Overhead | Yes | 42341.5069 | 2015-12-03 12:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0683 | 2015 | 12 | 3 | 12 | 10 | 15-0082505 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 196854 | 26.293 | 201_351 | 25-40mph | 15-30mph | HFTD - Distribution | 2015-12-03 12:10:00 | 427 | 26.9543 | FALSE | 25-40mph | CHAC1 | 3.2 | 2017-04-05T07:47:00Z | 5.99 | 2 | < 25mph | CHAC1 | 3.2 | 2017-04-05T07:47:00Z | 5.99 | 3 | < 25mph | CHAC1 | 3.2 | 2017-04-05T07:47:00Z | 5.99 | 4 | < 25mph | CHAC1 | 3.2 | 2017-04-05T07:47:00Z | 5.99 | 6 | < 25mph
PG&E | 2017-06-15 08:08 | 7:39 | 39.2276 | -121.2348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE CHIEF | 103676075 | Unknown | 21000 | Conductor | Overhead | Yes | 42901.3391 | 7:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1147 | 2017 | 6 | 15 | 7 | 39 | 17-0055387 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 740 | 10.5195 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 07:39:00 | 886 | 12.4202 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1789 | 7.9 | 2019-03-10T10:48:00Z | 8.01 | 16 | < 25mph |  |  |  | 0 | 0 | No data | E1789 | 7.9 | 2019-03-10T12:06:00Z | 8.99 | 32 | < 25mph
PG&E | 2017-08-14 | 23:52 | 37.1272 | -122.1689 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 015/127 | None | 60000 | Conductor | Overhead | Yes | 42961 | 23:52 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1333 | 2017 | 8 | 14 | 23 | 52 | INT-09976 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 1790869 | 16.3701 | 148_191 | <25mph | <15mph | HFTD - Transmission | 2017-08-14 23:52:00 | 1072 | 18.2518 | FALSE | <25mph | BNDC1 | 0.33 | 2017-04-27T16:50:00Z | 17 | 19 | < 25mph | BNDC1 | 0.33 | 2017-04-27T16:50:00Z | 17 | 30 | < 25mph | BNDC1 | 0.33 | 2017-04-27T16:50:00Z | 17 | 35 | < 25mph | BNDC1 | 0.33 | 2017-04-27T16:50:00Z | 17 | 58 | < 25mph
PG&E | 2016-09-12 | 12:38 | 38.7832 | -120.6006 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101421708 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42625 | 12:38 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0974 | 2016 | 9 | 12 | 12 | 38 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 15.5165 | 217_282 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 12:38:00 | 716 | 15.5342 | FALSE | <25mph | PG105 | 2.18 | 2019-12-27T20:50:00Z | 10.51 | 12 | < 25mph | PG077 | 7.81 | 2019-12-27T20:50:00Z | 11.18 | 37 | < 25mph | PG105 | 2.18 | 2019-12-27T20:50:00Z | 10.51 | 24 | < 25mph | PG077 | 7.81 | 2019-12-27T20:50:00Z | 11.18 | 73 | < 25mph
PG&E | 2016-04-21 09:25 | 2016-04-21 09:25 | 39.293 | -123.769 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 103312287 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0711 | 2016 | 4 | 21 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 8.8774 | 81_312 | <25mph | <15mph | HFTD - Distribution | 2016-04-21 09:25:00 | 455 | 20.2474 | FALSE | <25mph | E6025 | 0.21 | 2017-07-04T04:15:00Z | 3 | 4 | < 25mph | E6025 | 0.21 | 2017-07-04T04:15:00Z | 3 | 4 | < 25mph | E6025 | 0.21 | 2017-07-04T04:15:00Z | 3 | 8 | < 25mph | E6025 | 0.21 | 2017-07-04T04:15:00Z | 3 | 8 | < 25mph
PG&E | 2017-06-24 15:06 | 14:51 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 42910.6292 | 14:51 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1194 | 2017 | 6 | 24 | 14 | 51 | 17-0058332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 21296 | 10.4286 | 210_259 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 14:51:00 | 933 | 10.7263 | FALSE | <25mph | ANUC1 | 1.37 | 2017-02-10T21:53:00Z | 4 | 7 | < 25mph | MTZC1 | 6.33 | 2017-02-10T21:56:00Z | 5.99 | 8 | < 25mph | ANUC1 | 1.37 | 2017-02-10T21:53:00Z | 4 | 13 | < 25mph | MTZC1 | 6.33 | 2017-02-10T22:56:00Z | 8.01 | 15 | < 25mph
PG&E | 2017-09-06 | 20:08 | 37.2925 | -122.294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100256917 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1400 | 2017 | 9 | 6 | 20 | 8 | 17-0076502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4914 | 6.7999 | 143_200 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 20:08:00 | 1138 | 13.6021 | FALSE | <25mph | LAHC1 | 2.3 | 2018-06-19T00:07:00Z | 5.99 | 1 | < 25mph | E4825 | 7.69 | 2018-06-19T00:11:00Z | 10 | 18 | < 25mph | LAHC1 | 2.3 | 2018-06-19T01:07:00Z | 5.99 | 2 | < 25mph | E4825 | 7.69 | 2018-06-19T01:06:00Z | 10 | 35 | < 25mph
PG&E | 2018-08-22 | 21:56 | 39.0425 | -120.9695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100024728 | Verizon | 12000 | Conductor | Overhead | Yes | 43334 | 21:56 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1854 | 2018 | 8 | 22 | 21 | 56 | 18-0072654 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29727 | 9.3137 | 201_296 | <25mph | <15mph | HFTD - Distribution | 2018-08-22 21:56:00 | 1593 | 10.5291 | FALSE | <25mph | D9434 | 1.28 | 2016-02-02T18:38:00Z | 1.01 | 10 | < 25mph | AT999 | 4.33 | 2016-02-02T18:42:00Z | 4.99 | 42 | < 25mph | D9434 | 1.28 | 2016-02-02T19:38:00Z | 1.01 | 20 | < 25mph | AT999 | 4.33 | 2016-02-02T18:57:00Z | 8.01 | 75 | < 25mph
PG&E | 2016-05-18 | 18:24 | 39.7381 | -123.1587 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42508 | 18:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0735 | 2016 | 5 | 18 | 18 | 24 | 16-0036911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1482 | 13.4862 | 108_336 | <25mph | <15mph | HFTD - Distribution | 2016-05-18 18:24:00 | 480 | 21.4181 | FALSE | <25mph | C3111 | 2.79 | 2017-08-29T03:00:00Z | 1.01 | 2 | < 25mph | EELC1 | 7.26 | 2017-08-29T02:45:00Z | 4.99 | 3 | < 25mph | C3111 | 2.79 | 2017-08-29T03:30:00Z | 3 | 4 | < 25mph | EELC1 | 7.26 | 2017-08-29T02:45:00Z | 4.99 | 6 | < 25mph
PG&E | 2015-07-04 01:14 | 2015-07-04 01:14 | 38.9566 | -121.0434 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100037226 |  | 12000 | Other | Overhead | Yes | 42189.0514 | 2015-07-04 01:14 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0441 | 2015 | 7 | 4 | 1 | 14 | 15-0045440 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 53865 | 7.3476 | 198_292 | <25mph | <15mph | HFTD - Distribution | 2015-07-04 01:14:00 | 186 | 12.3228 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8862 | 5.23 | 2018-05-11T04:41:00Z | 1.01 | 23 | < 25mph |  |  |  | 0 | 0 | No data | D8862 | 5.23 | 2018-05-11T05:57:00Z | 2.01 | 46 | < 25mph
PG&E | 2015-10-09 06:32 | 2015-10-09 06:32 | 38.364 | -122.9173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 320 Freestone St, Frestone | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0642 | 2015 | 10 | 9 | 6 | 32 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 2.6818 | 117_260 | <25mph | <15mph | HFTD - Distribution | 2015-10-09 06:32:00 | 386 | 15.5803 | FALSE | <25mph | E9690 | 2.76 | 2019-04-25T17:13:00Z | 1.01 | 23 | < 25mph | BGAC1 | 8 | 2019-04-25T17:05:00Z | 7 | 63 | < 25mph | E9690 | 2.76 | 2019-04-25T18:03:00Z | 7 | 45 | < 25mph | AR323 | 5.17 | 2019-04-25T17:48:00Z | 8.99 | 123 | < 25mph
PG&E | 2016-10-14 04:33 | 4:32 | 40.5228 | -121.6813 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101513661 |  | 12000 | Conductor | Overhead | Yes | 42657.1893 | 4:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1032 | 2016 | 10 | 14 | 4 | 32 | 16-0071897 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 38950 | 28.7152 | 171_378 | 25-40mph | 15-30mph | HFTD - Distribution | 2016-10-14 04:32:00 | 773 | 31.1927 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | VIOC1 | 5.45 | 2019-04-02T17:52:00Z | 7 | 1 | < 25mph |  |  |  | 0 | 0 | No data | VIOC1 | 5.45 | 2019-04-02T18:52:00Z | 10 | 2 | < 25mph
PG&E | 2019-08-14 | 10:16 | 35.379 | -120.4232 | Vegetation | Hardwood Woodland | < 1 meter | Cal Fire |  | 512769069280 |  | 21000 | Conductor | Overhead | Yes | 43691 | 10:16 | Vegetation | [5 empty] | no-match |  | 2019 | 8 | 14 | 10 | 16 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.0314 | 226_94 | <25mph | <15mph | HFTD - Distribution | 2019-08-14 10:16:00 | 1976 | 14.3934 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-08-14 | 15:46 | 38.0878 | -122.6002 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103916882 | Verizon | 0 – 750 | Conductor | Overhead | Yes | 43326 | 15:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1844 | 2018 | 8 | 14 | 15 | 46 | 18-0069929 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 546 | 20.6189 | 130_244 | <25mph | <15mph | HFTD - Distribution | 2018-08-14 15:46:00 | 1583 | 26.2074 | FALSE | 25-40mph | NBRC1 | 3.72 | 2016-12-21T01:33:00Z | 7 | 18 | < 25mph | NBRC1 | 3.72 | 2016-12-21T01:33:00Z | 7 | 32 | < 25mph | NBRC1 | 3.72 | 2016-12-21T02:33:00Z | 10 | 36 | < 25mph | NBRC1 | 3.72 | 2016-12-21T02:33:00Z | 10 | 63 | < 25mph
PG&E | 2015-09-10 05:42 | 2015-09-10 05:42 | 37.4609 | -121.8434 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100619766 | None | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0588 | 2015 | 9 | 10 | 5 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 1.7354 | 163_209 | <25mph | <15mph | HFTD - Distribution | 2015-09-10 05:42:00 | 333 | 13.8129 | FALSE | <25mph | E3968 | 2.89 | 2015-11-07T06:50:00Z | 3 | 12 | < 25mph | RSPC1 | 6.56 | 2015-11-07T06:28:00Z | 11.01 | 16 | < 25mph | E3968 | 2.89 | 2015-11-07T07:35:00Z | 3 | 25 | < 25mph | RSPC1 | 6.56 | 2015-11-07T06:28:00Z | 11.01 | 33 | < 25mph
PG&E | 2017-06-24 15:06 | 14:51 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 42910.6292 | 14:51 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1194 | 2017 | 6 | 24 | 14 | 51 | 17-0058332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 21296 | 10.4286 | 210_259 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 14:51:00 | 933 | 10.7263 | FALSE | <25mph | TS389 | 1.42 | 2018-06-08T18:53:00Z | 11.01 | 2 | < 25mph | TS389 | 1.42 | 2018-06-08T18:53:00Z | 11.01 | 4 | < 25mph | TS389 | 1.42 | 2018-06-08T19:53:00Z | 12.01 | 4 | < 25mph | TS389 | 1.42 | 2018-06-08T19:53:00Z | 12.01 | 7 | < 25mph
PG&E | 2019-07-25 | 7:39 | 39.1735 | -123.5763 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Oj 2 P/Ss Of Cgc# 215532055340 |  | 12000 | Other | Overhead | Yes | 43671 | 7:39 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-380 | 2019 | 7 | 25 | 7 | 39 | 19-0080947 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 790 | 2.0398 | 89_305 | <25mph | <15mph | HFTD - Distribution | 2019-07-25 07:39:00 | 1928 | 13.3511 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1763 | 7.11 | 2018-03-04T13:58:00Z | 3 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E1763 | 7.11 | 2018-03-04T14:44:00Z | 4 | 8 | < 25mph
PG&E | 2018-08-28 | 12:50 | 40.2139 | -123.5966 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100994840 | Unknown | 12000 | Conductor | Overhead | Yes | 43340 | 12:50 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1866 | 2018 | 8 | 28 | 12 | 50 | 18-0074371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 82754 | 9.6027 | 90_363 | <25mph | <15mph | HFTD - Distribution | 2018-08-28 12:50:00 | 1605 | 19.5452 | FALSE | <25mph | ALDC1 | 1.95 | 2019-04-06T21:51:00Z | 17 | 1 | < 25mph | ALDC1 | 1.95 | 2019-04-06T21:51:00Z | 17 | 1 | < 25mph | ALDC1 | 1.95 | 2019-04-06T21:51:00Z | 17 | 2 | < 25mph | ALDC1 | 1.95 | 2019-04-06T21:51:00Z | 17 | 2 | < 25mph
PG&E | 2017-06-24 10:32 | 10:31 | 38.9438 | -121.0447 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100090318 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42910.439 | 10:31 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1193 | 2017 | 6 | 24 | 10 | 31 | 17-0058318 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 582 | 9.5424 | 198_291 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 10:31:00 | 932 | 10.7882 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG349 | 4.78 | 2019-06-16T18:00:00Z | 10.51 | 39 | < 25mph | KAUN | 2.38 | 2019-06-16T19:15:00Z | 11.5 | 1 | < 25mph | PG349 | 4.78 | 2019-06-16T18:30:00Z | 12.06 | 82 | < 25mph
PG&E | 2015-06-28 02:50 | 2015-06-28 02:50 | 35.491 | -120.731 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 13505 Santa Lucia Rd. Atascadero |  | 12000 | Conductor | Overhead | Yes | 42183.1181 | 2015-06-28 02:50 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0418 | 2015 | 6 | 28 | 2 | 50 | 15-0043807 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 12323 | 9.9634 | 212_101 | <25mph | <15mph | HFTD - Distribution | 2015-06-28 02:50:00 | 163 | 24.8049 | FALSE | <25mph | E6394 | 1.17 | 2017-07-04T22:29:00Z | 13 | 8 | < 25mph | E6394 | 1.17 | 2017-07-04T22:29:00Z | 13 | 15 | < 25mph | E6394 | 1.17 | 2017-07-04T23:59:00Z | 13 | 16 | < 25mph | E6394 | 1.17 | 2017-07-04T23:59:00Z | 13 | 30 | < 25mph
PG&E | 2015-09-19 09:51 | 2015-09-19 09:51 | 38.4755 | -122.9069 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FORESTVILLE | 103334444 |  | 12000 | Conductor | Overhead | Yes | 42266.4104 | 2015-09-19 09:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0603 | 2015 | 9 | 19 | 9 | 51 | 15-0062267 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 488 | 1.1332 | 117_266 | <25mph | <15mph | HFTD - Distribution | 2015-09-19 09:51:00 | 348 | 13.7107 | FALSE | <25mph | R30WW | 2.12 | 2017-12-14T22:00:00Z | 8.7 | 18 | < 25mph | R30WW | 2.12 | 2017-12-14T22:00:00Z | 8.7 | 109 | < 25mph | R30WW | 2.12 | 2017-12-14T22:00:00Z | 8.7 | 36 | < 25mph | R30WW | 2.12 | 2017-12-14T22:00:00Z | 8.7 | 218 | < 25mph
PG&E | 2018-11-17 | 17:20 | 38.7082 | -120.6927 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101421319 | Unknown | 12000 | Conductor | Overhead | Yes | 43421 | 17:20 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1977 | 2018 | 11 | 17 | 17 | 20 | 18-0100697 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 35749 | 6.6792 | 213_278 | <25mph | <15mph | HFTD - Distribution | 2018-11-17 17:20:00 | 1717 | 12.841 | FALSE | <25mph | E4543 | 3.98 | 2015-04-26T04:28:00Z | 1.01 | 4 | < 25mph | E3165 | 7.06 | 2015-04-26T04:34:00Z | 5.99 | 32 | < 25mph | E4543 | 3.98 | 2015-04-26T05:29:00Z | 1.01 | 8 | < 25mph | E5691 | 6.11 | 2015-04-26T05:35:00Z | 5.99 | 63 | < 25mph
PG&E | 2017-08-14 | 23:52 | 37.1272 | -122.1689 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 015/127 | None | 60000 | Conductor | Overhead | Yes | 42961 | 23:52 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1333 | 2017 | 8 | 14 | 23 | 52 | INT-09976 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 1790869 | 16.3701 | 148_191 | <25mph | <15mph | HFTD - Transmission | 2017-08-14 23:52:00 | 1072 | 18.2518 | FALSE | <25mph | BNDC1 | 0.33 | 2018-03-28T19:50:00Z | 14.99 | 18 | < 25mph | BNDC1 | 0.33 | 2018-03-28T19:50:00Z | 14.99 | 27 | < 25mph | BNDC1 | 0.33 | 2018-03-28T20:50:00Z | 14.99 | 36 | < 25mph | BNDC1 | 0.33 | 2018-03-28T20:50:00Z | 14.99 | 51 | < 25mph
PG&E | 2016-08-10 | 2016-08-10 08:36 | 37.0575 | -121.9556 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 101680487 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0917 | 2016 | 8 | 10 | 8 | 36 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 6.3982 | 157_187 | <25mph | <15mph | HFTD - Distribution | 2016-08-10 08:36:00 | 659 | 9.833 | FALSE | <25mph | E5965 | 0.91 | 2018-01-02T07:10:00Z | 3 | 37 | < 25mph | D8979 | 4.8 | 2018-01-02T07:38:00Z | 8.01 | 156 | < 25mph | E9039 | 1.19 | 2018-01-02T08:29:00Z | 3 | 74 | < 25mph | D8979 | 4.8 | 2018-01-02T07:58:00Z | 8.01 | 310 | < 25mph
PG&E | 2017-07-23 18:25 | 18:25 | 39.6723 | -123.5336 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103823226 | Unknown | 12000 | Conductor | Overhead | Yes | 42939.7676 | 18:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1284 | 2017 | 7 | 23 | 18 | 25 | 17-0064854 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 12864 | 11.8402 | 92_333 | <25mph | <15mph | HFTD - Distribution | 2017-07-23 18:25:00 | 1023 | 16.2282 | FALSE | <25mph | LAYC1 | 3.32 | 2018-12-16T05:29:00Z | 12.01 | 1 | < 25mph | LAYC1 | 3.32 | 2018-12-16T05:29:00Z | 12.01 | 1 | < 25mph | LAYC1 | 3.32 | 2018-12-16T06:29:00Z | 13 | 2 | < 25mph | LAYC1 | 3.32 | 2018-12-16T06:29:00Z | 13 | 2 | < 25mph
PG&E | 2017-08-15 19:29 | 19:28 | 39.5037 | -121.2783 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 100396172 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42962.8116 | 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1335 | 2017 | 8 | 15 | 19 | 28 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.8405 | 188_322 | <25mph | <15mph | HFTD - Distribution | 2017-08-15 19:28:00 | 1073 | 9.7276 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PKCC1 | 4.51 | 2015-03-16T05:10:00Z | 11.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | PKCC1 | 4.51 | 2015-03-16T06:10:00Z | 13 | 2 | < 25mph
PG&E | 2017-12-29 | 16:31 | 37.8517 | -122.1586 | Vegetation | Rural | < 3 Meters | Fire Agency | 925-933-1313 | 100488954 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1552 | 2017 | 12 | 29 | 16 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 4.4772 | 149_231 | <25mph | <15mph | HFTD - Distribution | 2017-12-29 16:31:00 | 1294 | 9.6531 | FALSE | <25mph | F2503 | 2.91 | 2019-02-04T01:46:00Z | 34.99 | 57 | 25-40mph | LTRC1 | 5.15 | 2019-02-04T01:28:00Z | 42.01 | 171 | 40-55mph | F2503 | 2.91 | 2019-02-04T01:46:00Z | 34.99 | 114 | 25-40mph | LTRC1 | 5.15 | 2019-02-04T01:28:00Z | 42.01 | 339 | 40-55mph
PG&E | 2018-10-16 | 10:44 | 40.5097 | -124.1624 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101004106 | Unknown | 12000 | Conductor | Overhead | Yes | 43389 | 10:44 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1942 | 2018 | 10 | 16 | 10 | 44 | 18-0090952 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 2081 | 4.5851 | 67_380 | <25mph | <15mph | HFTD - Distribution | 2018-10-16 10:44:00 | 1681 | 13.3626 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C5061 | 4.32 | 2018-10-20T18:19:00Z | 4.99 | 21 | < 25mph |  |  |  | 0 | 0 | No data | AT493 | 4.22 | 2018-10-20T19:17:00Z | 7 | 42 | < 25mph
PG&E | 2017-09-08 | 21:14 | 37.9604 | -120.3764 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | John Lite 209-984-5623 | 101042521 | Unknown | 17000 | Conductor | Overhead | Yes | 42986 | 21:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1403 | 2017 | 9 | 8 | 21 | 14 | 17-0077137 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49858 | 11.2644 | 227_237 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 21:14:00 | 1141 | 11.9927 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C3161 | 5.93 | 2016-09-15T08:08:00Z | 0 | 4 | < 25mph |  |  |  | 0 | 0 | No data | C3161 | 5.93 | 2016-09-15T08:38:00Z | 2.01 | 8 | < 25mph
PG&E | 2017-08-29 | 12:49 | 37.4507 | -119.6454 | Vegetation | Rural | > 5000 Acres | Fire Agency | USFS | 101017368 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-29 | 12:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1366 | 2017 | 8 | 29 | 12 | 49 | 17-0073823 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | 3rd Party | 3rd Party - Unknown | 5894785 | 7.4398 | 259_209 | <25mph | <15mph | HFTD - Distribution | 2017-08-29 12:49:00 | 1104 | 13.5545 | FALSE | <25mph | D0826 | 0.24 | 2019-09-26T09:32:00Z | 8.01 | 5 | < 25mph | MIAC1 | 5.9 | 2019-09-26T08:59:00Z | 8.99 | 48 | < 25mph | D0826 | 0.24 | 2019-09-26T09:32:00Z | 8.01 | 10 | < 25mph | MIAC1 | 5.9 | 2019-09-26T09:59:00Z | 8.99 | 94 | < 25mph
PG&E | 2015-08-17 20:57 | 2015-08-17 20:57 | 36.6867 | -119.0612 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46371 ORCHARD DRIVE |  | 12000 | Conductor | Overhead | Yes | 42233.8729 | 2015-08-17 20:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0540 | 2015 | 8 | 17 | 20 | 57 | 15-0055696 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 34398 | 8.6424 | 285_168 | <25mph | <15mph | HFTD - Distribution | 2015-08-17 20:57:00 | 284 | 13.6283 | FALSE | <25mph | PHRC1 | 2.47 | 2017-07-21T11:58:00Z | 12.01 | 1 | < 25mph | PHRC1 | 2.47 | 2017-07-21T11:58:00Z | 12.01 | 12 | < 25mph | PHRC1 | 2.47 | 2017-07-21T11:58:00Z | 12.01 | 2 | < 25mph | PHRC1 | 2.47 | 2017-07-21T11:58:00Z | 12.01 | 24 | < 25mph
PG&E | 2017-12-29 | 16:31 | 37.8517 | -122.1586 | Vegetation | Rural | < 3 Meters | Fire Agency | 925-933-1313 | 100488954 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1552 | 2017 | 12 | 29 | 16 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 4.4772 | 149_231 | <25mph | <15mph | HFTD - Distribution | 2017-12-29 16:31:00 | 1294 | 9.6531 | FALSE | <25mph | ONOC1 | 3.52 | 2018-10-07T19:33:00Z | 24.99 | 67 | < 25mph | LTRC1 | 5.15 | 2018-10-07T20:28:00Z | 25.99 | 170 | 25-40mph | PG054 | 3.53 | 2018-10-07T21:30:00Z | 26.31 | 133 | 25-40mph | LTRC1 | 5.15 | 2018-10-07T21:28:00Z | 27 | 339 | 25-40mph
PG&E | 2019-08-20 | 9:03 | 41.1088 | -121.5034 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-297 | 2019 | 8 | 20 | 9 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 2.4258 | 178_411 | <25mph | <15mph | HFTD - Distribution | 2019-08-20 09:03:00 | 1990 | 15.6046 | FALSE | <25mph | PG384 | 3.7 | 2019-07-16T12:00:00Z | 1.97 | 6 | < 25mph | PG384 | 3.7 | 2019-07-16T12:00:00Z | 1.97 | 6 | < 25mph | PG384 | 3.7 | 2019-07-16T12:00:00Z | 1.97 | 12 | < 25mph | PG384 | 3.7 | 2019-07-16T12:00:00Z | 1.97 | 12 | < 25mph
PG&E | 2016-09-15 | 15:56 | 37.1102 | -121.9509 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100520198 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42628 | 15:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0982 | 2016 | 9 | 15 | 15 | 56 | 16-0065001 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 28900 | 4.729 | 158_190 | <25mph | <15mph | HFTD - Distribution | 2016-09-15 15:56:00 | 724 | 12.2674 | FALSE | <25mph | E5965 | 2.76 | 2015-10-13T09:59:00Z | 2.01 | 54 | < 25mph | C5272 | 4.86 | 2015-10-13T09:42:00Z | 3 | 101 | < 25mph | E5965 | 2.76 | 2015-10-13T10:59:00Z | 3 | 104 | < 25mph | E5965 | 2.76 | 2015-10-13T10:59:00Z | 3 | 192 | < 25mph
3. Redwood Valley (Mendocino Lake Complex) | 2017-10-08 | 23:36 | 39.2487 | -123.1663 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1989 | 2017 | 10 | 8 | 23 | 36 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 24.7673 | 107_309 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 23:36:00 | 1212 | 30.3049 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PG036 | 5.99 | 2018-08-04T21:20:00Z | 16.22 | 28 | < 25mph |  |  |  | 0 | 0 | No data | PG036 | 5.99 | 2018-08-04T22:30:00Z | 17.09 | 58 | < 25mph
PG&E | 2016-06-12 01:45 | 1:45 | 37.4643 | -122.3459 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Unknown | 100265854 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42533.0729 | 1:45 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0796 | 2016 | 6 | 12 | 1 | 45 | 16-0042637 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 19836 | 11.0705 | 141_210 | <25mph | <15mph | HFTD - Distribution | 2016-06-12 01:45:00 | 534 | 17.9563 | FALSE | <25mph | PUGC1 | 2.7 | 2016-06-30T20:18:00Z | 11.01 | 4 | < 25mph | C4751 | 4.14 | 2016-06-30T20:01:00Z | 12.01 | 78 | < 25mph | PUGC1 | 2.7 | 2016-06-30T21:18:00Z | 11.01 | 10 | < 25mph | AU981 | 5.46 | 2016-06-30T21:09:00Z | 13 | 154 | < 25mph
PG&E | 2016-06-21 | 20:49 | 35.5352 | -120.8457 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101900832 |  | 12000 | Conductor | Overhead | Yes | 42542 | 20:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0812 | 2016 | 6 | 21 | 20 | 49 | 16-0044904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7806 | 8.2716 | 207_103 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 20:49:00 | 558 | 17.6234 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6394 | 6.56 | 2016-06-12T09:22:00Z | 13 | 5 | < 25mph |  |  |  | 0 | 0 | No data | E6394 | 6.56 | 2016-06-12T09:52:00Z | 13 | 9 | < 25mph
PG&E | 2018-06-28 | 12:27 | 38.5982 | -121.0081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | John Reis, 530-622-3858 | 101376954 | Unknown | 21000 | Conductor | Overhead | Yes | 43279 | 12:27 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1702 | 2018 | 6 | 28 | 12 | 27 | 18-0055479 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 24671 | 12.7651 | 199_272 | <25mph | <15mph | HFTD - Distribution | 2018-06-28 12:27:00 | 1443 | 13.4512 | FALSE | <25mph | E8856 | 2.62 | 2019-07-14T10:15:00Z | 11.01 | 13 | < 25mph | PG357 | 4.52 | 2019-07-14T10:50:00Z | 16.44 | 112 | < 25mph | E8856 | 2.62 | 2019-07-14T10:15:00Z | 11.01 | 25 | < 25mph | PG357 | 4.52 | 2019-07-14T10:50:00Z | 16.44 | 215 | < 25mph
PG&E | 2019-09-27 | 10:30 | 36.5336 | -121.1464 | Vegetation | Barren/Other | 0.25 - 10 Acres | Cal Fire |  | 182492105 |  | 21000 | Conductor | Overhead | Yes | 43735 | 10:30 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-359 | 2019 | 9 | 27 | 10 | 30 | 19-0104536 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20631 | 5.3593 | 193_158 | <25mph | <15mph | HFTD - Distribution | 2019-09-27 10:30:00 | 2062 | 16.3021 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.34 | 2017-09-27T11:37:00Z | 4.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | PCLC1 | 4.34 | 2017-09-27T12:37:00Z | 5.99 | 2 | < 25mph
PG&E | 2018-07-21 | 0:23 | 38.6927 | -120.7921 | Vegetation | Rural | < 3 meters | Fire Agency | CAMINO | 101415904 | AT&T | 12000 | Conductor | Overhead | Yes | 43302 | 0:23 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1774 | 2018 | 7 | 21 | 0 | 23 | 18-0062206 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 107552 | 9.7365 | 208_277 | <25mph | <15mph | HFTD - Distribution | 2018-07-21 00:23:00 | 1514 | 11.1911 | FALSE | <25mph | PG068 | 3.77 | 2019-01-25T03:50:00Z | 9.22 | 35 | < 25mph | PG027 | 6.96 | 2019-01-25T03:20:00Z | 9.86 | 83 | < 25mph | PG068 | 3.77 | 2019-01-25T03:50:00Z | 9.22 | 69 | < 25mph | E3165 | 7.94 | 2019-01-25T04:14:00Z | 10 | 165 | < 25mph
PG&E | 2018-10-20 | 14:31 | 40.5218 | -124.1137 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Str. 003/000 | None | 60000 | Conductor | Overhead | Yes | 43393 | 14:31 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1947 | 2018 | 10 | 20 | 14 | 31 | INT-11477 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 410982 | 9.6901 | 69_380 | <25mph | <15mph | HFTD - Transmission | 2018-10-20 14:31:00 | 1686 | 10.3412 | FALSE | <25mph | AT493 | 3.34 | 2018-12-21T22:45:00Z | 13 | 20 | < 25mph | AT493 | 3.34 | 2018-12-21T22:45:00Z | 13 | 20 | < 25mph | AT493 | 3.34 | 2018-12-21T23:26:00Z | 14 | 38 | < 25mph | AT493 | 3.34 | 2018-12-21T23:26:00Z | 14 | 38 | < 25mph
PG&E | 2015-08-04 16:05 | 2015-08-04 16:05 | 40.0822 | -121.1538 | Vegetation | Rural | < 0.25 Acres | Fire Agency | USFS | 100441220 | None | 0 – 750 | Fuse | Overhead | Yes | 42220.6701 | 2015-08-04 16:05 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0511 | 2015 | 8 | 4 | 16 | 5 | 15-0052743 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 4591 | 11.3093 | 193_354 | <25mph | <15mph | HFTD - Distribution | 2015-08-04 16:05:00 | 256 | 18.1222 | FALSE | <25mph | PG129 | 3.58 | 2019-12-29T00:00:00Z | 12.06 | 12 | < 25mph | PG129 | 3.58 | 2019-12-29T00:00:00Z | 12.06 | 19 | < 25mph | PG129 | 3.58 | 2019-12-29T00:40:00Z | 14.09 | 24 | < 25mph | PG129 | 3.58 | 2019-12-29T00:40:00Z | 14.09 | 38 | < 25mph
PG&E | 2018-06-05 | 10:13 | 40.6183 | -122.3173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JASON COLLINS 530-225-4628 | 101467801 | None | 12000 | Conductor | Overhead | Yes | 43256 | 10:13 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1631 | 2018 | 6 | 5 | 10 | 13 | 18-0047539 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 277 | 7.1547 | 144_384 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 10:13:00 | 1373 | 12.6046 | FALSE | <25mph | C5599 | 1.27 | 2016-12-23T12:31:00Z | 8.99 | 4 | < 25mph | RRAC1 | 7.21 | 2016-12-23T13:24:00Z | 15.99 | 5 | < 25mph | C5599 | 1.27 | 2016-12-23T13:32:00Z | 13 | 8 | < 25mph | KRDD | 7.24 | 2016-12-23T13:37:00Z | 21.85 | 12 | < 25mph
PG&E | 2015-07-16 19:11 | 2015-07-16 19:11 | 37.1989 | -119.7712 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 20334 ROAD 400 |  | 12000 | Conductor | Overhead | Yes | 42201.7993 | 2015-07-16 19:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0465 | 2015 | 7 | 16 | 19 | 11 | 15-0048064 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 8.6422 | 254_195 | <25mph | <15mph | HFTD - Distribution | 2015-07-16 19:11:00 | 210 | 13.1745 | FALSE | <25mph | E5766 | 3.27 | 2017-05-10T14:30:00Z | 2.01 | 9 | < 25mph | E5766 | 3.27 | 2017-05-10T14:30:00Z | 2.01 | 9 | < 25mph | E5766 | 3.27 | 2017-05-10T15:35:00Z | 5.99 | 17 | < 25mph | E5766 | 3.27 | 2017-05-10T15:35:00Z | 5.99 | 17 | < 25mph
PG&E | 2017-10-16 | 12:10 | 36.5831 | -121.9368 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101781248 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43024 | 12:10 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | Other/Unknown | 1493 | 2017 | 10 | 16 | 12 | 10 | 17-0087767 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 6313 | 5.0415 | 158_161 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:10:00 | 1236 | 13.6905 | FALSE | <25mph | E6019 | 2.26 | 2017-10-17T11:03:00Z | 8.01 | 30 | < 25mph | E6019 | 2.26 | 2017-10-17T11:03:00Z | 8.01 | 34 | < 25mph | E6019 | 2.26 | 2017-10-17T11:48:00Z | 10 | 62 | < 25mph | E6019 | 2.26 | 2017-10-17T11:48:00Z | 10 | 70 | < 25mph
PG&E | 2018-10-24 | 14:18 | 36.7265 | -119.1086 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CHRIS CHRISTOPHERSON (559)493-4320 I.C #18CAFKUO15649 | 100691946 | None | 12000 | Conductor | Overhead | Yes | 43397 | 14:18 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1950 | 2018 | 10 | 24 | 14 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 7.8375 | 283_170 | <25mph | <15mph | HFTD - Distribution | 2018-10-24 14:18:00 | 1689 | 7.8887 | FALSE | <25mph | PG258 | 2.78 | 2019-06-07T07:40:00Z | 6.58 | 19 | < 25mph | PG233 | 7.68 | 2019-06-07T07:20:00Z | 14.47 | 55 | < 25mph | PG258 | 2.78 | 2019-06-07T07:40:00Z | 6.58 | 31 | < 25mph | PG233 | 7.68 | 2019-06-07T07:20:00Z | 14.47 | 97 | < 25mph
PG&E | 2017-10-08 | 22:58 | 39.3642 | -121.1131 | Vegetation | Rural | < 3 Meters | Fire Agency | INCIDENT NUMBER 26268 | 100068104 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43016 | 22:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Fell into (No defect) | 1471 | 2017 | 10 | 8 | 22 | 58 | 17-0085355 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 198802 | 15.5554 | 195_314 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 22:58:00 | 1211 | 22.0344 | FALSE | <25mph | E3651 | 3.94 | 2019-08-25T05:25:00Z | 2.01 | 20 | < 25mph | PG424 | 6.76 | 2019-08-25T05:30:00Z | 6.58 | 68 | < 25mph | PG363 | 1.51 | 2019-08-25T05:40:00Z | 2.19 | 38 | < 25mph | PG348 | 8 | 2019-08-25T06:10:00Z | 7.67 | 129 | < 25mph
PG&E | 2016-06-24 | 2016-06-24 14:38 | 40.22 | -122.283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101526647 | PACIFIC BELL | 0 – 750 | Unknown | Overhead | Yes | 42545 | 2016-06-24 14:38 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0821 | 2016 | 6 | 24 | 14 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 11.9685 | 145_362 | <25mph | <15mph | HFTD - Distribution | 2016-06-24 14:38:00 | 564 | 17.4582 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KRBL | 5.07 | 2019-07-14T19:54:00Z | 20.71 | 3 | < 25mph |  |  |  | 0 | 0 | No data | KRBL | 5.07 | 2019-07-14T20:54:00Z | 21.85 | 6 | < 25mph
PG&E | 2019-03-13 | 16:08 | 39.8831 | -122.5498 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 6Fn0313191607 |  | 12000 | Conductor | Overhead | Yes | 43537 | 16:08 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-194 | 2019 | 3 | 13 | 16 | 8 | 19-0033617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 21012 | 20.7105 | 134_343 | <25mph | <15mph | HFTD - Distribution | 2019-03-13 16:08:00 | 1734 | 26.4067 | FALSE | 25-40mph | TCKC1 | 3.76 | 2019-10-09T17:28:00Z | 35.99 | 2 | 25-40mph | PG172 | 6.15 | 2019-10-09T16:40:00Z | 40.98 | 21 | 40-55mph | TCKC1 | 3.76 | 2019-10-09T18:28:00Z | 38.99 | 3 | 25-40mph | PG172 | 6.15 | 2019-10-09T16:40:00Z | 40.98 | 41 | 40-55mph
PG&E | 2016-08-03 | 2016-08-03 12:41 | 39.3269 | -120.6033 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100001032 |  | 12000 | Conductor | Overhead | Yes | 42585 | 2016-08-03 12:41 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0902 | 2016 | 8 | 3 | 12 | 41 | 16-0054769 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 20554 | 9.0542 | 216_312 | <25mph | <15mph | HFTD - Distribution | 2016-08-03 12:41:00 | 645 | 12.3394 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2015-06-04 13:17 | 2015-06-04 13:17 | 39.2694 | -123.7841 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42159.5535 | 2015-06-04 13:17 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0344 | 2015 | 6 | 4 | 13 | 17 | 15-0038501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20525 | 22.1312 | 81_311 | <25mph | <15mph | HFTD - Distribution | 2015-06-04 13:17:00 | 90 | 22.6218 | FALSE | <25mph | E6025 | 1.61 | 2015-10-25T17:02:00Z | 4.99 | 4 | < 25mph | E6025 | 1.61 | 2015-10-25T17:02:00Z | 4.99 | 5 | < 25mph | E6025 | 1.61 | 2015-10-25T18:00:00Z | 4.99 | 8 | < 25mph | E6025 | 1.61 | 2015-10-25T18:00:00Z | 4.99 | 9 | < 25mph
PG&E | 2019-05-31 | 15:25 | 40.4431 | -121.8211 |  | Hardwood Woodland | 1 meter - < 3 meters | Self Extinguished |  | 101556319 |  | 12000 | Conductor | Overhead | Yes | 43616 | 15:25 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-88 | 2019 | 5 | 31 | 15 | 25 | 19-0060901 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 55546 | 8.5736 | 165_374 | <25mph | <15mph | HFTD - Distribution | 2019-05-31 15:25:00 | 1795 | 18.5418 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-09-16 20:56 | 2016-09-16 20:56 | 39.8387 | -121.7023 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 100441760 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42629.8722 | 2016-09-16 20:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0983 | 2016 | 9 | 16 | 20 | 56 | 16-0065273 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 314427 | 11.5178 | 170_340 | <25mph | <15mph | HFTD - Distribution | 2016-09-16 20:56:00 | 725 | 12.6422 | FALSE | <25mph | C8878 | 3.59 | 2016-07-16T17:28:00Z | 0 | 12 | < 25mph | CSTC1 | 4.21 | 2016-07-16T16:51:00Z | 8.01 | 17 | < 25mph | C8878 | 3.59 | 2016-07-16T18:28:00Z | 0 | 24 | < 25mph | CSTC1 | 4.21 | 2016-07-16T17:51:00Z | 8.99 | 34 | < 25mph
PG&E | 2017-08-28 | 10:07 | 39.0472 | -120.7859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | FORESTHILL | 100019525 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 10:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1357 | 2017 | 8 | 28 | 10 | 7 | 17-0073379 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 10077 | 5.9792 | 209_297 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 10:07:00 | 1095 | 13.4783 | FALSE | <25mph | PG023 | 1.32 | 2018-09-30T06:40:00Z | 3.06 | 10 | < 25mph | PG023 | 1.32 | 2018-09-30T06:40:00Z | 3.06 | 17 | < 25mph | PG023 | 1.32 | 2018-09-30T06:50:00Z | 3.74 | 21 | < 25mph | FSHC1 | 4.22 | 2018-09-30T07:33:00Z | 4 | 35 | < 25mph
PG&E | 2017-11-11 12:17 | 11:57 | 35.1191 | -120.3936 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Jordan Dayley ph#929-3911,engine#3467 | 101931190 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43050.5115 | 11:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1518 | 2017 | 11 | 11 | 11 | 57 | 17-0094408 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29093 | 8.6182 | 227_80 | <25mph | <15mph | HFTD - Distribution | 2017-11-11 11:57:00 | 1260 | 14.1707 | FALSE | <25mph | AU609 | 1.13 | 2017-02-17T21:12:00Z | 25.99 | 5 | 25-40mph | AU609 | 1.13 | 2017-02-17T21:12:00Z | 25.99 | 11 | 25-40mph | AU609 | 1.13 | 2017-02-17T21:12:00Z | 25.99 | 11 | 25-40mph | AU609 | 1.13 | 2017-02-17T21:12:00Z | 25.99 | 23 | 25-40mph
PG&E | 2018-07-14 | 11:34 | 38.4026 | -122.5489 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103141862 | Verizon | 12000 | Conductor | Overhead | Yes | 43295 | 11:34 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1745 | 2018 | 7 | 14 | 11 | 34 | 18-0059821 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 6426 | 11.4725 | 133_262 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 11:34:00 | 1485 | 15.7933 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1582 | 5.93 | 2018-10-02T05:53:00Z | 2.01 | 17 | < 25mph |  |  |  | 0 | 0 | No data | PG091 | 6.4 | 2018-10-02T06:20:00Z | 2.19 | 33 | < 25mph
PG&E | 2017-09-03 | 17:52 | 37.4956 | -119.8367 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101086621 | Unknown | 21000 | Transformer | Overhead | Yes | 42981 | 17:52 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 1389 | 2017 | 9 | 3 | 17 | 52 | 17-0075617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 4512 | 13.9592 | 250_212 | <25mph | <15mph | HFTD - Distribution | 2017-09-03 17:52:00 | 1127 | 22.0754 | FALSE | <25mph | JSDC1 | 3.33 | 2015-05-13T00:47:00Z | 7 | 1 | < 25mph | MIAC1 | 7.27 | 2015-05-13T00:59:00Z | 14.99 | 6 | < 25mph | JSDC1 | 3.33 | 2015-05-13T01:47:00Z | 8.01 | 2 | < 25mph | MIAC1 | 7.27 | 2015-05-13T00:59:00Z | 14.99 | 12 | < 25mph
PG&E | 2017-10-23 | 21:24 | 37.3713 | -122.348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100270421 | Unknown | 12000 | Conductor | Overhead | Yes | 43031 | 21:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1507 | 2017 | 10 | 23 | 21 | 24 | 17-0089820 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1768 | 13.1103 | 140_205 | <25mph | <15mph | HFTD - Distribution | 2017-10-23 21:24:00 | 1249 | 22.0037 | FALSE | <25mph | E4551 | 1.61 | 2018-03-21T18:07:00Z | 12.01 | 6 | < 25mph | PUGC1 | 7.55 | 2018-03-21T17:18:00Z | 18.01 | 12 | < 25mph | E4551 | 1.61 | 2018-03-21T18:57:00Z | 14 | 12 | < 25mph | E2649 | 6.29 | 2018-03-21T18:37:00Z | 24.99 | 24 | < 25mph
PG&E | 2017-04-29 15:29 | 15:07 | 37.0349 | -119.5242 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100678661 | Unknown | 12000 | Conductor | Overhead | Yes | 42854.6453 | 15:07 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1078 | 2017 | 4 | 29 | 15 | 7 | 17-0043911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 7.6275 | 265_186 | <25mph | <15mph | HFTD - Distribution | 2017-04-29 15:07:00 | 818 | 19.1329 | FALSE | <25mph | PG410 | 1.48 | 2019-08-30T11:50:00Z | 6.06 | 19 | < 25mph | PG484 | 5.52 | 2019-08-30T12:00:00Z | 16.15 | 49 | < 25mph | PG410 | 1.48 | 2019-08-30T11:50:00Z | 6.06 | 38 | < 25mph | PG484 | 5.52 | 2019-08-30T12:00:00Z | 16.15 | 98 | < 25mph
PG&E | 2017-07-03 20:28 | 20:26 | 38.7923 | -120.9438 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101388730 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42919.853 | 20:26 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1218 | 2017 | 7 | 3 | 20 | 26 | 17-0060336 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 8134 | 10.0527 | 202_283 | <25mph | <15mph | HFTD - Distribution | 2017-07-03 20:26:00 | 957 | 12.5378 | FALSE | <25mph | PG364 | 2.44 | 2019-05-24T02:40:00Z | 5.48 | 12 | < 25mph | PG073 | 6.01 | 2019-05-24T02:00:00Z | 14.03 | 77 | < 25mph | PG364 | 2.44 | 2019-05-24T02:40:00Z | 5.48 | 24 | < 25mph | PG073 | 6.01 | 2019-05-24T02:00:00Z | 14.03 | 154 | < 25mph
PG&E | 2016-06-21 | 20:49 | 35.5352 | -120.8457 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101900832 |  | 12000 | Conductor | Overhead | Yes | 42542 | 20:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0812 | 2016 | 6 | 21 | 20 | 49 | 16-0044904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7806 | 8.2716 | 207_103 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 20:49:00 | 558 | 17.6234 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6394 | 6.56 | 2018-01-20T09:04:00Z | 5.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6394 | 6.56 | 2018-01-20T10:04:00Z | 5.99 | 8 | < 25mph
PG&E | 2015-08-30 17:05 | 2015-08-30 17:05 | 38.4039 | -120.5559 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | centennial mine rd |  | 12000 | Conductor | Overhead | Yes | 42246.7118 | 2015-08-30 17:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0567 | 2015 | 8 | 30 | 17 | 5 | 15-0058273 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 40298 | 10.8566 | 219_261 | <25mph | <15mph | HFTD - Distribution | 2015-08-30 17:05:00 | 311 | 12.2451 | FALSE | <25mph | AT450 | 1.93 | 2017-02-26T08:32:00Z | 0 | 12 | < 25mph | C9148 | 6.15 | 2017-02-26T07:35:00Z | 10 | 33 | < 25mph | AT450 | 1.93 | 2017-02-26T09:32:00Z | 0 | 24 | < 25mph | C9148 | 6.15 | 2017-02-26T07:35:00Z | 10 | 66 | < 25mph
PG&E | 2018-06-05 | 10:13 | 40.6183 | -122.3173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JASON COLLINS 530-225-4628 | 101467801 | None | 12000 | Conductor | Overhead | Yes | 43256 | 10:13 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1631 | 2018 | 6 | 5 | 10 | 13 | 18-0047539 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 277 | 7.1547 | 144_384 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 10:13:00 | 1373 | 12.6046 | FALSE | <25mph | C5599 | 1.27 | 2017-01-05T14:01:00Z | 15.99 | 4 | < 25mph | KRDD | 7.24 | 2017-01-05T14:00:00Z | 17.27 | 7 | < 25mph | C5599 | 1.27 | 2017-01-05T14:01:00Z | 15.99 | 8 | < 25mph | KRDD | 7.24 | 2017-01-05T14:53:00Z | 19.57 | 15 | < 25mph
PG&E | 2018-07-21 | 0:23 | 38.6927 | -120.7921 | Vegetation | Rural | < 3 meters | Fire Agency | CAMINO | 101415904 | AT&T | 12000 | Conductor | Overhead | Yes | 43302 | 0:23 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1774 | 2018 | 7 | 21 | 0 | 23 | 18-0062206 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 107552 | 9.7365 | 208_277 | <25mph | <15mph | HFTD - Distribution | 2018-07-21 00:23:00 | 1514 | 11.1911 | FALSE | <25mph | AV185 | 3.62 | 2016-10-21T10:35:00Z | 1.01 | 34 | < 25mph | AV185 | 3.62 | 2016-10-21T10:35:00Z | 1.01 | 65 | < 25mph | AV185 | 3.62 | 2016-10-21T11:20:00Z | 1.01 | 67 | < 25mph | E3165 | 7.94 | 2016-10-21T11:34:00Z | 4 | 128 | < 25mph
PG&E | 2015-09-09 10:47 | 2015-09-09 10:47 | 37.1041 | -121.8853 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100520291 |  | 12000 | Conductor | Overhead | Yes | 42256.4493 | 2015-09-09 10:47 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0587 | 2015 | 9 | 9 | 10 | 47 | 15-0060074 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 142401 | 4.2376 | 161_190 | <25mph | <15mph | HFTD - Distribution | 2015-09-09 10:47:00 | 331 | 18.9097 | FALSE | <25mph | SJS04 | 2.5 | 2019-01-23T00:50:00Z | 23.24 | 34 | < 25mph | SJS04 | 2.5 | 2019-01-23T00:50:00Z | 23.24 | 119 | < 25mph | SJS04 | 2.5 | 2019-01-23T00:50:00Z | 23.24 | 68 | < 25mph | SJS04 | 2.5 | 2019-01-23T00:50:00Z | 23.24 | 233 | < 25mph
PG&E | 2017-09-18 | 13:01 | 39.3889 | -121.4054 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 103795057 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42996 | 13:01 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1418 | 2017 | 9 | 18 | 13 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 17.7047 | 182_316 | <25mph | <15mph | HFTD - Distribution | 2017-09-18 13:01:00 | 1156 | 19.5678 | FALSE | <25mph | PG290 | 0.32 | 2019-05-30T11:10:00Z | 9.64 | 7 | < 25mph | PG309 | 7.97 | 2019-05-30T10:30:00Z | 10.74 | 29 | < 25mph | PG290 | 0.32 | 2019-05-30T11:10:00Z | 9.64 | 14 | < 25mph | PG309 | 7.97 | 2019-05-30T10:30:00Z | 10.74 | 56 | < 25mph
PG&E | 2017-07-18 | 11:30 | 38.0484 | -120.5565 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 012/071 | Unknown | 115000 | Conductor | Overhead | Yes | 42934 | 11:30 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1265 | 2017 | 7 | 18 | 11 | 30 | INT-09873 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 55499 | 7.0574 | 219_242 | <25mph | <15mph | HFTD - Transmission | 2017-07-18 11:30:00 | 1005 | 15.7901 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2017-10-08 | 22:19 | 39.7371 | -121.6464 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 103319605 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43016 | 22:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1468 | 2017 | 10 | 8 | 22 | 19 | 17-0085504 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 42839 | 9.4272 | 172_335 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 22:19:00 | 1208 | 31.7535 | FALSE | 25-40mph | PDEC1 | 1.62 | 2018-08-16T06:00:00Z | 1.01 | 1 | < 25mph | C4565 | 7.55 | 2018-08-16T06:33:00Z | 2.01 | 7 | < 25mph | PDEC1 | 1.62 | 2018-08-16T07:00:00Z | 1.01 | 2 | < 25mph | C4565 | 7.55 | 2018-08-16T07:33:00Z | 2.01 | 14 | < 25mph
PG&E | 2016-08-13 | 14:31 | 37.4642 | -119.8589 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire |  |  | 21000 | Conductor | Overhead | Yes | 42595 | 14:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0923 | 2016 | 8 | 13 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.5527 | 249_210 | <25mph | <15mph | HFTD - Distribution | 2016-08-13 14:31:00 | 667 | 11.4441 | FALSE | <25mph | C1522 | 2.94 | 2015-03-24T20:27:00Z | 13 | 5 | < 25mph | MPOC1 | 7.53 | 2015-03-24T20:07:00Z | 14.99 | 9 | < 25mph | C1522 | 2.94 | 2015-03-24T20:57:00Z | 13 | 9 | < 25mph | MIAC1 | 6.96 | 2015-03-24T20:59:00Z | 14.99 | 17 | < 25mph
PG&E | 2016-06-10 15:51 | 2016-06-10 15:51 | 39.9934 | -123.7883 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100992291 |  | 12000 | Conductor | Overhead | Yes | 42531.6604 | 2016-06-10 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0788 | 2016 | 6 | 10 | 15 | 51 | 16-0042501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | N.A. | 22.4156 | 82_351 | <25mph | <15mph | HFTD - Distribution | 2016-06-10 15:51:00 | 531 | 22.7996 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AV037 | 5.5 | 2016-05-03T06:53:00Z | 0 | 3 | < 25mph |  |  |  | 0 | 0 | No data | AV037 | 5.5 | 2016-05-03T08:03:00Z | 0 | 7 | < 25mph
PG&E | 2019-07-15 | 7:51 | 38.3266 | -122.568 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 42721104 |  | 12000 | Conductor | Overhead | Yes | 43661 | 7:51 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-343 | 2019 | 7 | 15 | 7 | 51 | 19-0077351 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2348 | 31.0114 | 132_257 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-07-15 07:51:00 | 1903 | 35.3209 | FALSE | 25-40mph | PG177 | 1.33 | 2019-12-29T18:30:00Z | 11.25 | 20 | < 25mph | PG177 | 1.33 | 2019-12-29T18:30:00Z | 11.25 | 100 | < 25mph | PG177 | 1.33 | 2019-12-29T19:50:00Z | 14.25 | 40 | < 25mph | PG177 | 1.33 | 2019-12-29T19:50:00Z | 14.25 | 200 | < 25mph
PG&E | 2015-06-27 12:48 | 2015-06-27 12:48 | 37.9474 | -120.4274 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101034512 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.5333 | 2015-06-27 12:48 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0414 | 2015 | 6 | 27 | 12 | 48 | 15-0043755 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 150075 | 11.0891 | 224_236 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 12:48:00 | 159 | 19.6587 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F0305 | 6 | 2017-09-18T20:30:00Z | 5.99 | 9 | < 25mph |  |  |  | 0 | 0 | No data | F0305 | 6 | 2017-09-18T20:30:00Z | 5.99 | 18 | < 25mph
PG&E | 2017-09-17 | 17:38 | 38.9946 | -121.0261 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100029537 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42995 | 17:38 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Branch (OverHanging) | 1417 | 2017 | 9 | 17 | 17 | 38 | 17-0079585 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 28509 | 11.5169 | 198_294 | <25mph | <15mph | HFTD - Distribution | 2017-09-17 17:38:00 | 1155 | 15.8476 | FALSE | <25mph | C0713 | 1.74 | 2017-01-31T05:34:00Z | 0 | 13 | < 25mph | AT999 | 7.97 | 2017-01-31T05:08:00Z | 3 | 35 | < 25mph | C0713 | 1.74 | 2017-01-31T06:34:00Z | 0 | 26 | < 25mph | AT999 | 7.97 | 2017-01-31T06:33:00Z | 3 | 69 | < 25mph
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 9:36 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 14.8685 | 222_261 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 09:36:00 | 925 | 23.4839 | FALSE | <25mph | AT450 | 2.61 | 2016-07-20T20:50:00Z | 13 | 16 | < 25mph | ESPC1 | 7.8 | 2016-07-20T20:13:00Z | 18.99 | 28 | < 25mph | AT450 | 2.61 | 2016-07-20T20:50:00Z | 13 | 32 | < 25mph | ESPC1 | 7.8 | 2016-07-20T21:13:00Z | 24 | 55 | < 25mph
PG&E | 2016-07-29 01:31 | 2016-07-29 01:31 | 41.0396 | -123.674 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Hoopa FD | 100962351 |  | 12000 | Conductor | Overhead | Yes | 42580.0632 | 2016-07-29 01:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0891 | 2016 | 7 | 29 | 1 | 31 | 16-0053478 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1418 | 4.1421 | 88_408 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 01:31:00 | 633 | 13.6696 | FALSE | <25mph | HOAC1 | 0.58 | 2016-12-25T05:40:00Z | 4.99 | 1 | < 25mph | HOAC1 | 0.58 | 2016-12-25T05:40:00Z | 4.99 | 1 | < 25mph | HOAC1 | 0.58 | 2016-12-25T06:40:00Z | 4.99 | 2 | < 25mph | HOAC1 | 0.58 | 2016-12-25T06:40:00Z | 4.99 | 2 | < 25mph
PG&E | 2017-04-04 13:36 | 13:29 | 35.6885 | -120.7653 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101945026 | None | 12000 | Conductor | Overhead | Yes | 42829.567 | 13:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1064 | 2017 | 4 | 4 | 13 | 29 | 17-0036460 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 167151 | 3.61 | 210_111 | <25mph | <15mph | HFTD - Distribution | 2017-04-04 13:29:00 | 804 | 8.6409 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D4060 | 7.1 | 2018-09-11T11:30:00Z | 3 | 4 | < 25mph |  |  |  | 0 | 0 | No data | D4060 | 7.1 | 2018-09-11T11:30:00Z | 3 | 8 | < 25mph
PG&E | 2015-09-24 13:56 | 2015-09-24 13:56 | 39.3508 | -121.2454 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 9692 Rices-Texas Hill rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42271.5806 | 2015-09-24 13:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0614 | 2015 | 9 | 24 | 13 | 56 | 15-0063159 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 51917 | 10.3419 | 189_313 | <25mph | <15mph | HFTD - Distribution | 2015-09-24 13:56:00 | 359 | 13.3743 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RRRC1 | 7.59 | 2015-05-12T20:13:00Z | 14.99 | 2 | < 25mph |  |  |  | 0 | 0 | No data | RRRC1 | 7.59 | 2015-05-12T21:13:00Z | 15.99 | 4 | < 25mph
PG&E | 2017-11-20 08:33 | 08:32 | 38.7584 | -120.8439 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101389405 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43059.3562 | 08:32 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1522 | 2017 | 11 | 20 | 8 | 32 | 17-0096436 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 12376 | 9.7427 | 206_281 | <25mph | <15mph | HFTD - Distribution | 2017-11-20 08:32:00 | 1264 | 12.0384 | FALSE | <25mph | E5691 | 2.94 | 2017-02-09T23:47:00Z | 14 | 12 | < 25mph | KPVF | 5.42 | 2017-02-10T00:15:00Z | 31.07 | 59 | 25-40mph | E5691 | 2.94 | 2017-02-10T00:47:00Z | 15.99 | 24 | < 25mph | KPVF | 5.42 | 2017-02-10T00:55:00Z | 35.68 | 122 | 25-40mph
PG&E | 2015-11-21 10:36 | 2015-11-21 10:36 | 38.0679 | -120.1872 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101045952 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42329.4417 | 2015-11-21 10:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0677 | 2015 | 11 | 21 | 10 | 36 | 15-0079868 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18350 | 7.816 | 235_243 | <25mph | <15mph | HFTD - Distribution | 2015-11-21 10:36:00 | 421 | 16.6927 | FALSE | <25mph | MOUC1 | 3.29 | 2016-04-15T20:02:00Z | 18.99 | 1 | < 25mph | MOUC1 | 3.29 | 2016-04-15T20:02:00Z | 18.99 | 1 | < 25mph | MOUC1 | 3.29 | 2016-04-15T21:02:00Z | 20 | 2 | < 25mph | MOUC1 | 3.29 | 2016-04-15T21:02:00Z | 20 | 2 | < 25mph
PG&E | 2017-06-30 01:20 | 01:20 | 39.821 | -121.5883 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103840463 | YES | 12000 | Conductor | Overhead | Yes | 42916.0559 | 01:20 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1210 | 2017 | 6 | 30 | 1 | 20 | 17-0059647 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 2888 | 7.4054 | 174_339 | <25mph | <15mph | HFTD - Distribution | 2017-06-30 01:20:00 | 948 | 9.8944 | FALSE | <25mph | C4565 | 1.69 | 2018-05-29T06:13:00Z | 2.01 | 6 | < 25mph | JBGC1 | 7.9 | 2018-05-29T06:13:00Z | 14.99 | 8 | < 25mph | C4565 | 1.69 | 2018-05-29T06:53:00Z | 2.01 | 12 | < 25mph | JBGC1 | 7.9 | 2018-05-29T06:13:00Z | 14.99 | 16 | < 25mph
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 9:36 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 14.8685 | 222_261 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 09:36:00 | 925 | 23.4839 | FALSE | <25mph | AT450 | 2.61 | 2015-01-31T17:35:00Z | 4 | 13 | < 25mph | C9148 | 7.6 | 2015-01-31T17:04:00Z | 23.98 | 24 | < 25mph | D9396 | 1.73 | 2015-01-31T18:09:00Z | 4.99 | 29 | < 25mph | C9148 | 7.6 | 2015-01-31T17:04:00Z | 23.98 | 51 | < 25mph
PG&E | 2016-06-21 | 20:49 | 35.5352 | -120.8457 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101900832 |  | 12000 | Conductor | Overhead | Yes | 42542 | 20:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0812 | 2016 | 6 | 21 | 20 | 49 | 16-0044904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7806 | 8.2716 | 207_103 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 20:49:00 | 558 | 17.6234 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6394 | 6.56 | 2015-08-18T18:43:00Z | 18.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6394 | 6.56 | 2015-08-18T18:43:00Z | 18.01 | 8 | < 25mph
PG&E | 2016-09-21 | 10:01 | 39.1173 | -121.071 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100014315 | PACIFIC BELL | 115000 | Conductor | Overhead | Yes | 42634 | 10:01 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0991 | 2016 | 9 | 21 | 10 | 1 | INT-08560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 18.3543 | 196_301 | <25mph | <15mph | HFTD - Transmission | 2016-09-21 10:01:00 | 734 | 24.3978 | FALSE | <25mph | E1789 | 3.84 | 2016-07-13T22:06:00Z | 10 | 14 | < 25mph | E1789 | 3.84 | 2016-07-13T22:06:00Z | 10 | 59 | < 25mph | E1789 | 3.84 | 2016-07-13T22:18:00Z | 11.01 | 30 | < 25mph | E1789 | 3.84 | 2016-07-13T22:18:00Z | 11.01 | 121 | < 25mph
PG&E | 2017-10-28 | 15:26 | 39.4516 | -123.3838 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102209084 | Unknown | 12000 | Conductor | Overhead | Yes | 43036 | 15:26 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | no-match | 1510 | 2017 | 10 | 28 | 15 | 26 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 10.3107 | 98_320 | <25mph | <15mph | HFTD - Distribution | 2017-10-28 15:26:00 | 1252 | 11.7696 | FALSE | <25mph | E4027 | 3.28 | 2016-05-20T16:03:00Z | 13 | 12 | < 25mph | E4027 | 3.28 | 2016-05-20T16:03:00Z | 13 | 25 | < 25mph | E4027 | 3.28 | 2016-05-20T17:08:00Z | 13 | 24 | < 25mph | E4027 | 3.28 | 2016-05-20T17:08:00Z | 13 | 49 | < 25mph
PG&E | 2015-07-30 17:56 | 2015-07-30 17:56 | 37.9021 | -120.4739 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101019808 |  | 17000 | Conductor | Overhead | Yes | 42215.7472 | 2015-07-30 17:56 | Contact From Object | N.A. | Other | Electric Facility | Unknown | osprey nest | Other/Unknown | 0499 | 2015 | 7 | 30 | 17 | 56 | 15-0051764 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 615 | 11.6086 | 222_234 | <25mph | <15mph | HFTD - Distribution | 2015-07-30 17:56:00 | 244 | 16.9062 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.96 | 2018-07-23T22:03:00Z | 18.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.96 | 2018-07-23T23:03:00Z | 20 | 2 | < 25mph
PG&E | 2016-07-16 00:58 | 2016-07-16 00:58 | 36.4379 | -121.9198 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101669758 |  | 12000 | Other | Overhead | Yes | 42567.0403 | 2016-07-16 00:58 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0855 | 2016 | 7 | 16 | 0 | 58 | 16-0050335 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 8976 | 11.1025 | 159_153 | <25mph | <15mph | HFTD - Distribution | 2016-07-16 00:58:00 | 598 | 18.5622 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6019 | 7.86 | 2017-08-18T23:52:00Z | 5.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6019 | 7.86 | 2017-08-18T23:52:00Z | 5.99 | 8 | < 25mph
PG&E | 2018-10-16 | 16:30 | 38.7754 | -122.8976 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MARK GRADEK (707) 889-4303 | 101962692 | AT&T | 12000 | Conductor | Overhead | Yes | 43389 | 16:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1943 | 2018 | 10 | 16 | 16 | 30 | 18-0091127 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 744 | 10.3513 | 118_282 | <25mph | <15mph | HFTD - Distribution | 2018-10-16 16:30:00 | 1682 | 19.9126 | FALSE | <25mph |  |  |  | 0 | 0 | No data | HWKC1 | 4.29 | 2017-02-16T01:56:00Z | 18.01 | 5 | < 25mph |  |  |  | 0 | 0 | No data | HWKC1 | 4.29 | 2017-02-16T02:56:00Z | 18.01 | 10 | < 25mph
PG&E | 2015-05-21 09:23 | 2015-05-21 09:23 | 38.5996 | -122.9935 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 4 SPANS LOAD SIDE 2993 |  | 12000 | Conductor | Overhead | Yes | 42145.391 | 2015-05-21 09:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0324 | 2015 | 5 | 21 | 9 | 23 | 15-0035686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2850 | 1.6525 | 114_273 | <25mph | <15mph | HFTD - Distribution | 2015-05-21 09:23:00 | 70 | 15.124 | FALSE | <25mph | PG549 | 0.94 | 2019-12-13T04:20:00Z | 4.23 | 6 | < 25mph | PG590 | 6.84 | 2019-12-13T04:20:00Z | 4.9 | 48 | < 25mph | PG549 | 0.94 | 2019-12-13T04:20:00Z | 4.23 | 12 | < 25mph | PG590 | 6.84 | 2019-12-13T04:20:00Z | 4.9 | 101 | < 25mph
PG&E | 2016-08-01 | 2016-08-01 18:29 | 38.6956 | -120.9283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412720 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0898 | 2016 | 8 | 1 | 18 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2359 | 203_277 | <25mph | <15mph | HFTD - Distribution | 2016-08-01 18:29:00 | 641 | 12.0255 | FALSE | <25mph | D4464 | 2.83 | 2015-02-23T18:39:00Z | 18.99 | 16 | < 25mph | C6129 | 4.28 | 2015-02-23T17:59:00Z | 28.97 | 71 | 25-40mph | D4464 | 2.83 | 2015-02-23T18:39:00Z | 18.99 | 32 | < 25mph | C6129 | 4.28 | 2015-02-23T18:49:00Z | 28.97 | 140 | 25-40mph
PG&E | 2015-08-24 22:48 | 2015-08-24 22:48 | 37.896 | -122.6011 | Vegetation | Rural | < 3 meters | Fire Agency | marin county fire | 200' east of pan toll rd 50' north of panoramic hwy |  | 12000 | Unknown | Overhead | Yes | 42240.95 | 2015-08-24 22:48 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0552 | 2015 | 8 | 24 | 22 | 48 | 15-0057082 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 1128 | 8.5935 | 130_234 | <25mph | <15mph | HFTD - Distribution | 2015-08-24 22:48:00 | 296 | 14.2171 | FALSE | <25mph | E9939 | 1.49 | 2019-12-30T14:45:00Z | 21 | 9 | < 25mph | E9939 | 1.49 | 2019-12-30T14:45:00Z | 21 | 66 | < 25mph | E9939 | 1.49 | 2019-12-30T16:00:00Z | 21 | 17 | < 25mph | PG489 | 5.61 | 2019-12-30T15:30:00Z | 22.15 | 140 | < 25mph
PG&E | 2016-08-21 | 2016-08-21 13:02 | 38.4445 | -122.2496 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102291451 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42603 | 2016-08-21 13:02 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0940 | 2016 | 8 | 21 | 13 | 2 | 16-0058847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 12780 | 10.3444 | 145_264 | <25mph | <15mph | HFTD - Distribution | 2016-08-21 13:02:00 | 683 | 21.5044 | FALSE | <25mph | ATLC1 | 2.26 | 2016-08-31T07:29:00Z | 8.01 | 1 | < 25mph | ATLC1 | 2.26 | 2016-08-31T07:29:00Z | 8.01 | 1 | < 25mph | ATLC1 | 2.26 | 2016-08-31T07:29:00Z | 8.01 | 2 | < 25mph | ATLC1 | 2.26 | 2016-08-31T07:29:00Z | 8.01 | 2 | < 25mph
PG&E | 2016-06-26 11:06 | 2016-06-26 11:06 | 40.4832 | -122.0466 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101483777 | FRONTIER | 12000 | Conductor | Overhead | Yes | 42547.4625 | 2016-06-26 11:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0826 | 2016 | 6 | 26 | 11 | 6 | 16-0045846 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 15520 | 6.1274 | 155_376 | <25mph | <15mph | HFTD - Distribution | 2016-06-26 11:06:00 | 566 | 14.8861 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2015-03-15 22:47 | 2015-03-15 22:47 | 38.3346 | -120.5325 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 103106530 |  | 12000 | Conductor | Overhead | Yes | 42078.9493 | 2015-03-15 22:47 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0279 | 2015 | 3 | 15 | 22 | 47 | 15-0019709 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 14520 | 7.4897 | 220_257 | <25mph | <15mph | HFTD - Distribution | 2015-03-15 22:47:00 | 25 | 18.5478 | FALSE | <25mph | AT317 | 2.19 | 2017-02-13T02:20:00Z | 5.99 | 10 | < 25mph | ESPC1 | 4.17 | 2017-02-13T02:13:00Z | 12.01 | 37 | < 25mph | AT317 | 2.19 | 2017-02-13T02:20:00Z | 5.99 | 20 | < 25mph | ESPC1 | 4.17 | 2017-02-13T02:13:00Z | 12.01 | 72 | < 25mph
PG&E | 2016-06-04 | 22:15 | 38.5117 | -122.9373 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42525 | 22:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0768 | 2016 | 6 | 4 | 22 | 15 | 16-0041119 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7220 | 6.1483 | 116_268 | <25mph | <15mph | HFTD - Distribution | 2016-06-04 22:15:00 | 514 | 16.4728 | FALSE | <25mph | D9841 | 2.58 | 2019-05-23T07:31:00Z | 0 | 37 | < 25mph | E9683 | 6.84 | 2019-05-23T07:30:00Z | 1.01 | 66 | < 25mph | D9841 | 2.58 | 2019-05-23T08:30:00Z | 0 | 73 | < 25mph | E9683 | 6.84 | 2019-05-23T07:30:00Z | 1.01 | 129 | < 25mph
PG&E | 2015-10-30 17:13 | 2015-10-30 17:13 | 38.3166 | -120.7226 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 7600 HWY 49, Jackson | None | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0662 | 2015 | 10 | 30 | 17 | 13 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 8.0122 | 211_256 | <25mph | <15mph | HFTD - Distribution | 2015-10-30 17:13:00 | 406 | 12.822 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.34 | 2016-07-17T21:56:00Z | 12.01 | 2 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.34 | 2016-07-17T22:56:00Z | 14 | 4 | < 25mph
PG&E | 2018-10-20 | 14:31 | 40.5218 | -124.1137 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Str. 003/000 | None | 60000 | Conductor | Overhead | Yes | 43393 | 14:31 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1947 | 2018 | 10 | 20 | 14 | 31 | INT-11477 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 410982 | 9.6901 | 69_380 | <25mph | <15mph | HFTD - Transmission | 2018-10-20 14:31:00 | 1686 | 10.3412 | FALSE | <25mph | C5061 | 3.19 | 2016-09-04T10:37:00Z | 3 | 23 | < 25mph | C5061 | 3.19 | 2016-09-04T10:37:00Z | 3 | 23 | < 25mph | C5061 | 3.19 | 2016-09-04T10:37:00Z | 3 | 45 | < 25mph | C5061 | 3.19 | 2016-09-04T10:37:00Z | 3 | 45 | < 25mph
PG&E | 2017-08-12 09:09 | 09:08 | 34.6689 | -120.0286 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103391912 | Unknown | 12000 | Conductor | Overhead | Yes | 42959.3812 | 09:08 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | wire cut | Other/Unknown | 1330 | 2017 | 8 | 12 | 9 | 8 | 17-0069829 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 26070 | 3.5662 | 244_55 | <25mph | <15mph | HFTD - Distribution | 2017-08-12 09:08:00 | 1068 | 23.4799 | FALSE | <25mph | UCSE | 1.88 | 2019-10-02T04:00:00Z | 8.19 | 13 | < 25mph | FGMC1 | 4.7 | 2019-10-02T04:35:00Z | 20 | 30 | < 25mph | UCSE | 1.88 | 2019-10-02T04:00:00Z | 8.19 | 26 | < 25mph | FGMC1 | 4.7 | 2019-10-02T04:35:00Z | 20 | 60 | < 25mph
PG&E | 2016-08-05 | 2016-08-05 12:42 | 38.4048 | -120.5292 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101244628 |  | 12000 | Conductor | Overhead | Yes | 42587 | 2016-08-05 12:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0906 | 2016 | 8 | 5 | 12 | 42 | 16-0055368 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 363 | 12.0247 | 220_261 | <25mph | <15mph | HFTD - Distribution | 2016-08-05 12:42:00 | 649 | 12.7612 | FALSE | <25mph | AT450 | 0.53 | 2016-08-23T19:35:00Z | 11.01 | 16 | < 25mph | AT450 | 0.53 | 2016-08-23T19:35:00Z | 11.01 | 27 | < 25mph | AT450 | 0.53 | 2016-08-23T19:35:00Z | 11.01 | 32 | < 25mph | AT450 | 0.53 | 2016-08-23T19:35:00Z | 11.01 | 54 | < 25mph
PG&E | 2017-06-13 | 14:30 | 37.8526 | -122.1853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Tower 005/035c | Unknown | 115000 | Conductor | Overhead | Yes | 42899 | 14:30 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1143 | 2017 | 6 | 13 | 14 | 30 | INT-09744 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | Balloons | 0 | 10.6352 | 148_231 | <25mph | <15mph | HFTD - Transmission | 2017-06-13 14:30:00 | 882 | 14.5193 | FALSE | <25mph | E5555 | 2.22 | 2016-12-15T17:07:00Z | 34 | 49 | 25-40mph | E5555 | 2.22 | 2016-12-15T17:07:00Z | 34 | 130 | 25-40mph | E5555 | 2.22 | 2016-12-15T17:07:00Z | 34 | 98 | 25-40mph | E5555 | 2.22 | 2016-12-15T17:07:00Z | 34 | 268 | 25-40mph
PG&E | 2017-07-11 22:13 | 22:12 | 37.0122 | -121.9497 | Vegetation | Rural | < 3 Meters | Fire Agency | CAPT PHIL CRAMBLET 831-479-6842 | 101676689 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42927.9254 | 22:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1244 | 2017 | 7 | 11 | 22 | 12 | 17-0062198 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 714 | 7.2694 | 158_185 | <25mph | <15mph | HFTD - Distribution | 2017-07-11 22:12:00 | 983 | 9.7577 | FALSE | <25mph | AR172 | 1.01 | 2015-08-12T07:30:00Z | 3 | 44 | < 25mph | E7291 | 4.78 | 2015-08-12T07:37:00Z | 4 | 135 | < 25mph | AR172 | 1.01 | 2015-08-12T08:30:00Z | 3 | 87 | < 25mph | E7291 | 4.78 | 2015-08-12T07:37:00Z | 4 | 263 | < 25mph
PG&E | 2016-08-09 | 2016-08-09 19:21 | 38.9187 | -120.9525 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | El Dorado County FD | 100038028 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0915 | 2016 | 8 | 9 | 19 | 21 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.2678 | 201_290 | <25mph | <15mph | HFTD - Distribution | 2016-08-09 19:21:00 | 658 | 10.7446 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG032 | 7.29 | 2018-08-20T10:10:00Z | 9.22 | 32 | < 25mph |  |  |  | 0 | 0 | No data | PG032 | 7.29 | 2018-08-20T10:10:00Z | 9.22 | 61 | < 25mph
PG&E | 2017-09-08 | 17:21 | 38.6039 | -120.9275 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101379094 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42986 | 17:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1402 | 2017 | 9 | 8 | 17 | 21 | 17-0077122 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 8504 | 10.5347 | 203_272 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 17:21:00 | 1140 | 11.5767 | FALSE | <25mph | BENC1 | 0.96 | 2016-08-11T22:59:00Z | 15.99 | 1 | < 25mph | BENC1 | 0.96 | 2016-08-11T22:59:00Z | 15.99 | 33 | < 25mph | BENC1 | 0.96 | 2016-08-11T23:59:00Z | 17 | 2 | < 25mph | BENC1 | 0.96 | 2016-08-11T23:59:00Z | 17 | 68 | < 25mph
PG&E | 2016-06-04 | 22:15 | 38.5117 | -122.9373 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42525 | 22:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0768 | 2016 | 6 | 4 | 22 | 15 | 16-0041119 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7220 | 6.1483 | 116_268 | <25mph | <15mph | HFTD - Distribution | 2016-06-04 22:15:00 | 514 | 16.4728 | FALSE | <25mph | D3481 | 2.53 | 2015-02-03T11:02:00Z | 1.01 | 25 | < 25mph | D3838 | 7.07 | 2015-02-03T10:46:00Z | 2.01 | 50 | < 25mph | D3481 | 2.53 | 2015-02-03T11:02:00Z | 1.01 | 48 | < 25mph | D3838 | 7.07 | 2015-02-03T11:46:00Z | 3 | 105 | < 25mph
PG&E | 2019-05-15 | 21:31 | 38.5731 | -122.9603 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Unknown |  | 103931177 |  | 12000 | Conductor | Overhead | Yes | 43600 | 21:31 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-316 | 2019 | 5 | 15 | 21 | 31 | 19-0052480 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 27780 | 16.5892 | 115_271 | <25mph | <15mph | HFTD - Distribution | 2019-05-15 21:31:00 | 1774 | 23.8094 | FALSE | <25mph | D9841 | 3.34 | 2015-09-12T21:54:00Z | 2.01 | 3 | < 25mph | AR798 | 4.72 | 2015-09-12T21:30:00Z | 5.99 | 35 | < 25mph | D9841 | 3.34 | 2015-09-12T21:54:00Z | 2.01 | 5 | < 25mph | KHES | 6.43 | 2015-09-12T22:55:00Z | 14.94 | 67 | < 25mph
PG&E | 2017-12-20 07:55 | 07:54 | 37.4012 | -122.3606 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100318864 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43089.3298 | 07:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1546 | 2017 | 12 | 20 | 7 | 54 | 17-0102756 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6602 | 16.1413 | 140_206 | <25mph | <15mph | HFTD - Distribution | 2017-12-20 07:54:00 | 1288 | 21.2088 | FALSE | <25mph | PG149 | 0.73 | 2019-04-25T10:50:00Z | 2.42 | 16 | < 25mph | PG056 | 5.25 | 2019-04-25T10:10:00Z | 8.55 | 37 | < 25mph | PG149 | 0.73 | 2019-04-25T12:00:00Z | 2.64 | 32 | < 25mph | PG056 | 5.25 | 2019-04-25T12:00:00Z | 9.86 | 75 | < 25mph
PG&E | 2016-08-30 | 2016-08-30 16:01 | 36.5941 | -121.9212 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Unknown | 101734977 |  | 21000 | Conductor | Overhead | Yes | 42612 | 2016-08-30 16:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0951 | 2016 | 8 | 30 | 16 | 1 | 16-0061130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 199327 | 14.6893 | 159_162 | <25mph | <15mph | HFTD - Distribution | 2016-08-30 16:01:00 | 694 | 14.6893 | FALSE | <25mph | E6019 | 2.96 | 2015-03-25T15:39:00Z | 5.99 | 40 | < 25mph | E6019 | 2.96 | 2015-03-25T15:39:00Z | 5.99 | 40 | < 25mph | D4637 | 3.09 | 2015-03-25T16:49:00Z | 8.99 | 92 | < 25mph | D4637 | 3.09 | 2015-03-25T16:49:00Z | 8.99 | 92 | < 25mph
PG&E | 2017-07-24 19:31 | 19:31 | 38.3519 | -120.7103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.8134 | 19:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1288 | 2017 | 7 | 24 | 19 | 31 | 17-0065145 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14281 | 10.3402 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 19:31:00 | 1027 | 12.2366 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG116 | 4.02 | 2019-01-12T20:20:00Z | 17.31 | 20 | < 25mph |  |  |  | 0 | 0 | No data | PG116 | 4.02 | 2019-01-12T20:20:00Z | 17.31 | 43 | < 25mph
PG&E | 2016-10-08 15:05 | 15:04 | 38.6686 | -120.9091 | Vegetation | RURAL | < 0.25 Acres | Customer | N.A. | 101380856 |  | 0 – 750 | Capacitor Bank | Overhead | Yes | 42651.6284 | 15:04 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1021 | 2016 | 10 | 8 | 15 | 4 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 10.4532 | 203_276 | <25mph | <15mph | HFTD - Distribution | 2016-10-08 15:04:00 | 762 | 14.8776 | FALSE | <25mph | D2736 | 2.92 | 2016-04-19T01:40:00Z | 4 | 18 | < 25mph | BENC1 | 5.53 | 2016-04-19T01:59:00Z | 5.99 | 75 | < 25mph | D2736 | 2.92 | 2016-04-19T01:40:00Z | 4 | 36 | < 25mph | BENC1 | 5.53 | 2016-04-19T01:59:00Z | 5.99 | 150 | < 25mph
PG&E | 2017-04-29 15:29 | 15:07 | 37.0349 | -119.5242 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100678661 | Unknown | 12000 | Conductor | Overhead | Yes | 42854.6453 | 15:07 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1078 | 2017 | 4 | 29 | 15 | 7 | 17-0043911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 7.6275 | 265_186 | <25mph | <15mph | HFTD - Distribution | 2017-04-29 15:07:00 | 818 | 19.1329 | FALSE | <25mph | PRHC1 | 2.76 | 2017-10-09T14:27:00Z | 11.01 | 1 | < 25mph | PRHC1 | 2.76 | 2017-10-09T14:27:00Z | 11.01 | 1 | < 25mph | PRHC1 | 2.76 | 2017-10-09T14:27:00Z | 11.01 | 2 | < 25mph | PRHC1 | 2.76 | 2017-10-09T14:27:00Z | 11.01 | 2 | < 25mph
PG&E | 2019-07-01 | 2:15 | 38.2955 | -120.8335 |  | Shrub | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-252 | 2019 | 7 | 1 | 2 | 15 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.9479 | 207_255 | <25mph | <15mph | HFTD - Distribution | 2019-07-01 02:15:00 | 1878 | 14.184 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.85 | 2019-01-30T14:05:00Z | 7 | 3 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.85 | 2019-01-30T14:05:00Z | 7 | 11 | < 25mph
PG&E | 2015-06-12 13:07 | 2015-06-12 13:07 | 40.4077 | -122.4104 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS STREET FROM 4139 OLD HAPPY VALLEY RD |  | 12000 | Lightning Arrestor | Overhead | No |  |  | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | no-match | 0378 | 2015 | 6 | 12 | 13 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Lightning Arrestor | N.A. | 9.7698 | 140_372 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 13:07:00 | 124 | 24.3549 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6886 | 5.64 | 2015-06-06T06:17:00Z | 23.98 | 8 | < 25mph |  |  |  | 0 | 0 | No data | E6886 | 5.64 | 2015-06-06T06:17:00Z | 23.98 | 16 | < 25mph
PG&E | 2015-02-07 18:38 | 2015-02-07 18:38 | 40.4674 | -123.6545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | mile marker 36.61, hwy 36, bridgeville |  | 12000 | Conductor | Overhead | Yes | 42042.7764 | 2015-02-07 18:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0262 | 2015 | 2 | 7 | 18 | 38 | 15-0011390 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 7691 | 20.9308 | 88_377 | <25mph | <15mph | HFTD - Distribution | 2015-02-07 18:38:00 | 9 | 24.639 | FALSE | <25mph | E8593 | 2.58 | 2018-06-08T00:10:00Z | 11.01 | 12 | < 25mph | MDDC1 | 6.88 | 2018-06-07T23:53:00Z | 12.01 | 13 | < 25mph | E8593 | 2.58 | 2018-06-08T00:45:00Z | 11.01 | 24 | < 25mph | MDDC1 | 6.88 | 2018-06-07T23:53:00Z | 12.01 | 26 | < 25mph
PG&E | 2018-10-14 | 20:08 | 38.8935 | -120.8497 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103674516 | Unknown | 21000 | Conductor | Overhead | Yes | 43387 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1940 | 2018 | 10 | 14 | 20 | 8 | 18-0090299 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 48095 | 8.663 | 206_288 | <25mph | <15mph | HFTD - Distribution | 2018-10-14 20:08:00 | 1679 | 24.0259 | FALSE | <25mph | D5266 | 1.24 | 2017-04-04T09:44:00Z | 3 | 16 | < 25mph | BDMC1 | 7.81 | 2017-04-04T09:36:00Z | 5.99 | 17 | < 25mph | D5266 | 1.24 | 2017-04-04T10:44:00Z | 3 | 29 | < 25mph | BDMC1 | 7.81 | 2017-04-04T10:36:00Z | 11.01 | 31 | < 25mph
PG&E | 2016-10-11 23:17 | 23:16 | 39.0201 | -120.8294 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire.foresthill fire | 100025501 |  | 60000 | Conductor | Overhead | Yes | 42654.9701 | 23:16 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error |  | no-match | 1028 | 2016 | 10 | 11 | 23 | 16 | INT-08640 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 0 | 7.6312 | 207_295 | <25mph | <15mph | HFTD - Transmission | 2016-10-11 23:16:00 | 769 | 11.1078 | FALSE | <25mph | AU268 | 0.89 | 2019-02-17T00:18:00Z | 2.01 | 4 | < 25mph | PG033 | 6.75 | 2019-02-17T00:20:00Z | 14.47 | 17 | < 25mph | AU268 | 0.89 | 2019-02-17T00:18:00Z | 2.01 | 9 | < 25mph | PG033 | 6.75 | 2019-02-17T00:20:00Z | 14.47 | 35 | < 25mph
PG&E | 2017-07-04 20:17 | 20:16 | 40.4228 | -122.3975 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SCOTT CORN 530-448-2414 | 101481860 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42920.8451 | 20:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1221 | 2017 | 7 | 4 | 20 | 16 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 13.3568 | 141_373 | <25mph | <15mph | HFTD - Distribution | 2017-07-04 20:16:00 | 960 | 18.8443 | FALSE | <25mph | PG174 | 1.52 | 2019-03-12T14:30:00Z | 5.03 | 6 | < 25mph | PG174 | 1.52 | 2019-03-12T14:30:00Z | 5.03 | 6 | < 25mph | PG174 | 1.52 | 2019-03-12T15:10:00Z | 8.12 | 12 | < 25mph | PG174 | 1.52 | 2019-03-12T15:10:00Z | 8.12 | 12 | < 25mph
PG&E | 2015-06-28 02:50 | 2015-06-28 02:50 | 35.491 | -120.731 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 13505 Santa Lucia Rd. Atascadero |  | 12000 | Conductor | Overhead | Yes | 42183.1181 | 2015-06-28 02:50 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0418 | 2015 | 6 | 28 | 2 | 50 | 15-0043807 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 12323 | 9.9634 | 212_101 | <25mph | <15mph | HFTD - Distribution | 2015-06-28 02:50:00 | 163 | 24.8049 | FALSE | <25mph | PG210 | 3.25 | 2019-04-25T01:30:00Z | 32.21 | 32 | 25-40mph | PG210 | 3.25 | 2019-04-25T01:30:00Z | 32.21 | 63 | 25-40mph | PG210 | 3.25 | 2019-04-25T01:30:00Z | 32.21 | 64 | 25-40mph | PG210 | 3.25 | 2019-04-25T01:30:00Z | 32.21 | 126 | 25-40mph
PG&E | 2018-08-08 | 16:02 | 36.4703 | -121.7143 | Vegetation | Rural | < 3 meters | Customer | N.A. | 103910535 | None | 12000 | Conductor | Overhead | Yes | 43320 | 16:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1830 | 2018 | 8 | 8 | 16 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 14.7322 | 168_155 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:02:00 | 1569 | 15.5625 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-01-21 21:32 | 2016-01-21 21:32 | 40.553 | -124.1116 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100994021 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42390.8972 | 2016-01-21 21:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0690 | 2016 | 1 | 21 | 21 | 32 | 16-0007239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 6468 | 26.2481 | 69_382 | 25-40mph | 15-30mph | HFTD - Distribution | 2016-01-21 21:32:00 | 434 | 29.6828 | FALSE | 25-40mph | AT493 | 1.6 | 2016-07-07T03:21:00Z | 10 | 28 | < 25mph | AT493 | 1.6 | 2016-07-07T03:21:00Z | 10 | 28 | < 25mph | AT493 | 1.6 | 2016-07-07T03:21:00Z | 10 | 56 | < 25mph | AT493 | 1.6 | 2016-07-07T03:21:00Z | 10 | 56 | < 25mph
PG&E | 2018-08-22 | 21:56 | 39.0425 | -120.9695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100024728 | Verizon | 12000 | Conductor | Overhead | Yes | 43334 | 21:56 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1854 | 2018 | 8 | 22 | 21 | 56 | 18-0072654 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29727 | 9.3137 | 201_296 | <25mph | <15mph | HFTD - Distribution | 2018-08-22 21:56:00 | 1593 | 10.5291 | FALSE | <25mph | PG377 | 3.76 | 2019-09-27T13:50:00Z | 9.8 | 22 | < 25mph | PG377 | 3.76 | 2019-09-27T13:50:00Z | 9.8 | 55 | < 25mph | PG377 | 3.76 | 2019-09-27T13:50:00Z | 9.8 | 40 | < 25mph | PG377 | 3.76 | 2019-09-27T13:50:00Z | 9.8 | 112 | < 25mph
PG&E | 2016-10-02 16:41 | 16:41 | 39.8888 | -121.6648 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103358082 |  | 12000 | Other | Overhead | Yes | 42645.6954 | 16:41 | Other | N.A. | N.A. | N.A. | Weather | lightning strike | Other/Unknown | 1013 | 2016 | 10 | 2 | 16 | 41 | 16-0069050 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 339550 | 8.5152 | 171_343 | <25mph | <15mph | HFTD - Distribution | 2016-10-02 16:41:00 | 755 | 17.2989 | FALSE | <25mph | C8878 | 1.4 | 2017-04-09T23:53:00Z | 7 | 13 | < 25mph | CSTC1 | 5.65 | 2017-04-09T23:51:00Z | 14.99 | 18 | < 25mph | C8878 | 1.4 | 2017-04-10T00:43:00Z | 7 | 25 | < 25mph | CSTC1 | 5.65 | 2017-04-10T00:51:00Z | 15.99 | 37 | < 25mph
PG&E | 2017-09-24 | 16:42 | 38.3869 | -122.9667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DOUG JONES | 101973946 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43002 | 16:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1432 | 2017 | 9 | 24 | 16 | 42 | 17-0081329 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 22574 | 19.6154 | 114_261 | <25mph | <15mph | HFTD - Distribution | 2017-09-24 16:42:00 | 1170 | 19.6154 | FALSE | <25mph | D2849 | 0.23 | 2019-03-11T20:18:00Z | 4 | 12 | < 25mph | BDZC1 | 7.15 | 2019-03-11T20:00:00Z | 9.8 | 78 | < 25mph | D2849 | 0.23 | 2019-03-11T21:08:00Z | 4.99 | 24 | < 25mph | UCBM | 7.15 | 2019-03-11T21:00:00Z | 15.1 | 153 | < 25mph
PG&E | 2019-04-09 | 15:27 | 37.7341 | -120.0776 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 101076921 |  | 21000 | Pole | Overhead | Yes | 43564 | 15:27 | Vegetation |  | Veg. contact | Pole |  |  | Branch (Not overhanging, > 12ft) | 2019-313 | 2019 | 4 | 9 | 15 | 27 | 19-0041008 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 179862 | 22.8983 | 240_225 | <25mph | <15mph | HFTD - Distribution | 2019-04-09 15:27:00 | 1738 | 29.8749 | FALSE | 25-40mph | PG112 | 3.29 | 2019-02-27T06:30:00Z | 18.86 | 12 | < 25mph | SEWC1 | 4.76 | 2019-02-27T06:16:00Z | 24 | 25 | < 25mph | PG112 | 3.29 | 2019-02-27T07:30:00Z | 23.67 | 24 | < 25mph | PG155 | 7.32 | 2019-02-27T07:50:00Z | 25.66 | 48 | 25-40mph
PG&E | 2017-07-01 | 12:02 | 39.8209 | -121.6418 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 003/039 | Unknown | 60000 | Conductor | Overhead | Yes | 42917 | 12:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1212 | 2017 | 7 | 1 | 12 | 2 | INT-09792 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.6345 | 172_339 | <25mph | <15mph | HFTD - Transmission | 2017-07-01 12:02:00 | 954 | 9.664 | FALSE | <25mph | C8878 | 3.55 | 2016-01-19T15:03:00Z | 18.01 | 23 | < 25mph | CSTC1 | 7.61 | 2016-01-19T14:51:00Z | 34.99 | 35 | 25-40mph | C8878 | 3.55 | 2016-01-19T15:03:00Z | 18.01 | 42 | < 25mph | CSTC1 | 7.61 | 2016-01-19T14:51:00Z | 34.99 | 66 | 25-40mph
PG&E | 2018-07-01 | 0:23 | 40.2697 | -124.2386 | Vegetation | Rural | < 3 meters | Fire Agency | fire chief | 100986962 | Unknown | 12000 | Conductor | Overhead | Yes | 43282 | 0:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1718 | 2018 | 7 | 1 | 0 | 23 | 18-0056043 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 22872 | 20.9894 | 63_366 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 00:23:00 | 1459 | 27.5371 | FALSE | 25-40mph | PTEC1 | 1.7 | 2018-10-27T00:08:00Z | 8.99 | 1 | < 25mph | PTEC1 | 1.7 | 2018-10-27T00:08:00Z | 8.99 | 1 | < 25mph | PTEC1 | 1.7 | 2018-10-27T01:08:00Z | 14 | 2 | < 25mph | PTEC1 | 1.7 | 2018-10-27T01:08:00Z | 14 | 2 | < 25mph
PG&E | 2018-11-09 | 4:49 | 39.8234 | -121.8382 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100402367 | AT&T | 12000 | Conductor | Overhead | Yes | 43413 | 4:49 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1963 | 2018 | 11 | 9 | 4 | 49 | 18-0098482 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 11900 | 0.23999 | 164_340 | <25mph | <15mph | HFTD - Distribution | 2018-11-09 04:49:00 | 1703 | 7.1467 | FALSE | <25mph | D8132 | 3.69 | 2015-10-16T22:08:00Z | 3 | 1 | < 25mph | CSTC1 | 4.96 | 2015-10-16T21:51:00Z | 12.01 | 14 | < 25mph | D8132 | 3.69 | 2015-10-16T22:50:00Z | 7 | 6 | < 25mph | CSTC1 | 4.96 | 2015-10-16T22:51:00Z | 12.01 | 33 | < 25mph
PG&E | 2015-02-23 13:25 | 2015-02-23 13:25 | 38.5046 | -122.7408 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RINCON VALLEY | BEHIND 4870 CARRIAGE LN SANTA ROSA |  | 12000 | Conductor | Overhead | Yes | 42058.559 | 2015-02-23 13:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0268 | 2015 | 2 | 23 | 13 | 25 | 15-0015168 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 85762 | 20.3218 | 124_267 | <25mph | <15mph | HFTD - Distribution | 2015-02-23 13:25:00 | 15 | 32.6885 | FALSE | 25-40mph | RSAC1 | 2.39 | 2015-03-01T10:29:00Z | 5.99 | 8 | < 25mph | RSAC1 | 2.39 | 2015-03-01T10:29:00Z | 5.99 | 74 | < 25mph | RSAC1 | 2.39 | 2015-03-01T11:29:00Z | 7 | 15 | < 25mph | RSAC1 | 2.39 | 2015-03-01T11:29:00Z | 7 | 146 | < 25mph
PG&E | 2016-07-27 17:05 | 2016-07-27 17:05 | 38.5392 | -122.7656 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102029945 |  | 60000 | Conductor | Overhead | Yes | 42578.7118 | 2016-07-27 17:05 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0882 | 2016 | 7 | 27 | 17 | 5 | FU-2016-047 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 18.1446 | 123_269 | <25mph | <15mph | HFTD - Transmission | 2016-07-27 17:05:00 | 625 | 18.1446 | FALSE | <25mph | BRSWW | 3.82 | 2019-08-08T18:30:00Z | 8.28 | 26 | < 25mph | PG005 | 4.75 | 2019-08-08T18:30:00Z | 13.15 | 117 | < 25mph | BRSWW | 3.82 | 2019-08-08T18:30:00Z | 8.28 | 52 | < 25mph | PG005 | 4.75 | 2019-08-08T18:30:00Z | 13.15 | 230 | < 25mph
PG&E | 2017-07-01 | 12:02 | 39.8209 | -121.6418 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 003/039 | Unknown | 60000 | Conductor | Overhead | Yes | 42917 | 12:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1212 | 2017 | 7 | 1 | 12 | 2 | INT-09792 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.6345 | 172_339 | <25mph | <15mph | HFTD - Transmission | 2017-07-01 12:02:00 | 954 | 9.664 | FALSE | <25mph | C8878 | 3.55 | 2015-04-11T02:39:00Z | 1.01 | 19 | < 25mph | CSTC1 | 7.61 | 2015-04-11T02:51:00Z | 8.99 | 21 | < 25mph | E4833 | 2.14 | 2015-04-11T03:53:00Z | 1.01 | 41 | < 25mph | CSTC1 | 7.61 | 2015-04-11T03:51:00Z | 10 | 45 | < 25mph
PG&E | 2018-02-12 | 20:20 | 39.9395 | -121.6494 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430947 | Unknown | 12000 | Conductor | Overhead | Yes | 43143 | 20:20 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1561 | 2018 | 2 | 12 | 20 | 20 | 18-0013604 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 149212 | 10.1876 | 172_346 | <25mph | <15mph | HFTD - Distribution | 2018-02-12 20:20:00 | 1303 | 14.6044 | FALSE | <25mph | PG134 | 2.86 | 2019-03-29T16:40:00Z | 8.55 | 6 | < 25mph | CSTC1 | 7.88 | 2019-03-29T15:51:00Z | 10 | 42 | < 25mph | PG134 | 2.86 | 2019-03-29T16:40:00Z | 8.55 | 12 | < 25mph | CSTC1 | 7.88 | 2019-03-29T16:51:00Z | 10 | 83 | < 25mph
PG&E | 2019-04-28 | 12:36 | 39.6756 | -121.5677 |  | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 100404366 |  | 12000 | Conductor | Overhead | Yes | 43583 | 12:36 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-166 | 2019 | 4 | 28 | 12 | 36 | 19-0046853 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 79810 | 6.7497 | 175_331 | <25mph | <15mph | HFTD - Distribution | 2019-04-28 12:36:00 | 1752 | 11.2512 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JBGC1 | 5.9 | 2017-12-24T15:13:00Z | 20 | 12 | < 25mph |  |  |  | 0 | 0 | No data | JBGC1 | 5.9 | 2017-12-24T16:13:00Z | 20 | 24 | < 25mph
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 9:36 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 14.8685 | 222_261 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 09:36:00 | 925 | 23.4839 | FALSE | <25mph | AT450 | 2.61 | 2015-12-12T21:53:00Z | 8.99 | 16 | < 25mph | ESPC1 | 7.8 | 2015-12-12T22:13:00Z | 11.01 | 28 | < 25mph | AT450 | 2.61 | 2015-12-12T21:53:00Z | 8.99 | 32 | < 25mph | ESPC1 | 7.8 | 2015-12-12T23:13:00Z | 12.01 | 55 | < 25mph
PG&E | 2016-07-15 14:09 | 2016-07-15 14:09 | 38.6965 | -120.8598 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412774 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.5896 | 2016-07-15 14:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0852 | 2016 | 7 | 15 | 14 | 9 | 16-0050274 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 11253 | 10.7453 | 205_277 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 14:09:00 | 595 | 14.2057 | FALSE | <25mph | PG106 | 2.6 | 2018-11-06T04:20:00Z | 5.26 | 48 | < 25mph | PG068 | 5.97 | 2018-11-06T04:30:00Z | 7.9 | 111 | < 25mph | PG027 | 3.79 | 2018-11-06T05:40:00Z | 5.7 | 95 | < 25mph | PG068 | 5.97 | 2018-11-06T04:30:00Z | 7.9 | 219 | < 25mph
PG&E | 2017-11-20 08:33 | 08:32 | 38.7584 | -120.8439 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101389405 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43059.3562 | 08:32 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1522 | 2017 | 11 | 20 | 8 | 32 | 17-0096436 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 12376 | 9.7427 | 206_281 | <25mph | <15mph | HFTD - Distribution | 2017-11-20 08:32:00 | 1264 | 12.0384 | FALSE | <25mph | E5691 | 2.94 | 2017-10-27T15:33:00Z | 0 | 12 | < 25mph | E3165 | 6.09 | 2017-10-27T14:55:00Z | 8.01 | 109 | < 25mph | E5691 | 2.94 | 2017-10-27T16:32:00Z | 0 | 24 | < 25mph | E3165 | 6.09 | 2017-10-27T14:55:00Z | 8.01 | 218 | < 25mph
PG&E | 2017-08-29 | 15:54 | 38.302 | -122.5431 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 911 | 102026119 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 42976 | 15:54 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1367 | 2017 | 8 | 29 | 15 | 54 | 17-0073928 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 485 | 16.1777 | 133_256 | <25mph | <15mph | HFTD - Distribution | 2017-08-29 15:54:00 | 1105 | 18.0049 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KO69 | 4.55 | 2018-11-11T19:55:00Z | 20.71 | 14 | < 25mph |  |  |  | 0 | 0 | No data | KO69 | 4.55 | 2018-11-11T19:55:00Z | 20.71 | 26 | < 25mph
PG&E | 2017-07-02 | 13:28 | 39.8605 | -121.6274 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 000/017c | Unknown | 60000 | Conductor | Overhead | Yes | 42918 | 13:28 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1216 | 2017 | 7 | 2 | 13 | 28 | INT-09794 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 10.1141 | 173_342 | <25mph | <15mph | HFTD - Transmission | 2017-07-02 13:28:00 | 956 | 11.4462 | FALSE | <25mph | PG333 | 3.91 | 2019-09-08T11:00:00Z | 7.09 | 54 | < 25mph | PG333 | 3.91 | 2019-09-08T11:00:00Z | 7.09 | 91 | < 25mph | PG333 | 3.91 | 2019-09-08T11:00:00Z | 7.09 | 102 | < 25mph | PG333 | 3.91 | 2019-09-08T11:00:00Z | 7.09 | 171 | < 25mph
PG&E | 2016-11-15 | 17:27 | 39.7275 | -121.6557 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100327525 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42689 | 17:27 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 1049 | 2016 | 11 | 15 | 17 | 27 | 16-0080083 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 69231 | 9.6883 | 172_334 | <25mph | <15mph | HFTD - Distribution | 2016-11-15 17:27:00 | 790 | 16.6369 | FALSE | <25mph | PDEC1 | 2.44 | 2017-09-11T11:00:00Z | 2.01 | 1 | < 25mph | PDEC1 | 2.44 | 2017-09-11T11:00:00Z | 2.01 | 1 | < 25mph | PDEC1 | 2.44 | 2017-09-11T12:00:00Z | 2.01 | 2 | < 25mph | PDEC1 | 2.44 | 2017-09-11T12:00:00Z | 2.01 | 2 | < 25mph
PG&E | 2019-04-09 | 14:07 | 34.6311 | -119.9813 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Fire Dept | Santa Barbra County FD | 101863014 |  | 12000 | Conductor | Overhead | Yes | 43564 | 14:07 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-263 | 2019 | 4 | 9 | 14 | 7 | 19-0040969 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 70756 | 38.5369 | 246_53 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-09 14:07:00 | 1737 | 43.1384 | FALSE | 40-55mph |  |  |  | 0 | 0 | No data | SYTC1 | 7.19 | 2017-04-14T13:24:00Z | 34.99 | 17 | 25-40mph |  |  |  | 0 | 0 | No data | SYTC1 | 7.19 | 2017-04-14T13:24:00Z | 34.99 | 32 | 25-40mph
PG&E | 2017-05-24 16:25 | 16:24 | 38.834 | -121.1197 | Vegetation | Rural | < 3 Meters | Fire Agency | Fire Capt | 103838109 | None | 12000 | Conductor | Overhead | Yes | 42879.6837 | 16:24 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | no-match | 1111 | 2017 | 5 | 24 | 16 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 20.975 | 194_285 | <25mph | <15mph | HFTD - Distribution | 2017-05-24 16:24:00 | 851 | 20.975 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 5.95 | 2015-02-19T00:56:00Z | 7 | 22 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 5.95 | 2015-02-19T00:56:00Z | 7 | 44 | < 25mph
PG&E | 2016-06-03 | 2016-06-03 12:16 | 38.6435 | -120.6959 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | cal-fire and usfs | 103119737 |  | 21000 | Conductor | Overhead | Yes | 42524 | 2016-06-03 12:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0764 | 2016 | 6 | 3 | 12 | 16 | 16-0040808 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 101354 | 7.6436 | 213_274 | <25mph | <15mph | HFTD - Distribution | 2016-06-03 12:16:00 | 507 | 11.74 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AV185 | 6.2 | 2016-08-27T08:58:00Z | 1.01 | 17 | < 25mph |  |  |  | 0 | 0 | No data | AV185 | 6.2 | 2016-08-27T09:23:00Z | 1.01 | 37 | < 25mph
PG&E | 2018-10-14 | 19:39 | 38.446 | -120.5147 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | IC- Dillon Gissell- 209-295-7735 | 103384485 | Unknown | 12000 | Conductor | Overhead | Yes | 43387 | 19:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1939 | 2018 | 10 | 14 | 19 | 39 | 18-0090288 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3497327 | 25.4932 | 220_264 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-14 19:39:00 | 1678 | 30.9108 | FALSE | 25-40mph | C9148 | 3.52 | 2016-12-17T05:04:00Z | 7 | 15 | < 25mph | C9148 | 3.52 | 2016-12-17T05:04:00Z | 7 | 19 | < 25mph | C9148 | 3.52 | 2016-12-17T06:04:00Z | 8.01 | 31 | < 25mph | C9148 | 3.52 | 2016-12-17T06:04:00Z | 8.01 | 39 | < 25mph
PG&E | 2015-09-10 18:39 | 2015-09-10 18:39 | 40.7569 | -123.7958 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 096/004 |  | 115000 | Conductor | Overhead | Yes | 42257.7771 | 2015-09-10 18:39 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0590 | 2015 | 9 | 10 | 18 | 39 | RM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 2.2423 | 82_393 | <25mph | <15mph | HFTD - Transmission | 2015-09-10 18:39:00 | 335 | 12.4043 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.39 | 2019-05-04T01:55:00Z | 7 | 7 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.39 | 2019-05-04T01:55:00Z | 7 | 14 | < 25mph
PG&E | 2016-07-28 14:24 | 2016-07-28 14:24 | 37.8232 | -120.1356 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101037045 |  | 17000 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Guy/Span Wire | N.A. | N.A. | Unknown |  | no-match | 0888 | 2016 | 7 | 28 | 14 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Guy/Span Wire | N.A. | 10.9021 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 14:24:00 | 631 | 11.4062 | FALSE | <25mph | E5394 | 3.86 | 2018-08-31T20:04:00Z | 10 | 5 | < 25mph | E5394 | 3.86 | 2018-08-31T20:04:00Z | 10 | 5 | < 25mph | SEWC1 | 2.46 | 2018-08-31T20:16:00Z | 15.99 | 10 | < 25mph | SEWC1 | 2.46 | 2018-08-31T20:16:00Z | 15.99 | 10 | < 25mph
PG&E | 2015-03-07 13:35 | 2015-03-07 13:35 | 38.7091 | -122.6484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 14417 western mine rd, Middletown |  | 12000 | Conductor | Overhead | Yes | 42070.566 | 2015-03-07 13:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0272 | 2015 | 3 | 7 | 13 | 35 | 15-0018003 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2263 | 3.8777 | 128_279 | <25mph | <15mph | HFTD - Distribution | 2015-03-07 13:35:00 | 18 | 14.4715 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-08-19 | 2016-08-19 16:23 | 39.2235 | -123.755 | Vegetation | RURAL | < 3 meters | Fire Agency | Albion-Little River FD | 102206661 |  | 12000 | Conductor | Overhead | Yes | 42601 | 2016-08-19 16:23 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0938 | 2016 | 8 | 19 | 16 | 23 | 16-0058677 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 95106 | 9.7374 | 82_308 | <25mph | <15mph | HFTD - Distribution | 2016-08-19 16:23:00 | 681 | 11.9986 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6025 | 4.66 | 2017-05-07T05:15:00Z | 21 | 3 | < 25mph |  |  |  | 0 | 0 | No data | E6025 | 4.66 | 2017-05-07T05:15:00Z | 21 | 6 | < 25mph
PG&E | 2018-08-13 | 15:33 | 38.708 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101377799 | Unknown | 21000 | Conductor | Overhead | Yes | 43325 | 15:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1840 | 2018 | 8 | 13 | 15 | 33 | 18-0069470 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1004 | 11.7134 | 201_278 | <25mph | <15mph | HFTD - Distribution | 2018-08-13 15:33:00 | 1579 | 13.7748 | FALSE | <25mph | PG073 | 2.99 | 2018-09-17T04:40:00Z | 6.35 | 62 | < 25mph | PG073 | 2.99 | 2018-09-17T04:40:00Z | 6.35 | 117 | < 25mph | PG073 | 2.99 | 2018-09-17T04:40:00Z | 6.35 | 124 | < 25mph | PG073 | 2.99 | 2018-09-17T04:40:00Z | 6.35 | 233 | < 25mph
PG&E | 2018-08-14 | 15:46 | 38.0878 | -122.6002 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103916882 | Verizon | 0 – 750 | Conductor | Overhead | Yes | 43326 | 15:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1844 | 2018 | 8 | 14 | 15 | 46 | 18-0069929 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 546 | 20.6189 | 130_244 | <25mph | <15mph | HFTD - Distribution | 2018-08-14 15:46:00 | 1583 | 26.2074 | FALSE | 25-40mph | NBRC1 | 3.72 | 2016-08-18T19:33:00Z | 13 | 25 | < 25mph | NBRC1 | 3.72 | 2016-08-18T19:33:00Z | 13 | 39 | < 25mph | NBRC1 | 3.72 | 2016-08-18T19:33:00Z | 13 | 48 | < 25mph | NBRC1 | 3.72 | 2016-08-18T19:33:00Z | 13 | 75 | < 25mph
PG&E | 2018-07-21 | 0:23 | 38.6927 | -120.7921 | Vegetation | Rural | < 3 meters | Fire Agency | CAMINO | 101415904 | AT&T | 12000 | Conductor | Overhead | Yes | 43302 | 0:23 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1774 | 2018 | 7 | 21 | 0 | 23 | 18-0062206 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 107552 | 9.7365 | 208_277 | <25mph | <15mph | HFTD - Distribution | 2018-07-21 00:23:00 | 1514 | 11.1911 | FALSE | <25mph | C6129 | 3.07 | 2017-05-11T02:39:00Z | 5.99 | 30 | < 25mph | E5691 | 4.25 | 2017-05-11T02:10:00Z | 8.01 | 57 | < 25mph | C6129 | 3.07 | 2017-05-11T02:39:00Z | 5.99 | 58 | < 25mph | E5691 | 4.25 | 2017-05-11T02:10:00Z | 8.01 | 111 | < 25mph
PG&E | 2017-07-10 18:00 | 17:00 | 37.3768 | -122.3597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | David Hibdon 831-254-1763 | 100270370 | Unknown | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1240 | 2017 | 7 | 10 | 17 | 0 | 17-0061857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3322 | 11.4741 | 140_205 | <25mph | <15mph | HFTD - Distribution | 2017-07-10 17:00:00 | 979 | 11.9313 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 7.57 | 2016-10-05T20:07:00Z | 15.99 | 7 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 7.57 | 2016-10-05T20:07:00Z | 15.99 | 16 | < 25mph
PG&E | 2016-07-28 08:12 | 2016-07-28 08:12 | 37.8207 | -120.1388 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101037043 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0884 | 2016 | 7 | 28 | 8 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 1.7128 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 08:12:00 | 627 | 11.4062 | FALSE | <25mph | SEWC1 | 2.5 | 2018-07-04T08:16:00Z | 13 | 5 | < 25mph | SEWC1 | 2.5 | 2018-07-04T08:16:00Z | 13 | 6 | < 25mph | SEWC1 | 2.5 | 2018-07-04T09:16:00Z | 14 | 10 | < 25mph | SEWC1 | 2.5 | 2018-07-04T09:16:00Z | 14 | 11 | < 25mph
PG&E | 2017-08-08 04:23 | 4:10 | 38.4949 | -122.6685 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 102025742 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42955.1829 | 4:10 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1325 | 2017 | 8 | 8 | 4 | 10 | 17-0068642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 2750 | 5.2658 | 127_267 | <25mph | <15mph | HFTD - Distribution | 2017-08-08 04:10:00 | 1062 | 14.7124 | FALSE | <25mph | E1582 | 3.16 | 2019-10-18T14:52:00Z | 5.99 | 28 | < 25mph | PG162 | 7.04 | 2019-10-18T14:50:00Z | 18.99 | 110 | < 25mph | E1582 | 3.16 | 2019-10-18T14:52:00Z | 5.99 | 55 | < 25mph | PG162 | 7.04 | 2019-10-18T14:50:00Z | 18.99 | 213 | < 25mph
PG&E | 2017-08-03 11:01 | 10:53 | 39.0732 | -121.0868 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100072742 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42950.4588 | 10:53 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1312 | 2017 | 8 | 3 | 10 | 53 | 17-0067679 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 127440 | 9.5869 | 196_298 | <25mph | <15mph | HFTD - Distribution | 2017-08-03 10:53:00 | 1050 | 11.8038 | FALSE | <25mph | C5488 | 3.14 | 2016-03-28T18:36:00Z | 7 | 6 | < 25mph | C0713 | 4.59 | 2016-03-28T18:34:00Z | 8.99 | 39 | < 25mph | C5488 | 3.14 | 2016-03-28T19:39:00Z | 11.01 | 11 | < 25mph | E1789 | 5.51 | 2016-03-28T20:12:00Z | 12.01 | 78 | < 25mph
PG&E | 2019-07-22 | 8:11 | 38.7687 | -120.9633 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | El Dorado County FD | 6Ht0722190809 |  | 21000 | Other | Overhead | Yes | 43668 | 8:11 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-49 | 2019 | 7 | 22 | 8 | 11 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.6529 | 201_281 | <25mph | <15mph | HFTD - Distribution | 2019-07-22 08:11:00 | 1920 | 11.9774 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 5.01 | 2015-12-13T21:56:00Z | 15.99 | 52 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 5.01 | 2015-12-13T21:56:00Z | 15.99 | 103 | < 25mph
PG&E | 2017-08-28 | 10:07 | 39.0472 | -120.7859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | FORESTHILL | 100019525 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 10:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1357 | 2017 | 8 | 28 | 10 | 7 | 17-0073379 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 10077 | 5.9792 | 209_297 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 10:07:00 | 1095 | 13.4783 | FALSE | <25mph | PG023 | 1.32 | 2019-08-29T16:20:00Z | 3.29 | 7 | < 25mph | PG481 | 6.75 | 2019-08-29T15:50:00Z | 12.28 | 15 | < 25mph | PG023 | 1.32 | 2019-08-29T17:40:00Z | 7.67 | 16 | < 25mph | PG481 | 6.75 | 2019-08-29T15:50:00Z | 12.28 | 31 | < 25mph
PG&E | 2018-07-01 | 8:13 | 39.4154 | -121.5122 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430344 | AT&T | 12000 | Conductor | Overhead | Yes | 43282 | 8:13 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1720 | 2018 | 7 | 1 | 8 | 13 | 18-0056061 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 7848 | 6.5616 | 178_317 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 08:13:00 | 1461 | 14.6967 | FALSE | <25mph | PG312 | 3.96 | 2019-12-28T23:20:00Z | 6.8 | 6 | < 25mph | TT309 | 6.67 | 2019-12-28T23:45:00Z | 8.99 | 39 | < 25mph | PG312 | 3.96 | 2019-12-28T23:20:00Z | 6.8 | 12 | < 25mph | TT309 | 6.67 | 2019-12-28T23:45:00Z | 8.99 | 77 | < 25mph
PG&E | 2017-09-03 | 12:52 | 37.2162 | -119.4807 | Vegetation | Rural | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103345573 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 2017-09-03 | 12:52 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1388 | 2017 | 9 | 3 | 12 | 52 | 17-0075546 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 2362 | 10.0918 | 266_196 | <25mph | <15mph | HFTD - Distribution | 2017-09-03 12:52:00 | 1126 | 25.526 | FALSE | 25-40mph | NFRC1 | 1.81 | 2015-05-13T14:55:00Z | 7 | 4 | < 25mph | NFRC1 | 1.81 | 2015-05-13T14:55:00Z | 7 | 4 | < 25mph | NFRC1 | 1.81 | 2015-05-13T15:55:00Z | 10 | 8 | < 25mph | NFRC1 | 1.81 | 2015-05-13T15:55:00Z | 10 | 8 | < 25mph
PG&E | 2019-09-10 | 7:13 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 82841102 |  | 12000 | Conductor | Overhead | Yes | 43718 | 7:13 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-369 | 2019 | 9 | 10 | 7 | 13 | 19-0097264 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 23500 | 14.6244 | 147_193 | <25mph | <15mph | HFTD - Distribution | 2019-09-10 07:13:00 | 2029 | 17.7422 | FALSE | <25mph | PG055 | 1.57 | 2018-09-25T00:20:00Z | 5.03 | 7 | < 25mph | C1844 | 4.46 | 2018-09-25T00:49:00Z | 8.99 | 51 | < 25mph | PG055 | 1.57 | 2018-09-25T00:20:00Z | 5.03 | 14 | < 25mph | C1844 | 4.46 | 2018-09-25T00:49:00Z | 8.99 | 98 | < 25mph
PG&E | 2015-08-30 17:05 | 2015-08-30 17:05 | 38.4039 | -120.5559 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | centennial mine rd |  | 12000 | Conductor | Overhead | Yes | 42246.7118 | 2015-08-30 17:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0567 | 2015 | 8 | 30 | 17 | 5 | 15-0058273 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 40298 | 10.8566 | 219_261 | <25mph | <15mph | HFTD - Distribution | 2015-08-30 17:05:00 | 311 | 12.2451 | FALSE | <25mph | AT450 | 1.93 | 2016-04-11T01:24:00Z | 4 | 12 | < 25mph | AT450 | 1.93 | 2016-04-11T01:24:00Z | 4 | 23 | < 25mph | AT450 | 1.93 | 2016-04-11T01:24:00Z | 4 | 24 | < 25mph | AT450 | 1.93 | 2016-04-11T01:24:00Z | 4 | 45 | < 25mph
PG&E | 2019-07-30 | 15:15 | 39.1207 | -121.072 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 152691104 |  | 12000 | Conductor | Overhead | Yes | 43676 | 15:15 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-386 | 2019 | 7 | 30 | 15 | 15 | 19-0082713 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 31302 | 12.2921 | 196_301 | <25mph | <15mph | HFTD - Distribution | 2019-07-30 15:15:00 | 1942 | 13.0851 | FALSE | <25mph | E1789 | 3.69 | 2016-08-08T06:12:00Z | 7 | 10 | < 25mph | E1789 | 3.69 | 2016-08-08T06:12:00Z | 7 | 72 | < 25mph | E1789 | 3.69 | 2016-08-08T07:24:00Z | 7 | 20 | < 25mph | E1789 | 3.69 | 2016-08-08T07:24:00Z | 7 | 139 | < 25mph
PG&E | 2018-06-09 | 0:46 | 35.0745 | -120.5167 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101927520 | Unknown | 12000 | Conductor | Overhead | Yes | 43260 | 0:46 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1645 | 2018 | 6 | 9 | 0 | 46 | 18-0049171 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 16825 | 5.84 | 221_78 | <25mph | <15mph | HFTD - Distribution | 2018-06-09 00:46:00 | 1387 | 22.9582 | FALSE | <25mph | E8214 | 3.18 | 2017-07-09T19:16:00Z | 8.01 | 14 | < 25mph | C9687 | 5.06 | 2017-07-09T19:23:00Z | 8.99 | 32 | < 25mph | D6295 | 3.81 | 2017-07-09T20:08:00Z | 11.01 | 31 | < 25mph | D6295 | 3.81 | 2017-07-09T20:08:00Z | 11.01 | 69 | < 25mph
PG&E | 2017-09-20 | 2:06 | 37.2597 | -122.3222 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100322388 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42998 | 2:06 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1424 | 2017 | 9 | 20 | 2 | 6 | 17-0080179 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 36593 | 8.989 | 141_198 | <25mph | <15mph | HFTD - Distribution | 2017-09-20 02:06:00 | 1162 | 20.1127 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG152 | 7.27 | 2018-12-11T01:00:00Z | 16.44 | 8 | < 25mph |  |  |  | 0 | 0 | No data | PG152 | 7.27 | 2018-12-11T01:00:00Z | 16.44 | 15 | < 25mph
PG&E | 2018-09-11 | 5:23 | 37.376 | -119.6304 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | TROY CHEEK 209-966-3621 | 101023184 | Unknown | 12000 | Conductor | Overhead | Yes | 43354 | 5:23 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1891 | 2018 | 9 | 11 | 5 | 23 | 18-0078387 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 288 | 4.3046 | 260_205 | <25mph | <15mph | HFTD - Distribution | 2018-09-11 05:23:00 | 1630 | 11.3584 | FALSE | <25mph | BSNC1 | 0.17 | 2015-03-25T17:48:00Z | 8.99 | 26 | < 25mph | D2149 | 5.42 | 2015-03-25T18:34:00Z | 8.99 | 62 | < 25mph | AT301 | 3.14 | 2015-03-25T19:32:00Z | 11.99 | 52 | < 25mph | AT301 | 3.14 | 2015-03-25T19:32:00Z | 11.99 | 125 | < 25mph
PG&E | 2015-05-09 13:10 | 2015-05-09 13:10 | 39.2343 | -121.2468 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100000103 | None | 21000 | Conductor | Overhead | Yes | 42133.5486 | 2015-05-09 13:10 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0311 | 2015 | 5 | 9 | 13 | 10 | 15-0033085 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 382926 | 12.172 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 13:10:00 | 57 | 17.071 | FALSE | <25mph | E2572 | 3.27 | 2016-01-04T23:48:00Z | 8.99 | 10 | < 25mph | E6355 | 7.8 | 2016-01-04T23:23:00Z | 13 | 22 | < 25mph | E2572 | 3.27 | 2016-01-04T23:48:00Z | 8.99 | 21 | < 25mph | E6355 | 7.8 | 2016-01-04T23:23:00Z | 13 | 45 | < 25mph
PG&E | 2016-09-25 10:35 | 2016-09-25 10:35 | 38.8019 | -122.8176 | Vegetation | RURAL | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103613996 |  | 115000 | Other | Overhead | Yes | 2016-09-25 10:35 | 2016-09-25 10:35 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1004 | 2016 | 9 | 25 | 10 | 35 | INT-08572 | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Equip Failure - Other | 0 | 28.1055 | 121_284 | 25-40mph | 15-30mph | HFTD - Transmission | 2016-09-25 10:35:00 | 743 | 28.9174 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | HWKC1 | 4.73 | 2016-07-16T10:56:00Z | 14.99 | 2 | < 25mph |  |  |  | 0 | 0 | No data | HWKC1 | 4.73 | 2016-07-16T10:56:00Z | 14.99 | 4 | < 25mph
PG&E | 2017-12-16 | 11:51 | 38.8171 | -122.7041 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Shawn Ohare | 102167231 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43085 | 11:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1540 | 2017 | 12 | 16 | 11 | 51 | 17-0102101 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26120 | 34.3488 | 126_285 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-12-16 11:51:00 | 1282 | 35.345 | FALSE | 25-40mph | LKRC1 | 2.09 | 2018-12-31T09:05:00Z | 24 | 13 | < 25mph | PG110 | 7.78 | 2018-12-31T09:20:00Z | 30.69 | 38 | 25-40mph | PG096 | 2.2 | 2018-12-31T10:30:00Z | 26.08 | 26 | 25-40mph | PG110 | 7.78 | 2018-12-31T09:20:00Z | 30.69 | 76 | 25-40mph
PG&E | 2018-07-17 | 11:11 | 35.6986 | -120.9777 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | dennis byrnes 8055434244 inc # = 18ca-slu-007640 | 103886652 | Unknown | 21000 | Conductor | Overhead | Yes | 43298 | 11:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1755 | 2018 | 7 | 17 | 11 | 11 | 18-0060637 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 9121 | 4.768 | 201_112 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 11:11:00 | 1495 | 12.6145 | FALSE | <25mph | E9175 | 3.58 | 2018-10-25T19:10:00Z | 4.99 | 13 | < 25mph | D4060 | 6.73 | 2018-10-25T19:30:00Z | 8.01 | 18 | < 25mph | E9175 | 3.58 | 2018-10-25T19:10:00Z | 4.99 | 25 | < 25mph | D4060 | 6.73 | 2018-10-25T20:45:00Z | 10 | 35 | < 25mph
PG&E | 2019-07-18 | 10:27 | 38.3033 | -120.6718 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | B561 |  | 12000 | Other | Overhead | Yes | 43664 | 10:27 | Equipment - PG&E | Other |  |  |  |  | Other/Unknown | 2019-68 | 2019 | 7 | 18 | 10 | 27 | 19-0078904 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45558 | 8.6789 | 214_256 | <25mph | <15mph | HFTD - Distribution | 2019-07-18 10:27:00 | 1910 | 16.0413 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ANUC1 | 7.14 | 2018-05-19T02:53:00Z | 4.99 | 2 | < 25mph |  |  |  | 0 | 0 | No data | ANUC1 | 7.14 | 2018-05-19T02:53:00Z | 4.99 | 4 | < 25mph
PG&E | 2018-06-09 | 0:46 | 35.0745 | -120.5167 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101927520 | Unknown | 12000 | Conductor | Overhead | Yes | 43260 | 0:46 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1645 | 2018 | 6 | 9 | 0 | 46 | 18-0049171 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 16825 | 5.84 | 221_78 | <25mph | <15mph | HFTD - Distribution | 2018-06-09 00:46:00 | 1387 | 22.9582 | FALSE | <25mph | F0412 | 2.71 | 2017-11-17T00:45:00Z | 2.01 | 18 | < 25mph | AU609 | 7.04 | 2017-11-17T00:47:00Z | 3 | 38 | < 25mph | D6295 | 3.81 | 2017-11-17T01:46:00Z | 4.99 | 34 | < 25mph | D6295 | 3.81 | 2017-11-17T01:46:00Z | 4.99 | 72 | < 25mph
PG&E | 2015-09-19 09:51 | 2015-09-19 09:51 | 38.4755 | -122.9069 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FORESTVILLE | 103334444 |  | 12000 | Conductor | Overhead | Yes | 42266.4104 | 2015-09-19 09:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0603 | 2015 | 9 | 19 | 9 | 51 | 15-0062267 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 488 | 1.1332 | 117_266 | <25mph | <15mph | HFTD - Distribution | 2015-09-19 09:51:00 | 348 | 13.7107 | FALSE | <25mph | D4623 | 2.94 | 2016-07-05T20:13:00Z | 13 | 8 | < 25mph | E9070 | 4.38 | 2016-07-05T20:40:00Z | 18.01 | 106 | < 25mph | D4623 | 2.94 | 2016-07-05T20:13:00Z | 13 | 14 | < 25mph | E9070 | 4.38 | 2016-07-05T21:36:00Z | 27 | 212 | 25-40mph
PG&E | 2019-08-16 | 10:31 | 39.3714 | -121.3221 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103191101 |  | 12000 | Conductor | Overhead | Yes | 43693 | 10:31 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-397 | 2019 | 8 | 16 | 10 | 31 | 19-0088805 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4580 | 6.4736 | 186_315 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 10:31:00 | 1984 | 15.7456 | FALSE | <25mph | BNGC1 | 3.48 | 2019-05-06T17:51:00Z | 10 | 1 | < 25mph | PG309 | 6.1 | 2019-05-06T17:20:00Z | 10.51 | 13 | < 25mph | BNGC1 | 3.48 | 2019-05-06T18:51:00Z | 11.01 | 2 | < 25mph | PG290 | 4.62 | 2019-05-06T19:00:00Z | 13.15 | 26 | < 25mph
PG&E | 2016-08-13 | 2016-08-13 14:00 | 39.2009 | -121.213 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100011376 | PACIFIC BELL | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0924 | 2016 | 8 | 13 | 14 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 9.674 | 190_305 | <25mph | <15mph | HFTD - Distribution | 2016-08-13 14:00:00 | 666 | 11.9455 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG348 | 4.58 | 2019-05-16T16:20:00Z | 21.03 | 38 | < 25mph |  |  |  | 0 | 0 | No data | PG348 | 4.58 | 2019-05-16T17:50:00Z | 23.02 | 77 | < 25mph
PG&E | 2018-05-11 | 10:13 | 38.387 | -122.9856 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101973909 | Unknown | 12000 | Conductor | Overhead | Yes | 43231 | 10:13 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1585 | 2018 | 5 | 11 | 10 | 13 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.6545 | 114_261 | <25mph | <15mph | HFTD - Distribution | 2018-05-11 10:13:00 | 1327 | 21.7544 | FALSE | <25mph | D2849 | 0.89 | 2017-04-08T15:01:00Z | 3 | 8 | < 25mph | UCBM | 6.47 | 2017-04-08T14:40:00Z | 19.71 | 48 | < 25mph | D2849 | 0.89 | 2017-04-08T15:46:00Z | 5.99 | 17 | < 25mph | BDZC1 | 6.47 | 2017-04-08T15:44:00Z | 31.21 | 107 | 25-40mph
PG&E | 2017-05-24 16:25 | 16:24 | 38.834 | -121.1197 | Vegetation | Rural | < 3 Meters | Fire Agency | Fire Capt | 103838109 | None | 12000 | Conductor | Overhead | Yes | 42879.6837 | 16:24 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | no-match | 1111 | 2017 | 5 | 24 | 16 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 20.975 | 194_285 | <25mph | <15mph | HFTD - Distribution | 2017-05-24 16:24:00 | 851 | 20.975 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D0140 | 6.56 | 2015-08-21T09:20:00Z | 8.01 | 15 | < 25mph |  |  |  | 0 | 0 | No data | D0140 | 6.56 | 2015-08-21T10:00:00Z | 10 | 30 | < 25mph
PG&E | 2015-06-12 13:07 | 2015-06-12 13:07 | 40.4077 | -122.4104 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS STREET FROM 4139 OLD HAPPY VALLEY RD |  | 12000 | Lightning Arrestor | Overhead | No |  |  | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | no-match | 0378 | 2015 | 6 | 12 | 13 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Lightning Arrestor | N.A. | 9.7698 | 140_372 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 13:07:00 | 124 | 24.3549 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6886 | 5.64 | 2018-06-23T03:16:00Z | 8.01 | 8 | < 25mph |  |  |  | 0 | 0 | No data | E6886 | 5.64 | 2018-06-23T04:46:00Z | 11.01 | 16 | < 25mph
PG&E | 2016-08-13 | 14:31 | 37.4642 | -119.8589 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire |  |  | 21000 | Conductor | Overhead | Yes | 42595 | 14:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0923 | 2016 | 8 | 13 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.5527 | 249_210 | <25mph | <15mph | HFTD - Distribution | 2016-08-13 14:31:00 | 667 | 11.4441 | FALSE | <25mph | C1522 | 2.94 | 2015-06-30T12:37:00Z | 3 | 2 | < 25mph | MPOC1 | 7.53 | 2015-06-30T13:07:00Z | 8.01 | 6 | < 25mph | C1522 | 2.94 | 2015-06-30T12:37:00Z | 3 | 4 | < 25mph | MPOC1 | 7.53 | 2015-06-30T14:07:00Z | 8.01 | 12 | < 25mph
PG&E | 2016-10-08 15:05 | 15:04 | 38.6686 | -120.9091 | Vegetation | RURAL | < 0.25 Acres | Customer | N.A. | 101380856 |  | 0 – 750 | Capacitor Bank | Overhead | Yes | 42651.6284 | 15:04 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1021 | 2016 | 10 | 8 | 15 | 4 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 10.4532 | 203_276 | <25mph | <15mph | HFTD - Distribution | 2016-10-08 15:04:00 | 762 | 14.8776 | FALSE | <25mph | PG106 | 3.14 | 2018-12-10T06:20:00Z | 7.25 | 42 | < 25mph | PG106 | 3.14 | 2018-12-10T06:20:00Z | 7.25 | 123 | < 25mph | PG106 | 3.14 | 2018-12-10T06:20:00Z | 7.25 | 84 | < 25mph | PG073 | 6.84 | 2018-12-10T07:50:00Z | 9.42 | 246 | < 25mph
PG&E | 2015-07-01 12:57 | 2015-07-01 12:57 | 39.4146 | -121.379 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42186.5396 | 2015-07-01 12:57 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0434 | 2015 | 7 | 1 | 12 | 57 | 15-0044609 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 12.6482 | 183_317 | <25mph | <15mph | HFTD - Distribution | 2015-07-01 12:57:00 | 179 | 18.7031 | FALSE | <25mph | BNGC1 | 2.37 | 2018-11-07T13:51:00Z | 1.01 | 1 | < 25mph | PG080 | 6.41 | 2018-11-07T13:20:00Z | 6.58 | 8 | < 25mph | BNGC1 | 2.37 | 2018-11-07T14:51:00Z | 1.01 | 2 | < 25mph | PG080 | 6.41 | 2018-11-07T13:20:00Z | 6.58 | 16 | < 25mph
PG&E | 2015-08-19 06:20 | 2015-08-19 06:20 | 39.2831 | -123.2931 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | MTR#50001225 | None | 12000 | Conductor | Overhead | Yes | 42235.2639 | 2015-08-19 06:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0545 | 2015 | 8 | 19 | 6 | 20 | 15-0055982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5403 | 1.4303 | 102_311 | <25mph | <15mph | HFTD - Distribution | 2015-08-19 06:20:00 | 289 | 19.8186 | FALSE | <25mph | AU552 | 3.69 | 2016-09-20T09:48:00Z | 4.99 | 15 | < 25mph | AU552 | 3.69 | 2016-09-20T09:48:00Z | 4.99 | 39 | < 25mph | AU552 | 3.69 | 2016-09-20T09:48:00Z | 4.99 | 30 | < 25mph | AU552 | 3.69 | 2016-09-20T09:48:00Z | 4.99 | 77 | < 25mph
PG&E | 2018-08-13 | 15:33 | 38.708 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101377799 | Unknown | 21000 | Conductor | Overhead | Yes | 43325 | 15:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1840 | 2018 | 8 | 13 | 15 | 33 | 18-0069470 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1004 | 11.7134 | 201_278 | <25mph | <15mph | HFTD - Distribution | 2018-08-13 15:33:00 | 1579 | 13.7748 | FALSE | <25mph | D7401 | 3.18 | 2015-10-01T21:34:00Z | 4.99 | 34 | < 25mph | D4314 | 7.77 | 2015-10-01T21:43:00Z | 8.01 | 64 | < 25mph | D7401 | 3.18 | 2015-10-01T22:19:00Z | 7 | 65 | < 25mph | D4314 | 7.77 | 2015-10-01T22:43:00Z | 11.01 | 125 | < 25mph
PG&E | 2019-07-25 | 0:15 | 39.0662 | -120.9754 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Placer Hills FD | 152491101 |  | 12000 | Conductor | Overhead | Yes | 43671 | 0:15 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-379 | 2019 | 7 | 25 | 0 | 15 | 19-0080924 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7845 | 8.7511 | 200_298 | <25mph | <15mph | HFTD - Distribution | 2019-07-25 00:15:00 | 1927 | 11.2312 | FALSE | <25mph | AT999 | 2.66 | 2017-12-08T10:38:00Z | 1.01 | 8 | < 25mph | AU268 | 7.7 | 2017-12-08T09:56:00Z | 1.01 | 35 | < 25mph | AT999 | 2.66 | 2017-12-08T11:23:00Z | 2.01 | 16 | < 25mph | AU268 | 7.7 | 2017-12-08T11:17:00Z | 3 | 75 | < 25mph
PG&E | 2019-08-11 | 1:19 | 39.1152 | -121.001 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100097796 |  | 12000 | Other | Overhead | Yes | 43688 | 1:19 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-387 | 2019 | 8 | 11 | 1 | 19 | 19-0086613 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6200 | 9.9563 | 199_300 | <25mph | <15mph | HFTD - Distribution | 2019-08-11 01:19:00 | 1965 | 18.5914 | FALSE | <25mph | C5488 | 3.22 | 2017-11-12T18:54:00Z | 7 | 22 | < 25mph | E1789 | 7.39 | 2017-11-12T18:18:00Z | 8.01 | 63 | < 25mph | C5488 | 3.22 | 2017-11-12T19:54:00Z | 8.99 | 44 | < 25mph | C5488 | 3.22 | 2017-11-12T19:54:00Z | 8.99 | 127 | < 25mph
PG&E | 2017-10-02 | 14:56 | 38.9102 | -120.9185 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100110800 | None | 21000 | Other | Overhead | Yes | 43010 | 14:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1447 | 2017 | 10 | 2 | 14 | 56 | 17-0083516 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 160 | 17.2967 | 203_289 | <25mph | <15mph | HFTD - Distribution | 2017-10-02 14:56:00 | 1185 | 22.7009 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.3 | 2015-06-14T01:56:00Z | 10 | 19 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.3 | 2015-06-14T02:56:00Z | 10 | 38 | < 25mph
PG&E | 2018-12-12 | 12:09 | 38.727 | -120.7947 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 101404403 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43446 | 12:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1984 | 2018 | 12 | 12 | 12 | 9 | No ILIS or TOTL available | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.1462 | 208_279 | <25mph | <15mph | HFTD - Distribution | 2018-12-12 12:09:00 | 1724 | 13.5134 | FALSE | <25mph | AV185 | 2.92 | 2017-10-18T04:00:00Z | 1.01 | 44 | < 25mph | E3165 | 5.8 | 2017-10-18T04:26:00Z | 5.99 | 112 | < 25mph | AV185 | 2.92 | 2017-10-18T05:00:00Z | 1.01 | 84 | < 25mph | E3165 | 5.8 | 2017-10-18T04:36:00Z | 7 | 219 | < 25mph
PG&E | 2015-06-27 22:28 | 2015-06-27 22:28 | 38.1194 | -120.6218 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 101281699 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.9361 | 2015-06-27 22:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0417 | 2015 | 6 | 27 | 22 | 28 | 15-0043798 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 517 | 14.2862 | 216_246 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 22:28:00 | 162 | 15.5829 | FALSE | <25mph | C9085 | 3.92 | 2015-11-16T21:17:00Z | 10 | 3 | < 25mph | C9085 | 3.92 | 2015-11-16T21:17:00Z | 10 | 3 | < 25mph | C9085 | 3.92 | 2015-11-16T21:17:00Z | 10 | 4 | < 25mph | C9085 | 3.92 | 2015-11-16T21:17:00Z | 10 | 4 | < 25mph
PG&E | 2016-08-25 | 2016-08-25 12:04 | 36.9726 | -119.3816 | Vegetation | RURAL | < 3 meters | Utility: PG&E | N.A. | 100651318 | PONDEROSA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0945 | 2016 | 8 | 25 | 12 | 4 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.3948 | 271_183 | <25mph | <15mph | HFTD - Distribution | 2016-08-25 12:04:00 | 689 | 15.1668 | FALSE | <25mph |  |  |  | 0 | 0 | No data | FSBC1 | 7.76 | 2016-10-12T05:53:00Z | 7 | 7 | < 25mph |  |  |  | 0 | 0 | No data | FSBC1 | 7.76 | 2016-10-12T05:53:00Z | 7 | 14 | < 25mph
PG&E | 2019-04-09 | 15:27 | 37.7341 | -120.0776 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 101076921 |  | 21000 | Pole | Overhead | Yes | 43564 | 15:27 | Vegetation |  | Veg. contact | Pole |  |  | Branch (Not overhanging, > 12ft) | 2019-313 | 2019 | 4 | 9 | 15 | 27 | 19-0041008 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 179862 | 22.8983 | 240_225 | <25mph | <15mph | HFTD - Distribution | 2019-04-09 15:27:00 | 1738 | 29.8749 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | SEWC1 | 4.76 | 2016-12-18T14:16:00Z | 11.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | SEWC1 | 4.76 | 2016-12-18T14:16:00Z | 11.01 | 2 | < 25mph
PG&E | 2018-07-01 | 8:13 | 39.4154 | -121.5122 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430344 | AT&T | 12000 | Conductor | Overhead | Yes | 43282 | 8:13 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1720 | 2018 | 7 | 1 | 8 | 13 | 18-0056061 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 7848 | 6.5616 | 178_317 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 08:13:00 | 1461 | 14.6967 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BNGC1 | 7.14 | 2016-09-29T10:51:00Z | 5.99 | 2 | < 25mph |  |  |  | 0 | 0 | No data | BNGC1 | 7.14 | 2016-09-29T10:51:00Z | 5.99 | 4 | < 25mph
PG&E | 2015-07-24 14:30 | 2015-07-24 14:30 | 36.6913 | -119.0312 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46970 DUNLAP RD | YES | 0 – 750 | Transformer | Overhead | Yes | 42209.6042 | 2015-07-24 14:30 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0482 | 2015 | 7 | 24 | 14 | 30 | 15-0050401 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 281 | 12.3885 | 287_168 | <25mph | <15mph | HFTD - Distribution | 2015-07-24 14:30:00 | 227 | 13.0893 | FALSE | <25mph | PHRC1 | 0.81 | 2015-07-29T20:58:00Z | 13 | 1 | < 25mph | PRGC1 | 5.41 | 2015-07-29T21:00:00Z | 15.99 | 15 | < 25mph | PHRC1 | 0.81 | 2015-07-29T21:58:00Z | 13 | 2 | < 25mph | PRGC1 | 5.41 | 2015-07-29T21:00:00Z | 15.99 | 28 | < 25mph
PG&E | 2018-06-11 | 17:49 | 34.7329 | -120.0861 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103015183 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43262 | 17:49 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1649 | 2018 | 6 | 11 | 17 | 49 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 16.7571 | 241_59 | <25mph | <15mph | HFTD - Distribution | 2018-06-11 17:49:00 | 1391 | 18.839 | FALSE | <25mph | UCSE | 3.69 | 2019-07-21T19:10:00Z | 11.3 | 18 | < 25mph | PG143 | 6.49 | 2019-07-21T19:00:00Z | 12.71 | 27 | < 25mph | PG214 | 2.52 | 2019-07-21T20:10:00Z | 13.38 | 36 | < 25mph | PG143 | 6.49 | 2019-07-21T19:40:00Z | 15.12 | 54 | < 25mph
PG&E | 2015-02-07 18:38 | 2015-02-07 18:38 | 40.4674 | -123.6545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | mile marker 36.61, hwy 36, bridgeville |  | 12000 | Conductor | Overhead | Yes | 42042.7764 | 2015-02-07 18:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0262 | 2015 | 2 | 7 | 18 | 38 | 15-0011390 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 7691 | 20.9308 | 88_377 | <25mph | <15mph | HFTD - Distribution | 2015-02-07 18:38:00 | 9 | 24.639 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2019-06-17 | 10:25 | 38.511 | -122.2134 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 43051101 |  | 12000 | Conductor | Overhead | Yes | 43633 | 10:25 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-84 | 2019 | 6 | 17 | 10 | 25 | 19-0068579 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 306900 | 10.2943 | 147_267 | <25mph | <15mph | HFTD - Distribution | 2019-06-17 10:25:00 | 1843 | 15.8677 | FALSE | <25mph | ATLC1 | 3.74 | 2016-03-03T17:29:00Z | 22.01 | 1 | < 25mph | ATLC1 | 3.74 | 2016-03-03T17:29:00Z | 22.01 | 1 | < 25mph | ATLC1 | 3.74 | 2016-03-03T17:29:00Z | 22.01 | 2 | < 25mph | ATLC1 | 3.74 | 2016-03-03T17:29:00Z | 22.01 | 2 | < 25mph
PG&E | 2017-06-15 08:08 | 7:39 | 39.2276 | -121.2348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE CHIEF | 103676075 | Unknown | 21000 | Conductor | Overhead | Yes | 42901.3391 | 7:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1147 | 2017 | 6 | 15 | 7 | 39 | 17-0055387 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 740 | 10.5195 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 07:39:00 | 886 | 12.4202 | FALSE | <25mph | PG448 | 2.04 | 2019-08-30T04:20:00Z | 5.03 | 6 | < 25mph | PG381 | 7 | 2019-08-30T05:00:00Z | 10.09 | 41 | < 25mph | PG448 | 2.04 | 2019-08-30T04:20:00Z | 5.03 | 12 | < 25mph | PG381 | 7 | 2019-08-30T05:30:00Z | 14.32 | 75 | < 25mph
PG&E | 2017-05-25 17:36 | 16:55 | 38.3986 | -122.9876 | Vegetation | Rural | < 3 Meters | Utility: PG&E | N.A. | 101974034 | Unknown | 12000 | Conductor | Overhead | Yes | 42880.7334 | 16:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1114 | 2017 | 5 | 25 | 16 | 55 | 17-0050815 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 2644 | 12.6436 | 114_262 | <25mph | <15mph | HFTD - Distribution | 2017-05-25 16:55:00 | 854 | 13.2306 | FALSE | <25mph | D2849 | 1.17 | 2016-06-20T05:59:00Z | 3 | 12 | < 25mph | UCBM | 7.05 | 2016-06-20T05:40:00Z | 23.8 | 84 | < 25mph | D2849 | 1.17 | 2016-06-20T06:09:00Z | 3 | 24 | < 25mph | UCBM | 7.05 | 2016-06-20T05:40:00Z | 23.8 | 170 | < 25mph
PG&E | 2016-07-21 21:45 | 2016-07-21 21:45 | 40.8566 | -122.3387 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101455670 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0870 | 2016 | 7 | 21 | 21 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.7351 | 143_397 | <25mph | <15mph | HFTD - Distribution | 2016-07-21 21:45:00 | 613 | 15.1303 | FALSE | <25mph | CTANT | 1.58 | 2015-07-27T15:30:00Z | 11.81 | 4 | < 25mph | SLFC1 | 6.48 | 2015-07-27T15:19:00Z | 22.01 | 8 | < 25mph | CTANT | 1.58 | 2015-07-27T15:30:00Z | 11.81 | 6 | < 25mph | SLFC1 | 6.48 | 2015-07-27T15:19:00Z | 22.01 | 14 | < 25mph
PG&E | 2018-09-01 | 14:25 | 36.8088 | -121.5916 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Twr 35/222 | None | 115000 | Conductor | Overhead | Yes | 43344 | 14:25 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1875 | 2018 | 9 | 1 | 14 | 25 | INT-11331 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 702145 | 13.8683 | 173_173 | <25mph | <15mph | HFTD - Transmission | 2018-09-01 14:25:00 | 1614 | 16.3299 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-09-15 | 15:56 | 37.1102 | -121.9509 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100520198 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42628 | 15:56 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0982 | 2016 | 9 | 15 | 15 | 56 | 16-0065001 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 28900 | 4.729 | 158_190 | <25mph | <15mph | HFTD - Distribution | 2016-09-15 15:56:00 | 724 | 12.2674 | FALSE | <25mph | D8700 | 3.83 | 2018-02-24T18:30:00Z | 14 | 53 | < 25mph | D8700 | 3.83 | 2018-02-24T18:30:00Z | 14 | 85 | < 25mph | D8700 | 3.83 | 2018-02-24T19:30:00Z | 15.99 | 104 | < 25mph | D8700 | 3.83 | 2018-02-24T19:30:00Z | 15.99 | 166 | < 25mph
PG&E | 2016-06-21 | 2016-06-21 16:53 | 38.4233 | -122.5448 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | KENWOOD FIRE XST | 102036904 | Yes | 0 – 750 | Conductor | Overhead | Yes | 42542 | 2016-06-21 16:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0814 | 2016 | 6 | 21 | 16 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 14.0146 | 133_263 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 16:53:00 | 556 | 14.0381 | FALSE | <25mph | KENWW | 1.1 | 2017-12-29T21:00:00Z | 6.4 | 1 | < 25mph | KENWW | 1.1 | 2017-12-29T21:00:00Z | 6.4 | 15 | < 25mph | KENWW | 1.1 | 2017-12-29T22:00:00Z | 6.4 | 2 | < 25mph | F11WW | 6.18 | 2017-12-29T22:00:00Z | 7.81 | 31 | < 25mph
PG&E | 2019-07-17 | 7:49 | 34.5066 | -120.2247 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Santa Barbara County FD | 4Bx0717190747 |  | 12000 | Other | Overhead | Yes | 43663 | 7:49 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-425 | 2019 | 7 | 17 | 7 | 49 | 19-0078239 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 19608 | 17.3045 | 235_46 | <25mph | <15mph | HFTD - Distribution | 2019-07-17 07:49:00 | 1908 | 28.4942 | FALSE | 25-40mph | UP481 | 2.43 | 2017-10-03T06:10:00Z | 13 | 13 | < 25mph | UP481 | 2.43 | 2017-10-03T06:10:00Z | 13 | 13 | < 25mph | UP481 | 2.43 | 2017-10-03T07:40:00Z | 13 | 28 | < 25mph | UP481 | 2.43 | 2017-10-03T07:40:00Z | 13 | 28 | < 25mph
PG&E | 2016-05-15 15:54 | 2016-05-15 15:54 | 36.7948 | -119.3966 | Vegetation | RURAL | 100 - 299 Acres | Fire Agency | Cal Fire | 100729685 | None | 12000 | Conductor | Overhead | Yes | 42505.6625 | 2016-05-15 15:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0730 | 2016 | 5 | 15 | 15 | 54 | 16-0036136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 180310 | 10.5903 | 270_173 | <25mph | <15mph | HFTD - Distribution | 2016-05-15 15:54:00 | 474 | 14.7659 | FALSE | <25mph |  |  |  | 0 | 0 | No data | FCHC1 | 7.54 | 2015-08-28T23:00:00Z | 14.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | FCHC1 | 7.54 | 2015-08-28T23:00:00Z | 14.99 | 2 | < 25mph
PG&E | 2018-07-14 | 12:40 | 38.5793 | -122.878 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103122744 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 12:40 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1746 | 2018 | 7 | 14 | 12 | 40 | 18-0059799 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20804 | 12.0574 | 118_272 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 12:40:00 | 1486 | 14.4502 | FALSE | <25mph | D2144 | 3.55 | 2016-01-12T21:43:00Z | 4 | 15 | < 25mph | E6724 | 5.13 | 2016-01-12T22:09:00Z | 4.99 | 29 | < 25mph | D2144 | 3.55 | 2016-01-12T21:43:00Z | 4 | 30 | < 25mph | E6724 | 5.13 | 2016-01-12T22:19:00Z | 13 | 58 | < 25mph
PG&E | 2015-03-04 18:44 | 2015-03-04 18:44 | 38.9995 | -122.7545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kelseyville FD | 102156367 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42067.7806 | 2015-03-04 18:44 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0271 | 2015 | 3 | 4 | 18 | 44 | 15-0017374 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29532 | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2015-03-04 18:44:00 | NA | 0 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.58 | 2019-07-20T05:57:00Z | 14 | 23 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.58 | 2019-07-20T05:57:00Z | 14 | 46 | < 25mph
PG&E | 2015-09-10 16:24 | 2015-09-10 16:24 | 38.5049 | -122.3535 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103159970 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42257.6833 | 2015-09-10 16:24 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0589 | 2015 | 9 | 10 | 16 | 24 | 15-0060610 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 130124 | 14.3548 | 141_267 | <25mph | <15mph | HFTD - Distribution | 2015-09-10 16:24:00 | 334 | 16.5969 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AT925 | 6.82 | 2016-09-04T19:09:00Z | 3 | 13 | < 25mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.22 | 2016-09-04T19:29:00Z | 11.01 | 26 | < 25mph
PG&E | 2017-07-07 | 15:09 | 40.9054 | -122.3806 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101455950 | Unknown | 12000 | Conductor | Overhead | Yes | 42923 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1229 | 2017 | 7 | 7 | 15 | 9 | 17-0061903 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.0906 | 142_400 | <25mph | <15mph | HFTD - Distribution | 2017-07-07 15:09:00 | 969 | 11.4161 | FALSE | <25mph | CTANT | 2.76 | 2016-01-07T04:00:00Z | 6.22 | 9 | < 25mph | CTANT | 2.76 | 2016-01-07T04:00:00Z | 6.22 | 9 | < 25mph | CTANT | 2.76 | 2016-01-07T04:30:00Z | 7.45 | 18 | < 25mph | CTANT | 2.76 | 2016-01-07T04:30:00Z | 7.45 | 18 | < 25mph
PG&E | 2019-07-25 | 0:15 | 39.0662 | -120.9754 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Placer Hills FD | 152491101 |  | 12000 | Conductor | Overhead | Yes | 43671 | 0:15 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-379 | 2019 | 7 | 25 | 0 | 15 | 19-0080924 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7845 | 8.7511 | 200_298 | <25mph | <15mph | HFTD - Distribution | 2019-07-25 00:15:00 | 1927 | 11.2312 | FALSE | <25mph | AT999 | 2.66 | 2015-10-21T07:46:00Z | 3 | 18 | < 25mph | AU268 | 7.7 | 2015-10-21T07:04:00Z | 3 | 39 | < 25mph | AT999 | 2.66 | 2015-10-21T08:54:00Z | 4.99 | 32 | < 25mph | AT999 | 2.66 | 2015-10-21T08:54:00Z | 4.99 | 72 | < 25mph
PG&E | 2017-12-20 07:55 | 07:54 | 37.4012 | -122.3606 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100318864 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43089.3298 | 07:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1546 | 2017 | 12 | 20 | 7 | 54 | 17-0102756 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6602 | 16.1413 | 140_206 | <25mph | <15mph | HFTD - Distribution | 2017-12-20 07:54:00 | 1288 | 21.2088 | FALSE | <25mph | E4863 | 2.73 | 2017-12-02T12:18:00Z | 2.01 | 5 | < 25mph | PUGC1 | 6.04 | 2017-12-02T12:18:00Z | 3 | 10 | < 25mph | E4863 | 2.73 | 2017-12-02T12:18:00Z | 2.01 | 5 | < 25mph | PUGC1 | 6.04 | 2017-12-02T13:18:00Z | 3 | 11 | < 25mph
PG&E | 2015-11-09 05:55 | 2015-11-09 05:55 | 34.9984 | -120.3634 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42317.2465 | 2015-11-09 05:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0673 | 2015 | 11 | 9 | 5 | 55 | 15-0076534 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 205393 | 8.4294 | 228_73 | <25mph | <15mph | HFTD - Distribution | 2015-11-09 05:55:00 | 417 | 17.7768 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AU609 | 7.47 | 2015-03-16T11:54:00Z | 2.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | AU609 | 7.47 | 2015-03-16T12:54:00Z | 3 | 8 | < 25mph
7. Camp Fire | 2018-11-08 | 6:33 | 39.8134 | -121.4347 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 60000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1993 | 2018 | 11 | 8 | 6 | 33 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Conductor | 826291590 | 33.1236 | 181_339 | 25-40mph | 30-45mph | HFTD - Transmission | 2018-11-08 06:33:00 | 1699 | 39.0185 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | JBGC1 | 6.08 | 2015-03-26T08:13:00Z | 35.99 | 1 | 25-40mph |  |  |  | 0 | 0 | No data | JBGC1 | 6.08 | 2015-03-26T08:13:00Z | 35.99 | 2 | 25-40mph
PG&E | 2017-09-08 | 17:21 | 38.6039 | -120.9275 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101379094 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42986 | 17:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1402 | 2017 | 9 | 8 | 17 | 21 | 17-0077122 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 8504 | 10.5347 | 203_272 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 17:21:00 | 1140 | 11.5767 | FALSE | <25mph | BENC1 | 0.96 | 2018-05-10T09:59:00Z | 4 | 14 | < 25mph | BENC1 | 0.96 | 2018-05-10T09:59:00Z | 4 | 47 | < 25mph | BENC1 | 0.96 | 2018-05-10T10:59:00Z | 5.99 | 26 | < 25mph | BENC1 | 0.96 | 2018-05-10T10:59:00Z | 5.99 | 91 | < 25mph
PG&E | 2018-08-08 | 16:03 | 37.2974 | -122.2651 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 100307515 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 16:03 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1831 | 2018 | 8 | 8 | 16 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.1654 | 144_201 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:03:00 | 1570 | 9.1654 | FALSE | <25mph | LAHC1 | 0.77 | 2017-07-06T03:07:00Z | 4.99 | 1 | < 25mph | LOAC1 | 7.85 | 2017-07-06T03:10:00Z | 4.99 | 25 | < 25mph | LAHC1 | 0.77 | 2017-07-06T03:07:00Z | 4.99 | 2 | < 25mph | LOAC1 | 7.85 | 2017-07-06T03:10:00Z | 4.99 | 49 | < 25mph
PG&E | 2017-08-28 | 9:14 | 38.7443 | -122.6491 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 103781085 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42975 | 9:14 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1356 | 2017 | 8 | 28 | 9 | 14 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 4.693 | 128_281 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 09:14:00 | 1094 | 16.6198 | FALSE | <25mph | PG079 | 1.04 | 2019-04-25T20:10:00Z | 18.19 | 12 | < 25mph | PG079 | 1.04 | 2019-04-25T20:10:00Z | 18.19 | 46 | < 25mph | PG079 | 1.04 | 2019-04-25T20:50:00Z | 22.79 | 24 | < 25mph | PG079 | 1.04 | 2019-04-25T20:50:00Z | 22.79 | 92 | < 25mph
PG&E | 2015-07-04 01:14 | 2015-07-04 01:14 | 38.9566 | -121.0434 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100037226 |  | 12000 | Other | Overhead | Yes | 42189.0514 | 2015-07-04 01:14 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0441 | 2015 | 7 | 4 | 1 | 14 | 15-0045440 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 53865 | 7.3476 | 198_292 | <25mph | <15mph | HFTD - Distribution | 2015-07-04 01:14:00 | 186 | 12.3228 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C0713 | 4.12 | 2017-03-25T20:19:00Z | 11.01 | 31 | < 25mph |  |  |  | 0 | 0 | No data | C0713 | 4.12 | 2017-03-25T21:24:00Z | 13 | 61 | < 25mph
PG&E | 2015-07-18 17:00 | 2015-07-18 17:00 | 38.8383 | -123.6297 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | off HWY 1 PA |  | 12000 | Conductor | Overhead | Yes | 42203.7083 | 2015-07-18 17:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0470 | 2015 | 7 | 18 | 17 | 0 | 15-0048394 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 51806 | 18.0824 | 86_287 | <25mph | <15mph | HFTD - Distribution | 2015-07-18 17:00:00 | 215 | 27.3037 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | ANVC1 | 6.68 | 2017-02-06T13:36:00Z | 8.99 | 9 | < 25mph |  |  |  | 0 | 0 | No data | ANVC1 | 6.68 | 2017-02-06T15:00:00Z | 10.98 | 18 | < 25mph
PG&E | 2019-04-28 | 12:36 | 39.6756 | -121.5677 |  | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 100404366 |  | 12000 | Conductor | Overhead | Yes | 43583 | 12:36 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-166 | 2019 | 4 | 28 | 12 | 36 | 19-0046853 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 79810 | 6.7497 | 175_331 | <25mph | <15mph | HFTD - Distribution | 2019-04-28 12:36:00 | 1752 | 11.2512 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JBGC1 | 5.9 | 2015-03-17T13:13:00Z | 11.01 | 11 | < 25mph |  |  |  | 0 | 0 | No data | JBGC1 | 5.9 | 2015-03-17T14:13:00Z | 12.01 | 20 | < 25mph
PG&E | 2015-02-06 06:01 | 2015-02-06 06:01 | 38.6059 | -121.0221 | Vegetation | Rural | < 3 meters | Fire Agency |  | 6661 Ryan Ranch Road, El Dorado Hills |  | 21000 | Conductor | Overhead | Yes | 42041.2507 | 2015-02-06 06:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0259 | 2015 | 2 | 6 | 6 | 1 | 15-0009876 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 51996 | 16.7927 | 199_272 | <25mph | <15mph | HFTD - Distribution | 2015-02-06 06:01:00 | 6 | 30.3484 | FALSE | 25-40mph | D4314 | 3.45 | 2015-06-20T16:43:00Z | 8.01 | 12 | < 25mph | D4314 | 3.45 | 2015-06-20T16:43:00Z | 8.01 | 45 | < 25mph | D4314 | 3.45 | 2015-06-20T17:43:00Z | 8.99 | 24 | < 25mph | BENC1 | 4.89 | 2015-06-20T16:59:00Z | 11.01 | 90 | < 25mph
PG&E | 2019-05-17 | 15:12 | 38.4797 | -123.1486 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 42811111 |  | 12000 | Conductor | Overhead | Yes | 43602 | 15:12 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-200 | 2019 | 5 | 17 | 15 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 19.5511 | 107_266 | <25mph | <15mph | HFTD - Distribution | 2019-05-17 15:12:00 | 1775 | 20.334 | FALSE | <25mph | E8483 | 3.61 | 2019-04-28T21:00:00Z | 14.99 | 4 | < 25mph | E8483 | 3.61 | 2019-04-28T21:00:00Z | 14.99 | 15 | < 25mph | E8483 | 3.61 | 2019-04-28T21:00:00Z | 14.99 | 8 | < 25mph | E8483 | 3.61 | 2019-04-28T21:00:00Z | 14.99 | 29 | < 25mph
PG&E | 2015-05-09 13:10 | 2015-05-09 13:10 | 39.2343 | -121.2468 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100000103 | None | 21000 | Conductor | Overhead | Yes | 42133.5486 | 2015-05-09 13:10 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0311 | 2015 | 5 | 9 | 13 | 10 | 15-0033085 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 382926 | 12.172 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 13:10:00 | 57 | 17.071 | FALSE | <25mph | E2572 | 3.27 | 2017-05-20T07:08:00Z | 1.01 | 12 | < 25mph | E2572 | 3.27 | 2017-05-20T07:08:00Z | 1.01 | 18 | < 25mph | E2572 | 3.27 | 2017-05-20T07:53:00Z | 1.01 | 22 | < 25mph | E2572 | 3.27 | 2017-05-20T07:53:00Z | 1.01 | 34 | < 25mph
PG&E | 2016-06-21 | 20:49 | 35.5352 | -120.8457 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101900832 |  | 12000 | Conductor | Overhead | Yes | 42542 | 20:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0812 | 2016 | 6 | 21 | 20 | 49 | 16-0044904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7806 | 8.2716 | 207_103 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 20:49:00 | 558 | 17.6234 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2017-09-01 | 8:00 | 37.3757 | -119.8886 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101067028 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42979 | 8:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1378 | 2017 | 9 | 1 | 8 | 0 | 17-0074724 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 680 | 5.98 | 248_205 | <25mph | <15mph | HFTD - Distribution | 2017-09-01 08:00:00 | 1116 | 14.9658 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MCFC1 | 7.03 | 2016-12-20T09:02:00Z | 4 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MCFC1 | 7.03 | 2016-12-20T10:02:00Z | 4 | 2 | < 25mph
PG&E | 2018-03-06 | 17:57 | 38.2811 | -120.8965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-647-5220 | 101238429 | AT&T | 12000 | Conductor | Overhead | Yes | 43165 | 17:57 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1566 | 2018 | 3 | 6 | 17 | 57 | 18-0020396 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 142000 | 3.9357 | 204_254 | <25mph | <15mph | HFTD - Distribution | 2018-03-06 17:57:00 | 1308 | 12.1612 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.07 | 2018-03-06T15:05:00Z | 8.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | CMAC1 | 4.3 | 2018-03-06T15:59:00Z | 11.01 | 8 | < 25mph
PG&E | 2018-08-12 | 14:46 | 38.6443 | -120.9211 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101410516 | Unknown | 21000 | Conductor | Overhead | Yes | 43324 | 14:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1838 | 2018 | 8 | 12 | 14 | 46 | 18-0069084 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4032 | 11.2318 | 203_274 | <25mph | <15mph | HFTD - Distribution | 2018-08-12 14:46:00 | 1577 | 12.412 | FALSE | <25mph | BENC1 | 3.75 | 2016-12-26T12:59:00Z | 10 | 13 | < 25mph | BENC1 | 3.75 | 2016-12-26T12:59:00Z | 10 | 83 | < 25mph | BENC1 | 3.75 | 2016-12-26T12:59:00Z | 10 | 26 | < 25mph | BENC1 | 3.75 | 2016-12-26T12:59:00Z | 10 | 163 | < 25mph
PG&E | 2018-06-09 | 0:46 | 35.0745 | -120.5167 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101927520 | Unknown | 12000 | Conductor | Overhead | Yes | 43260 | 0:46 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1645 | 2018 | 6 | 9 | 0 | 46 | 18-0049171 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 16825 | 5.84 | 221_78 | <25mph | <15mph | HFTD - Distribution | 2018-06-09 00:46:00 | 1387 | 22.9582 | FALSE | <25mph | E8214 | 3.18 | 2017-08-07T15:40:00Z | 4 | 17 | < 25mph | E8214 | 3.18 | 2017-08-07T15:40:00Z | 4 | 38 | < 25mph | E8214 | 3.18 | 2017-08-07T15:55:00Z | 5.99 | 30 | < 25mph | E8214 | 3.18 | 2017-08-07T15:55:00Z | 5.99 | 70 | < 25mph
PG&E | 2019-07-15 | 7:51 | 38.3266 | -122.568 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 42721104 |  | 12000 | Conductor | Overhead | Yes | 43661 | 7:51 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-343 | 2019 | 7 | 15 | 7 | 51 | 19-0077351 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2348 | 31.0114 | 132_257 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-07-15 07:51:00 | 1903 | 35.3209 | FALSE | 25-40mph | F11WW | 3.53 | 2018-05-02T14:00:00Z | 7.4 | 1 | < 25mph | F11WW | 3.53 | 2018-05-02T14:00:00Z | 7.4 | 24 | < 25mph | F11WW | 3.53 | 2018-05-02T14:00:00Z | 7.4 | 2 | < 25mph | KO69 | 5.16 | 2018-05-02T14:15:00Z | 11.5 | 50 | < 25mph
PG&E | 2018-06-15 | 9:51 | 37.1986 | -119.4709 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RANCHARIA ENGINE 4255 USFS ENG 52 | 101058060 | Unknown | 12000 | Conductor | Overhead | Yes | 43266 | 9:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1660 | 2018 | 6 | 15 | 9 | 51 | 18-0051354 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 35146 | 7.0865 | 267_195 | <25mph | <15mph | HFTD - Distribution | 2018-06-15 09:51:00 | 1402 | 16.2916 | FALSE | <25mph | C6459 | 3.69 | 2017-07-01T22:00:00Z | 8.99 | 4 | < 25mph | C6459 | 3.69 | 2017-07-01T22:00:00Z | 8.99 | 4 | < 25mph | C6459 | 3.69 | 2017-07-01T22:00:00Z | 8.99 | 8 | < 25mph | C6459 | 3.69 | 2017-07-01T22:00:00Z | 8.99 | 8 | < 25mph
PG&E | 2016-05-12 20:15 | 2016-05-12 20:15 | 35.1922 | -120.4563 | Vegetation | RURAL | < 3 meters | Self Extinguished | N.A. | 101857280 |  | 12000 | Conductor | Overhead | Yes | 42502.8438 | 2016-05-12 20:15 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0727 | 2016 | 5 | 12 | 20 | 15 | 16-0035728 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 54088 | 8.5669 | 224_84 | <25mph | <15mph | HFTD - Distribution | 2016-05-12 20:15:00 | 471 | 14.182 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AU609 | 7.02 | 2015-05-27T01:57:00Z | 10 | 9 | < 25mph |  |  |  | 0 | 0 | No data | AU609 | 7.02 | 2015-05-27T01:57:00Z | 10 | 20 | < 25mph
PG&E | 2016-10-11 23:17 | 23:16 | 39.0201 | -120.8294 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire.foresthill fire | 100025501 |  | 60000 | Conductor | Overhead | Yes | 42654.9701 | 23:16 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error |  | no-match | 1028 | 2016 | 10 | 11 | 23 | 16 | INT-08640 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 0 | 7.6312 | 207_295 | <25mph | <15mph | HFTD - Transmission | 2016-10-11 23:16:00 | 769 | 11.1078 | FALSE | <25mph | AU268 | 0.89 | 2017-09-16T05:20:00Z | 0 | 3 | < 25mph | FSHC1 | 7.19 | 2017-09-16T04:33:00Z | 8.01 | 8 | < 25mph | AU268 | 0.89 | 2017-09-16T06:14:00Z | 0 | 6 | < 25mph | FSHC1 | 7.19 | 2017-09-16T04:33:00Z | 8.01 | 18 | < 25mph
PG&E | 2017-08-14 07:56 | 07:56 | 39.1794 | -120.9761 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100083743 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42961.3308 | 07:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1334 | 2017 | 8 | 14 | 7 | 56 | 17-0070063 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3012 | 6.4958 | 200_304 | <25mph | <15mph | HFTD - Distribution | 2017-08-14 07:56:00 | 1071 | 15.2686 | FALSE | <25mph | C1397 | 3.58 | 2015-07-07T14:11:00Z | 1.01 | 6 | < 25mph | AT999 | 5.18 | 2015-07-07T15:04:00Z | 3 | 45 | < 25mph | D8321 | 3.61 | 2015-07-07T16:00:00Z | 2.01 | 15 | < 25mph | E5439 | 6.04 | 2015-07-07T16:00:00Z | 5.99 | 102 | < 25mph
PG&E | 2015-06-27 12:48 | 2015-06-27 12:48 | 37.9474 | -120.4274 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101034512 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.5333 | 2015-06-27 12:48 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0414 | 2015 | 6 | 27 | 12 | 48 | 15-0043755 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 150075 | 11.0891 | 224_236 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 12:48:00 | 159 | 19.6587 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-08-10 | 2016-08-10 08:36 | 37.0575 | -121.9556 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 101680487 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0917 | 2016 | 8 | 10 | 8 | 36 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 6.3982 | 157_187 | <25mph | <15mph | HFTD - Distribution | 2016-08-10 08:36:00 | 659 | 9.833 | FALSE | <25mph | E5965 | 0.91 | 2016-01-28T04:55:00Z | 3 | 41 | < 25mph | E7977 | 6.13 | 2016-01-28T05:17:00Z | 8.01 | 162 | < 25mph | E5965 | 0.91 | 2016-01-28T06:40:00Z | 3 | 82 | < 25mph | C9585 | 6.04 | 2016-01-28T06:37:00Z | 10 | 321 | < 25mph
PG&E | 2016-08-03 | 2016-08-03 04:38 | 38.8474 | -120.812 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire garden valley fire | 103809676 |  | 21000 | Conductor | Overhead | Yes | 42585 | 2016-08-03 04:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0901 | 2016 | 8 | 3 | 4 | 38 | 16-0054597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2751 | 9.4989 | 208_286 | <25mph | <15mph | HFTD - Distribution | 2016-08-03 04:38:00 | 644 | 11.5219 | FALSE | <25mph | D5266 | 2.62 | 2016-04-07T05:04:00Z | 4 | 12 | < 25mph | BDMC1 | 6.95 | 2016-04-07T04:36:00Z | 20 | 37 | < 25mph | D5266 | 2.62 | 2016-04-07T05:04:00Z | 4 | 24 | < 25mph | BDMC1 | 6.95 | 2016-04-07T05:36:00Z | 20 | 74 | < 25mph
PG&E | 2017-12-14 | 17:16 | 34.5878 | -120.3566 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101911004 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 43083 | 17:16 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1538 | 2017 | 12 | 14 | 17 | 16 | 17-0101672 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2896 | 2.7073 | 229_51 | <25mph | <15mph | HFTD - Distribution | 2017-12-14 17:16:00 | 1280 | 11.3138 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2332 | 7.61 | 2017-12-18T06:47:00Z | 12.01 | 9 | < 25mph |  |  |  | 0 | 0 | No data | E2332 | 7.61 | 2017-12-18T06:47:00Z | 12.01 | 13 | < 25mph
PG&E | 2015-08-14 15:09 | 2015-08-14 15:09 | 40.9829 | -121.7802 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101514540 |  | 21000 | Conductor | Overhead | Yes | 42230.6312 | 2015-08-14 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0530 | 2015 | 8 | 14 | 15 | 9 | 15-0055136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3072 | 14.8278 | 167_404 | <25mph | <15mph | HFTD - Distribution | 2015-08-14 15:09:00 | 274 | 16.5644 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AS418 | 7.42 | 2016-01-09T01:47:00Z | 1.01 | 6 | < 25mph |  |  |  | 0 | 0 | No data | AS418 | 7.42 | 2016-01-09T02:07:00Z | 2.01 | 12 | < 25mph
PG&E | 2015-05-09 21:37 | 2015-05-09 21:37 | 39.2848 | -121.0219 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100004095 | Pacific Bell | 12000 | Fuse | Overhead | Yes | 42133.9007 | 2015-05-09 21:37 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0312 | 2015 | 5 | 9 | 21 | 37 | 15-0033109 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 11 | 9.2188 | 198_310 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 21:37:00 | 58 | 15.4234 | FALSE | <25mph | PG030 | 0.52 | 2018-07-15T07:50:00Z | 3.06 | 30 | < 25mph | RRRC1 | 5.26 | 2018-07-15T08:13:00Z | 7 | 77 | < 25mph | PG030 | 0.52 | 2018-07-15T07:50:00Z | 3.06 | 58 | < 25mph | RRRC1 | 5.26 | 2018-07-15T09:13:00Z | 7 | 148 | < 25mph
PG&E | 2016-05-31 04:02 | 2016-05-31 04:02 | 35.7984 | -120.9743 | Vegetation | RURAL | < 0.25 Acres | Utility: PG&E | N.A. | 101863413 |  | 12000 | Conductor | Overhead | Yes | 42521.1681 | 2016-05-31 04:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0754 | 2016 | 5 | 31 | 4 | 2 | 16-0039748 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 51888 | 1.5922 | 201_118 | <25mph | <15mph | HFTD - Distribution | 2016-05-31 04:02:00 | 497 | 16.9662 | FALSE | <25mph | E9175 | 3.45 | 2016-11-22T22:10:00Z | 4 | 12 | < 25mph | D4060 | 6.86 | 2016-11-22T22:45:00Z | 4.99 | 16 | < 25mph | E9175 | 3.45 | 2016-11-22T22:10:00Z | 4 | 24 | < 25mph | D4060 | 6.86 | 2016-11-22T22:45:00Z | 4.99 | 32 | < 25mph
PG&E | 2018-06-13 | 22:40 | 38.4901 | -122.6661 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SRS181640125 | 101966547 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 22:40 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1656 | 2018 | 6 | 13 | 22 | 40 | 18-0050782 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 295146 | 2.5247 | 128_267 | <25mph | <15mph | HFTD - Distribution | 2018-06-13 22:40:00 | 1398 | 17.8767 | FALSE | <25mph | RSAC1 | 2.6 | 2015-11-29T05:29:00Z | 7 | 20 | < 25mph | RSAC1 | 2.6 | 2015-11-29T05:29:00Z | 7 | 75 | < 25mph | RSAC1 | 2.6 | 2015-11-29T05:29:00Z | 7 | 37 | < 25mph | D9521 | 4.94 | 2015-11-29T06:26:00Z | 7 | 146 | < 25mph
PG&E | 2017-06-03 13:35 | 13:26 | 38.9017 | -121.2056 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100043664 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42889.5662 | 13:26 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1122 | 2017 | 6 | 3 | 13 | 26 | 17-0052543 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29512 | 13.2044 | 191_289 | <25mph | <15mph | HFTD - Distribution | 2017-06-03 13:26:00 | 862 | 14.9142 | FALSE | <25mph | LICC1 | 3.58 | 2019-07-19T07:13:00Z | 10 | 14 | < 25mph | AR944 | 7.74 | 2019-07-19T07:30:00Z | 11.01 | 53 | < 25mph | LICC1 | 3.58 | 2019-07-19T08:13:00Z | 10 | 27 | < 25mph | AR944 | 7.74 | 2019-07-19T07:30:00Z | 11.01 | 100 | < 25mph
PG&E | 2018-07-23 | 17:27 | 39.734 | -121.4965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103843963 | AT&T | 12000 | Conductor | Overhead | Yes | 43304 | 17:27 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1782 | 2018 | 7 | 23 | 17 | 27 | 18-0062874 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 183629 | 9.1915 | 178_335 | <25mph | <15mph | HFTD - Distribution | 2018-07-23 17:27:00 | 1522 | 13.4352 | FALSE | <25mph | JBGC1 | 0.42 | 2019-10-25T09:13:00Z | 44.98 | 19 | 40-55mph | JBGC1 | 0.42 | 2019-10-25T09:13:00Z | 44.98 | 98 | 40-55mph | JBGC1 | 0.42 | 2019-10-25T09:13:00Z | 44.98 | 38 | 40-55mph | JBGC1 | 0.42 | 2019-10-25T09:13:00Z | 44.98 | 196 | 40-55mph
PG&E | 2015-09-10 16:24 | 2015-09-10 16:24 | 38.5049 | -122.3535 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103159970 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42257.6833 | 2015-09-10 16:24 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0589 | 2015 | 9 | 10 | 16 | 24 | 15-0060610 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 130124 | 14.3548 | 141_267 | <25mph | <15mph | HFTD - Distribution | 2015-09-10 16:24:00 | 334 | 16.5969 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.22 | 2017-05-06T19:29:00Z | 12.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.22 | 2017-05-06T19:29:00Z | 12.01 | 2 | < 25mph
PG&E | 2017-09-27 | 19:06 | 40.7592 | -123.995 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103660812 | Unknown | 12000 | Conductor | Overhead | Yes | 43005 | 19:06 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1437 | 2017 | 9 | 27 | 19 | 6 | 17-0082303 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 35394 | 10.6184 | 74_393 | <25mph | <15mph | HFTD - Distribution | 2017-09-27 19:06:00 | 1175 | 13.0154 | FALSE | <25mph | PG285 | 2.79 | 2019-10-25T10:20:00Z | 3.13 | 6 | < 25mph | KNNC1 | 4.42 | 2019-10-25T09:55:00Z | 5.99 | 14 | < 25mph | PG285 | 2.79 | 2019-10-25T10:20:00Z | 3.13 | 12 | < 25mph | KNNC1 | 4.42 | 2019-10-25T09:55:00Z | 5.99 | 29 | < 25mph
PG&E | 2016-09-26 | 10:40 | 38.0157 | -122.6889 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | marin county fire | 102252082 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42639 | 10:40 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1005 | 2016 | 9 | 26 | 10 | 40 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 4.5159 | 126_240 | <25mph | <15mph | HFTD - Distribution | 2016-09-26 10:40:00 | 747 | 11.2091 | FALSE | <25mph | BBEC1 | 1.12 | 2017-06-19T22:11:00Z | 14 | 2 | < 25mph | E0433 | 7.88 | 2017-06-19T21:45:00Z | 17 | 25 | < 25mph | BBEC1 | 1.12 | 2017-06-19T22:11:00Z | 14 | 4 | < 25mph | E0433 | 7.88 | 2017-06-19T23:05:00Z | 18.99 | 52 | < 25mph
PG&E | 2018-09-16 | 8:26 | 35.3046 | -120.6389 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | Pole 4/23A | None | 70000 | Conductor | Overhead | Yes | 43359 | 8:26 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1903 | 2018 | 9 | 16 | 8 | 26 | INT-11371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 29925 | 32.6873 | 216_90 | 25-40mph | 30-45mph | HFTD - Transmission | 2018-09-16 08:26:00 | 1642 | 35.3808 | FALSE | 25-40mph | ARGC1 | 2.25 | 2017-03-03T14:54:00Z | 4 | 1 | < 25mph | ARGC1 | 2.25 | 2017-03-03T14:54:00Z | 4 | 5 | < 25mph | ARGC1 | 2.25 | 2017-03-03T14:54:00Z | 4 | 2 | < 25mph | ARGC1 | 2.25 | 2017-03-03T14:54:00Z | 4 | 10 | < 25mph
PG&E | 2019-07-25 | 0:15 | 39.0662 | -120.9754 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Placer Hills FD | 152491101 |  | 12000 | Conductor | Overhead | Yes | 43671 | 0:15 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-379 | 2019 | 7 | 25 | 0 | 15 | 19-0080924 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7845 | 8.7511 | 200_298 | <25mph | <15mph | HFTD - Distribution | 2019-07-25 00:15:00 | 1927 | 11.2312 | FALSE | <25mph | C5488 | 2.88 | 2015-10-06T19:25:00Z | 8.99 | 12 | < 25mph | C5488 | 2.88 | 2015-10-06T19:25:00Z | 8.99 | 26 | < 25mph | C5488 | 2.88 | 2015-10-06T19:25:00Z | 8.99 | 25 | < 25mph | C0713 | 5.01 | 2015-10-06T20:34:00Z | 12.01 | 56 | < 25mph
2. Cascade (Neu Wind Complex) | 2017-10-08 | 23:45 | 39.322 | -121.4021 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1988 | 2017 | 10 | 8 | 23 | 45 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Equip Failure | Conductor | 0 | 17.3686 | 182_312 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 23:45:00 | 1213 | 29.7104 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | BNGC1 | 4.15 | 2017-08-25T04:51:00Z | 2.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | BNGC1 | 4.15 | 2017-08-25T05:51:00Z | 3 | 2 | < 25mph
PG&E | 2019-04-20 | 6:57 | 37.8686 | -121.6843 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | East County FD | Unknown |  | 17000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-321 | 2019 | 4 | 20 | 6 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 39.0116 | 170_232 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-20 06:57:00 | 1744 | 39.0116 | FALSE | 25-40mph | D3588 | 2.98 | 2019-07-23T08:24:00Z | 4 | 4 | < 25mph | PG066 | 6.23 | 2019-07-23T07:50:00Z | 22.37 | 105 | < 25mph | D3588 | 2.98 | 2019-07-23T09:25:00Z | 8.01 | 8 | < 25mph | KC83 | 4.32 | 2019-07-23T09:35:00Z | 29.93 | 206 | 25-40mph
PG&E | 2017-10-09 | 1:02 | 38.7037 | -120.6725 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101408485 | Unknown | 21000 | Other | Overhead | Yes | 43017 | 1:02 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1473 | 2017 | 10 | 9 | 1 | 2 | 17-0085324 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 419843 | 26.702 | 214_278 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-10-09 01:02:00 | 1216 | 29.779 | FALSE | 25-40mph | PG566 | 3.65 | 2019-09-22T11:20:00Z | 4.61 | 14 | < 25mph | PG104 | 7.1 | 2019-09-22T11:40:00Z | 14.25 | 76 | < 25mph | PG566 | 3.65 | 2019-09-22T12:20:00Z | 4.9 | 28 | < 25mph | PG104 | 7.1 | 2019-09-22T11:40:00Z | 14.25 | 152 | < 25mph
PG&E | 2016-06-21 | 2016-06-21 16:53 | 38.4233 | -122.5448 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | KENWOOD FIRE XST | 102036904 | Yes | 0 – 750 | Conductor | Overhead | Yes | 42542 | 2016-06-21 16:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0814 | 2016 | 6 | 21 | 16 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 14.0146 | 133_263 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 16:53:00 | 556 | 14.0381 | FALSE | <25mph | KENWW | 1.1 | 2017-06-06T06:00:00Z | 6.4 | 5 | < 25mph | KENWW | 1.1 | 2017-06-06T06:00:00Z | 6.4 | 21 | < 25mph | KENWW | 1.1 | 2017-06-06T06:00:00Z | 6.4 | 9 | < 25mph | KENWW | 1.1 | 2017-06-06T06:00:00Z | 6.4 | 40 | < 25mph
PG&E | 2018-07-19 | 0:08 | 36.9372 | -119.4557 | Vegetation | Rural | < 0.25 Acres | Fire Agency | incident # 10559 | 100677019 | AT&T | 12000 | Conductor | Overhead | Yes | 43300 | 0:08 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1766 | 2018 | 7 | 19 | 0 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 10.281 | 268_181 | <25mph | <15mph | HFTD - Distribution | 2018-07-19 00:08:00 | 1506 | 18.2382 | FALSE | <25mph | FCHC1 | 3.86 | 2017-05-25T15:00:00Z | 5.99 | 1 | < 25mph | FCHC1 | 3.86 | 2017-05-25T15:00:00Z | 5.99 | 1 | < 25mph | FCHC1 | 3.86 | 2017-05-25T16:00:00Z | 10 | 2 | < 25mph | FCHC1 | 3.86 | 2017-05-25T16:00:00Z | 10 | 2 | < 25mph
PG&E | 2017-08-02 | 9:42 | 39.2274 | -123.1081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 5/0 | None | 60000 | Conductor | Overhead | Yes | 42949 | 9:42 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1307 | 2017 | 8 | 2 | 9 | 42 | INT-09925 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 4.0697 | 109_308 | <25mph | <15mph | HFTD - Transmission | 2017-08-02 09:42:00 | 1047 | 15.4312 | FALSE | <25mph |  |  |  | 0 | 0 | No data | COWC1 | 7.26 | 2016-01-14T01:01:00Z | 28.01 | 13 | 25-40mph |  |  |  | 0 | 0 | No data | COWC1 | 7.26 | 2016-01-14T01:01:00Z | 28.01 | 26 | 25-40mph
PG&E | 2016-07-29 | 18:16 | 38.5769 | -122.6187 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Selma Fire Department |  |  | 12000 | Conductor | Overhead | Yes | 42580 | 18:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0890 | 2016 | 7 | 29 | 18 | 16 | 16-0053726 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 177834 | 13.7145 | 130_271 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 18:16:00 | 635 | 15.1116 | FALSE | <25mph | D9521 | 3.41 | 2015-02-26T23:26:00Z | 11.99 | 16 | < 25mph | E2362 | 7.38 | 2015-02-26T22:40:00Z | 13 | 24 | < 25mph | E2050 | 1.89 | 2015-02-27T00:05:00Z | 14 | 34 | < 25mph | E2362 | 7.38 | 2015-02-27T00:26:00Z | 14 | 50 | < 25mph
PG&E | 2018-05-19 | 19:44 | 40.2665 | -122.2727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103899310 | Unknown | 12000 | Conductor | Overhead | Yes | 43239 | 19:44 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1599 | 2018 | 5 | 19 | 19 | 44 | 18-0042559 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 31980 | 15.59 | 146_364 | <25mph | <15mph | HFTD - Distribution | 2018-05-19 19:44:00 | 1341 | 18.253 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 7.1 | 2016-02-13T12:13:00Z | 5.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 7.1 | 2016-02-13T12:13:00Z | 5.99 | 8 | < 25mph
PG&E | 2019-06-17 | 10:25 | 38.511 | -122.2134 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 43051101 |  | 12000 | Conductor | Overhead | Yes | 43633 | 10:25 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-84 | 2019 | 6 | 17 | 10 | 25 | 19-0068579 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 306900 | 10.2943 | 147_267 | <25mph | <15mph | HFTD - Distribution | 2019-06-17 10:25:00 | 1843 | 15.8677 | FALSE | <25mph | ATLC1 | 3.74 | 2017-03-19T04:29:00Z | 17 | 1 | < 25mph | ATLC1 | 3.74 | 2017-03-19T04:29:00Z | 17 | 1 | < 25mph | ATLC1 | 3.74 | 2017-03-19T04:29:00Z | 17 | 2 | < 25mph | ATLC1 | 3.74 | 2017-03-19T04:29:00Z | 17 | 2 | < 25mph
PG&E | 2016-08-17 | 2016-08-17 18:37 | 37.3078 | -119.6511 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101020932 |  | 21000 | Conductor | Overhead | Yes | 42599 | 2016-08-17 18:37 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0934 | 2016 | 8 | 17 | 18 | 37 | 16-0058019 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 59379 | 5.4346 | 259_201 | <25mph | <15mph | HFTD - Distribution | 2016-08-17 18:37:00 | 677 | 11.1875 | FALSE | <25mph | D7171 | 3.9 | 2017-10-09T07:20:00Z | 4 | 26 | < 25mph | BSNC1 | 5.02 | 2017-10-09T06:48:00Z | 7 | 39 | < 25mph | D7171 | 3.9 | 2017-10-09T07:54:00Z | 4 | 53 | < 25mph | BSNC1 | 5.02 | 2017-10-09T07:48:00Z | 7 | 79 | < 25mph
PG&E | 2019-07-15 | 7:51 | 38.3266 | -122.568 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 42721104 |  | 12000 | Conductor | Overhead | Yes | 43661 | 7:51 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-343 | 2019 | 7 | 15 | 7 | 51 | 19-0077351 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2348 | 31.0114 | 132_257 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-07-15 07:51:00 | 1903 | 35.3209 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | KO69 | 5.16 | 2015-03-31T23:55:00Z | 25.32 | 33 | 25-40mph |  |  |  | 0 | 0 | No data | KO69 | 5.16 | 2015-03-31T23:55:00Z | 25.32 | 63 | 25-40mph
PG&E | 2018-07-17 | 11:58 | 37.2217 | -121.6778 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Luis Morado state arson fire fighter | 100601345 | Unknown | 12000 | Conductor | Overhead | Yes | 43298 | 11:58 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1756 | 2018 | 7 | 17 | 11 | 58 | 18-0060617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 5865 | 5.1834 | 170_196 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 11:58:00 | 1496 | 14.408 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D3723 | 5.62 | 2019-04-21T12:46:00Z | 0 | 21 | < 25mph |  |  |  | 0 | 0 | No data | D3723 | 5.62 | 2019-04-21T13:45:00Z | 0 | 43 | < 25mph
PG&E | 2016-04-13 19:28 | 2016-04-13 19:28 | 40.4954 | -124.1219 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103659313 |  | 12000 | Conductor | Overhead | Yes | 42473.8111 | 2016-04-13 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0706 | 2016 | 4 | 13 | 19 | 28 | 16-0028421 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 688 | 19.0823 | 68_379 | <25mph | <15mph | HFTD - Distribution | 2016-04-13 19:28:00 | 450 | 22.9769 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C5061 | 4.94 | 2018-04-22T04:30:00Z | 8.01 | 22 | < 25mph |  |  |  | 0 | 0 | No data | AT493 | 5.02 | 2018-04-22T05:52:00Z | 8.01 | 42 | < 25mph
PG&E | 2019-07-18 | 19:57 | 37.081 | -119.4865 |  | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | No |  |  | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-09 | 2019 | 7 | 18 | 19 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.8761 | 266_189 | <25mph | <15mph | HFTD - Distribution | 2019-07-18 19:57:00 | 1914 | 14.7588 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTQC1 | 6.58 | 2015-08-12T07:52:00Z | 4 | 2 | < 25mph |  |  |  | 0 | 0 | No data | MTQC1 | 6.58 | 2015-08-12T08:52:00Z | 4 | 4 | < 25mph
PG&E | 2018-07-29 | 17:29 | 38.5777 | -120.8556 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101383255 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43310 | 17:29 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1797 | 2018 | 7 | 29 | 17 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.882 | 206_271 | <25mph | <15mph | HFTD - Distribution | 2018-07-29 17:29:00 | 1537 | 11.0812 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BENC1 | 4.31 | 2015-11-26T01:59:00Z | 7 | 13 | < 25mph |  |  |  | 0 | 0 | No data | BENC1 | 4.31 | 2015-11-26T02:59:00Z | 7 | 26 | < 25mph
PG&E | 2017-05-15 | 3:05 | 35.6261 | -120.8962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101873299 | Unknown | 21000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1097 | 2017 | 5 | 15 | 3 | 5 | 17-0047837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 337188 | 4.016 | 204_108 | <25mph | <15mph | HFTD - Distribution | 2017-05-15 03:05:00 | 837 | 18.5139 | FALSE | <25mph | PG494 | 1.46 | 2019-09-24T13:10:00Z | 3.74 | 7 | < 25mph | PG175 | 5.58 | 2019-09-24T13:00:00Z | 16.22 | 25 | < 25mph | PG494 | 1.46 | 2019-09-24T14:10:00Z | 4.9 | 14 | < 25mph | PG175 | 5.58 | 2019-09-24T14:10:00Z | 17.31 | 50 | < 25mph
PG&E | 2016-06-26 | 2016-06-26 16:38 | 39.5042 | -121.4475 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100375810 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42547 | 2016-06-26 16:38 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0823 | 2016 | 6 | 26 | 16 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 9.04 | 180_322 | <25mph | <15mph | HFTD - Distribution | 2016-06-26 16:38:00 | 567 | 14.524 | FALSE | <25mph | TT309 | 3.14 | 2016-08-04T02:45:00Z | 14.99 | 1 | < 25mph | TT309 | 3.14 | 2016-08-04T02:45:00Z | 14.99 | 1 | < 25mph | TT309 | 3.14 | 2016-08-04T02:45:00Z | 14.99 | 2 | < 25mph | TT309 | 3.14 | 2016-08-04T02:45:00Z | 14.99 | 2 | < 25mph
PG&E | 2015-07-07 10:42 | 2015-07-07 10:42 | 39.1138 | -121.0655 | Vegetation | Rural | < 0.25 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42192.4458 | 2015-07-07 10:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0448 | 2015 | 7 | 7 | 10 | 42 | 15-0045985 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 46738 | 10.1548 | 197_300 | <25mph | <15mph | HFTD - Distribution | 2015-07-07 10:42:00 | 193 | 12.5396 | FALSE | <25mph | AV369 | 3.22 | 2018-02-07T01:24:00Z | 2.01 | 23 | < 25mph | E1789 | 4.22 | 2018-02-07T01:36:00Z | 4 | 90 | < 25mph | AV369 | 3.22 | 2018-02-07T01:24:00Z | 2.01 | 45 | < 25mph | E1789 | 4.22 | 2018-02-07T03:12:00Z | 5.99 | 176 | < 25mph
PG&E | 2015-07-30 19:11 | 2015-07-30 19:11 | 37.8102 | -120.1287 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE |  |  | 17000 | Conductor | Overhead | Yes | 42215.7993 | 2015-07-30 19:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0500 | 2015 | 7 | 30 | 19 | 11 | 15-0051772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26776 | 10.007 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2015-07-30 19:11:00 | 245 | 11.7658 | FALSE | <25mph | SEWC1 | 1.66 | 2017-11-05T12:16:00Z | 10 | 5 | < 25mph | SEWC1 | 1.66 | 2017-11-05T12:16:00Z | 10 | 5 | < 25mph | SEWC1 | 1.66 | 2017-11-05T12:16:00Z | 10 | 10 | < 25mph | SEWC1 | 1.66 | 2017-11-05T12:16:00Z | 10 | 10 | < 25mph
PG&E | 2016-06-06 | 2016-06-06 19:48 | 38.9129 | -121.1192 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire/placer fire | 100050264 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42527 | 2016-06-06 19:48 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0775 | 2016 | 6 | 6 | 19 | 48 | 16-0041497 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 2039 | 14.8039 | 194_289 | <25mph | <15mph | HFTD - Distribution | 2016-06-06 19:48:00 | 518 | 15.3816 | FALSE | <25mph | KAUN | 3.43 | 2017-03-05T04:35:00Z | 18.41 | 7 | < 25mph | KAUN | 3.43 | 2017-03-05T04:35:00Z | 18.41 | 7 | < 25mph | KAUN | 3.43 | 2017-03-05T06:15:00Z | 21.85 | 12 | < 25mph | KAUN | 3.43 | 2017-03-05T06:15:00Z | 21.85 | 12 | < 25mph
PG&E | 2017-09-08 | 17:21 | 38.6039 | -120.9275 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101379094 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42986 | 17:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1402 | 2017 | 9 | 8 | 17 | 21 | 17-0077122 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 8504 | 10.5347 | 203_272 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 17:21:00 | 1140 | 11.5767 | FALSE | <25mph | BENC1 | 0.96 | 2017-06-16T14:59:00Z | 4 | 12 | < 25mph | D7401 | 7.08 | 2017-06-16T15:04:00Z | 4 | 48 | < 25mph | E8856 | 1.83 | 2017-06-16T15:50:00Z | 4.99 | 24 | < 25mph | D7401 | 7.08 | 2017-06-16T16:04:00Z | 8.99 | 98 | < 25mph
PG&E | 2016-07-20 19:15 | 2016-07-20 19:15 | 37.7712 | -121.8104 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100898986 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42571.8021 | 2016-07-20 19:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0865 | 2016 | 7 | 20 | 19 | 15 | 16-0051308 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3013 | 17.1873 | 164_226 | <25mph | <15mph | HFTD - Distribution | 2016-07-20 19:15:00 | 608 | 18.9944 | FALSE | <25mph | PG002 | 2.9 | 2018-11-21T02:40:00Z | 7.25 | 13 | < 25mph | PG002 | 2.9 | 2018-11-21T02:40:00Z | 7.25 | 47 | < 25mph | PG002 | 2.9 | 2018-11-21T03:40:00Z | 7.45 | 26 | < 25mph | PG002 | 2.9 | 2018-11-21T03:40:00Z | 7.45 | 91 | < 25mph
PG&E | 2017-07-03 20:28 | 20:26 | 38.7923 | -120.9438 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101388730 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42919.853 | 20:26 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1218 | 2017 | 7 | 3 | 20 | 26 | 17-0060336 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 8134 | 10.0527 | 202_283 | <25mph | <15mph | HFTD - Distribution | 2017-07-03 20:26:00 | 957 | 12.5378 | FALSE | <25mph | PG364 | 2.44 | 2019-09-02T07:00:00Z | 1.25 | 12 | < 25mph | PG366 | 5.88 | 2019-09-02T06:50:00Z | 11.41 | 84 | < 25mph | PG024 | 1.59 | 2019-09-02T07:50:00Z | 3.22 | 24 | < 25mph | PG366 | 5.88 | 2019-09-02T08:00:00Z | 14.16 | 167 | < 25mph
PG&E | 2017-08-02 | 9:42 | 39.2274 | -123.1081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 5/0 | None | 60000 | Conductor | Overhead | Yes | 42949 | 9:42 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1307 | 2017 | 8 | 2 | 9 | 42 | INT-09925 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 4.0697 | 109_308 | <25mph | <15mph | HFTD - Transmission | 2017-08-02 09:42:00 | 1047 | 15.4312 | FALSE | <25mph |  |  |  | 0 | 0 | No data | COWC1 | 7.26 | 2015-06-12T08:01:00Z | 15.99 | 14 | < 25mph |  |  |  | 0 | 0 | No data | COWC1 | 7.26 | 2015-06-12T08:01:00Z | 15.99 | 27 | < 25mph
PG&E | 2019-08-16 | 10:31 | 39.3714 | -121.3221 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103191101 |  | 12000 | Conductor | Overhead | Yes | 43693 | 10:31 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-397 | 2019 | 8 | 16 | 10 | 31 | 19-0088805 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4580 | 6.4736 | 186_315 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 10:31:00 | 1984 | 15.7456 | FALSE | <25mph | BNGC1 | 3.48 | 2016-02-04T16:51:00Z | 4 | 1 | < 25mph | BNGC1 | 3.48 | 2016-02-04T16:51:00Z | 4 | 1 | < 25mph | BNGC1 | 3.48 | 2016-02-04T17:51:00Z | 7 | 2 | < 25mph | BNGC1 | 3.48 | 2016-02-04T17:51:00Z | 7 | 2 | < 25mph
PG&E | 2017-04-04 13:36 | 13:29 | 35.6885 | -120.7653 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101945026 | None | 12000 | Conductor | Overhead | Yes | 42829.567 | 13:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1064 | 2017 | 4 | 4 | 13 | 29 | 17-0036460 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 167151 | 3.61 | 210_111 | <25mph | <15mph | HFTD - Distribution | 2017-04-04 13:29:00 | 804 | 8.6409 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D4060 | 7.1 | 2015-05-15T04:45:00Z | 4 | 4 | < 25mph |  |  |  | 0 | 0 | No data | D4060 | 7.1 | 2015-05-15T04:45:00Z | 4 | 8 | < 25mph
PG&E | 2019-08-12 | 20:06 | 39.0952 | -123.4937 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 102177212 |  | 12000 | Conductor | Overhead | Yes | 43689 | 20:06 | Vegetation |  | Veg. contact |  |  |  | Fell into (No defect) | 2019-400 | 2019 | 8 | 12 | 20 | 6 | 19-0087090 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2508 | 13.5331 | 93_301 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 20:06:00 | 1970 | 19.4805 | FALSE | <25mph | E1763 | 1.72 | 2019-01-02T06:30:00Z | 0 | 4 | < 25mph | E1763 | 1.72 | 2019-01-02T06:30:00Z | 0 | 4 | < 25mph | E1763 | 1.72 | 2019-01-02T07:30:00Z | 0 | 8 | < 25mph | E1763 | 1.72 | 2019-01-02T07:30:00Z | 0 | 8 | < 25mph
PG&E | 2016-07-29 | 18:16 | 38.5769 | -122.6187 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Selma Fire Department |  |  | 12000 | Conductor | Overhead | Yes | 42580 | 18:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0890 | 2016 | 7 | 29 | 18 | 16 | 16-0053726 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 177834 | 13.7145 | 130_271 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 18:16:00 | 635 | 15.1116 | FALSE | <25mph | PG229 | 2.9 | 2019-11-03T11:10:00Z | 6.51 | 26 | < 25mph | PG132 | 6.42 | 2019-11-03T11:20:00Z | 18.86 | 73 | < 25mph | PG229 | 2.9 | 2019-11-03T11:10:00Z | 6.51 | 51 | < 25mph | PG132 | 6.42 | 2019-11-03T11:20:00Z | 18.86 | 145 | < 25mph
PG&E | 2019-09-11 | 21:03 | 38.3132 | -120.9809 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 163341103 |  | 12000 | Conductor | Overhead | Yes | 43719 | 21:03 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-370 | 2019 | 9 | 11 | 21 | 3 | 19-0098003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25994 | 11.7888 | 200_256 | <25mph | <15mph | HFTD - Distribution | 2019-09-11 21:03:00 | 2035 | 13.1911 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 5.36 | 2017-09-25T07:05:00Z | 12.01 | 3 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 5.36 | 2017-09-25T08:05:00Z | 13 | 6 | < 25mph
PG&E | 2016-08-02 | 2016-08-02 16:15 | 37.0312 | -119.4395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Fresno County FD | 100675986 |  | 12000 | Conductor | Overhead | Yes | 42584 | 2016-08-02 16:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0900 | 2016 | 8 | 2 | 16 | 15 | 16-0054552 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 265566 | 14.0604 | 268_186 | <25mph | <15mph | HFTD - Distribution | 2016-08-02 16:15:00 | 643 | 14.6638 | FALSE | <25mph | PG218 | 3.81 | 2019-04-26T22:20:00Z | 14.47 | 49 | < 25mph | PG218 | 3.81 | 2019-04-26T22:20:00Z | 14.47 | 69 | < 25mph | PG218 | 3.81 | 2019-04-27T00:00:00Z | 15.57 | 91 | < 25mph | PG218 | 3.81 | 2019-04-27T00:00:00Z | 15.57 | 129 | < 25mph
PG&E | 2016-04-08 13:14 | 2016-04-08 13:14 | 39.0429 | -121.1002 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100086751 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42468.5514 | 2016-04-08 13:14 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0705 | 2016 | 4 | 8 | 13 | 14 | 16-0027237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 11817 | 10.7666 | 195_296 | <25mph | <15mph | HFTD - Distribution | 2016-04-08 13:14:00 | 449 | 10.7666 | FALSE | <25mph | PG332 | 3.71 | 2019-11-21T07:00:00Z | 3.74 | 23 | < 25mph | E1789 | 7.22 | 2019-11-21T06:54:00Z | 8.01 | 73 | < 25mph | PG332 | 3.71 | 2019-11-21T07:30:00Z | 3.87 | 43 | < 25mph | E1789 | 7.22 | 2019-11-21T06:54:00Z | 8.01 | 144 | < 25mph
PG&E | 2016-08-15 | 2016-08-15 15:43 | 37.8784 | -120.4488 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101020079 |  | 17000 | Conductor | Overhead | Yes | 42597 | 2016-08-15 15:43 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0928 | 2016 | 8 | 15 | 15 | 43 | 16-0057465 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 122905 | 10.0906 | 223_232 | <25mph | <15mph | HFTD - Distribution | 2016-08-15 15:43:00 | 671 | 12.9875 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.26 | 2018-06-09T22:03:00Z | 21 | 1 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.26 | 2018-06-09T22:03:00Z | 21 | 2 | < 25mph
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 9:36 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 14.8685 | 222_261 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 09:36:00 | 925 | 23.4839 | FALSE | <25mph | AT450 | 2.61 | 2016-07-30T09:04:00Z | 0 | 10 | < 25mph | C9148 | 7.6 | 2016-07-30T08:34:00Z | 8.01 | 22 | < 25mph | AT450 | 2.61 | 2016-07-30T09:19:00Z | 3 | 20 | < 25mph | C9148 | 7.6 | 2016-07-30T09:49:00Z | 8.99 | 43 | < 25mph
PG&E | 2016-08-13 | 14:31 | 37.4642 | -119.8589 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire |  |  | 21000 | Conductor | Overhead | Yes | 42595 | 14:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0923 | 2016 | 8 | 13 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.5527 | 249_210 | <25mph | <15mph | HFTD - Distribution | 2016-08-13 14:31:00 | 667 | 11.4441 | FALSE | <25mph | E9110 | 3.11 | 2017-06-12T16:30:00Z | 7 | 7 | < 25mph | MIAC1 | 6.96 | 2017-06-12T16:59:00Z | 8.01 | 11 | < 25mph | C1522 | 2.94 | 2017-06-12T18:21:00Z | 8.99 | 12 | < 25mph | C1522 | 2.94 | 2017-06-12T18:21:00Z | 8.99 | 20 | < 25mph
PG&E | 2019-07-01 | 2:15 | 38.2955 | -120.8335 |  | Shrub | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-252 | 2019 | 7 | 1 | 2 | 15 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.9479 | 207_255 | <25mph | <15mph | HFTD - Distribution | 2019-07-01 02:15:00 | 1878 | 14.184 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.85 | 2015-01-06T17:05:00Z | 7 | 2 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.85 | 2015-01-06T17:05:00Z | 7 | 4 | < 25mph
PG&E | 2016-08-30 | 2016-08-30 16:01 | 36.5941 | -121.9212 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Unknown | 101734977 |  | 21000 | Conductor | Overhead | Yes | 42612 | 2016-08-30 16:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0951 | 2016 | 8 | 30 | 16 | 1 | 16-0061130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 199327 | 14.6893 | 159_162 | <25mph | <15mph | HFTD - Distribution | 2016-08-30 16:01:00 | 694 | 14.6893 | FALSE | <25mph | E6019 | 2.96 | 2018-12-03T02:15:00Z | 3 | 42 | < 25mph | E8875 | 4.34 | 2018-12-03T01:31:00Z | 8.01 | 47 | < 25mph | E6019 | 2.96 | 2018-12-03T03:00:00Z | 5.99 | 87 | < 25mph | E8875 | 4.34 | 2018-12-03T01:31:00Z | 8.01 | 96 | < 25mph
PG&E | 2017-09-18 | 13:01 | 39.3889 | -121.4054 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 103795057 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42996 | 13:01 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1418 | 2017 | 9 | 18 | 13 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 17.7047 | 182_316 | <25mph | <15mph | HFTD - Distribution | 2017-09-18 13:01:00 | 1156 | 19.5678 | FALSE | <25mph | BNGC1 | 1.17 | 2017-02-13T23:51:00Z | 5.99 | 1 | < 25mph | BNGC1 | 1.17 | 2017-02-13T23:51:00Z | 5.99 | 1 | < 25mph | BNGC1 | 1.17 | 2017-02-13T23:51:00Z | 5.99 | 2 | < 25mph | BNGC1 | 1.17 | 2017-02-13T23:51:00Z | 5.99 | 2 | < 25mph
PG&E | 2017-08-14 07:56 | 07:56 | 39.1794 | -120.9761 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100083743 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42961.3308 | 07:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1334 | 2017 | 8 | 14 | 7 | 56 | 17-0070063 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3012 | 6.4958 | 200_304 | <25mph | <15mph | HFTD - Distribution | 2017-08-14 07:56:00 | 1071 | 15.2686 | FALSE | <25mph | PG059 | 3.1 | 2018-09-25T13:00:00Z | 8.77 | 18 | < 25mph | SETC1 | 4.92 | 2018-09-25T13:28:00Z | 11.01 | 65 | < 25mph | PG059 | 3.1 | 2018-09-25T13:40:00Z | 9.86 | 36 | < 25mph | SETC1 | 4.92 | 2018-09-25T14:28:00Z | 12.01 | 137 | < 25mph
PG&E | 2015-06-28 02:50 | 2015-06-28 02:50 | 35.491 | -120.731 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 13505 Santa Lucia Rd. Atascadero |  | 12000 | Conductor | Overhead | Yes | 42183.1181 | 2015-06-28 02:50 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0418 | 2015 | 6 | 28 | 2 | 50 | 15-0043807 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 12323 | 9.9634 | 212_101 | <25mph | <15mph | HFTD - Distribution | 2015-06-28 02:50:00 | 163 | 24.8049 | FALSE | <25mph | E6394 | 1.17 | 2017-12-20T14:10:00Z | 4.99 | 17 | < 25mph | E6394 | 1.17 | 2017-12-20T14:10:00Z | 4.99 | 24 | < 25mph | E6394 | 1.17 | 2017-12-20T15:09:00Z | 8.01 | 32 | < 25mph | E6394 | 1.17 | 2017-12-20T15:09:00Z | 8.01 | 43 | < 25mph
PG&E | 2017-10-16 | 12:10 | 36.5831 | -121.9368 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101781248 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43024 | 12:10 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | Other/Unknown | 1493 | 2017 | 10 | 16 | 12 | 10 | 17-0087767 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 6313 | 5.0415 | 158_161 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:10:00 | 1236 | 13.6905 | FALSE | <25mph | E8505 | 1.61 | 2019-12-31T02:15:00Z | 14 | 45 | < 25mph | E8505 | 1.61 | 2019-12-31T02:15:00Z | 14 | 49 | < 25mph | E8505 | 1.61 | 2019-12-31T02:15:00Z | 14 | 87 | < 25mph | E8505 | 1.61 | 2019-12-31T02:15:00Z | 14 | 95 | < 25mph
PG&E | 2015-05-06 17:17 | 2015-05-06 17:17 | 37.4273 | -119.8803 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | BOOSTER 8179 INDIAN PEEK N/O MIWUK | None | 21000 | Other | Overhead | Yes | 42130.7201 | 2015-05-06 17:17 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0307 | 2015 | 5 | 6 | 17 | 17 | 15-0032311 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 81600 | 12.4413 | 249_208 | <25mph | <15mph | HFTD - Distribution | 2015-05-06 17:17:00 | 53 | 13.2212 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MIAC1 | 7.42 | 2016-03-13T00:59:00Z | 14 | 3 | < 25mph |  |  |  | 0 | 0 | No data | MIAC1 | 7.42 | 2016-03-13T00:59:00Z | 14 | 6 | < 25mph
PG&E | 2018-07-25 | 0:42 | 39.7791 | -121.6173 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100327443 | Unknown | 12000 | Conductor | Overhead | Yes | 43306 | 0:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1788 | 2018 | 7 | 25 | 0 | 42 | 18-0063320 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6742 | 1.3279 | 173_337 | <25mph | <15mph | HFTD - Distribution | 2018-07-25 00:42:00 | 1528 | 11.7229 | FALSE | <25mph | PG382 | 2.96 | 2019-06-14T16:40:00Z | 10.51 | 25 | < 25mph | PG382 | 2.96 | 2019-06-14T16:40:00Z | 10.51 | 78 | < 25mph | PG382 | 2.96 | 2019-06-14T18:20:00Z | 11.41 | 50 | < 25mph | PG382 | 2.96 | 2019-06-14T18:20:00Z | 11.41 | 156 | < 25mph
PG&E | 2019-08-16 | 8:19 | 40.1235 | -123.8758 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Self Extinguished |  | 192221102-2101118022{5563} |  | 12000 | Conductor | Overhead | Yes | 43693 | 8:19 | Vegetation | [5 empty] | Other/Unknown |  | 2019 | 8 | 16 | 8 | 19 | 19-0088744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 2979 | 5.7689 | 78_358 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 08:19:00 | 1983 | 18.468 | FALSE | <25mph | ERCC1 | 2.93 | 2017-03-01T01:28:00Z | 11.01 | 1 | < 25mph | ERCC1 | 2.93 | 2017-03-01T01:28:00Z | 11.01 | 6 | < 25mph | ERCC1 | 2.93 | 2017-03-01T01:28:00Z | 11.01 | 2 | < 25mph | ERCC1 | 2.93 | 2017-03-01T01:28:00Z | 11.01 | 12 | < 25mph
PG&E | 2018-07-17 | 19:40 | 40.5927 | -122.4886 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101477082 | AT&T | 12000 | Conductor | Overhead | Yes | 43298 | 19:40 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1760 | 2018 | 7 | 17 | 19 | 40 | 18-0060840 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 30162 | 14.3022 | 137_382 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 19:40:00 | 1500 | 21.6282 | FALSE | <25mph | MMOC1 | 1.8 | 2015-07-29T20:00:00Z | 8.99 | 3 | < 25mph | E6886 | 7.8 | 2015-07-29T19:46:00Z | 12.01 | 12 | < 25mph | MMOC1 | 1.8 | 2015-07-29T21:00:00Z | 10 | 8 | < 25mph | E6886 | 7.8 | 2015-07-29T20:46:00Z | 12.01 | 25 | < 25mph
PG&E | 2015-01-26 03:51 | 2015-01-26 03:51 | 37.0539 | -122.1587 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42030.1604 | 2015-01-26 03:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0258 | 2015 | 1 | 26 | 3 | 51 | 15-0007000 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7602 | 14.3078 | 149_187 | <25mph | <15mph | HFTD - Distribution | 2015-01-26 03:51:00 | 5 | 14.9656 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BNDC1 | 5.38 | 2016-09-03T12:50:00Z | 17 | 44 | < 25mph | E1977 | 2.39 | 2016-09-03T14:01:00Z | 0 | 2 | < 25mph | BNDC1 | 5.38 | 2016-09-03T12:50:00Z | 17 | 91 | < 25mph
PG&E | 2019-04-09 | 14:07 | 34.6311 | -119.9813 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Fire Dept | Santa Barbra County FD | 101863014 |  | 12000 | Conductor | Overhead | Yes | 43564 | 14:07 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-263 | 2019 | 4 | 9 | 14 | 7 | 19-0040969 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 70756 | 38.5369 | 246_53 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-09 14:07:00 | 1737 | 43.1384 | FALSE | 40-55mph |  |  |  | 0 | 0 | No data | FGMC1 | 7.28 | 2017-01-20T06:35:00Z | 4.99 | 10 | < 25mph |  |  |  | 0 | 0 | No data | FGMC1 | 7.28 | 2017-01-20T07:35:00Z | 5.99 | 19 | < 25mph
PG&E | 2018-06-28 | 12:27 | 38.5982 | -121.0081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | John Reis, 530-622-3858 | 101376954 | Unknown | 21000 | Conductor | Overhead | Yes | 43279 | 12:27 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1702 | 2018 | 6 | 28 | 12 | 27 | 18-0055479 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 24671 | 12.7651 | 199_272 | <25mph | <15mph | HFTD - Distribution | 2018-06-28 12:27:00 | 1443 | 13.4512 | FALSE | <25mph | E8856 | 2.62 | 2016-04-03T16:10:00Z | 1.01 | 12 | < 25mph | D4464 | 6.53 | 2016-04-03T15:34:00Z | 10 | 33 | < 25mph | E8856 | 2.62 | 2016-04-03T16:10:00Z | 1.01 | 24 | < 25mph | D4464 | 6.53 | 2016-04-03T15:34:00Z | 10 | 66 | < 25mph
PG&E | 2015-07-07 15:27 | 2015-07-07 15:27 | 35.155 | -120.5442 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 303corraltos cyn rd | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42192.6438 | 2015-07-07 15:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0449 | 2015 | 7 | 7 | 15 | 27 | 15-0046127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 98566 | 24.1391 | 220_82 | <25mph | <15mph | HFTD - Distribution | 2015-07-07 15:27:00 | 194 | 24.1391 | FALSE | <25mph | D6295 | 2.38 | 2017-10-19T21:16:00Z | 11.01 | 22 | < 25mph | KSBP | 7.64 | 2017-10-19T21:25:00Z | 25.32 | 27 | 25-40mph | F0194 | 3.06 | 2017-10-19T22:11:00Z | 11.01 | 43 | < 25mph | KSBP | 7.64 | 2017-10-19T21:25:00Z | 25.32 | 53 | 25-40mph
PG&E | 2019-07-01 | 2:15 | 38.2955 | -120.8335 |  | Shrub | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-252 | 2019 | 7 | 1 | 2 | 15 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.9479 | 207_255 | <25mph | <15mph | HFTD - Distribution | 2019-07-01 02:15:00 | 1878 | 14.184 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.85 | 2017-08-19T17:05:00Z | 7 | 2 | < 25mph |  |  |  | 0 | 0 | No data | CMAC1 | 5.28 | 2017-08-19T17:59:00Z | 8.01 | 4 | < 25mph
PG&E | 2019-04-09 | 15:27 | 37.7341 | -120.0776 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 101076921 |  | 21000 | Pole | Overhead | Yes | 43564 | 15:27 | Vegetation |  | Veg. contact | Pole |  |  | Branch (Not overhanging, > 12ft) | 2019-313 | 2019 | 4 | 9 | 15 | 27 | 19-0041008 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 179862 | 22.8983 | 240_225 | <25mph | <15mph | HFTD - Distribution | 2019-04-09 15:27:00 | 1738 | 29.8749 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | SEWC1 | 4.76 | 2017-07-18T18:16:00Z | 11.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | SEWC1 | 4.76 | 2017-07-18T18:16:00Z | 11.01 | 2 | < 25mph
PG&E | 2015-06-09 15:24 | 2015-06-09 15:24 | 38.3651 | -122.2541 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | load side 2987 | Yes | 21000 | Conductor | Overhead | Yes | 42164.6417 | 2015-06-09 15:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0368 | 2015 | 6 | 9 | 15 | 24 | 15-0039825 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 651298 | 15.2247 | 145_259 | <25mph | <15mph | HFTD - Distribution | 2015-06-09 15:24:00 | 114 | 15.4726 | FALSE | <25mph | AT068 | 1.44 | 2016-09-01T17:00:00Z | 0 | 1 | < 25mph | AS725 | 4.29 | 2016-09-01T16:55:00Z | 3 | 10 | < 25mph | AT068 | 1.44 | 2016-09-01T17:00:00Z | 0 | 1 | < 25mph | AS725 | 4.29 | 2016-09-01T17:45:00Z | 4 | 18 | < 25mph
PG&E | 2017-10-20 | 6:18 | 39.2922 | -121.0157 | Vegetation | Rural | < 3 Meters | Fire Agency | PHILLIP NUNNINK INCIDENT # 27272 | 100087647 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43028 | 6:18 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1499 | 2017 | 10 | 20 | 6 | 18 | 17-0088957 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 102410 | 6.1464 | 199_310 | <25mph | <15mph | HFTD - Distribution | 2017-10-20 06:18:00 | 1242 | 23.0997 | FALSE | <25mph | E3651 | 3.59 | 2015-07-18T10:30:00Z | 3 | 13 | < 25mph | RRRC1 | 5.48 | 2015-07-18T10:13:00Z | 8.99 | 62 | < 25mph | E3651 | 3.59 | 2015-07-18T11:30:00Z | 3 | 28 | < 25mph | RRRC1 | 5.48 | 2015-07-18T11:13:00Z | 12.01 | 115 | < 25mph
PG&E | 2016-05-29 14:19 | 2016-05-29 14:19 | 40.5795 | -122.4694 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103156596 | Yes | 12000 | Conductor | Overhead | Yes | 42519.5965 | 2016-05-29 14:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0751 | 2016 | 5 | 29 | 14 | 19 | 16-0039619 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3860 | 1.6611 | 138_382 | <25mph | <15mph | HFTD - Distribution | 2016-05-29 14:19:00 | 494 | 20.6013 | FALSE | <25mph | PG296 | 1.37 | 2019-04-22T18:40:00Z | 10.29 | 23 | < 25mph | E6886 | 6.63 | 2019-04-22T19:15:00Z | 11.01 | 38 | < 25mph | PG296 | 1.37 | 2019-04-22T20:00:00Z | 13.38 | 46 | < 25mph | PG296 | 1.37 | 2019-04-22T20:00:00Z | 13.38 | 78 | < 25mph
PG&E | 2018-08-20 | 9:34 | 39.8014 | -121.5813 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100400441 | Unknown | 12000 | Conductor | Overhead | Yes | 43332 | 9:34 | Contact From Object | N.A. | Other | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1849 | 2018 | 8 | 20 | 9 | 34 | 18-0071596 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 394259 | 5.4464 | 175_338 | <25mph | <15mph | HFTD - Distribution | 2018-08-20 09:34:00 | 1588 | 11.8754 | FALSE | <25mph | E4833 | 1.36 | 2015-05-18T10:25:00Z | 0 | 9 | < 25mph | JBGC1 | 6.67 | 2015-05-18T10:13:00Z | 7 | 23 | < 25mph | E4833 | 1.36 | 2015-05-18T11:19:00Z | 1.01 | 17 | < 25mph | JBGC1 | 6.67 | 2015-05-18T10:13:00Z | 7 | 45 | < 25mph
PG&E | 2018-11-01 | 20:45 | 38.372 | -123.0507 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103852431 | AT&T | 12000 | Conductor | Overhead | Yes | 43405 | 20:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1958 | 2018 | 11 | 1 | 20 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.9426 | 111_260 | <25mph | <15mph | HFTD - Distribution | 2018-11-01 20:45:00 | 1697 | 13.8199 | FALSE | <25mph | BBYC1 | 3.77 | 2017-07-20T13:10:00Z | 7.96 | 1 | < 25mph | UCBM | 4.05 | 2017-07-20T13:10:00Z | 23.2 | 25 | < 25mph | BBYC1 | 3.77 | 2017-07-20T14:10:00Z | 8.7 | 2 | < 25mph | BDZC1 | 4.05 | 2017-07-20T14:04:00Z | 24.61 | 55 | < 25mph
PG&E | 2015-06-09 16:20 | 2015-06-09 16:20 | 38.3822 | -122.4316 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102269716 | Pacific Bell | 21000 | Unknown | Overhead | Yes | 42164.6806 | 2015-06-09 16:20 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0369 | 2015 | 6 | 9 | 16 | 20 | 15-0039860 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 4184 | 20.783 | 138_260 | <25mph | <15mph | HFTD - Distribution | 2015-06-09 16:20:00 | 115 | 24.1918 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7241 | 7.11 | 2015-08-01T06:11:00Z | 7 | 21 | < 25mph |  |  |  | 0 | 0 | No data | E7241 | 7.11 | 2015-08-01T07:01:00Z | 10 | 39 | < 25mph
PG&E | 2017-10-16 | 12:10 | 36.5831 | -121.9368 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101781248 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43024 | 12:10 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | Other/Unknown | 1493 | 2017 | 10 | 16 | 12 | 10 | 17-0087767 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 6313 | 5.0415 | 158_161 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:10:00 | 1236 | 13.6905 | FALSE | <25mph | E8505 | 1.61 | 2016-07-11T02:18:00Z | 20 | 42 | < 25mph | E8505 | 1.61 | 2016-07-11T02:18:00Z | 20 | 47 | < 25mph | E6407 | 2.44 | 2016-07-11T03:28:00Z | 21 | 81 | < 25mph | E6407 | 2.44 | 2016-07-11T03:28:00Z | 21 | 90 | < 25mph
PG&E | 2017-12-19 | 19:45 | 40.7271 | -122.3263 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101457738 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43088 | 19:45 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1545 | 2017 | 12 | 19 | 19 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 12.0712 | 144_390 | <25mph | <15mph | HFTD - Distribution | 2017-12-19 19:45:00 | 1287 | 14.9625 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2019-04-09 | 15:27 | 37.7341 | -120.0776 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 101076921 |  | 21000 | Pole | Overhead | Yes | 43564 | 15:27 | Vegetation |  | Veg. contact | Pole |  |  | Branch (Not overhanging, > 12ft) | 2019-313 | 2019 | 4 | 9 | 15 | 27 | 19-0041008 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 179862 | 22.8983 | 240_225 | <25mph | <15mph | HFTD - Distribution | 2019-04-09 15:27:00 | 1738 | 29.8749 | FALSE | 25-40mph | PG112 | 3.29 | 2019-02-16T09:40:00Z | 5.91 | 14 | < 25mph | SEWC1 | 4.76 | 2019-02-16T09:16:00Z | 5.99 | 29 | < 25mph | PG112 | 3.29 | 2019-02-16T10:50:00Z | 8.12 | 26 | < 25mph | PG112 | 3.29 | 2019-02-16T10:50:00Z | 8.12 | 54 | < 25mph
PG&E | 2016-06-26 | 2016-06-26 16:38 | 39.5042 | -121.4475 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100375810 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42547 | 2016-06-26 16:38 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0823 | 2016 | 6 | 26 | 16 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 9.04 | 180_322 | <25mph | <15mph | HFTD - Distribution | 2016-06-26 16:38:00 | 567 | 14.524 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2017-10-23 | 21:24 | 37.3713 | -122.348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100270421 | Unknown | 12000 | Conductor | Overhead | Yes | 43031 | 21:24 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1507 | 2017 | 10 | 23 | 21 | 24 | 17-0089820 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1768 | 13.1103 | 140_205 | <25mph | <15mph | HFTD - Distribution | 2017-10-23 21:24:00 | 1249 | 22.0037 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PUGC1 | 7.55 | 2016-06-10T03:18:00Z | 22.01 | 8 | < 25mph |  |  |  | 0 | 0 | No data | PUGC1 | 7.55 | 2016-06-10T03:18:00Z | 22.01 | 20 | < 25mph
PG&E | 2017-07-24 14:02 | 14:01 | 37.2635 | -122.3364 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike klink 650-879-0121 | 100322130 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42940.5845 | 14:01 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1286 | 2017 | 7 | 24 | 14 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 18.4533 | 141_199 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 14:01:00 | 1025 | 18.6394 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 5.31 | 2017-05-19T09:07:00Z | 3 | 1 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 5.31 | 2017-05-19T10:07:00Z | 3 | 2 | < 25mph
PG&E | 2018-08-07 | 21:03 | 38.2129 | -120.9184 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102042811 | Unknown | 12000 | Conductor | Overhead | Yes | 43319 | 21:03 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1828 | 2018 | 8 | 7 | 21 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2018-08-07 21:03:00 | NA | 0 | FALSE | <25mph | CMAC1 | 2.92 | 2017-03-09T06:59:00Z | 2.01 | 1 | < 25mph | CMAC1 | 2.92 | 2017-03-09T06:59:00Z | 2.01 | 1 | < 25mph | CMAC1 | 2.92 | 2017-03-09T07:59:00Z | 3 | 2 | < 25mph | CMAC1 | 2.92 | 2017-03-09T07:59:00Z | 3 | 2 | < 25mph
PG&E | 2015-06-06 15:38 | 2015-06-06 15:38 | 39.0409 | -123.4019 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 11480 ANDERSON VALLEY WAY @ BRIDGE |  | 12000 | Conductor | Overhead | Yes | 42161.6514 | 2015-06-06 15:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0355 | 2015 | 6 | 6 | 15 | 38 | 15-0039056 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 1748 | 19.2204 | 97_298 | <25mph | <15mph | HFTD - Distribution | 2015-06-06 15:38:00 | 101 | 19.2204 | FALSE | <25mph | E4777 | 3.27 | 2015-03-13T23:22:00Z | 11.99 | 1 | < 25mph | BNVC1 | 4.68 | 2015-03-13T23:50:00Z | 14.99 | 6 | < 25mph | E4777 | 3.27 | 2015-03-13T23:22:00Z | 11.99 | 4 | < 25mph | BNVC1 | 4.68 | 2015-03-13T23:50:00Z | 14.99 | 14 | < 25mph
PG&E | 2017-07-11 22:13 | 22:12 | 37.0122 | -121.9497 | Vegetation | Rural | < 3 Meters | Fire Agency | CAPT PHIL CRAMBLET 831-479-6842 | 101676689 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42927.9254 | 22:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1244 | 2017 | 7 | 11 | 22 | 12 | 17-0062198 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 714 | 7.2694 | 158_185 | <25mph | <15mph | HFTD - Distribution | 2017-07-11 22:12:00 | 983 | 9.7577 | FALSE | <25mph | E0065 | 1.9 | 2016-10-11T17:02:00Z | 5.99 | 44 | < 25mph | C4503 | 5.28 | 2016-10-11T17:15:00Z | 7 | 184 | < 25mph | E0065 | 1.9 | 2016-10-11T18:11:00Z | 7 | 86 | < 25mph | D6358 | 4.67 | 2016-10-11T18:18:00Z | 10 | 356 | < 25mph
PG&E | 2018-10-08 | 11:03 | 38.2621 | -122.7881 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101987186 | AT&T | 12000 | Conductor | Overhead | No | N.A. | N.A. | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1933 | 2018 | 10 | 8 | 11 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 15.6859 | 122_254 | <25mph | <15mph | HFTD - Distribution | 2018-10-08 11:03:00 | 1672 | 17.3485 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D9961 | 6.8 | 2015-06-19T21:40:00Z | 13 | 29 | < 25mph |  |  |  | 0 | 0 | No data | D9961 | 6.8 | 2015-06-19T21:40:00Z | 13 | 51 | < 25mph
PG&E | 2019-09-30 | 14:29 | 34.6139 | -120.1799 | Contact with High Voltage, 3rd party | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 183041102 |  | 12000 | Conductor | Overhead | Yes | 43738 | 14:29 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-13 | 2019 | 9 | 30 | 14 | 29 | 19-0105582 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 4080 | 26.8876 | 237_52 | 25-40mph | 15-30mph | HFTD - Distribution | 2019-09-30 14:29:00 | 2072 | 27.9753 | FALSE | 25-40mph | C9206 | 2.6 | 2017-09-02T01:05:00Z | 4.99 | 8 | < 25mph | AP901 | 4.92 | 2017-09-02T01:00:00Z | 12.01 | 12 | < 25mph | C9206 | 2.6 | 2017-09-02T01:05:00Z | 4.99 | 11 | < 25mph | AP901 | 4.92 | 2017-09-02T01:00:00Z | 12.01 | 19 | < 25mph
PG&E | 2019-01-16 | 0:17 | 38.0621 | -120.1964 | Vegetation | Conifer Forest | Structure Only | Cal Fire |  | 163661701 |  | 17000 | Conductor | Overhead | Yes | 43481 | 0:17 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-01 | 2019 | 1 | 16 | 0 | 17 | 19-0010443 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1041827 | 14.8061 | 234_243 | <25mph | <15mph | HFTD - Distribution | 2019-01-16 00:17:00 | 1728 | 28.2081 | FALSE | 25-40mph | MOUC1 | 2.77 | 2016-08-04T23:02:00Z | 14.99 | 1 | < 25mph | MOUC1 | 2.77 | 2016-08-04T23:02:00Z | 14.99 | 1 | < 25mph | MOUC1 | 2.77 | 2016-08-05T00:02:00Z | 14.99 | 2 | < 25mph | MOUC1 | 2.77 | 2016-08-05T00:02:00Z | 14.99 | 2 | < 25mph
PG&E | 2017-05-15 16:14 | 16:00 | 37.1766 | -119.8189 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SHAUN FAIRBANKS 559-683-4823 | 101108423 | SIERRA | 21000 | Conductor | Overhead | Yes | 42870.6767 | 16:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1099 | 2017 | 5 | 15 | 16 | 0 | 17-0048096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20007 | 15.7465 | 251_194 | <25mph | <15mph | HFTD - Distribution | 2017-05-15 16:00:00 | 839 | 20.7849 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5766 | 4.44 | 2015-01-20T09:42:00Z | 4 | 12 | < 25mph |  |  |  | 0 | 0 | No data | E5766 | 4.44 | 2015-01-20T09:42:00Z | 4 | 24 | < 25mph
PG&E | 2016-01-21 21:32 | 2016-01-21 21:32 | 40.553 | -124.1116 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100994021 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42390.8972 | 2016-01-21 21:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0690 | 2016 | 1 | 21 | 21 | 32 | 16-0007239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 6468 | 26.2481 | 69_382 | 25-40mph | 15-30mph | HFTD - Distribution | 2016-01-21 21:32:00 | 434 | 29.6828 | FALSE | 25-40mph | KFOT | 1.14 | 2018-09-14T00:15:00Z | 17.27 | 23 | < 25mph | KFOT | 1.14 | 2018-09-14T00:15:00Z | 17.27 | 23 | < 25mph | KFOT | 1.14 | 2018-09-14T00:15:00Z | 17.27 | 42 | < 25mph | KFOT | 1.14 | 2018-09-14T00:15:00Z | 17.27 | 42 | < 25mph
PG&E | 2016-08-12 | 2016-08-12 10:08 | 38.8751 | -122.4223 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 102168360 |  | 12000 | Conductor | Overhead | Yes | 42594 | 2016-08-12 10:08 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0922 | 2016 | 8 | 12 | 10 | 8 | 16-0056982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 1368 | 5.1025 | 138_288 | <25mph | <15mph | HFTD - Distribution | 2016-08-12 10:08:00 | 665 | 17.0718 | FALSE | <25mph | KNXC1 | 0.95 | 2017-09-13T12:09:00Z | 4.99 | 1 | < 25mph | KNXC1 | 0.95 | 2017-09-13T12:09:00Z | 4.99 | 9 | < 25mph | KNXC1 | 0.95 | 2017-09-13T13:09:00Z | 10 | 2 | < 25mph | KNXC1 | 0.95 | 2017-09-13T13:09:00Z | 10 | 18 | < 25mph
PG&E | 2016-08-15 | 2016-08-15 15:43 | 37.8784 | -120.4488 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101020079 |  | 17000 | Conductor | Overhead | Yes | 42597 | 2016-08-15 15:43 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0928 | 2016 | 8 | 15 | 15 | 43 | 16-0057465 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 122905 | 10.0906 | 223_232 | <25mph | <15mph | HFTD - Distribution | 2016-08-15 15:43:00 | 671 | 12.9875 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.26 | 2018-03-20T12:03:00Z | 4.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 4.26 | 2018-03-20T13:03:00Z | 13 | 2 | < 25mph
PG&E | 2015-06-15 15:35 | 2015-06-15 15:35 | 37.1852 | -121.7595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Jose city | 100618215 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42170.6493 | 2015-06-15 15:35 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0384 | 2015 | 6 | 15 | 15 | 35 | 15-0041178 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 345 | 20.7397 | 166_194 | <25mph | <15mph | HFTD - Distribution | 2015-06-15 15:35:00 | 130 | 21.599 | FALSE | <25mph | D1269 | 2.38 | 2016-02-27T15:31:00Z | 0 | 1 | < 25mph | C9520 | 5.63 | 2016-02-27T15:30:00Z | 4 | 73 | < 25mph | D1269 | 2.38 | 2016-02-27T15:31:00Z | 0 | 1 | < 25mph | E5617 | 5.37 | 2016-02-27T16:53:00Z | 4.99 | 148 | < 25mph
PG&E | 2018-03-06 | 17:57 | 38.2811 | -120.8965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-647-5220 | 101238429 | AT&T | 12000 | Conductor | Overhead | Yes | 43165 | 17:57 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1566 | 2018 | 3 | 6 | 17 | 57 | 18-0020396 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 142000 | 3.9357 | 204_254 | <25mph | <15mph | HFTD - Distribution | 2018-03-06 17:57:00 | 1308 | 12.1612 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.07 | 2017-05-21T23:05:00Z | 13 | 3 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.07 | 2017-05-22T00:05:00Z | 15.99 | 6 | < 25mph
PG&E | 2019-10-04 | 19:07 | 40.4964 | -122.0448 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | Yes | 43742 | 19:07 | Equipment - Overloaded | Other |  |  |  |  | no-match | 2019-257 | 2019 | 10 | 4 | 19 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 6.2955 | 155_377 | <25mph | <15mph | HFTD - Distribution | 2019-10-04 19:07:00 | 2076 | 10.3362 | FALSE | <25mph | AR225 | 3.27 | 2015-07-10T00:50:00Z | 14.99 | 12 | < 25mph | AR225 | 3.27 | 2015-07-10T00:50:00Z | 14.99 | 12 | < 25mph | AR225 | 3.27 | 2015-07-10T01:55:00Z | 14.99 | 24 | < 25mph | AR225 | 3.27 | 2015-07-10T01:55:00Z | 14.99 | 24 | < 25mph
PG&E | 2019-09-22 | 11:56 | 37.5168 | -119.9159 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103967994 |  | 21000 | Pole | Overhead | Yes | 43730 | 11:56 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-452 | 2019 | 9 | 22 | 11 | 56 | 19-0102232 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 133232 | 11.5782 | 247_213 | <25mph | <15mph | HFTD - Distribution | 2019-09-22 11:56:00 | 2051 | 13.905 | FALSE | <25mph | PG189 | 1.46 | 2019-06-20T15:00:00Z | 10.96 | 13 | < 25mph | PG189 | 1.46 | 2019-06-20T15:00:00Z | 10.96 | 30 | < 25mph | PG189 | 1.46 | 2019-06-20T15:20:00Z | 12.48 | 26 | < 25mph | PG189 | 1.46 | 2019-06-20T15:20:00Z | 12.48 | 59 | < 25mph
PG&E | 2018-06-05 | 10:13 | 40.6183 | -122.3173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JASON COLLINS 530-225-4628 | 101467801 | None | 12000 | Conductor | Overhead | Yes | 43256 | 10:13 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1631 | 2018 | 6 | 5 | 10 | 13 | 18-0047539 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 277 | 7.1547 | 144_384 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 10:13:00 | 1373 | 12.6046 | FALSE | <25mph | C5599 | 1.27 | 2015-10-20T15:16:00Z | 18.99 | 4 | < 25mph | C5599 | 1.27 | 2015-10-20T15:16:00Z | 18.99 | 23 | < 25mph | C5599 | 1.27 | 2015-10-20T16:46:00Z | 21 | 8 | < 25mph | RRAC1 | 7.21 | 2015-10-20T16:24:00Z | 24.99 | 47 | < 25mph
PG&E | 2018-10-15 | 3:23 | 38.2897 | -120.5803 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103378003 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43388 | 3:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1941 | 2018 | 10 | 15 | 3 | 23 | 18-0090342 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1464 | 26.0611 | 218_255 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-15 03:23:00 | 1680 | 26.2858 | FALSE | 25-40mph | AT317 | 3.74 | 2019-08-03T21:29:00Z | 13 | 12 | < 25mph | PG397 | 4.86 | 2019-08-03T21:30:00Z | 18.63 | 70 | < 25mph | AT317 | 3.74 | 2019-08-03T21:29:00Z | 13 | 24 | < 25mph | PG397 | 4.86 | 2019-08-03T21:30:00Z | 18.63 | 140 | < 25mph
PG&E | 2017-06-15 15:04 | 15:01 | 39.3913 | -123.3054 | Vegetation | Rural | < 0.25 Acres | Fire Agency | STEPHEN | 103838176 | YES | 12000 | Conductor | Overhead | Yes | 42901.6279 | 15:01 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1148 | 2017 | 6 | 15 | 15 | 1 | 17-0055557 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 180469 | 19.6681 | 101_317 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 15:01:00 | 887 | 19.7788 | FALSE | <25mph | AT319 | 1.89 | 2015-04-20T11:33:00Z | 3 | 24 | < 25mph | AT319 | 1.89 | 2015-04-20T11:33:00Z | 3 | 28 | < 25mph | AT319 | 1.89 | 2015-04-20T13:18:00Z | 3 | 48 | < 25mph | AT319 | 1.89 | 2015-04-20T13:18:00Z | 3 | 56 | < 25mph
PG&E | 2015-06-30 18:18 | 2015-06-30 18:18 | 36.2199 | -121.7534 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | loadside of 88973 | unknown | 12000 | Conductor | Overhead | Yes | 42185.7625 | 2015-06-30 18:18 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0432 | 2015 | 6 | 30 | 18 | 18 | 15-0044405 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 158 | 5.7006 | 166_141 | <25mph | <15mph | HFTD - Distribution | 2015-06-30 18:18:00 | 177 | 8.2628 | FALSE | <25mph | PPSC1 | 2.3 | 2015-06-24T07:04:00Z | 3 | 1 | < 25mph | E4662 | 6.7 | 2015-06-24T06:30:00Z | 4 | 5 | < 25mph | PPSC1 | 2.3 | 2015-06-24T08:04:00Z | 8.01 | 2 | < 25mph | PPSC1 | 2.3 | 2015-06-24T08:04:00Z | 8.01 | 6 | < 25mph
PG&E | 2019-09-16 | 14:39 | 37.3762 | -119.8729 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 254452102 |  | 21000 | Conductor | Overhead | Yes | 43724 | 14:39 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-417 | 2019 | 9 | 16 | 14 | 39 | 19-0099772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 121254 | 13.3091 | 249_205 | <25mph | <15mph | HFTD - Distribution | 2019-09-16 14:39:00 | 2045 | 14.9838 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E9110 | 4.38 | 2018-06-26T21:43:00Z | 14 | 9 | < 25mph |  |  |  | 0 | 0 | No data | E9110 | 4.38 | 2018-06-26T21:43:00Z | 14 | 18 | < 25mph
PG&E | 2017-05-25 17:36 | 16:55 | 38.3986 | -122.9876 | Vegetation | Rural | < 3 Meters | Utility: PG&E | N.A. | 101974034 | Unknown | 12000 | Conductor | Overhead | Yes | 42880.7334 | 16:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1114 | 2017 | 5 | 25 | 16 | 55 | 17-0050815 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 2644 | 12.6436 | 114_262 | <25mph | <15mph | HFTD - Distribution | 2017-05-25 16:55:00 | 854 | 13.2306 | FALSE | <25mph | D2849 | 1.17 | 2017-02-19T00:47:00Z | 10 | 12 | < 25mph | UCBM | 7.05 | 2017-02-19T00:00:00Z | 34.69 | 58 | 25-40mph | D2849 | 1.17 | 2017-02-19T00:47:00Z | 10 | 24 | < 25mph | UCBM | 7.05 | 2017-02-19T00:00:00Z | 34.69 | 114 | 25-40mph
PG&E | 2015-06-15 15:35 | 2015-06-15 15:35 | 37.1852 | -121.7595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Jose city | 100618215 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42170.6493 | 2015-06-15 15:35 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0384 | 2015 | 6 | 15 | 15 | 35 | 15-0041178 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 345 | 20.7397 | 166_194 | <25mph | <15mph | HFTD - Distribution | 2015-06-15 15:35:00 | 130 | 21.599 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D3723 | 7.2 | 2016-06-16T06:09:00Z | 8.01 | 67 | < 25mph |  |  |  | 0 | 0 | No data | D3723 | 7.2 | 2016-06-16T06:09:00Z | 8.01 | 132 | < 25mph
PG&E | 2016-11-15 | 17:27 | 39.7275 | -121.6557 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100327525 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42689 | 17:27 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 1049 | 2016 | 11 | 15 | 17 | 27 | 16-0080083 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 69231 | 9.6883 | 172_334 | <25mph | <15mph | HFTD - Distribution | 2016-11-15 17:27:00 | 790 | 16.6369 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E4833 | 6.1 | 2015-05-19T09:40:00Z | 1.01 | 7 | < 25mph |  |  |  | 0 | 0 | No data | E4833 | 6.1 | 2015-05-19T09:40:00Z | 1.01 | 13 | < 25mph
PG&E | 2019-06-10 | 16:18 | 38.1107 | -122.9025 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 42291101 |  | 12000 | Conductor | Overhead | Yes | 43626 | 16:18 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-401 | 2019 | 6 | 10 | 16 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.6937 | 117_246 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 16:18:00 | 1826 | 12.047 | FALSE | <25mph | PREC1 | 1.92 | 2018-01-28T17:05:00Z | 4.99 | 13 | < 25mph | PREC1 | 1.92 | 2018-01-28T17:05:00Z | 4.99 | 13 | < 25mph | PRWC1 | 2.82 | 2018-01-28T19:00:00Z | 7 | 26 | < 25mph | PRWC1 | 2.82 | 2018-01-28T19:00:00Z | 7 | 26 | < 25mph
PG&E | 2018-07-01 | 0:23 | 40.2697 | -124.2386 | Vegetation | Rural | < 3 meters | Fire Agency | fire chief | 100986962 | Unknown | 12000 | Conductor | Overhead | Yes | 43282 | 0:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1718 | 2018 | 7 | 1 | 0 | 23 | 18-0056043 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 22872 | 20.9894 | 63_366 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 00:23:00 | 1459 | 27.5371 | FALSE | 25-40mph | PTEC1 | 1.7 | 2019-12-20T10:08:00Z | 38.99 | 1 | 25-40mph | PTEC1 | 1.7 | 2019-12-20T10:08:00Z | 38.99 | 8 | 25-40mph | PTEC1 | 1.7 | 2019-12-20T11:08:00Z | 42.01 | 2 | 40-55mph | PTEC1 | 1.7 | 2019-12-20T11:08:00Z | 42.01 | 15 | 40-55mph
PG&E | 2015-07-16 19:11 | 2015-07-16 19:11 | 37.1989 | -119.7712 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 20334 ROAD 400 |  | 12000 | Conductor | Overhead | Yes | 42201.7993 | 2015-07-16 19:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0465 | 2015 | 7 | 16 | 19 | 11 | 15-0048064 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 8.6422 | 254_195 | <25mph | <15mph | HFTD - Distribution | 2015-07-16 19:11:00 | 210 | 13.1745 | FALSE | <25mph | E5766 | 3.27 | 2018-03-12T09:45:00Z | 0 | 19 | < 25mph | E5766 | 3.27 | 2018-03-12T09:45:00Z | 0 | 19 | < 25mph | E5766 | 3.27 | 2018-03-12T10:45:00Z | 0 | 37 | < 25mph | E5766 | 3.27 | 2018-03-12T10:45:00Z | 0 | 37 | < 25mph
PG&E | 2015-11-09 05:55 | 2015-11-09 05:55 | 34.9984 | -120.3634 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42317.2465 | 2015-11-09 05:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0673 | 2015 | 11 | 9 | 5 | 55 | 15-0076534 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 205393 | 8.4294 | 228_73 | <25mph | <15mph | HFTD - Distribution | 2015-11-09 05:55:00 | 417 | 17.7768 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F0412 | 7.53 | 2019-06-11T04:45:00Z | 2.01 | 10 | < 25mph |  |  |  | 0 | 0 | No data | F0412 | 7.53 | 2019-06-11T04:45:00Z | 2.01 | 21 | < 25mph
PG&E | 2015-09-28 09:42 | 2015-09-28 09:42 | 37.9623 | -122.1765 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100458692 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42275.4042 | 2015-09-28 09:42 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0619 | 2015 | 9 | 28 | 9 | 42 | 15-0066062 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 2125 | 9.6053 | 148_237 | <25mph | <15mph | HFTD - Distribution | 2015-09-28 09:42:00 | 364 | 19.5931 | FALSE | <25mph | PLEC1 | 3.75 | 2016-04-24T03:28:00Z | 22.01 | 7 | < 25mph | PLEC1 | 3.75 | 2016-04-24T03:28:00Z | 22.01 | 164 | < 25mph | PLEC1 | 3.75 | 2016-04-24T03:28:00Z | 22.01 | 14 | < 25mph | UPBC1 | 6.07 | 2016-04-24T05:24:00Z | 22.97 | 321 | < 25mph
PG&E | 2018-06-16 | 19:58 | 37.907 | -121.8063 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100483910 | Unknown | 21000 | Conductor | Overhead | Yes | 43267 | 19:58 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1670 | 2018 | 6 | 16 | 19 | 58 | 18-0051687 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 3322 | 40.9858 | 164_234 | 40-55mph | 30-45mph | HFTD - Distribution | 2018-06-16 19:58:00 | 1412 | 43.1884 | FALSE | 40-55mph |  |  |  | 0 | 0 | No data | SJS02 | 6.13 | 2017-07-13T02:35:00Z | 27.18 | 36 | 25-40mph |  |  |  | 0 | 0 | No data | SJS02 | 6.13 | 2017-07-13T02:35:00Z | 27.18 | 72 | 25-40mph
PG&E | 2017-09-06 | 19:26 | 40.8392 | -122.3635 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103643183 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 19:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1399 | 2017 | 9 | 6 | 19 | 26 | 17-0076501 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 23830 | 6.5088 | 142_396 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 19:26:00 | 1137 | 12.365 | FALSE | <25mph | CTANT | 1.93 | 2019-12-03T23:00:00Z | 4.47 | 10 | < 25mph | PG519 | 6.8 | 2019-12-03T22:50:00Z | 16.44 | 27 | < 25mph | CTANT | 1.93 | 2019-12-03T23:45:00Z | 4.47 | 20 | < 25mph | PG519 | 6.8 | 2019-12-03T23:40:00Z | 17.31 | 54 | < 25mph
PG&E | 2018-06-05 | 13:45 | 38.5432 | -122.7202 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 102031673 | Unknown | 12000 | Conductor | Overhead | Yes | 43256 | 13:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1633 | 2018 | 6 | 5 | 13 | 45 | 18-0047625 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 40599 | 7.3889 | 125_270 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 13:45:00 | 1375 | 15.9614 | FALSE | <25mph | PG005 | 2.46 | 2019-03-29T00:50:00Z | 12.06 | 16 | < 25mph | PG005 | 2.46 | 2019-03-29T00:50:00Z | 12.06 | 65 | < 25mph | PG005 | 2.46 | 2019-03-29T01:00:00Z | 15.57 | 32 | < 25mph | PG005 | 2.46 | 2019-03-29T01:00:00Z | 15.57 | 130 | < 25mph
PG&E | 2019-07-25 | 7:39 | 39.1735 | -123.5763 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Oj 2 P/Ss Of Cgc# 215532055340 |  | 12000 | Other | Overhead | Yes | 43671 | 7:39 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-380 | 2019 | 7 | 25 | 7 | 39 | 19-0080947 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 790 | 2.0398 | 89_305 | <25mph | <15mph | HFTD - Distribution | 2019-07-25 07:39:00 | 1928 | 13.3511 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1763 | 7.11 | 2017-02-06T01:36:00Z | 24 | 3 | < 25mph |  |  |  | 0 | 0 | No data | E1763 | 7.11 | 2017-02-06T01:36:00Z | 24 | 6 | < 25mph
PG&E | 2015-06-27 21:15 | 2015-06-27 21:15 | 39.2699 | -121.0403 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 16151 INDAIN FLAT RD |  | 12000 | Conductor | Overhead | Yes | 42182.8854 | 2015-06-27 21:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0416 | 2015 | 6 | 27 | 21 | 15 | 15-0043789 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4210 | 5.8168 | 198_309 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 21:15:00 | 161 | 11.6482 | FALSE | <25mph | D8321 | 3.83 | 2016-10-06T00:30:00Z | 5.99 | 48 | < 25mph | RRRC1 | 4.73 | 2016-10-06T00:13:00Z | 14 | 73 | < 25mph | D8321 | 3.83 | 2016-10-06T00:30:00Z | 5.99 | 94 | < 25mph | RRRC1 | 4.73 | 2016-10-06T01:13:00Z | 14 | 144 | < 25mph
PG&E | 2017-06-16 22:30 | 22:30 | 38.0373 | -122.1847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101424286 | Unknown | 21000 | Conductor | Overhead | Yes | 42902.9378 | 22:30 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1156 | 2017 | 6 | 16 | 22 | 30 | 17-0055882 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 12000 | 25.2975 | 148_241 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-06-16 22:30:00 | 895 | 25.6656 | FALSE | 25-40mph | MZXC1 | 3.24 | 2019-07-12T18:36:00Z | 18.99 | 25 | < 25mph | PCOC1 | 8 | 2019-07-12T18:06:00Z | 20 | 95 | < 25mph | MZXC1 | 3.24 | 2019-07-12T19:30:00Z | 20.98 | 51 | < 25mph | MZXC1 | 3.24 | 2019-07-12T19:30:00Z | 20.98 | 189 | < 25mph
PG&E | 2018-07-14 | 12:40 | 38.5793 | -122.878 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103122744 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 12:40 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1746 | 2018 | 7 | 14 | 12 | 40 | 18-0059799 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20804 | 12.0574 | 118_272 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 12:40:00 | 1486 | 14.4502 | FALSE | <25mph | AU487 | 3.65 | 2015-06-29T07:50:00Z | 4 | 16 | < 25mph | E6724 | 5.13 | 2015-06-29T07:40:00Z | 5.99 | 30 | < 25mph | AU487 | 3.65 | 2015-06-29T09:35:00Z | 4 | 31 | < 25mph | E6724 | 5.13 | 2015-06-29T07:40:00Z | 5.99 | 59 | < 25mph
PG&E | 2019-09-26 | 14:12 | 36.9517 | -121.8278 | Vegetation | Shrub | 1 meter - < 3 meters | Cal Fire |  | 2287 |  | 21000 | Conductor | Overhead | Yes | 43734 | 14:12 | Vegetation |  | Veg. contact |  |  |  | Branch (OverHanging) | 2019-352 | 2019 | 9 | 26 | 14 | 12 | 19-0104163 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 2856 | 23.4173 | 163_181 | <25mph | <15mph | HFTD - Distribution | 2019-09-26 14:12:00 | 2060 | 23.8621 | FALSE | <25mph | D6358 | 3.5 | 2019-06-22T22:34:00Z | 11.01 | 17 | < 25mph | C9585 | 7.9 | 2019-06-22T22:22:00Z | 13 | 84 | < 25mph | D6358 | 3.5 | 2019-06-22T22:34:00Z | 11.01 | 34 | < 25mph | C9585 | 7.9 | 2019-06-22T22:22:00Z | 13 | 162 | < 25mph
PG&E | 2017-05-09 18:41 | 18:26 | 40.8689 | -123.5156 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | todd wright fire chief. 5307392493 | 103796045 | Unknown | 12000 | Conductor | Overhead | Yes | 42864.7782 | 18:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1092 | 2017 | 5 | 9 | 18 | 26 | 17-0046642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 108117 | 15.9566 | 94_399 | <25mph | <15mph | HFTD - Distribution | 2017-05-09 18:26:00 | 832 | 17.9691 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8984 | 6.51 | 2018-05-10T21:01:00Z | 14 | 4 | < 25mph |  |  |  | 0 | 0 | No data | D8984 | 6.51 | 2018-05-10T21:01:00Z | 14 | 8 | < 25mph
PG&E | 2017-09-12 | 9:24 | 39.741 | -121.6079 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 911 | 100330302 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42990 | 9:24 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1410 | 2017 | 9 | 12 | 9 | 24 | 17-0078149 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 402890 | 5.7135 | 174_335 | <25mph | <15mph | HFTD - Distribution | 2017-09-12 09:24:00 | 1148 | 23.672 | FALSE | <25mph |  |  |  | 0 | 0 | No data | JBGC1 | 6.33 | 2017-07-26T09:13:00Z | 12.01 | 6 | < 25mph | PDEC1 | 1.25 | 2017-07-26T10:00:00Z | 2.01 | 1 | < 25mph | JBGC1 | 6.33 | 2017-07-26T10:13:00Z | 12.01 | 14 | < 25mph
PG&E | 2015-07-26 12:25 | 2015-07-26 12:25 | 39.1586 | -121.0634 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 15499 ALLISON RANCH RD |  | 12000 | Conductor | Overhead | Yes | 42211.5174 | 2015-07-26 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0485 | 2015 | 7 | 26 | 12 | 25 | 15-0050558 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2224 | 13.0644 | 197_303 | <25mph | <15mph | HFTD - Distribution | 2015-07-26 12:25:00 | 230 | 13.6917 | FALSE | <25mph | E1789 | 3.9 | 2018-08-03T12:48:00Z | 4.99 | 14 | < 25mph | PG059 | 7.97 | 2018-08-03T12:50:00Z | 7.67 | 71 | < 25mph | E1789 | 3.9 | 2018-08-03T14:18:00Z | 4.99 | 28 | < 25mph | PG059 | 7.97 | 2018-08-03T12:50:00Z | 7.67 | 150 | < 25mph
PG&E | 2019-09-13 | 6:30 | 37.3348 | -121.7716 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 83392110 |  | 21000 | Splice/Clamp/Connector | Overhead | Yes | 43721 | 6:30 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-444 | 2019 | 9 | 13 | 6 | 30 | 19-0098560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 35534 | 3.3882 | 166_202 | <25mph | <15mph | HFTD - Distribution | 2019-09-13 06:30:00 | 2037 | 14.1926 | FALSE | <25mph | E8563 | 3.34 | 2016-04-07T05:43:00Z | 7 | 18 | < 25mph | SJS01 | 6.07 | 2016-04-07T06:15:00Z | 8.12 | 96 | < 25mph | E8563 | 3.34 | 2016-04-07T06:53:00Z | 7 | 36 | < 25mph | SJS01 | 6.07 | 2016-04-07T06:50:00Z | 11.41 | 189 | < 25mph
PG&E | 2017-07-04 20:17 | 20:16 | 40.4228 | -122.3975 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SCOTT CORN 530-448-2414 | 101481860 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42920.8451 | 20:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1221 | 2017 | 7 | 4 | 20 | 16 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 13.3568 | 141_373 | <25mph | <15mph | HFTD - Distribution | 2017-07-04 20:16:00 | 960 | 18.8443 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6886 | 4.89 | 2018-03-30T10:44:00Z | 2.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6886 | 4.89 | 2018-03-30T10:44:00Z | 2.01 | 8 | < 25mph
PG&E | 2018-07-14 | 12:40 | 38.5793 | -122.878 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103122744 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 12:40 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1746 | 2018 | 7 | 14 | 12 | 40 | 18-0059799 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20804 | 12.0574 | 118_272 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 12:40:00 | 1486 | 14.4502 | FALSE | <25mph | AU487 | 3.65 | 2016-07-26T09:30:00Z | 0 | 16 | < 25mph | E6724 | 5.13 | 2016-07-26T09:29:00Z | 0 | 37 | < 25mph | AU487 | 3.65 | 2016-07-26T10:30:00Z | 0 | 32 | < 25mph | E6724 | 5.13 | 2016-07-26T10:09:00Z | 0 | 74 | < 25mph
PG&E | 2018-11-09 | 8:59 | 37.2809 | -122.1214 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100546562 | AT&T | 12000 | Conductor | Overhead | Yes | 43413 | 8:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1964 | 2018 | 11 | 9 | 8 | 59 | 18-0098521 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 77077 | 5.2345 | 150_200 | <25mph | <15mph | HFTD - Distribution | 2018-11-09 08:59:00 | 1704 | 17.3931 | FALSE | <25mph | E0516 | 1.72 | 2017-04-22T17:21:00Z | 5.99 | 22 | < 25mph | E8945 | 6.54 | 2017-04-22T17:21:00Z | 10 | 121 | < 25mph | F0333 | 0.11 | 2017-04-22T18:20:00Z | 5.99 | 50 | < 25mph | E8945 | 6.54 | 2017-04-22T17:21:00Z | 10 | 250 | < 25mph
PG&E | 2015-03-14 02:30 | 2015-03-14 02:30 | 38.9038 | -122.7579 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 9210 Wildcat Road, Kelseyville |  | 12000 | Conductor | Overhead | Yes | 42077.1042 | 2015-03-14 02:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0274 | 2015 | 3 | 14 | 2 | 30 | 15-0019556 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2280 | 8.9688 | 124_289 | <25mph | <15mph | HFTD - Distribution | 2015-03-14 02:30:00 | 20 | 8.9688 | FALSE | <25mph | KELC1 | 2.83 | 2016-09-11T23:57:00Z | 22.01 | 1 | < 25mph | KELC1 | 2.83 | 2016-09-11T23:57:00Z | 22.01 | 6 | < 25mph | KELC1 | 2.83 | 2016-09-12T00:57:00Z | 25.99 | 2 | 25-40mph | KELC1 | 2.83 | 2016-09-12T00:57:00Z | 25.99 | 12 | 25-40mph
PG&E | 2016-08-09 | 2016-08-09 19:21 | 38.9187 | -120.9525 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | El Dorado County FD | 100038028 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0915 | 2016 | 8 | 9 | 19 | 21 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.2678 | 201_290 | <25mph | <15mph | HFTD - Distribution | 2016-08-09 19:21:00 | 658 | 10.7446 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8862 | 6.76 | 2016-04-01T06:29:00Z | 4.99 | 18 | < 25mph |  |  |  | 0 | 0 | No data | D8862 | 6.76 | 2016-04-01T07:44:00Z | 8.99 | 34 | < 25mph
PG&E | 2017-06-25 02:47 | 0:23 | 39.4043 | -123.3869 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102193088 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42911.1159 | 0:23 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1197 | 2017 | 6 | 25 | 0 | 23 | 17-0058406 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 23100 | 15.6787 | 98_318 | <25mph | <15mph | HFTD - Distribution | 2017-06-25 00:23:00 | 935 | 19.8426 | FALSE | <25mph | E4027 | 2.16 | 2016-07-24T05:28:00Z | 3 | 12 | < 25mph | E4027 | 2.16 | 2016-07-24T05:28:00Z | 3 | 12 | < 25mph | E4027 | 2.16 | 2016-07-24T05:28:00Z | 3 | 24 | < 25mph | E4027 | 2.16 | 2016-07-24T05:28:00Z | 3 | 24 | < 25mph
PG&E | 2018-05-11 | 10:13 | 38.387 | -122.9856 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101973909 | Unknown | 12000 | Conductor | Overhead | Yes | 43231 | 10:13 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1585 | 2018 | 5 | 11 | 10 | 13 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.6545 | 114_261 | <25mph | <15mph | HFTD - Distribution | 2018-05-11 10:13:00 | 1327 | 21.7544 | FALSE | <25mph | D2849 | 0.89 | 2017-02-23T07:14:00Z | 4.99 | 12 | < 25mph | BDZC1 | 6.47 | 2017-02-23T07:14:00Z | 27.4 | 50 | 25-40mph | D2849 | 0.89 | 2017-02-23T08:19:00Z | 5.99 | 24 | < 25mph | BDZC1 | 6.47 | 2017-02-23T07:14:00Z | 27.4 | 98 | 25-40mph
2. Cascade (Neu Wind Complex) | 2017-10-08 | 23:45 | 39.322 | -121.4021 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1988 | 2017 | 10 | 8 | 23 | 45 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Equip Failure | Conductor | 0 | 17.3686 | 182_312 | <25mph | <15mph | HFTD - Distribution | 2017-10-08 23:45:00 | 1213 | 29.7104 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | BNGC1 | 4.15 | 2017-11-24T03:51:00Z | 3 | 1 | < 25mph |  |  |  | 0 | 0 | No data | BNGC1 | 4.15 | 2017-11-24T03:51:00Z | 3 | 2 | < 25mph
PG&E | 2015-06-28 02:50 | 2015-06-28 02:50 | 35.491 | -120.731 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 13505 Santa Lucia Rd. Atascadero |  | 12000 | Conductor | Overhead | Yes | 42183.1181 | 2015-06-28 02:50 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0418 | 2015 | 6 | 28 | 2 | 50 | 15-0043807 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 12323 | 9.9634 | 212_101 | <25mph | <15mph | HFTD - Distribution | 2015-06-28 02:50:00 | 163 | 24.8049 | FALSE | <25mph | PG191 | 1.82 | 2019-05-18T06:10:00Z | 11.83 | 33 | < 25mph | PG142 | 6.23 | 2019-05-18T05:50:00Z | 20.83 | 64 | < 25mph | PG191 | 1.82 | 2019-05-18T06:10:00Z | 11.83 | 64 | < 25mph | PG142 | 6.23 | 2019-05-18T05:50:00Z | 20.83 | 126 | < 25mph
PG&E | 2019-10-04 | 19:07 | 40.4964 | -122.0448 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | Yes | 43742 | 19:07 | Equipment - Overloaded | Other |  |  |  |  | no-match | 2019-257 | 2019 | 10 | 4 | 19 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 6.2955 | 155_377 | <25mph | <15mph | HFTD - Distribution | 2019-10-04 19:07:00 | 2076 | 10.3362 | FALSE | <25mph | PG107 | 2.58 | 2018-12-31T12:10:00Z | 8.99 | 6 | < 25mph | PG107 | 2.58 | 2018-12-31T12:10:00Z | 8.99 | 6 | < 25mph | PG107 | 2.58 | 2018-12-31T12:50:00Z | 15.57 | 12 | < 25mph | PG107 | 2.58 | 2018-12-31T12:50:00Z | 15.57 | 12 | < 25mph
PG&E | 2017-11-20 08:33 | 08:32 | 38.7584 | -120.8439 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101389405 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43059.3562 | 08:32 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1522 | 2017 | 11 | 20 | 8 | 32 | 17-0096436 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 12376 | 9.7427 | 206_281 | <25mph | <15mph | HFTD - Distribution | 2017-11-20 08:32:00 | 1264 | 12.0384 | FALSE | <25mph | E5691 | 2.94 | 2018-06-22T18:29:00Z | 4 | 12 | < 25mph | C6129 | 4.36 | 2018-06-22T18:04:00Z | 8.99 | 74 | < 25mph | E5691 | 2.94 | 2018-06-22T19:19:00Z | 5.99 | 24 | < 25mph | PG024 | 5.44 | 2018-06-22T19:10:00Z | 8.99 | 149 | < 25mph
PG&E | 2016-07-15 05:19 | 2016-07-15 05:19 | 35.1839 | -120.5018 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101846594 |  | 12000 | Conductor | Overhead | Yes | 42566.2215 | 2016-07-15 05:19 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0851 | 2016 | 7 | 15 | 5 | 19 | 16-0050086 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 62404 | 2.6454 | 222_84 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 05:19:00 | 594 | 14.1102 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D6295 | 5.2 | 2015-02-10T18:56:00Z | 13 | 11 | < 25mph |  |  |  | 0 | 0 | No data | D6295 | 5.2 | 2015-02-10T19:26:00Z | 14.99 | 26 | < 25mph
PG&E | 2015-10-09 06:32 | 2015-10-09 06:32 | 38.364 | -122.9173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 320 Freestone St, Frestone | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0642 | 2015 | 10 | 9 | 6 | 32 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 2.6818 | 117_260 | <25mph | <15mph | HFTD - Distribution | 2015-10-09 06:32:00 | 386 | 15.5803 | FALSE | <25mph | E5234 | 0.7 | 2016-08-20T22:02:00Z | 12.01 | 22 | < 25mph | C3627 | 5.48 | 2016-08-20T22:06:00Z | 15.99 | 48 | < 25mph | E5234 | 0.7 | 2016-08-20T22:02:00Z | 12.01 | 44 | < 25mph | C3627 | 5.48 | 2016-08-20T22:56:00Z | 18.01 | 94 | < 25mph
PG&E | 2019-09-13 | 8:53 | 39.0754 | -121.1717 | Bird Found | Herbaceous | 0.25 - 10 Acres | Fire Dept | Consolidated FD | Etr0913190810 |  | 12000 | Other | Overhead | Yes | 43721 | 8:53 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-46 | 2019 | 9 | 13 | 8 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 10.4382 | 192_298 | <25mph | <15mph | HFTD - Distribution | 2019-09-13 08:53:00 | 2038 | 13.5808 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1789 | 5.17 | 2016-09-06T04:42:00Z | 5.99 | 16 | < 25mph |  |  |  | 0 | 0 | No data | E1789 | 5.17 | 2016-09-06T04:42:00Z | 5.99 | 32 | < 25mph
PG&E | 2017-07-15 14:35 | 14:34 | 39.6231 | -121.5328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | russ fowler | 100404385 | Unknown | 12000 | Conductor | Overhead | Yes | 42931.6076 | 14:34 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1254 | 2017 | 7 | 15 | 14 | 34 | 17-0063126 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 54372 | 7.6156 | 177_329 | <25mph | <15mph | HFTD - Distribution | 2017-07-15 14:34:00 | 993 | 11.3229 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CICC1 | 5.91 | 2019-02-17T10:54:00Z | 15.99 | 7 | < 25mph |  |  |  | 0 | 0 | No data | CICC1 | 5.91 | 2019-02-17T10:54:00Z | 15.99 | 14 | < 25mph
PG&E | 2016-07-03 15:00 | 2016-07-03 15:00 | 38.0348 | -120.3809 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101050507 |  | 17000 | Conductor | Overhead | Yes | 42554.625 | 2016-07-03 15:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0837 | 2016 | 7 | 3 | 15 | 0 | 16-0047689 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38812 | 10.6263 | 226_241 | <25mph | <15mph | HFTD - Distribution | 2016-07-03 15:00:00 | 580 | 12.5395 | FALSE | <25mph | F0305 | 3.78 | 2017-12-18T23:00:00Z | 1.01 | 12 | < 25mph | MOUC1 | 7.53 | 2017-12-18T23:02:00Z | 8.99 | 13 | < 25mph | F0305 | 3.78 | 2017-12-18T23:00:00Z | 1.01 | 21 | < 25mph | MOUC1 | 7.53 | 2017-12-18T23:02:00Z | 8.99 | 22 | < 25mph
PG&E | 2015-05-09 13:10 | 2015-05-09 13:10 | 39.2343 | -121.2468 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100000103 | None | 21000 | Conductor | Overhead | Yes | 42133.5486 | 2015-05-09 13:10 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0311 | 2015 | 5 | 9 | 13 | 10 | 15-0033085 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 382926 | 12.172 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 13:10:00 | 57 | 17.071 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6355 | 7.8 | 2019-04-19T21:33:00Z | 8.99 | 12 | < 25mph |  |  |  | 0 | 0 | No data | E6355 | 7.8 | 2019-04-19T22:24:00Z | 14.99 | 24 | < 25mph
PG&E | 2019-09-13 | 6:30 | 37.3348 | -121.7716 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 83392110 |  | 21000 | Splice/Clamp/Connector | Overhead | Yes | 43721 | 6:30 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-444 | 2019 | 9 | 13 | 6 | 30 | 19-0098560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 35534 | 3.3882 | 166_202 | <25mph | <15mph | HFTD - Distribution | 2019-09-13 06:30:00 | 2037 | 14.1926 | FALSE | <25mph | UCBO | 3.77 | 2017-11-23T16:40:00Z | 5.3 | 23 | < 25mph | MIPC1 | 7.48 | 2017-11-23T17:19:00Z | 5.99 | 95 | < 25mph | UCBO | 3.77 | 2017-11-23T17:30:00Z | 7.4 | 47 | < 25mph | UCBO | 3.77 | 2017-11-23T17:30:00Z | 7.4 | 191 | < 25mph
PG&E | 2018-09-06 | 16:19 | 39.0904 | -120.9464 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 100020676 | Unknown | 12000 | Conductor | Overhead | Yes | 43349 | 16:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1886 | 2018 | 9 | 6 | 16 | 19 | 18-0077280 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 30780 | 10.0605 | 202_299 | <25mph | <15mph | HFTD - Distribution | 2018-09-06 16:19:00 | 1625 | 12.3694 | FALSE | <25mph | AT999 | 2.11 | 2017-01-10T04:28:00Z | 14 | 18 | < 25mph | C5488 | 4.54 | 2017-01-10T04:59:00Z | 23 | 52 | < 25mph | AT999 | 2.11 | 2017-01-10T05:18:00Z | 18.01 | 34 | < 25mph | SETC1 | 7.26 | 2017-01-10T05:28:00Z | 31 | 105 | 25-40mph
PG&E | 2018-07-21 | 14:51 | 35.6846 | -120.9427 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101943190 | Unknown | 21000 | Conductor | Overhead | Yes | 43302 | 14:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1775 | 2018 | 7 | 21 | 14 | 51 | 18-0062364 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 110814 | 14.9597 | 202_111 | <25mph | <15mph | HFTD - Distribution | 2018-07-21 14:51:00 | 1515 | 21.9627 | FALSE | <25mph | TABC1 | 2.21 | 2015-01-04T21:07:00Z | 8.99 | 1 | < 25mph | TABC1 | 2.21 | 2015-01-04T21:07:00Z | 8.99 | 5 | < 25mph | TABC1 | 2.21 | 2015-01-04T21:07:00Z | 8.99 | 2 | < 25mph | TABC1 | 2.21 | 2015-01-04T21:07:00Z | 8.99 | 10 | < 25mph
PG&E | 2018-10-24 | 14:18 | 36.7265 | -119.1086 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CHRIS CHRISTOPHERSON (559)493-4320 I.C #18CAFKUO15649 | 100691946 | None | 12000 | Conductor | Overhead | Yes | 43397 | 14:18 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1950 | 2018 | 10 | 24 | 14 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 7.8375 | 283_170 | <25mph | <15mph | HFTD - Distribution | 2018-10-24 14:18:00 | 1689 | 7.8887 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PHRC1 | 5.37 | 2018-07-31T05:58:00Z | 8.99 | 18 | < 25mph |  |  |  | 0 | 0 | No data | PHRC1 | 5.37 | 2018-07-31T06:58:00Z | 10 | 35 | < 25mph
PG&E | 2015-02-06 06:01 | 2015-02-06 06:01 | 38.6059 | -121.0221 | Vegetation | Rural | < 3 meters | Fire Agency |  | 6661 Ryan Ranch Road, El Dorado Hills |  | 21000 | Conductor | Overhead | Yes | 42041.2507 | 2015-02-06 06:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0259 | 2015 | 2 | 6 | 6 | 1 | 15-0009876 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 51996 | 16.7927 | 199_272 | <25mph | <15mph | HFTD - Distribution | 2015-02-06 06:01:00 | 6 | 30.3484 | FALSE | 25-40mph | E8856 | 3.45 | 2018-10-24T02:15:00Z | 0 | 13 | < 25mph | BENC1 | 4.89 | 2018-10-24T01:59:00Z | 5.99 | 78 | < 25mph | E8856 | 3.45 | 2018-10-24T03:15:00Z | 0 | 25 | < 25mph | BENC1 | 4.89 | 2018-10-24T02:59:00Z | 5.99 | 160 | < 25mph
PG&E | 2015-11-15 16:30 | 2015-11-15 16:30 | 37.0007 | -121.885 | Vegetation | Rural | < 3 meters | Customer |  | 101691004 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42323.6875 | 2015-11-15 16:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0676 | 2015 | 11 | 15 | 16 | 30 | 15-0077978 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 25920 | 24.6094 | 161_184 | <25mph | <15mph | HFTD - Distribution | 2015-11-15 16:30:00 | 420 | 25.3186 | FALSE | 25-40mph | E7291 | 2.82 | 2017-10-05T13:36:00Z | 8.01 | 40 | < 25mph | E7291 | 2.82 | 2017-10-05T13:36:00Z | 8.01 | 116 | < 25mph | E7291 | 2.82 | 2017-10-05T14:21:00Z | 8.01 | 80 | < 25mph | E7291 | 2.82 | 2017-10-05T14:21:00Z | 8.01 | 235 | < 25mph
PG&E | 2015-07-18 17:00 | 2015-07-18 17:00 | 38.8383 | -123.6297 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | off HWY 1 PA |  | 12000 | Conductor | Overhead | Yes | 42203.7083 | 2015-07-18 17:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0470 | 2015 | 7 | 18 | 17 | 0 | 15-0048394 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 51806 | 18.0824 | 86_287 | <25mph | <15mph | HFTD - Distribution | 2015-07-18 17:00:00 | 215 | 27.3037 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | ANVC1 | 6.68 | 2017-03-15T12:48:00Z | 7 | 11 | < 25mph |  |  |  | 0 | 0 | No data | ANVC1 | 6.68 | 2017-03-15T13:18:00Z | 7 | 21 | < 25mph
PG&E | 2017-08-08 20:35 | 20:35 | 37.2637 | -119.7103 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TROY CHEEK1-209-966-3621 | 103793352 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42955.8578 | 20:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1327 | 2017 | 8 | 8 | 20 | 35 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.9357 | 256_199 | <25mph | <15mph | HFTD - Distribution | 2017-08-08 20:35:00 | 1065 | 11.9714 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D7778 | 4.64 | 2017-08-10T17:57:00Z | 12.01 | 38 | < 25mph |  |  |  | 0 | 0 | No data | AT301 | 5.87 | 2017-08-10T19:47:00Z | 14.99 | 76 | < 25mph
PG&E | 2016-08-03 | 2016-08-03 04:38 | 38.8474 | -120.812 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire garden valley fire | 103809676 |  | 21000 | Conductor | Overhead | Yes | 42585 | 2016-08-03 04:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0901 | 2016 | 8 | 3 | 4 | 38 | 16-0054597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2751 | 9.4989 | 208_286 | <25mph | <15mph | HFTD - Distribution | 2016-08-03 04:38:00 | 644 | 11.5219 | FALSE | <25mph | PG022 | 1.4 | 2019-12-23T13:50:00Z | 0 | 12 | < 25mph | PG481 | 7.16 | 2019-12-23T13:50:00Z | 6.8 | 61 | < 25mph | PG022 | 1.4 | 2019-12-23T14:30:00Z | 1.97 | 24 | < 25mph | PG481 | 7.16 | 2019-12-23T13:50:00Z | 6.8 | 122 | < 25mph
PG&E | 2015-06-12 23:32 | 2015-06-12 23:32 | 39.2308 | -121.1559 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 10903 PROSPECTOR RD ROUGH AND READY | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42167.9806 | 2015-06-12 23:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0380 | 2015 | 6 | 12 | 23 | 32 | 15-0040789 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 20 | 12.2901 | 193_307 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 23:32:00 | 126 | 14.4252 | FALSE | <25mph | E6355 | 3.14 | 2016-09-05T10:51:00Z | 0 | 18 | < 25mph | RRRC1 | 5.44 | 2016-09-05T10:13:00Z | 5.99 | 65 | < 25mph | E6355 | 3.14 | 2016-09-05T11:51:00Z | 0 | 33 | < 25mph | RRRC1 | 5.44 | 2016-09-05T11:13:00Z | 5.99 | 127 | < 25mph
PG&E | 2016-06-20 | 2016-06-20 16:45 | 41.0697 | -123.6789 | Vegetation | RURAL | < 3 meters | Fire Agency | Hoopa FD | 101011420 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42541 | 2016-06-20 16:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0811 | 2016 | 6 | 20 | 16 | 45 | 16-0044577 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7361 | 15.1157 | 88_410 | <25mph | <15mph | HFTD - Distribution | 2016-06-20 16:45:00 | 554 | 15.1157 | FALSE | <25mph | BIIC1 | 2.95 | 2019-08-03T13:40:00Z | 7 | 8 | < 25mph | BIIC1 | 2.95 | 2019-08-03T13:40:00Z | 7 | 8 | < 25mph | BIIC1 | 2.95 | 2019-08-03T13:40:00Z | 7 | 16 | < 25mph | BIIC1 | 2.95 | 2019-08-03T13:40:00Z | 7 | 16 | < 25mph
PG&E | 2015-07-04 01:14 | 2015-07-04 01:14 | 38.9566 | -121.0434 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100037226 |  | 12000 | Other | Overhead | Yes | 42189.0514 | 2015-07-04 01:14 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0441 | 2015 | 7 | 4 | 1 | 14 | 15-0045440 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 53865 | 7.3476 | 198_292 | <25mph | <15mph | HFTD - Distribution | 2015-07-04 01:14:00 | 186 | 12.3228 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8862 | 5.23 | 2016-07-28T19:01:00Z | 7 | 23 | < 25mph |  |  |  | 0 | 0 | No data | D8862 | 5.23 | 2016-07-28T20:02:00Z | 7 | 45 | < 25mph
PG&E | 2017-10-09 | 1:02 | 38.7037 | -120.6725 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101408485 | Unknown | 21000 | Other | Overhead | Yes | 43017 | 1:02 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1473 | 2017 | 10 | 9 | 1 | 2 | 17-0085324 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 419843 | 26.702 | 214_278 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-10-09 01:02:00 | 1216 | 29.779 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E3165 | 7.84 | 2015-01-17T06:38:00Z | 2.01 | 23 | < 25mph |  |  |  | 0 | 0 | No data | E3165 | 7.84 | 2015-01-17T07:38:00Z | 2.01 | 44 | < 25mph
PG&E | 2019-06-19 | 11:44 | 39.8612 | -121.6907 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100400933 |  | 12000 | Conductor | Overhead | Yes | 43635 | 11:44 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-224 | 2019 | 6 | 19 | 11 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.9144 | 170_342 | <25mph | <15mph | HFTD - Distribution | 2019-06-19 11:44:00 | 1855 | 12.1329 | FALSE | <25mph | C8878 | 2.27 | 2016-08-12T07:58:00Z | 0 | 10 | < 25mph | CSTC1 | 4.21 | 2016-08-12T07:51:00Z | 12.01 | 13 | < 25mph | C8878 | 2.27 | 2016-08-12T08:53:00Z | 0 | 19 | < 25mph | CSTC1 | 4.21 | 2016-08-12T07:51:00Z | 12.01 | 26 | < 25mph
PG&E | 2015-12-03 12:10 | 2015-12-03 12:10 | 40.0277 | -120.9652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | usfs | spanish creek campground |  | 12000 | Conductor | Overhead | Yes | 42341.5069 | 2015-12-03 12:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0683 | 2015 | 12 | 3 | 12 | 10 | 15-0082505 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 196854 | 26.293 | 201_351 | 25-40mph | 15-30mph | HFTD - Distribution | 2015-12-03 12:10:00 | 427 | 26.9543 | FALSE | 25-40mph | CHAC1 | 3.2 | 2016-08-30T07:47:00Z | 7 | 2 | < 25mph | CHAC1 | 3.2 | 2016-08-30T07:47:00Z | 7 | 3 | < 25mph | CHAC1 | 3.2 | 2016-08-30T07:47:00Z | 7 | 4 | < 25mph | CHAC1 | 3.2 | 2016-08-30T07:47:00Z | 7 | 6 | < 25mph
PG&E | 2018-07-01 | 0:23 | 40.2697 | -124.2386 | Vegetation | Rural | < 3 meters | Fire Agency | fire chief | 100986962 | Unknown | 12000 | Conductor | Overhead | Yes | 43282 | 0:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1718 | 2018 | 7 | 1 | 0 | 23 | 18-0056043 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 22872 | 20.9894 | 63_366 | <25mph | <15mph | HFTD - Distribution | 2018-07-01 00:23:00 | 1459 | 27.5371 | FALSE | 25-40mph | PTEC1 | 1.7 | 2019-04-19T10:08:00Z | 11.01 | 1 | < 25mph | PTEC1 | 1.7 | 2019-04-19T10:08:00Z | 11.01 | 1 | < 25mph | PTEC1 | 1.7 | 2019-04-19T10:08:00Z | 11.01 | 2 | < 25mph | PTEC1 | 1.7 | 2019-04-19T10:08:00Z | 11.01 | 2 | < 25mph
PG&E | 2018-07-30 | 14:36 | 38.1987 | -120.3638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NICK WEBB ( 209) 532-7424 | 103336176 | Unknown | 17000 | Conductor | Overhead | Yes | 43311 | 14:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1800 | 2018 | 7 | 30 | 14 | 36 | 18-0065131 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18530 | 10.5817 | 227_250 | <25mph | <15mph | HFTD - Distribution | 2018-07-30 14:36:00 | 1540 | 14.4256 | FALSE | <25mph | E8204 | 0 | 2017-04-12T18:38:00Z | 5.99 | 4 | < 25mph | E9838 | 7.59 | 2017-04-12T18:27:00Z | 15.99 | 19 | < 25mph | E8204 | 0 | 2017-04-12T19:28:00Z | 11.01 | 8 | < 25mph | E9838 | 7.59 | 2017-04-12T20:03:00Z | 15.99 | 35 | < 25mph
PG&E | 2017-05-15 16:14 | 16:00 | 37.1766 | -119.8189 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SHAUN FAIRBANKS 559-683-4823 | 101108423 | SIERRA | 21000 | Conductor | Overhead | Yes | 42870.6767 | 16:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1099 | 2017 | 5 | 15 | 16 | 0 | 17-0048096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20007 | 15.7465 | 251_194 | <25mph | <15mph | HFTD - Distribution | 2017-05-15 16:00:00 | 839 | 20.7849 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5766 | 4.44 | 2018-05-20T21:15:00Z | 10 | 13 | < 25mph |  |  |  | 0 | 0 | No data | E5766 | 4.44 | 2018-05-20T22:15:00Z | 11.01 | 25 | < 25mph
PG&E | 2017-07-12 20:22 | 20:21 | 40.0808 | -123.8339 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103841917 | Unknown | 12000 | Conductor | Overhead | Yes | 42928.8485 | 20:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1249 | 2017 | 7 | 12 | 20 | 21 | 17-0062445 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 4616 | 11.5535 | 80_355 | <25mph | <15mph | HFTD - Distribution | 2017-07-12 20:21:00 | 988 | 18.1059 | FALSE | <25mph | AV037 | 2.72 | 2019-12-07T00:33:00Z | 10 | 4 | < 25mph | PG282 | 7.95 | 2019-12-07T00:00:00Z | 35.52 | 19 | 25-40mph | AV037 | 2.72 | 2019-12-07T00:43:00Z | 11.01 | 7 | < 25mph | PG282 | 7.95 | 2019-12-07T00:00:00Z | 35.52 | 35 | 25-40mph
PG&E | 2019-08-12 | 20:06 | 39.0952 | -123.4937 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 102177212 |  | 12000 | Conductor | Overhead | Yes | 43689 | 20:06 | Vegetation |  | Veg. contact |  |  |  | Fell into (No defect) | 2019-400 | 2019 | 8 | 12 | 20 | 6 | 19-0087090 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2508 | 13.5331 | 93_301 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 20:06:00 | 1970 | 19.4805 | FALSE | <25mph | E1763 | 1.72 | 2016-12-25T11:48:00Z | 4.99 | 5 | < 25mph | E1763 | 1.72 | 2016-12-25T11:48:00Z | 4.99 | 5 | < 25mph | E1763 | 1.72 | 2016-12-25T12:03:00Z | 4.99 | 9 | < 25mph | E1763 | 1.72 | 2016-12-25T12:03:00Z | 4.99 | 9 | < 25mph
PG&E | 2018-06-08 | 19:03 | 35.154 | -120.594 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101852092 | AT&T | 12000 | Conductor | Overhead | Yes | 43259 | 19:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1644 | 2018 | 6 | 8 | 19 | 3 | 18-0049130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2473 | 24.0333 | 218_82 | <25mph | <15mph | HFTD - Distribution | 2018-06-08 19:03:00 | 1386 | 25.9327 | FALSE | 25-40mph | C9687 | 2.18 | 2019-03-25T14:55:00Z | 5.99 | 29 | < 25mph | PG168 | 7.7 | 2019-03-25T15:40:00Z | 6.58 | 43 | < 25mph | C9687 | 2.18 | 2019-03-25T14:55:00Z | 5.99 | 59 | < 25mph | PG168 | 7.7 | 2019-03-25T15:40:00Z | 6.58 | 88 | < 25mph
PG&E | 2018-08-08 | 16:03 | 37.2974 | -122.2651 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 100307515 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 16:03 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1831 | 2018 | 8 | 8 | 16 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.1654 | 144_201 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:03:00 | 1570 | 9.1654 | FALSE | <25mph | LAHC1 | 0.77 | 2017-08-03T18:07:00Z | 5.99 | 1 | < 25mph | LOAC1 | 7.85 | 2017-08-03T18:10:00Z | 5.99 | 18 | < 25mph | LAHC1 | 0.77 | 2017-08-03T18:07:00Z | 5.99 | 2 | < 25mph | C6623 | 7.36 | 2017-08-03T19:33:00Z | 7 | 37 | < 25mph
PG&E | 2015-08-30 17:05 | 2015-08-30 17:05 | 38.4039 | -120.5559 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | centennial mine rd |  | 12000 | Conductor | Overhead | Yes | 42246.7118 | 2015-08-30 17:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0567 | 2015 | 8 | 30 | 17 | 5 | 15-0058273 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 40298 | 10.8566 | 219_261 | <25mph | <15mph | HFTD - Distribution | 2015-08-30 17:05:00 | 311 | 12.2451 | FALSE | <25mph | AT450 | 1.93 | 2016-12-24T22:54:00Z | 8.01 | 12 | < 25mph | C9148 | 6.15 | 2016-12-24T22:18:00Z | 13 | 28 | < 25mph | AT450 | 1.93 | 2016-12-24T23:04:00Z | 10 | 24 | < 25mph | C9148 | 6.15 | 2016-12-24T23:03:00Z | 13 | 55 | < 25mph
PG&E | 2018-05-19 | 19:44 | 40.2665 | -122.2727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103899310 | Unknown | 12000 | Conductor | Overhead | Yes | 43239 | 19:44 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1599 | 2018 | 5 | 19 | 19 | 44 | 18-0042559 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 31980 | 15.59 | 146_364 | <25mph | <15mph | HFTD - Distribution | 2018-05-19 19:44:00 | 1341 | 18.253 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 7.1 | 2019-01-05T05:01:00Z | 5.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 7.1 | 2019-01-05T05:01:00Z | 5.99 | 8 | < 25mph
PG&E | 2016-08-07 | 2016-08-07 14:20 | 37.2316 | -122.1552 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire/woodside fire | 103413747 |  | 12000 | Conductor | Overhead | Yes | 42589 | 2016-08-07 14:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0910 | 2016 | 8 | 7 | 14 | 20 | 16-0055597 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29869 | 12.3369 | 149_197 | <25mph | <15mph | HFTD - Distribution | 2016-08-07 14:20:00 | 653 | 12.9748 | FALSE | <25mph | E6800 | 0.63 | 2018-01-31T02:01:00Z | 3 | 16 | < 25mph | BNDC1 | 7.02 | 2018-01-31T01:50:00Z | 8.01 | 60 | < 25mph | E6800 | 0.63 | 2018-01-31T02:16:00Z | 4 | 32 | < 25mph | BNDC1 | 7.02 | 2018-01-31T02:50:00Z | 10 | 120 | < 25mph
PG&E | 2015-06-12 23:32 | 2015-06-12 23:32 | 39.2308 | -121.1559 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 10903 PROSPECTOR RD ROUGH AND READY | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42167.9806 | 2015-06-12 23:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0380 | 2015 | 6 | 12 | 23 | 32 | 15-0040789 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 20 | 12.2901 | 193_307 | <25mph | <15mph | HFTD - Distribution | 2015-06-12 23:32:00 | 126 | 14.4252 | FALSE | <25mph | E2572 | 1.63 | 2016-05-26T04:08:00Z | 3 | 18 | < 25mph | E5439 | 5.49 | 2016-05-26T04:25:00Z | 8.01 | 53 | < 25mph | E2572 | 1.63 | 2016-05-26T04:08:00Z | 3 | 36 | < 25mph | E5439 | 5.49 | 2016-05-26T04:30:00Z | 8.01 | 106 | < 25mph
PG&E | 2015-06-15 15:35 | 2015-06-15 15:35 | 37.1852 | -121.7595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Jose city | 100618215 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42170.6493 | 2015-06-15 15:35 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0384 | 2015 | 6 | 15 | 15 | 35 | 15-0041178 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 345 | 20.7397 | 166_194 | <25mph | <15mph | HFTD - Distribution | 2015-06-15 15:35:00 | 130 | 21.599 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C9520 | 5.63 | 2016-05-08T22:30:00Z | 8.01 | 63 | < 25mph |  |  |  | 0 | 0 | No data | E5617 | 5.37 | 2016-05-08T23:57:00Z | 11.01 | 118 | < 25mph
PG&E | 2015-05-27 21:44 | 2015-05-27 21:44 | 39.169 | -120.9612 | Vegetation | Rural | < 0.25 Acres | Fire Agency | PEARDALE F.D. | 100077687 |  | 12000 | Conductor | Overhead | Yes | 42151.9056 | 2015-05-27 21:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0329 | 2015 | 5 | 27 | 21 | 44 | 15-0036850 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10828 | 3.691 | 201_303 | <25mph | <15mph | HFTD - Distribution | 2015-05-27 21:44:00 | 75 | 11.9096 | FALSE | <25mph | PG059 | 2.56 | 2018-10-26T20:40:00Z | 10.09 | 7 | < 25mph | PG059 | 2.56 | 2018-10-26T20:40:00Z | 10.09 | 68 | < 25mph | PG059 | 2.56 | 2018-10-26T20:40:00Z | 10.09 | 13 | < 25mph | PG059 | 2.56 | 2018-10-26T20:40:00Z | 10.09 | 138 | < 25mph
PG&E | 2018-08-21 | 10:13 | 38.6972 | -120.889 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101385436 | Unknown | 12000 | Conductor | Overhead | Yes | 43333 | 10:13 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1852 | 2018 | 8 | 21 | 10 | 13 | 18-0072055 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4572 | 5.9109 | 204_277 | <25mph | <15mph | HFTD - Distribution | 2018-08-21 10:13:00 | 1591 | 12.0437 | FALSE | <25mph | D2736 | 1.65 | 2015-12-08T13:05:00Z | 0 | 14 | < 25mph | BENC1 | 7.73 | 2015-12-08T12:59:00Z | 5.99 | 48 | < 25mph | D2736 | 1.65 | 2015-12-08T13:45:00Z | 1.01 | 28 | < 25mph | BENC1 | 7.73 | 2015-12-08T13:59:00Z | 5.99 | 96 | < 25mph
PG&E | 2018-08-08 | 16:03 | 37.2974 | -122.2651 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 100307515 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 16:03 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1831 | 2018 | 8 | 8 | 16 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.1654 | 144_201 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:03:00 | 1570 | 9.1654 | FALSE | <25mph | LAHC1 | 0.77 | 2016-08-24T01:07:00Z | 7 | 1 | < 25mph | LOAC1 | 7.85 | 2016-08-24T01:10:00Z | 8.01 | 24 | < 25mph | LAHC1 | 0.77 | 2016-08-24T01:07:00Z | 7 | 2 | < 25mph | E2649 | 7.57 | 2016-08-24T01:34:00Z | 14 | 48 | < 25mph
PG&E | 2015-03-04 18:44 | 2015-03-04 18:44 | 38.9995 | -122.7545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kelseyville FD | 102156367 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42067.7806 | 2015-03-04 18:44 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0271 | 2015 | 3 | 4 | 18 | 44 | 15-0017374 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29532 | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2015-03-04 18:44:00 | NA | 0 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.58 | 2019-05-18T23:57:00Z | 21 | 22 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.58 | 2019-05-18T23:57:00Z | 21 | 44 | < 25mph
PG&E | 2017-07-19 | 5:52 | 37.0905 | -119.6047 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Tower 003/001 | Unknown | 115000 | Conductor | Overhead | Yes | 42935 | 5:52 | Contact From Object | N.A. | Other | Electric Facility | Unknown |  | no-match | 1269 | 2017 | 7 | 19 | 5 | 52 | INT-09877 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 0 | 0.36815 | 261_189 | <25mph | <15mph | HFTD - Transmission | 2017-07-19 05:52:00 | 1008 | 14.3689 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PRHC1 | 5.59 | 2018-12-06T08:27:00Z | 4 | 1 | < 25mph |  |  |  | 0 | 0 | No data | PRHC1 | 5.59 | 2018-12-06T09:27:00Z | 8.01 | 2 | < 25mph
PG&E | 2018-07-21 | 14:51 | 35.6846 | -120.9427 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101943190 | Unknown | 21000 | Conductor | Overhead | Yes | 43302 | 14:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1775 | 2018 | 7 | 21 | 14 | 51 | 18-0062364 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 110814 | 14.9597 | 202_111 | <25mph | <15mph | HFTD - Distribution | 2018-07-21 14:51:00 | 1515 | 21.9627 | FALSE | <25mph | TABC1 | 2.21 | 2018-02-18T13:07:00Z | 2.01 | 1 | < 25mph | TABC1 | 2.21 | 2018-02-18T13:07:00Z | 2.01 | 17 | < 25mph | TABC1 | 2.21 | 2018-02-18T14:07:00Z | 2.01 | 2 | < 25mph | D4060 | 5.73 | 2018-02-18T13:44:00Z | 2.01 | 34 | < 25mph
PG&E | 2019-09-15 | 12:38 | 38.1194 | -120.8013 | Vehicle | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103959405 |  | 12000 | Pole | Overhead | Yes | 43723 | 12:38 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-118 | 2019 | 9 | 15 | 12 | 38 | 19-0099234 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 5378 | 7.5852 | 208_246 | <25mph | <15mph | HFTD - Distribution | 2019-09-15 12:38:00 | 2043 | 14.1961 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-06-27 | 18:46 | 40.218 | -123.7989 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TJ alderpoint fire | 100990381 | Unknown | 12000 | Conductor | Overhead | Yes | 43278 | 18:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1700 | 2018 | 6 | 27 | 18 | 46 | 18-0055205 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 21357 | 17.7599 | 81_363 | <25mph | <15mph | HFTD - Distribution | 2018-06-27 18:46:00 | 1441 | 20.5507 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ERCC1 | 5.65 | 2018-11-22T04:28:00Z | 8.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | ERCC1 | 5.65 | 2018-11-22T05:28:00Z | 8.99 | 2 | < 25mph
PG&E | 2018-09-27 | 12:43 | 38.5148 | -122.4463 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Twr 000/010 | None | 60000 | Conductor | Overhead | Yes | 43370 | 12:43 | Contact From Object | N.A. | Other | Electric Facility | Human Error | helicopter | no-match | 1917 | 2018 | 9 | 27 | 12 | 43 | INT-11394 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1488992 | 4.4433 | 137_268 | <25mph | <15mph | HFTD - Transmission | 2018-09-27 12:43:00 | 1656 | 10.4879 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TR110 | 4.13 | 2018-06-06T00:49:00Z | 10 | 1 | < 25mph |  |  |  | 0 | 0 | No data | TR110 | 4.13 | 2018-06-06T01:49:00Z | 10 | 2 | < 25mph
PG&E | 2019-07-27 | 8:22 | 40.3789 | -122.1873 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Self Extinguished |  | 103461102 |  | 12000 | Conductor | Overhead | Yes | 43673 | 8:22 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-382 | 2019 | 7 | 27 | 8 | 22 | 19-0081756 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 456 | 4.4493 | 149_370 | <25mph | <15mph | HFTD - Distribution | 2019-07-27 08:22:00 | 1935 | 12.5056 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AP525 | 5.17 | 2017-04-10T22:25:00Z | 8.01 | 5 | < 25mph |  |  |  | 0 | 0 | No data | AP525 | 5.17 | 2017-04-10T22:25:00Z | 8.01 | 11 | < 25mph
PG&E | 2015-10-16 09:43 | 2015-10-16 09:43 | 39.187 | -123.2015 | Vegetation | Rural | < 3 meters | Unknown |  | 102196855 |  | 12000 | Conductor | Overhead | Yes | 42293.4049 | 2015-10-16 09:43 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0653 | 2015 | 10 | 16 | 9 | 43 | 15-0070948 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 65228 | 2.2696 | 105_305 | <25mph | <15mph | HFTD - Distribution | 2015-10-16 09:43:00 | 397 | 16.8813 | FALSE | <25mph | E7513 | 1.34 | 2015-09-29T10:58:00Z | 1.01 | 12 | < 25mph | E7513 | 1.34 | 2015-09-29T10:58:00Z | 1.01 | 25 | < 25mph | E7513 | 1.34 | 2015-09-29T12:18:00Z | 1.01 | 24 | < 25mph | E7513 | 1.34 | 2015-09-29T12:18:00Z | 1.01 | 49 | < 25mph
PG&E | 2019-06-06 | 20:30 | 38.4969 | -122.6435 |  | Barren/Other | < 1 meter | Self Extinguished |  | Unknown |  | 230000 | Circuit Breaker | Overhead | Yes | 43622 | 20:30 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | no-match | 2019-102 | 2019 | 6 | 6 | 20 | 30 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 16.883 | 129_267 | <25mph | <15mph | HFTD - Transmission | 2019-06-06 20:30:00 | 1804 | 23.129 | FALSE | <25mph | RSAC1 | 3.91 | 2016-08-06T02:29:00Z | 13 | 15 | < 25mph | RSAC1 | 3.91 | 2016-08-06T02:29:00Z | 13 | 73 | < 25mph | RSAC1 | 3.91 | 2016-08-06T02:29:00Z | 13 | 27 | < 25mph | RSAC1 | 3.91 | 2016-08-06T02:29:00Z | 13 | 141 | < 25mph
PG&E | 2018-06-15 | 10:05 | 38.6238 | -121.0221 | Vegetation | Rural | < 3 meters | Customer | N.A. | 101376538 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43266 | 10:05 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1661 | 2018 | 6 | 15 | 10 | 5 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 10.3423 | 199_273 | <25mph | <15mph | HFTD - Distribution | 2018-06-15 10:05:00 | 1403 | 17.1425 | FALSE | <25mph | D4314 | 3.9 | 2015-04-22T03:48:00Z | 2.01 | 12 | < 25mph | BENC1 | 5.3 | 2015-04-22T03:59:00Z | 7 | 46 | < 25mph | D4314 | 3.9 | 2015-04-22T03:48:00Z | 2.01 | 24 | < 25mph | BENC1 | 5.3 | 2015-04-22T04:59:00Z | 8.01 | 92 | < 25mph
PG&E | 2018-07-29 | 17:29 | 38.5777 | -120.8556 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101383255 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43310 | 17:29 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1797 | 2018 | 7 | 29 | 17 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.882 | 206_271 | <25mph | <15mph | HFTD - Distribution | 2018-07-29 17:29:00 | 1537 | 11.0812 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E8856 | 5.75 | 2017-06-07T16:35:00Z | 10 | 24 | < 25mph |  |  |  | 0 | 0 | No data | E8856 | 5.75 | 2017-06-07T17:40:00Z | 11.01 | 47 | < 25mph
PG&E | 2018-06-30 | 22:18 | 40.6043 | -122.24 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101469808 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43281 | 22:18 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1716 | 2018 | 6 | 30 | 22 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 10.6263 | 147_383 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 22:18:00 | 1457 | 24.79 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RRAC1 | 6.7 | 2016-09-04T00:24:00Z | 22.01 | 3 | < 25mph |  |  |  | 0 | 0 | No data | RRAC1 | 6.7 | 2016-09-04T00:24:00Z | 22.01 | 8 | < 25mph
PG&E | 2018-08-08 | 16:02 | 36.4703 | -121.7143 | Vegetation | Rural | < 3 meters | Customer | N.A. | 103910535 | None | 12000 | Conductor | Overhead | Yes | 43320 | 16:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1830 | 2018 | 8 | 8 | 16 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 14.7322 | 168_155 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:02:00 | 1569 | 15.5625 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2017-06-16 19:15 | 19:14 | 38.3443 | -122.7812 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101970801 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42902.8019 | 19:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1155 | 2017 | 6 | 16 | 19 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 20.0158 | 122_259 | <25mph | <15mph | HFTD - Distribution | 2017-06-16 19:14:00 | 894 | 22.0101 | FALSE | <25mph | AR323 | 3.41 | 2015-05-28T08:20:00Z | 0 | 6 | < 25mph | D9961 | 7.98 | 2015-05-28T08:13:00Z | 5.99 | 69 | < 25mph | AR323 | 3.41 | 2015-05-28T09:10:00Z | 1.01 | 12 | < 25mph | D9961 | 7.98 | 2015-05-28T08:13:00Z | 5.99 | 139 | < 25mph
PG&E | 2017-05-14 | 11:59 | 38.0798 | -122.8665 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102247059 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42869 | 11:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1095 | 2017 | 5 | 14 | 11 | 59 | 17-0047802 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 377483 | 24.3878 | 118_244 | <25mph | <15mph | HFTD - Distribution | 2017-05-14 11:59:00 | 835 | 24.3878 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PRWC1 | 4.65 | 2016-10-10T17:10:00Z | 11.83 | 13 | < 25mph |  |  |  | 0 | 0 | No data | PRWC1 | 4.65 | 2016-10-10T17:10:00Z | 11.83 | 26 | < 25mph
PG&E | 2017-07-11 22:13 | 22:12 | 37.0122 | -121.9497 | Vegetation | Rural | < 3 Meters | Fire Agency | CAPT PHIL CRAMBLET 831-479-6842 | 101676689 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42927.9254 | 22:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1244 | 2017 | 7 | 11 | 22 | 12 | 17-0062198 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 714 | 7.2694 | 158_185 | <25mph | <15mph | HFTD - Distribution | 2017-07-11 22:12:00 | 983 | 9.7577 | FALSE | <25mph | E9039 | 2.97 | 2018-04-01T21:58:00Z | 10 | 41 | < 25mph | UCYL | 7.78 | 2018-04-01T22:10:00Z | 22.01 | 148 | < 25mph | E9039 | 2.97 | 2018-04-01T23:23:00Z | 14 | 83 | < 25mph | UCYL | 7.78 | 2018-04-01T22:10:00Z | 22.01 | 298 | < 25mph
PG&E | 2015-10-31 07:45 | 2015-10-31 07:45 | 38.1157 | -120.8931 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal FIRE | 103763040 |  | 12000 | Conductor | Overhead | Yes | 42308.3229 | 2015-10-31 07:45 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0663 | 2015 | 10 | 31 | 7 | 45 | 15-0074424 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 314565 | 11.8471 | 204_245 | <25mph | <15mph | HFTD - Distribution | 2015-10-31 07:45:00 | 407 | 12.187 | FALSE | <25mph | PG375 | 2.03 | 2019-10-20T04:30:00Z | 7.38 | 6 | < 25mph | PG375 | 2.03 | 2019-10-20T04:30:00Z | 7.38 | 19 | < 25mph | PG375 | 2.03 | 2019-10-20T05:00:00Z | 9.86 | 12 | < 25mph | PG375 | 2.03 | 2019-10-20T05:00:00Z | 9.86 | 38 | < 25mph
PG&E | 2019-07-27 | 8:22 | 40.3789 | -122.1873 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Self Extinguished |  | 103461102 |  | 12000 | Conductor | Overhead | Yes | 43673 | 8:22 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-382 | 2019 | 7 | 27 | 8 | 22 | 19-0081756 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 456 | 4.4493 | 149_370 | <25mph | <15mph | HFTD - Distribution | 2019-07-27 08:22:00 | 1935 | 12.5056 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AP525 | 5.17 | 2016-05-15T03:35:00Z | 0 | 6 | < 25mph |  |  |  | 0 | 0 | No data | AP525 | 5.17 | 2016-05-15T04:25:00Z | 5.99 | 12 | < 25mph
PG&E | 2019-07-23 | 16:55 | 37.2128 | -119.505 | Gun Shot | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | 252521103 |  | 12000 | Conductor | Overhead | Yes | 43669 | 16:55 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-434 | 2019 | 7 | 23 | 16 | 55 | 19-0080383 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 513358 | 13.6168 | 265_196 | <25mph | <15mph | HFTD - Distribution | 2019-07-23 16:55:00 | 1923 | 13.6168 | FALSE | <25mph | NFRC1 | 1.4 | 2019-01-05T07:55:00Z | 8.01 | 2 | < 25mph | NFRC1 | 1.4 | 2019-01-05T07:55:00Z | 8.01 | 2 | < 25mph | NFRC1 | 1.4 | 2019-01-05T07:55:00Z | 8.01 | 3 | < 25mph | NFRC1 | 1.4 | 2019-01-05T07:55:00Z | 8.01 | 3 | < 25mph
PG&E | 2018-06-30 | 22:36 | 39.1141 | -121.077 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Matt Wallen (530) 277-3312 Incident # NEU015486 | 100105380 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 22:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1717 | 2018 | 6 | 30 | 22 | 36 | 18-0056039 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 8004 | 7.8488 | 196_300 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 22:36:00 | 1458 | 15.8656 | FALSE | <25mph | E1789 | 3.68 | 2017-02-15T19:18:00Z | 8.01 | 28 | < 25mph | E1789 | 3.68 | 2017-02-15T19:18:00Z | 8.01 | 70 | < 25mph | E1789 | 3.68 | 2017-02-15T19:18:00Z | 8.01 | 56 | < 25mph | E1789 | 3.68 | 2017-02-15T19:18:00Z | 8.01 | 143 | < 25mph
PG&E | 2015-07-18 17:00 | 2015-07-18 17:00 | 38.8383 | -123.6297 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | off HWY 1 PA |  | 12000 | Conductor | Overhead | Yes | 42203.7083 | 2015-07-18 17:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0470 | 2015 | 7 | 18 | 17 | 0 | 15-0048394 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 51806 | 18.0824 | 86_287 | <25mph | <15mph | HFTD - Distribution | 2015-07-18 17:00:00 | 215 | 27.3037 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | ANVC1 | 6.68 | 2019-08-20T05:48:00Z | 8.01 | 17 | < 25mph |  |  |  | 0 | 0 | No data | ANVC1 | 6.68 | 2019-08-20T06:54:00Z | 8.01 | 33 | < 25mph
PG&E | 2018-06-05 | 13:45 | 38.5432 | -122.7202 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 102031673 | Unknown | 12000 | Conductor | Overhead | Yes | 43256 | 13:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1633 | 2018 | 6 | 5 | 13 | 45 | 18-0047625 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 40599 | 7.3889 | 125_270 | <25mph | <15mph | HFTD - Distribution | 2018-06-05 13:45:00 | 1375 | 15.9614 | FALSE | <25mph | E1553 | 2.52 | 2016-11-07T21:14:00Z | 8.99 | 14 | < 25mph | RSAC1 | 4.49 | 2016-11-07T21:29:00Z | 11.01 | 83 | < 25mph | E1553 | 2.52 | 2016-11-07T21:14:00Z | 8.99 | 28 | < 25mph | RSAC1 | 4.49 | 2016-11-07T21:29:00Z | 11.01 | 163 | < 25mph
PG&E | 2018-11-16 | 17:02 | 38.7574 | -120.9012 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101409894 | AT&T | 21000 | Conductor | Overhead | Yes | 43420 | 17:02 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1976 | 2018 | 11 | 16 | 17 | 2 | 18-0100490 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 119860 | 5.5125 | 204_281 | <25mph | <15mph | HFTD - Distribution | 2018-11-16 17:02:00 | 1716 | 12.5682 | FALSE | <25mph | D2736 | 3.3 | 2018-05-04T04:20:00Z | 0 | 12 | < 25mph | PLTC1 | 7.76 | 2018-05-04T03:56:00Z | 4 | 60 | < 25mph | D2736 | 3.3 | 2018-05-04T05:20:00Z | 0 | 24 | < 25mph | PLTC1 | 7.76 | 2018-05-04T03:56:00Z | 4 | 109 | < 25mph
PG&E | 2019-06-03 | 14:47 | 40.4419 | -122.3036 |  | Herbaceous | 1 meter - < 3 meters | Fire Dept | Anderson FD | 101495889 |  | 12000 | Insulator | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-456 | 2019 | 6 | 3 | 14 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 9.9807 | 145_374 | <25mph | <15mph | HFTD - Distribution | 2019-06-03 14:47:00 | 1799 | 16.209 | FALSE | <25mph | AP525 | 3.17 | 2016-10-07T03:55:00Z | 0 | 6 | < 25mph | RRAC1 | 5.14 | 2016-10-07T03:24:00Z | 7 | 11 | < 25mph | AP525 | 3.17 | 2016-10-07T04:55:00Z | 0 | 12 | < 25mph | RRAC1 | 5.14 | 2016-10-07T04:24:00Z | 7 | 22 | < 25mph
PG&E | 2019-09-28 | 13:16 | 37.2553 | -119.5057 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 252531103 |  | 12000 | Conductor | Overhead | Yes | 43736 | 13:16 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-36 | 2019 | 9 | 28 | 13 | 16 | 19-0104972 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 1296 | 12.1111 | 265_198 | <25mph | <15mph | HFTD - Distribution | 2019-09-28 13:16:00 | 2064 | 13.545 | FALSE | <25mph | NFRC1 | 1.54 | 2018-04-28T18:55:00Z | 8.99 | 1 | < 25mph | AT344 | 5.5 | 2018-04-28T19:00:00Z | 11.01 | 36 | < 25mph | NFRC1 | 1.54 | 2018-04-28T19:55:00Z | 11.01 | 2 | < 25mph | D7778 | 7.57 | 2018-04-28T20:00:00Z | 11.01 | 67 | < 25mph
PG&E | 2017-07-24 19:31 | 19:31 | 38.3519 | -120.7103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.8134 | 19:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1288 | 2017 | 7 | 24 | 19 | 31 | 17-0065145 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14281 | 10.3402 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 19:31:00 | 1027 | 12.2366 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2015-01-13T08:56:00Z | 7 | 2 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2015-01-13T09:56:00Z | 11.01 | 3 | < 25mph
PG&E | 2016-07-28 08:12 | 2016-07-28 08:12 | 37.8207 | -120.1388 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101037043 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0884 | 2016 | 7 | 28 | 8 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 1.7128 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 08:12:00 | 627 | 11.4062 | FALSE | <25mph | SEWC1 | 2.5 | 2017-07-15T22:16:00Z | 18.01 | 5 | < 25mph | SEWC1 | 2.5 | 2017-07-15T22:16:00Z | 18.01 | 5 | < 25mph | SEWC1 | 2.5 | 2017-07-15T23:16:00Z | 18.01 | 10 | < 25mph | SEWC1 | 2.5 | 2017-07-15T23:16:00Z | 18.01 | 10 | < 25mph
PG&E | 2017-09-24 | 16:42 | 38.3869 | -122.9667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DOUG JONES | 101973946 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43002 | 16:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1432 | 2017 | 9 | 24 | 16 | 42 | 17-0081329 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 22574 | 19.6154 | 114_261 | <25mph | <15mph | HFTD - Distribution | 2017-09-24 16:42:00 | 1170 | 19.6154 | FALSE | <25mph | D2849 | 0.23 | 2016-07-15T10:14:00Z | 3 | 18 | < 25mph | UCBM | 7.15 | 2016-07-15T10:10:00Z | 15.5 | 76 | < 25mph | D2849 | 0.23 | 2016-07-15T11:14:00Z | 3 | 36 | < 25mph | UCBM | 7.15 | 2016-07-15T10:10:00Z | 15.5 | 153 | < 25mph
PG&E | 2017-04-28 16:21 | 15:49 | 38.7679 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chris paper fire investigator, 530/677-1868. incident #caaeuo11821 | 101409833 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42853.6815 | 15:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1077 | 2017 | 4 | 28 | 15 | 49 | 17-0043771 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 82614 | 19.7837 | 201_281 | <25mph | <15mph | HFTD - Distribution | 2017-04-28 15:49:00 | 817 | 25.4223 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | D7413 | 7.64 | 2015-03-02T19:52:00Z | 15.99 | 51 | < 25mph |  |  |  | 0 | 0 | No data | C6129 | 7.91 | 2015-03-02T20:59:00Z | 16.98 | 102 | < 25mph
PG&E | 2017-08-15 19:29 | 19:28 | 39.5037 | -121.2783 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 100396172 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42962.8116 | 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1335 | 2017 | 8 | 15 | 19 | 28 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.8405 | 188_322 | <25mph | <15mph | HFTD - Distribution | 2017-08-15 19:28:00 | 1073 | 9.7276 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PKCC1 | 4.51 | 2015-02-08T03:10:00Z | 17 | 1 | < 25mph |  |  |  | 0 | 0 | No data | PKCC1 | 4.51 | 2015-02-08T03:10:00Z | 17 | 2 | < 25mph
PG&E | 2015-04-04 16:49 | 2015-04-04 16:49 | 38.8824 | -122.5914 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 20748 Jerusalem Grade Road, Middletown |  | 12000 | Other | Overhead | Yes | 42098.7007 | 2015-04-04 16:49 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0285 | 2015 | 4 | 4 | 16 | 49 | 15-0024208 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 20448 | 16.9925 | 131_288 | <25mph | <15mph | HFTD - Distribution | 2015-04-04 16:49:00 | 31 | 19.3597 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5568 | 5.16 | 2015-12-26T13:54:00Z | 13 | 5 | < 25mph |  |  |  | 0 | 0 | No data | E5568 | 5.16 | 2015-12-26T15:24:00Z | 20 | 10 | < 25mph
PG&E | 2017-05-25 17:36 | 16:55 | 38.3986 | -122.9876 | Vegetation | Rural | < 3 Meters | Utility: PG&E | N.A. | 101974034 | Unknown | 12000 | Conductor | Overhead | Yes | 42880.7334 | 16:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1114 | 2017 | 5 | 25 | 16 | 55 | 17-0050815 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 2644 | 12.6436 | 114_262 | <25mph | <15mph | HFTD - Distribution | 2017-05-25 16:55:00 | 854 | 13.2306 | FALSE | <25mph | PG380 | 1.5 | 2019-07-04T01:50:00Z | 14.25 | 18 | < 25mph | BGAC1 | 6.79 | 2019-07-04T02:05:00Z | 34.99 | 78 | 25-40mph | PG380 | 1.5 | 2019-07-04T01:50:00Z | 14.25 | 36 | < 25mph | BGAC1 | 6.79 | 2019-07-04T02:05:00Z | 34.99 | 158 | 25-40mph
PG&E | 2017-08-29 | 12:49 | 37.4507 | -119.6454 | Vegetation | Rural | > 5000 Acres | Fire Agency | USFS | 101017368 | Unknown | 12000 | Conductor | Overhead | Yes | 2017-08-29 | 12:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1366 | 2017 | 8 | 29 | 12 | 49 | 17-0073823 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | 3rd Party | 3rd Party - Unknown | 5894785 | 7.4398 | 259_209 | <25mph | <15mph | HFTD - Distribution | 2017-08-29 12:49:00 | 1104 | 13.5545 | FALSE | <25mph | D0826 | 0.24 | 2015-05-15T12:01:00Z | 0 | 2 | < 25mph | MIAC1 | 5.9 | 2015-05-15T11:59:00Z | 5.99 | 30 | < 25mph | D0826 | 0.24 | 2015-05-15T13:01:00Z | 0 | 4 | < 25mph | MIAC1 | 5.9 | 2015-05-15T11:59:00Z | 5.99 | 59 | < 25mph
PG&E | 2017-07-28 19:21 | 19:20 | 35.7276 | -120.9903 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Luis Obispo CDF | 101945496 | None | 21000 | Conductor | Overhead | Yes | 42944.8062 | 19:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1295 | 2017 | 7 | 28 | 19 | 20 | 17-0066392 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 8300 | 11.4004 | 200_114 | <25mph | <15mph | HFTD - Distribution | 2017-07-28 19:20:00 | 1033 | 13.3732 | FALSE | <25mph | E9175 | 1.53 | 2018-12-04T00:00:00Z | 2.01 | 12 | < 25mph | PG169 | 6.35 | 2018-12-04T00:00:00Z | 9.64 | 29 | < 25mph | E9175 | 1.53 | 2018-12-04T00:00:00Z | 2.01 | 24 | < 25mph | PG169 | 6.35 | 2018-12-04T00:00:00Z | 9.64 | 58 | < 25mph
PG&E | 2015-08-13 03:46 | 2015-08-13 03:46 | 37.2072 | -119.7343 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 44365 SAVAGE RD COARSEGOLD |  | 21000 | Conductor | Overhead | Yes | 42229.1569 | 2015-08-13 03:46 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0526 | 2015 | 8 | 13 | 3 | 46 | 15-0054655 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 7600 | 7.8941 | 255_196 | <25mph | <15mph | HFTD - Distribution | 2015-08-13 03:46:00 | 270 | 10.403 | FALSE | <25mph | D7022 | 2.54 | 2015-05-08T23:12:00Z | 4.99 | 6 | < 25mph | E5766 | 4.34 | 2015-05-08T22:48:00Z | 5.99 | 18 | < 25mph | D7022 | 2.54 | 2015-05-09T00:02:00Z | 5.99 | 12 | < 25mph | E5766 | 4.34 | 2015-05-08T22:48:00Z | 5.99 | 36 | < 25mph
PG&E | 2019-06-06 | 9:01 | 35.6384 | -118.9687 | Bird Found | Herbaceous | 0.25 - 10 Acres | Fire Dept | Kern County FD | 100216096 |  | 21000 | Conductor | Overhead | No |  |  | Contact - Animal - Other |  | Animal contact |  | Animal Contact |  | no-match | 2019-228 | 2019 | 6 | 6 | 9 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 4.6796 | 291_110 | <25mph | <15mph | HFTD - Distribution | 2019-06-06 09:01:00 | 1803 | 21.162 | FALSE | <25mph | PG159 | 2.52 | 2018-12-22T21:20:00Z | 14.47 | 12 | < 25mph | PG159 | 2.52 | 2018-12-22T21:20:00Z | 14.47 | 12 | < 25mph | PG159 | 2.52 | 2018-12-22T22:20:00Z | 16.22 | 24 | < 25mph | PG159 | 2.52 | 2018-12-22T22:20:00Z | 16.22 | 24 | < 25mph
PG&E | 2016-09-18 | 14:33 | 37.1619 | -122.1347 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire & Boulder Creek Fire Dept. | 103410909 | Yes | 12000 | Conductor | Overhead | Yes | 42631 | 14:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0986 | 2016 | 9 | 18 | 14 | 33 | 16-0065437 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 54983 | 5.897 | 150_193 | <25mph | <15mph | HFTD - Distribution | 2016-09-18 14:33:00 | 728 | 11.3228 | FALSE | <25mph | BNDC1 | 2.99 | 2016-04-11T11:50:00Z | 4 | 21 | < 25mph | BNDC1 | 2.99 | 2016-04-11T11:50:00Z | 4 | 50 | < 25mph | BNDC1 | 2.99 | 2016-04-11T12:50:00Z | 4.99 | 42 | < 25mph | BNDC1 | 2.99 | 2016-04-11T12:50:00Z | 4.99 | 99 | < 25mph
PG&E | 2018-09-14 | 15:08 | 35.328 | -120.6982 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Sean Hernandez Cell # 805 903 3423 | 103400199 | Unknown | 12000 | Conductor | Overhead | Yes | 43357 | 15:08 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1898 | 2018 | 9 | 14 | 15 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 24.1105 | 213_92 | <25mph | <15mph | HFTD - Distribution | 2018-09-14 15:08:00 | 1637 | 24.1304 | FALSE | <25mph | ARGC1 | 2.05 | 2017-05-11T11:54:00Z | 4 | 1 | < 25mph | ARGC1 | 2.05 | 2017-05-11T11:54:00Z | 4 | 5 | < 25mph | ARGC1 | 2.05 | 2017-05-11T11:54:00Z | 4 | 2 | < 25mph | ARGC1 | 2.05 | 2017-05-11T11:54:00Z | 4 | 9 | < 25mph
PG&E | 2019-09-11 | 18:56 | 37.9937 | -122.137 | Bird Found | Hardwood Woodland | Other | Unknown |  | Unknown |  | 115000 | Other | Overhead | Yes | 43719 | 18:56 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-42 | 2019 | 9 | 11 | 18 | 56 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | N.A. | 16.9097 | 150_239 | <25mph | <15mph | HFTD - Transmission | 2019-09-11 18:56:00 | 2034 | 19.7995 | FALSE | <25mph | UPBC1 | 3.21 | 2017-02-18T23:18:00Z | 29.97 | 39 | 25-40mph | UPBC1 | 3.21 | 2017-02-18T23:18:00Z | 29.97 | 137 | 25-40mph | UPBC1 | 3.21 | 2017-02-19T00:36:00Z | 30.18 | 74 | 25-40mph | UPBC1 | 3.21 | 2017-02-19T00:36:00Z | 30.18 | 270 | 25-40mph
PG&E | 2017-05-25 15:05 | 15:05 | 36.5217 | -121.8473 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Buddy Bloxham 831-236-5659 | 101778611 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42880.6288 | 15:05 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1113 | 2017 | 5 | 25 | 15 | 5 | 17-0050761 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 13965 | 25.8899 | 162_158 | 25-40mph | 15-30mph | HFTD - Distribution | 2017-05-25 15:05:00 | 853 | 26.2648 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E8505 | 7.82 | 2016-03-06T04:14:00Z | 48 | 65 | 40-55mph |  |  |  | 0 | 0 | No data | E8505 | 7.82 | 2016-03-06T04:14:00Z | 48 | 126 | 40-55mph
PG&E | 2015-07-07 10:42 | 2015-07-07 10:42 | 39.1138 | -121.0655 | Vegetation | Rural | < 0.25 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42192.4458 | 2015-07-07 10:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0448 | 2015 | 7 | 7 | 10 | 42 | 15-0045985 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 46738 | 10.1548 | 197_300 | <25mph | <15mph | HFTD - Distribution | 2015-07-07 10:42:00 | 193 | 12.5396 | FALSE | <25mph | C5488 | 3.42 | 2015-07-02T14:24:00Z | 4 | 6 | < 25mph | E1789 | 4.22 | 2015-07-02T14:24:00Z | 8.01 | 70 | < 25mph | C5488 | 3.42 | 2015-07-02T16:05:00Z | 4.99 | 12 | < 25mph | E1789 | 4.22 | 2015-07-02T15:42:00Z | 8.99 | 128 | < 25mph
PG&E | 2016-07-25 15:32 | 2016-07-25 15:32 | 38.3522 | -120.7107 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42576.6472 | 2016-07-25 15:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0878 | 2016 | 7 | 25 | 15 | 32 | 16-0052398 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 19951 | 10.4912 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-25 15:32:00 | 621 | 14.4675 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2016-06-03T00:56:00Z | 10 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2016-06-03T00:56:00Z | 10 | 2 | < 25mph
PG&E | 2016-06-21 | 2016-06-21 16:53 | 38.4233 | -122.5448 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | KENWOOD FIRE XST | 102036904 | Yes | 0 – 750 | Conductor | Overhead | Yes | 42542 | 2016-06-21 16:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0814 | 2016 | 6 | 21 | 16 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 14.0146 | 133_263 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 16:53:00 | 556 | 14.0381 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2362 | 7.21 | 2016-04-14T15:27:00Z | 3 | 17 | < 25mph |  |  |  | 0 | 0 | No data | E1582 | 5.25 | 2016-04-14T16:33:00Z | 5.99 | 32 | < 25mph
PG&E | 2017-11-20 08:33 | 08:32 | 38.7584 | -120.8439 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101389405 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43059.3562 | 08:32 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1522 | 2017 | 11 | 20 | 8 | 32 | 17-0096436 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 12376 | 9.7427 | 206_281 | <25mph | <15mph | HFTD - Distribution | 2017-11-20 08:32:00 | 1264 | 12.0384 | FALSE | <25mph | E5691 | 2.94 | 2015-06-20T00:10:00Z | 8.99 | 12 | < 25mph | E5691 | 2.94 | 2015-06-20T00:10:00Z | 8.99 | 46 | < 25mph | E5691 | 2.94 | 2015-06-20T00:10:00Z | 8.99 | 24 | < 25mph | E5691 | 2.94 | 2015-06-20T00:10:00Z | 8.99 | 90 | < 25mph
PG&E | 2019-07-19 | 11:59 | 37.9162 | -120.349 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 163351703 |  | 17000 | Conductor | Overhead | Yes | 43665 | 11:59 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-376 | 2019 | 7 | 19 | 11 | 59 | 19-0079030 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24042 | 10.7946 | 228_234 | <25mph | <15mph | HFTD - Distribution | 2019-07-19 11:59:00 | 1915 | 10.8841 | FALSE | <25mph | C3161 | 3.6 | 2015-03-23T03:30:00Z | 14 | 4 | < 25mph | C3161 | 3.6 | 2015-03-23T03:30:00Z | 14 | 4 | < 25mph | C3161 | 3.6 | 2015-03-23T03:30:00Z | 14 | 8 | < 25mph | C3161 | 3.6 | 2015-03-23T03:30:00Z | 14 | 8 | < 25mph
PG&E | 2017-08-30 | 22:37 | 38.9993 | -120.9887 | Vegetation | Rural | < 3 Meters | Fire Agency | Andy 530-889-0111 | 100026238 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42977 | 22:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1370 | 2017 | 8 | 30 | 22 | 37 | 17-0074333 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 3750 | 7.3126 | 200_294 | <25mph | <15mph | HFTD - Distribution | 2017-08-30 22:37:00 | 1108 | 12.9461 | FALSE | <25mph | C0713 | 3.13 | 2017-09-06T21:54:00Z | 10 | 20 | < 25mph | C5488 | 5.56 | 2017-09-06T21:25:00Z | 14.99 | 33 | < 25mph | C0713 | 3.13 | 2017-09-06T22:21:00Z | 10 | 37 | < 25mph | C5488 | 5.56 | 2017-09-06T21:25:00Z | 14.99 | 62 | < 25mph
PG&E | 2015-07-04 01:14 | 2015-07-04 01:14 | 38.9566 | -121.0434 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100037226 |  | 12000 | Other | Overhead | Yes | 42189.0514 | 2015-07-04 01:14 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0441 | 2015 | 7 | 4 | 1 | 14 | 15-0045440 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 53865 | 7.3476 | 198_292 | <25mph | <15mph | HFTD - Distribution | 2015-07-04 01:14:00 | 186 | 12.3228 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8862 | 5.23 | 2018-10-06T11:24:00Z | 3 | 26 | < 25mph |  |  |  | 0 | 0 | No data | D8862 | 5.23 | 2018-10-06T12:40:00Z | 4 | 47 | < 25mph
PG&E | 2016-10-11 23:17 | 23:16 | 39.0201 | -120.8294 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire.foresthill fire | 100025501 |  | 60000 | Conductor | Overhead | Yes | 42654.9701 | 23:16 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error |  | no-match | 1028 | 2016 | 10 | 11 | 23 | 16 | INT-08640 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 0 | 7.6312 | 207_295 | <25mph | <15mph | HFTD - Transmission | 2016-10-11 23:16:00 | 769 | 11.1078 | FALSE | <25mph | AU268 | 0.89 | 2015-01-10T03:59:00Z | 1.01 | 6 | < 25mph | FSHC1 | 7.19 | 2015-01-10T04:33:00Z | 4 | 13 | < 25mph | AU268 | 0.89 | 2015-01-10T05:02:00Z | 1.01 | 9 | < 25mph | FSHC1 | 7.19 | 2015-01-10T05:33:00Z | 4.99 | 23 | < 25mph
PG&E | 2017-07-12 20:22 | 20:21 | 40.0808 | -123.8339 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103841917 | Unknown | 12000 | Conductor | Overhead | Yes | 42928.8485 | 20:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1249 | 2017 | 7 | 12 | 20 | 21 | 17-0062445 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 4616 | 11.5535 | 80_355 | <25mph | <15mph | HFTD - Distribution | 2017-07-12 20:21:00 | 988 | 18.1059 | FALSE | <25mph | AV037 | 2.72 | 2019-10-07T21:53:00Z | 4.99 | 4 | < 25mph | PG282 | 7.95 | 2019-10-07T21:20:00Z | 11.41 | 17 | < 25mph | AV037 | 2.72 | 2019-10-07T22:43:00Z | 7 | 6 | < 25mph | PG282 | 7.95 | 2019-10-07T22:00:00Z | 11.41 | 32 | < 25mph
PG&E | 2017-07-28 | 14:02 | 40.9997 | -121.9579 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101512624 | Unknown | 12000 | Conductor | Overhead | Yes | 42944 | 14:02 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1293 | 2017 | 7 | 28 | 14 | 2 | 17-0066367 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 46581 | 11.7167 | 159_405 | <25mph | <15mph | HFTD - Distribution | 2017-07-28 14:02:00 | 1031 | 11.7167 | FALSE | <25mph | OMTC1 | 1.45 | 2015-10-13T09:26:00Z | 4 | 1 | < 25mph | OMTC1 | 1.45 | 2015-10-13T09:26:00Z | 4 | 1 | < 25mph | OMTC1 | 1.45 | 2015-10-13T10:26:00Z | 4.99 | 2 | < 25mph | OMTC1 | 1.45 | 2015-10-13T10:26:00Z | 4.99 | 2 | < 25mph
PG&E | 2017-12-20 07:55 | 07:54 | 37.4012 | -122.3606 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100318864 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43089.3298 | 07:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1546 | 2017 | 12 | 20 | 7 | 54 | 17-0102756 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6602 | 16.1413 | 140_206 | <25mph | <15mph | HFTD - Distribution | 2017-12-20 07:54:00 | 1288 | 21.2088 | FALSE | <25mph | PG149 | 0.73 | 2019-12-24T18:00:00Z | 5.55 | 18 | < 25mph | PG150 | 6.83 | 2019-12-24T17:30:00Z | 12.57 | 74 | < 25mph | PG149 | 0.73 | 2019-12-24T19:00:00Z | 13.8 | 37 | < 25mph | PG515 | 7.35 | 2019-12-24T18:30:00Z | 16.28 | 151 | < 25mph
PG&E | 2015-09-12 09:51 | 2015-09-12 09:51 | 39.1164 | -121.0693 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | TOP OF AVALON PLACE, GRASS VALLEY TOWER NUMBER 19/152 40689729 |  | 115000 | Conductor | Overhead | Yes | 42259.4104 | 2015-09-12 09:51 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0594 | 2015 | 9 | 12 | 9 | 51 | VD-2015-079 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.5014 | 196_301 | <25mph | <15mph | HFTD - Transmission | 2015-09-12 09:51:00 | 339 | 14.0472 | FALSE | <25mph | E1789 | 3.95 | 2015-09-13T14:00:00Z | 8.99 | 8 | < 25mph | E1789 | 3.95 | 2015-09-13T14:00:00Z | 8.99 | 65 | < 25mph | E1789 | 3.95 | 2015-09-13T14:00:00Z | 8.99 | 17 | < 25mph | E1789 | 3.95 | 2015-09-13T14:00:00Z | 8.99 | 119 | < 25mph
PG&E | 2017-10-08 | 19:44 | 39.7446 | -121.597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100330456 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 19:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1464 | 2017 | 10 | 8 | 19 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 33.2724 | 174_335 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-08 19:44:00 | 1202 | 34.7906 | FALSE | 25-40mph | E2076 | 1.3 | 2015-11-14T21:25:00Z | 5.99 | 11 | < 25mph | E2076 | 1.3 | 2015-11-14T21:25:00Z | 5.99 | 22 | < 25mph | E2076 | 1.3 | 2015-11-14T21:25:00Z | 5.99 | 22 | < 25mph | E4833 | 4.34 | 2015-11-14T22:32:00Z | 8.01 | 42 | < 25mph
PG&E | 2019-06-08 | 18:51 | 38.6105 | -122.9732 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 42751113 |  | 12000 | Conductor | Overhead | Yes | 43624 | 18:51 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-355 | 2019 | 6 | 8 | 18 | 51 | 19-0064689 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 44664 | 14.8219 | 114_273 | <25mph | <15mph | HFTD - Distribution | 2019-06-08 18:51:00 | 1812 | 19.8533 | FALSE | <25mph |  |  |  | 0 | 0 | No data | R08WW | 7.77 | 2017-06-23T07:00:00Z | 4.7 | 30 | < 25mph |  |  |  | 0 | 0 | No data | R08WW | 7.77 | 2017-06-23T07:00:00Z | 4.7 | 65 | < 25mph
PG&E | 2017-10-10 | 13:36 | 38.931 | -123.3023 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 102214553 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43018 | 13:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1481 | 2017 | 10 | 10 | 13 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.7263 | 101_291 | <25mph | <15mph | HFTD - Distribution | 2017-10-10 13:36:00 | 1224 | 17.0479 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E4371 | 5.14 | 2017-12-27T20:55:00Z | 10 | 8 | < 25mph |  |  |  | 0 | 0 | No data | E4371 | 5.14 | 2017-12-27T22:09:00Z | 10 | 16 | < 25mph
PG&E | 2018-08-07 | 17:15 | 37.1181 | -122.1093 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101670606 | AT&T | 12000 | Conductor | Overhead | Yes | 43319 | 17:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1827 | 2018 | 8 | 7 | 17 | 15 | 18-0067641 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1988 | 17.3453 | 151_191 | <25mph | <15mph | HFTD - Distribution | 2018-08-07 17:15:00 | 1567 | 17.3453 | FALSE | <25mph | BNDC1 | 3.6 | 2019-12-21T23:50:00Z | 24.99 | 43 | < 25mph | BNDC1 | 3.6 | 2019-12-21T23:50:00Z | 24.99 | 116 | < 25mph | BNDC1 | 3.6 | 2019-12-21T23:50:00Z | 24.99 | 86 | < 25mph | BNDC1 | 3.6 | 2019-12-21T23:50:00Z | 24.99 | 231 | < 25mph
PG&E | 2017-10-20 | 6:18 | 39.2922 | -121.0157 | Vegetation | Rural | < 3 Meters | Fire Agency | PHILLIP NUNNINK INCIDENT # 27272 | 100087647 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43028 | 6:18 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1499 | 2017 | 10 | 20 | 6 | 18 | 17-0088957 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 102410 | 6.1464 | 199_310 | <25mph | <15mph | HFTD - Distribution | 2017-10-20 06:18:00 | 1242 | 23.0997 | FALSE | <25mph | PG026 | 3.98 | 2018-07-01T09:50:00Z | 5.26 | 32 | < 25mph | RRRC1 | 5.48 | 2018-07-01T09:13:00Z | 7 | 70 | < 25mph | PG026 | 3.98 | 2018-07-01T10:50:00Z | 6.13 | 64 | < 25mph | RRRC1 | 5.48 | 2018-07-01T09:13:00Z | 7 | 140 | < 25mph
PG&E | 2015-08-03 00:07 | 2015-08-03 00:07 | 40.5056 | -122.347 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | COTTONWOOD FIRE DEPT | 101503428 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42219.0049 | 2015-08-03 00:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0509 | 2015 | 8 | 3 | 0 | 7 | 15-0052184 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 10427 | 9.7241 | 143_378 | <25mph | <15mph | HFTD - Distribution | 2015-08-03 00:07:00 | 254 | 13.2206 | FALSE | <25mph | RRAC1 | 2.97 | 2016-11-11T16:24:00Z | 2.01 | 1 | < 25mph | E6886 | 4.94 | 2016-11-11T16:28:00Z | 3 | 14 | < 25mph | RRAC1 | 2.97 | 2016-11-11T17:24:00Z | 3 | 2 | < 25mph | E6886 | 4.94 | 2016-11-11T17:28:00Z | 3 | 28 | < 25mph
PG&E | 2016-08-22 | 2016-08-22 16:10 | 37.9666 | -120.2395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Toulumne City FD | 101043683 |  | 17000 | Conductor | Overhead | Yes | 42604 | 2016-08-22 16:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0941 | 2016 | 8 | 22 | 16 | 10 | 16-0059149 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 78534 | 13.4322 | 233_237 | <25mph | <15mph | HFTD - Distribution | 2016-08-22 16:10:00 | 684 | 13.7297 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.67 | 2017-06-08T03:02:00Z | 11.01 | 5 | < 25mph |  |  |  | 0 | 0 | No data | MOUC1 | 6.67 | 2017-06-08T04:02:00Z | 14 | 10 | < 25mph
PG&E | 2018-07-14 | 11:34 | 38.4026 | -122.5489 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103141862 | Verizon | 12000 | Conductor | Overhead | Yes | 43295 | 11:34 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1745 | 2018 | 7 | 14 | 11 | 34 | 18-0059821 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 6426 | 11.4725 | 133_262 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 11:34:00 | 1485 | 15.7933 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG177 | 4.3 | 2018-12-25T13:40:00Z | 18.86 | 26 | < 25mph |  |  |  | 0 | 0 | No data | PG177 | 4.3 | 2018-12-25T13:40:00Z | 18.86 | 52 | < 25mph
PG&E | 2016-06-19 | 2016-06-19 17:19 | 38.4508 | -122.3546 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire--napa fire | 102256859 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42540 | 2016-06-19 17:19 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0808 | 2016 | 6 | 19 | 17 | 19 | 16-0044337 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 672 | 13.296 | 141_264 | <25mph | <15mph | HFTD - Distribution | 2016-06-19 17:19:00 | 552 | 13.7776 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.13 | 2016-01-28T12:29:00Z | 10 | 1 | < 25mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.13 | 2016-01-28T13:29:00Z | 14.99 | 2 | < 25mph
PG&E | 2016-01-21 21:32 | 2016-01-21 21:32 | 40.553 | -124.1116 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100994021 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42390.8972 | 2016-01-21 21:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0690 | 2016 | 1 | 21 | 21 | 32 | 16-0007239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 6468 | 26.2481 | 69_382 | 25-40mph | 15-30mph | HFTD - Distribution | 2016-01-21 21:32:00 | 434 | 29.6828 | FALSE | 25-40mph | AT493 | 1.6 | 2018-04-24T21:42:00Z | 13 | 22 | < 25mph | AT493 | 1.6 | 2018-04-24T21:42:00Z | 13 | 22 | < 25mph | AT493 | 1.6 | 2018-04-24T21:42:00Z | 13 | 44 | < 25mph | AT493 | 1.6 | 2018-04-24T21:42:00Z | 13 | 44 | < 25mph
PG&E | 2017-06-25 02:47 | 0:23 | 39.4043 | -123.3869 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102193088 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42911.1159 | 0:23 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1197 | 2017 | 6 | 25 | 0 | 23 | 17-0058406 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 23100 | 15.6787 | 98_318 | <25mph | <15mph | HFTD - Distribution | 2017-06-25 00:23:00 | 935 | 19.8426 | FALSE | <25mph | AT319 | 3.31 | 2016-10-19T19:18:00Z | 4 | 24 | < 25mph | AU552 | 7.7 | 2016-10-19T19:29:00Z | 14 | 39 | < 25mph | E4027 | 2.16 | 2016-10-19T20:28:00Z | 4 | 48 | < 25mph | AU552 | 7.7 | 2016-10-19T20:21:00Z | 14 | 78 | < 25mph
PG&E | 2015-06-28 21:07 | 2015-06-28 21:07 | 39.7405 | -121.4974 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | DEADWOOD RD, JARBO GAP |  | 12000 | Conductor | Overhead | Yes | 42183.8799 | 2015-06-28 21:07 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0424 | 2015 | 6 | 28 | 21 | 7 | 15-0043869 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 45683 | 12.2547 | 178_335 | <25mph | <15mph | HFTD - Distribution | 2015-06-28 21:07:00 | 169 | 17.5682 | FALSE | <25mph | JBGC1 | 0.55 | 2016-11-27T01:13:00Z | 11.01 | 1 | < 25mph | JBGC1 | 0.55 | 2016-11-27T01:13:00Z | 11.01 | 5 | < 25mph | JBGC1 | 0.55 | 2016-11-27T02:13:00Z | 11.01 | 2 | < 25mph | JBGC1 | 0.55 | 2016-11-27T02:13:00Z | 11.01 | 7 | < 25mph
PG&E | 2017-08-14 | 23:52 | 37.1272 | -122.1689 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 015/127 | None | 60000 | Conductor | Overhead | Yes | 42961 | 23:52 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1333 | 2017 | 8 | 14 | 23 | 52 | INT-09976 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 1790869 | 16.3701 | 148_191 | <25mph | <15mph | HFTD - Transmission | 2017-08-14 23:52:00 | 1072 | 18.2518 | FALSE | <25mph | BNDC1 | 0.33 | 2017-06-28T09:50:00Z | 11.01 | 27 | < 25mph | BNDC1 | 0.33 | 2017-06-28T09:50:00Z | 11.01 | 42 | < 25mph | BNDC1 | 0.33 | 2017-06-28T09:50:00Z | 11.01 | 54 | < 25mph | BNDC1 | 0.33 | 2017-06-28T09:50:00Z | 11.01 | 83 | < 25mph
PG&E | 2018-06-27 | 18:46 | 40.218 | -123.7989 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TJ alderpoint fire | 100990381 | Unknown | 12000 | Conductor | Overhead | Yes | 43278 | 18:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1700 | 2018 | 6 | 27 | 18 | 46 | 18-0055205 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 21357 | 17.7599 | 81_363 | <25mph | <15mph | HFTD - Distribution | 2018-06-27 18:46:00 | 1441 | 20.5507 | FALSE | <25mph | PG273 | 3.19 | 2019-10-15T08:00:00Z | 2.64 | 12 | < 25mph | PG418 | 5.01 | 2019-10-15T08:10:00Z | 13.87 | 19 | < 25mph | PG273 | 3.19 | 2019-10-15T09:10:00Z | 4.38 | 24 | < 25mph | PG418 | 5.01 | 2019-10-15T08:10:00Z | 13.87 | 38 | < 25mph
PG&E | 2016-07-27 11:53 | 2016-07-27 11:53 | 37.8649 | -120.5134 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101041792 |  | 17000 | Conductor | Overhead | Yes | 42578.4951 | 2016-07-27 11:53 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0880 | 2016 | 7 | 27 | 11 | 53 | 16-0052942 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 14734 | 9.7065 | 221_232 | <25mph | <15mph | HFTD - Distribution | 2016-07-27 11:53:00 | 622 | 14.5426 | FALSE | <25mph | GNSC1 | 2.2 | 2015-09-28T22:03:00Z | 12.01 | 1 | < 25mph | GNSC1 | 2.2 | 2015-09-28T22:03:00Z | 12.01 | 7 | < 25mph | GNSC1 | 2.2 | 2015-09-28T22:03:00Z | 12.01 | 2 | < 25mph | GNSC1 | 2.2 | 2015-09-28T22:03:00Z | 12.01 | 15 | < 25mph
PG&E | 2018-06-27 | 18:46 | 40.218 | -123.7989 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TJ alderpoint fire | 100990381 | Unknown | 12000 | Conductor | Overhead | Yes | 43278 | 18:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1700 | 2018 | 6 | 27 | 18 | 46 | 18-0055205 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 21357 | 17.7599 | 81_363 | <25mph | <15mph | HFTD - Distribution | 2018-06-27 18:46:00 | 1441 | 20.5507 | FALSE | <25mph |  |  |  | 0 | 0 | No data | ERCC1 | 5.65 | 2015-11-10T08:28:00Z | 2.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | ERCC1 | 5.65 | 2015-11-10T09:28:00Z | 3 | 2 | < 25mph
PG&E | 2018-08-07 | 21:03 | 38.2129 | -120.9184 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102042811 | Unknown | 12000 | Conductor | Overhead | Yes | 43319 | 21:03 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1828 | 2018 | 8 | 7 | 21 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2018-08-07 21:03:00 | NA | 0 | FALSE | <25mph | CMAC1 | 2.92 | 2017-12-14T08:59:00Z | 3 | 1 | < 25mph | CMAC1 | 2.92 | 2017-12-14T08:59:00Z | 3 | 1 | < 25mph | CMAC1 | 2.92 | 2017-12-14T09:59:00Z | 3 | 2 | < 25mph | CMAC1 | 2.92 | 2017-12-14T09:59:00Z | 3 | 2 | < 25mph
PG&E | 2015-09-24 13:56 | 2015-09-24 13:56 | 39.3508 | -121.2454 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 9692 Rices-Texas Hill rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42271.5806 | 2015-09-24 13:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0614 | 2015 | 9 | 24 | 13 | 56 | 15-0063159 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 51917 | 10.3419 | 189_313 | <25mph | <15mph | HFTD - Distribution | 2015-09-24 13:56:00 | 359 | 13.3743 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RRRC1 | 7.59 | 2016-11-08T23:13:00Z | 8.99 | 2 | < 25mph |  |  |  | 0 | 0 | No data | RRRC1 | 7.59 | 2016-11-08T23:13:00Z | 8.99 | 4 | < 25mph
PG&E | 2017-09-04 | 3:29 | 39.8317 | -121.8444 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102300100 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1392 | 2017 | 9 | 4 | 3 | 29 | 17-0075723 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 214974 | 9.8341 | 164_340 | <25mph | <15mph | HFTD - Distribution | 2017-09-04 03:29:00 | 1130 | 13.8789 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8204 | 5.42 | 2015-02-13T07:13:00Z | 8.99 | 14 | < 25mph |  |  |  | 0 | 0 | No data | D8204 | 5.42 | 2015-02-13T08:03:00Z | 8.99 | 29 | < 25mph
PG&E | 2017-04-29 15:29 | 15:07 | 37.0349 | -119.5242 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100678661 | Unknown | 12000 | Conductor | Overhead | Yes | 42854.6453 | 15:07 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1078 | 2017 | 4 | 29 | 15 | 7 | 17-0043911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 7.6275 | 265_186 | <25mph | <15mph | HFTD - Distribution | 2017-04-29 15:07:00 | 818 | 19.1329 | FALSE | <25mph | PRHC1 | 2.76 | 2015-09-10T06:27:00Z | 3 | 1 | < 25mph | PRHC1 | 2.76 | 2015-09-10T06:27:00Z | 3 | 1 | < 25mph | PRHC1 | 2.76 | 2015-09-10T07:27:00Z | 4 | 2 | < 25mph | PRHC1 | 2.76 | 2015-09-10T07:27:00Z | 4 | 2 | < 25mph
PG&E | 2017-09-06 | 20:08 | 37.2925 | -122.294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100256917 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1400 | 2017 | 9 | 6 | 20 | 8 | 17-0076502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4914 | 6.7999 | 143_200 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 20:08:00 | 1138 | 13.6021 | FALSE | <25mph | LAHC1 | 2.3 | 2016-03-05T02:07:00Z | 8.99 | 1 | < 25mph | LAHC1 | 2.3 | 2016-03-05T02:07:00Z | 8.99 | 13 | < 25mph | LAHC1 | 2.3 | 2016-03-05T03:07:00Z | 11.01 | 2 | < 25mph | LAHC1 | 2.3 | 2016-03-05T03:07:00Z | 11.01 | 26 | < 25mph
PG&E | 2019-08-16 | 10:31 | 39.3714 | -121.3221 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103191101 |  | 12000 | Conductor | Overhead | Yes | 43693 | 10:31 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-397 | 2019 | 8 | 16 | 10 | 31 | 19-0088805 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4580 | 6.4736 | 186_315 | <25mph | <15mph | HFTD - Distribution | 2019-08-16 10:31:00 | 1984 | 15.7456 | FALSE | <25mph | BNGC1 | 3.48 | 2019-03-19T13:51:00Z | 3 | 1 | < 25mph | BNGC1 | 3.48 | 2019-03-19T13:51:00Z | 3 | 1 | < 25mph | BNGC1 | 3.48 | 2019-03-19T14:51:00Z | 4.99 | 2 | < 25mph | BNGC1 | 3.48 | 2019-03-19T14:51:00Z | 4.99 | 2 | < 25mph
PG&E | 2018-07-14 | 11:34 | 38.4026 | -122.5489 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103141862 | Verizon | 12000 | Conductor | Overhead | Yes | 43295 | 11:34 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1745 | 2018 | 7 | 14 | 11 | 34 | 18-0059821 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 6426 | 11.4725 | 133_262 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 11:34:00 | 1485 | 15.7933 | FALSE | <25mph | KENWW | 0.52 | 2017-08-31T09:00:00Z | 2.8 | 4 | < 25mph | E1582 | 5.93 | 2017-08-31T09:13:00Z | 7 | 13 | < 25mph | KENWW | 0.52 | 2017-08-31T09:00:00Z | 2.8 | 8 | < 25mph | E1582 | 5.93 | 2017-08-31T09:13:00Z | 7 | 24 | < 25mph
PG&E | 2019-09-28 | 13:16 | 37.2553 | -119.5057 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 252531103 |  | 12000 | Conductor | Overhead | Yes | 43736 | 13:16 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-36 | 2019 | 9 | 28 | 13 | 16 | 19-0104972 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 1296 | 12.1111 | 265_198 | <25mph | <15mph | HFTD - Distribution | 2019-09-28 13:16:00 | 2064 | 13.545 | FALSE | <25mph | C6459 | 1.57 | 2017-02-17T15:00:00Z | 4.99 | 4 | < 25mph | D7778 | 7.57 | 2017-02-17T15:24:00Z | 7 | 35 | < 25mph | NFRC1 | 1.54 | 2017-02-17T15:55:00Z | 8.99 | 8 | < 25mph | D7778 | 7.57 | 2017-02-17T16:09:00Z | 27 | 71 | 25-40mph
PG&E | 2017-04-25 12:39 | 12:38 | 38.6583 | -120.9762 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101376746 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 42850.5271 | 12:38 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1072 | 2017 | 4 | 25 | 12 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 9.948 | 200_275 | <25mph | <15mph | HFTD - Distribution | 2017-04-25 12:38:00 | 812 | 10.5664 | FALSE | <25mph | PG072 | 3.57 | 2018-08-09T22:30:00Z | 12.48 | 20 | < 25mph | C6129 | 7.33 | 2018-08-09T22:19:00Z | 18.01 | 106 | < 25mph | PG072 | 3.57 | 2018-08-09T22:30:00Z | 12.48 | 40 | < 25mph | C6129 | 7.33 | 2018-08-09T22:19:00Z | 18.01 | 211 | < 25mph
PG&E | 2017-10-02 | 16:05 | 38.7182 | -120.9756 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101375963 | Unknown | 21000 | Conductor | Overhead | Yes | 43010 | 16:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1448 | 2017 | 10 | 2 | 16 | 5 | 17-0083539 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4797 | 14.669 | 201_279 | <25mph | <15mph | HFTD - Distribution | 2017-10-02 16:05:00 | 1186 | 17.4155 | FALSE | <25mph | D7401 | 3.14 | 2017-11-17T15:18:00Z | 0 | 82 | < 25mph | E4740 | 4.79 | 2017-11-17T15:10:00Z | 2.01 | 103 | < 25mph | D7401 | 3.14 | 2017-11-17T16:18:00Z | 2.01 | 162 | < 25mph | E4740 | 4.79 | 2017-11-17T16:00:00Z | 2.01 | 206 | < 25mph
PG&E | 2017-07-16 11:59 | 11:59 | 36.6669 | -121.7515 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101761892 | None | 21000 | Fuse | Overhead | Yes | 42932.4994 | 11:59 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1259 | 2017 | 7 | 16 | 11 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 22.4318 | 166_166 | <25mph | <15mph | HFTD - Distribution | 2017-07-16 11:59:00 | 998 | 30.0095 | FALSE | 25-40mph | E6666 | 1.85 | 2015-06-11T09:10:00Z | 7 | 18 | < 25mph | E6666 | 1.85 | 2015-06-11T09:10:00Z | 7 | 18 | < 25mph | E6666 | 1.85 | 2015-06-11T10:25:00Z | 8.99 | 36 | < 25mph | E6666 | 1.85 | 2015-06-11T10:25:00Z | 8.99 | 36 | < 25mph
PG&E | 2015-08-14 15:09 | 2015-08-14 15:09 | 40.9829 | -121.7802 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101514540 |  | 21000 | Conductor | Overhead | Yes | 42230.6312 | 2015-08-14 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0530 | 2015 | 8 | 14 | 15 | 9 | 15-0055136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3072 | 14.8278 | 167_404 | <25mph | <15mph | HFTD - Distribution | 2015-08-14 15:09:00 | 274 | 16.5644 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AS418 | 7.42 | 2015-12-27T22:38:00Z | 7 | 6 | < 25mph |  |  |  | 0 | 0 | No data | AS418 | 7.42 | 2015-12-27T22:38:00Z | 7 | 12 | < 25mph
PG&E | 2018-06-13 | 22:40 | 38.4901 | -122.6661 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SRS181640125 | 101966547 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 22:40 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1656 | 2018 | 6 | 13 | 22 | 40 | 18-0050782 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 295146 | 2.5247 | 128_267 | <25mph | <15mph | HFTD - Distribution | 2018-06-13 22:40:00 | 1398 | 17.8767 | FALSE | <25mph | RSAC1 | 2.6 | 2016-07-07T07:29:00Z | 4.99 | 22 | < 25mph | C0677 | 5.63 | 2016-07-07T07:37:00Z | 8.99 | 65 | < 25mph | RSAC1 | 2.6 | 2016-07-07T08:29:00Z | 4.99 | 42 | < 25mph | C0677 | 5.63 | 2016-07-07T07:37:00Z | 8.99 | 127 | < 25mph
PG&E | 2016-05-31 04:02 | 2016-05-31 04:02 | 35.7984 | -120.9743 | Vegetation | RURAL | < 0.25 Acres | Utility: PG&E | N.A. | 101863413 |  | 12000 | Conductor | Overhead | Yes | 42521.1681 | 2016-05-31 04:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0754 | 2016 | 5 | 31 | 4 | 2 | 16-0039748 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 51888 | 1.5922 | 201_118 | <25mph | <15mph | HFTD - Distribution | 2016-05-31 04:02:00 | 497 | 16.9662 | FALSE | <25mph | E9175 | 3.45 | 2018-11-09T08:40:00Z | 1.01 | 11 | < 25mph | D4060 | 6.86 | 2018-11-09T08:01:00Z | 4 | 15 | < 25mph | E9175 | 3.45 | 2018-11-09T08:40:00Z | 1.01 | 23 | < 25mph | D4060 | 6.86 | 2018-11-09T09:31:00Z | 4 | 31 | < 25mph
PG&E | 2019-06-03 | 14:31 | 40.6822 | -122.2806 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 101466598 |  | 12000 | Transformer | Overhead | Yes | 43619 | 14:31 | Equipment - Overloaded | Transformer |  |  |  |  | no-match | 2019-161 | 2019 | 6 | 3 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 6.522 | 146_387 | <25mph | <15mph | HFTD - Distribution | 2019-06-03 14:31:00 | 1798 | 12.4331 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C5599 | 6.05 | 2018-04-11T11:17:00Z | 5.99 | 3 | < 25mph |  |  |  | 0 | 0 | No data | C5599 | 6.05 | 2018-04-11T11:17:00Z | 5.99 | 7 | < 25mph
PG&E | 2019-05-29 | 16:54 | 37.0371 | -119.5209 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 100680674 |  | 12000 | Pole | Overhead | Yes | 43614 | 16:54 | Vegetation |  | Veg. contact | Pole |  |  | Dead | 2019-202 | 2019 | 5 | 29 | 16 | 54 | 19-0059237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 6780 | 6.6167 | 265_186 | <25mph | <15mph | HFTD - Distribution | 2019-05-29 16:54:00 | 1787 | 9.3593 | FALSE | <25mph | PRHC1 | 3 | 2018-12-04T21:27:00Z | 4 | 1 | < 25mph | PRHC1 | 3 | 2018-12-04T21:27:00Z | 4 | 1 | < 25mph | PRHC1 | 3 | 2018-12-04T22:27:00Z | 7 | 2 | < 25mph | PRHC1 | 3 | 2018-12-04T22:27:00Z | 7 | 2 | < 25mph
PG&E | 2015-07-15 09:00 | 2015-07-15 09:00 | 36.997 | -121.7381 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101795728 |  | 21000 | Conductor | Overhead | Yes | 42200.375 | 2015-07-15 09:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0463 | 2015 | 7 | 15 | 9 | 0 | 15-0047650 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3800 | 8.5113 | 167_184 | <25mph | <15mph | HFTD - Distribution | 2015-07-15 09:00:00 | 208 | 13.379 | FALSE | <25mph | CTOC1 | 3.71 | 2016-10-17T20:27:00Z | 11.01 | 1 | < 25mph | C4503 | 7.38 | 2016-10-17T20:30:00Z | 14 | 22 | < 25mph | CTOC1 | 3.71 | 2016-10-17T21:27:00Z | 11.01 | 2 | < 25mph | C4503 | 7.38 | 2016-10-17T20:30:00Z | 14 | 38 | < 25mph
PG&E | 2016-08-21 | 2016-08-21 13:02 | 38.4445 | -122.2496 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102291451 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42603 | 2016-08-21 13:02 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0940 | 2016 | 8 | 21 | 13 | 2 | 16-0058847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 12780 | 10.3444 | 145_264 | <25mph | <15mph | HFTD - Distribution | 2016-08-21 13:02:00 | 683 | 21.5044 | FALSE | <25mph | ATLC1 | 2.26 | 2018-09-07T14:29:00Z | 11.01 | 13 | < 25mph | ATLC1 | 2.26 | 2018-09-07T14:29:00Z | 11.01 | 35 | < 25mph | ATLC1 | 2.26 | 2018-09-07T14:29:00Z | 11.01 | 26 | < 25mph | ATLC1 | 2.26 | 2018-09-07T14:29:00Z | 11.01 | 70 | < 25mph
PG&E | 2015-05-09 13:10 | 2015-05-09 13:10 | 39.2343 | -121.2468 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100000103 | None | 21000 | Conductor | Overhead | Yes | 42133.5486 | 2015-05-09 13:10 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0311 | 2015 | 5 | 9 | 13 | 10 | 15-0033085 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 382926 | 12.172 | 189_307 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 13:10:00 | 57 | 17.071 | FALSE | <25mph | E2572 | 3.27 | 2016-06-07T19:38:00Z | 4.99 | 12 | < 25mph | E6355 | 7.8 | 2016-06-07T19:36:00Z | 4.99 | 18 | < 25mph | E2572 | 3.27 | 2016-06-07T20:39:00Z | 4.99 | 23 | < 25mph | E6355 | 7.8 | 2016-06-07T20:29:00Z | 8.99 | 34 | < 25mph
PG&E | 2017-04-04 13:36 | 13:29 | 35.6885 | -120.7653 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101945026 | None | 12000 | Conductor | Overhead | Yes | 42829.567 | 13:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1064 | 2017 | 4 | 4 | 13 | 29 | 17-0036460 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 167151 | 3.61 | 210_111 | <25mph | <15mph | HFTD - Distribution | 2017-04-04 13:29:00 | 804 | 8.6409 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D4060 | 7.1 | 2015-01-17T12:27:00Z | 3 | 4 | < 25mph |  |  |  | 0 | 0 | No data | D4060 | 7.1 | 2015-01-17T13:27:00Z | 4 | 8 | < 25mph
PG&E | 2015-09-04 07:49 | 2015-09-04 07:49 | 40.2318 | -122.3643 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | E/O FRONTIER RD & N/O WAGON WAY |  | 12000 | Conductor | Overhead | Yes | 42251.3257 | 2015-09-04 07:49 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0577 | 2015 | 9 | 4 | 7 | 49 | 15-0059323 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 9563 | 2.343 | 142_362 | <25mph | <15mph | HFTD - Distribution | 2015-09-04 07:49:00 | 321 | 17.9748 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 5.07 | 2019-08-19T18:45:00Z | 21 | 10 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 5.07 | 2019-08-19T20:30:00Z | 24 | 20 | < 25mph
PG&E | 2016-07-20 19:15 | 2016-07-20 19:15 | 37.7712 | -121.8104 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100898986 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42571.8021 | 2016-07-20 19:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0865 | 2016 | 7 | 20 | 19 | 15 | 16-0051308 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3013 | 17.1873 | 164_226 | <25mph | <15mph | HFTD - Distribution | 2016-07-20 19:15:00 | 608 | 18.9944 | FALSE | <25mph | LVMC1 | 3.62 | 2015-03-16T05:02:00Z | 14.99 | 1 | < 25mph | LVMC1 | 3.62 | 2015-03-16T05:02:00Z | 14.99 | 39 | < 25mph | LVMC1 | 3.62 | 2015-03-16T05:02:00Z | 14.99 | 2 | < 25mph | LVMC1 | 3.62 | 2015-03-16T05:02:00Z | 14.99 | 77 | < 25mph
PG&E | 2015-05-09 21:37 | 2015-05-09 21:37 | 39.2848 | -121.0219 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100004095 | Pacific Bell | 12000 | Fuse | Overhead | Yes | 42133.9007 | 2015-05-09 21:37 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0312 | 2015 | 5 | 9 | 21 | 37 | 15-0033109 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 11 | 9.2188 | 198_310 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 21:37:00 | 58 | 15.4234 | FALSE | <25mph | E3651 | 3.92 | 2019-06-13T14:30:00Z | 3 | 43 | < 25mph | PG348 | 7.89 | 2019-06-13T13:50:00Z | 15.99 | 113 | < 25mph | E3651 | 3.92 | 2019-06-13T14:30:00Z | 3 | 86 | < 25mph | PG348 | 7.89 | 2019-06-13T13:50:00Z | 15.99 | 229 | < 25mph
PG&E | 2015-06-15 15:35 | 2015-06-15 15:35 | 37.1852 | -121.7595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Jose city | 100618215 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42170.6493 | 2015-06-15 15:35 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0384 | 2015 | 6 | 15 | 15 | 35 | 15-0041178 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 345 | 20.7397 | 166_194 | <25mph | <15mph | HFTD - Distribution | 2015-06-15 15:35:00 | 130 | 21.599 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C7168 | 4.25 | 2017-06-19T18:24:00Z | 8.99 | 60 | < 25mph |  |  |  | 0 | 0 | No data | C7168 | 4.25 | 2017-06-19T18:24:00Z | 8.99 | 109 | < 25mph
PG&E | 2018-08-22 | 21:56 | 39.0425 | -120.9695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100024728 | Verizon | 12000 | Conductor | Overhead | Yes | 43334 | 21:56 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1854 | 2018 | 8 | 22 | 21 | 56 | 18-0072654 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29727 | 9.3137 | 201_296 | <25mph | <15mph | HFTD - Distribution | 2018-08-22 21:56:00 | 1593 | 10.5291 | FALSE | <25mph | D9434 | 1.28 | 2017-06-20T04:25:00Z | 1.01 | 10 | < 25mph | D9434 | 1.28 | 2017-06-20T04:25:00Z | 1.01 | 53 | < 25mph | D9434 | 1.28 | 2017-06-20T04:25:00Z | 1.01 | 19 | < 25mph | AT999 | 4.33 | 2017-06-20T05:45:00Z | 4 | 95 | < 25mph
PG&E | 2016-08-10 | 2016-08-10 08:36 | 37.0575 | -121.9556 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 101680487 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0917 | 2016 | 8 | 10 | 8 | 36 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 6.3982 | 157_187 | <25mph | <15mph | HFTD - Distribution | 2016-08-10 08:36:00 | 659 | 9.833 | FALSE | <25mph | D8700 | 0.25 | 2016-07-15T16:22:00Z | 8.01 | 41 | < 25mph | D8700 | 0.25 | 2016-07-15T16:22:00Z | 8.01 | 179 | < 25mph | E5965 | 0.91 | 2016-07-15T17:49:00Z | 10 | 82 | < 25mph | E5965 | 0.91 | 2016-07-15T17:49:00Z | 10 | 351 | < 25mph
PG&E | 2017-08-12 09:09 | 09:08 | 34.6689 | -120.0286 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103391912 | Unknown | 12000 | Conductor | Overhead | Yes | 42959.3812 | 09:08 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | wire cut | Other/Unknown | 1330 | 2017 | 8 | 12 | 9 | 8 | 17-0069829 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 26070 | 3.5662 | 244_55 | <25mph | <15mph | HFTD - Distribution | 2017-08-12 09:08:00 | 1068 | 23.4799 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AP901 | 5.95 | 2015-10-16T20:40:00Z | 13 | 9 | < 25mph |  |  |  | 0 | 0 | No data | AP901 | 5.95 | 2015-10-16T20:50:00Z | 14.99 | 16 | < 25mph
PG&E | 2016-10-14 04:33 | 4:32 | 40.5228 | -121.6813 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101513661 |  | 12000 | Conductor | Overhead | Yes | 42657.1893 | 4:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1032 | 2016 | 10 | 14 | 4 | 32 | 16-0071897 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 38950 | 28.7152 | 171_378 | 25-40mph | 15-30mph | HFTD - Distribution | 2016-10-14 04:32:00 | 773 | 31.1927 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | VIOC1 | 5.45 | 2015-12-19T08:52:00Z | 5.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | VIOC1 | 5.45 | 2015-12-19T09:52:00Z | 12.01 | 2 | < 25mph
PG&E | 2018-08-08 | 16:02 | 36.4703 | -121.7143 | Vegetation | Rural | < 3 meters | Customer | N.A. | 103910535 | None | 12000 | Conductor | Overhead | Yes | 43320 | 16:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1830 | 2018 | 8 | 8 | 16 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 14.7322 | 168_155 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:02:00 | 1569 | 15.5625 | FALSE | <25mph | PG206 | 1.48 | 2019-06-06T12:00:00Z | 4.38 | 6 | < 25mph | PG318 | 7.15 | 2019-06-06T11:50:00Z | 22.15 | 34 | < 25mph | PG206 | 1.48 | 2019-06-06T13:00:00Z | 7.25 | 12 | < 25mph | PG318 | 7.15 | 2019-06-06T11:50:00Z | 22.15 | 68 | < 25mph
PG&E | 2017-05-14 | 11:59 | 38.0798 | -122.8665 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102247059 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42869 | 11:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1095 | 2017 | 5 | 14 | 11 | 59 | 17-0047802 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 377483 | 24.3878 | 118_244 | <25mph | <15mph | HFTD - Distribution | 2017-05-14 11:59:00 | 835 | 24.3878 | FALSE | <25mph | PG046 | 0 | 2018-06-17T01:10:00Z | 19.28 | 6 | < 25mph | PG046 | 0 | 2018-06-17T01:10:00Z | 19.28 | 19 | < 25mph | PG046 | 0 | 2018-06-17T02:00:00Z | 28.5 | 12 | 25-40mph | PG046 | 0 | 2018-06-17T02:00:00Z | 28.5 | 38 | 25-40mph
PG&E | 2019-07-25 | 7:39 | 39.1735 | -123.5763 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Oj 2 P/Ss Of Cgc# 215532055340 |  | 12000 | Other | Overhead | Yes | 43671 | 7:39 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-380 | 2019 | 7 | 25 | 7 | 39 | 19-0080947 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 790 | 2.0398 | 89_305 | <25mph | <15mph | HFTD - Distribution | 2019-07-25 07:39:00 | 1928 | 13.3511 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1763 | 7.11 | 2018-06-01T20:17:00Z | 10 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E1763 | 7.11 | 2018-06-01T20:17:00Z | 10 | 8 | < 25mph
PG&E | 2016-08-25 | 2016-08-25 12:04 | 36.9726 | -119.3816 | Vegetation | RURAL | < 3 meters | Utility: PG&E | N.A. | 100651318 | PONDEROSA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0945 | 2016 | 8 | 25 | 12 | 4 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.3948 | 271_183 | <25mph | <15mph | HFTD - Distribution | 2016-08-25 12:04:00 | 689 | 15.1668 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5633 | 4.89 | 2018-02-20T23:16:00Z | 10 | 7 | < 25mph |  |  |  | 0 | 0 | No data | TRMC1 | 5.94 | 2018-02-21T00:52:00Z | 11.01 | 14 | < 25mph
PG&E | 2017-12-19 | 19:45 | 40.7271 | -122.3263 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101457738 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43088 | 19:45 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1545 | 2017 | 12 | 19 | 19 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 12.0712 | 144_390 | <25mph | <15mph | HFTD - Distribution | 2017-12-19 19:45:00 | 1287 | 14.9625 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2019-09-13 | 6:30 | 37.3348 | -121.7716 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 83392110 |  | 21000 | Splice/Clamp/Connector | Overhead | Yes | 43721 | 6:30 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-444 | 2019 | 9 | 13 | 6 | 30 | 19-0098560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 35534 | 3.3882 | 166_202 | <25mph | <15mph | HFTD - Distribution | 2019-09-13 06:30:00 | 2037 | 14.1926 | FALSE | <25mph | UCBO | 3.77 | 2016-02-28T15:20:00Z | 4 | 18 | < 25mph | MIPC1 | 7.48 | 2016-02-28T15:19:00Z | 8.01 | 96 | < 25mph | E8563 | 3.34 | 2016-02-28T16:51:00Z | 4.99 | 36 | < 25mph | MIPC1 | 7.48 | 2016-02-28T16:19:00Z | 8.99 | 188 | < 25mph
PG&E | 2016-07-21 21:45 | 2016-07-21 21:45 | 40.8566 | -122.3387 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101455670 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0870 | 2016 | 7 | 21 | 21 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.7351 | 143_397 | <25mph | <15mph | HFTD - Distribution | 2016-07-21 21:45:00 | 613 | 15.1303 | FALSE | <25mph | CTANT | 1.58 | 2017-03-21T01:45:00Z | 3.11 | 4 | < 25mph | SLFC1 | 6.48 | 2017-03-21T02:19:00Z | 25.99 | 9 | 25-40mph | CTANT | 1.58 | 2017-03-21T03:30:00Z | 5.59 | 8 | < 25mph | SLFC1 | 6.48 | 2017-03-21T03:19:00Z | 28.99 | 18 | 25-40mph
PG&E | 2017-08-31 | 6:42 | 35.616 | -120.8577 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Derrick | 101860075 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 6:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1372 | 2017 | 8 | 31 | 6 | 42 | 17-0074386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1620 | 12.088 | 206_107 | <25mph | <15mph | HFTD - Distribution | 2017-08-31 06:42:00 | 1110 | 13.8216 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TABC1 | 4.66 | 2017-10-17T12:07:00Z | 2.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | TABC1 | 4.66 | 2017-10-17T13:07:00Z | 2.01 | 2 | < 25mph
PG&E | 2017-07-24 21:45 | 21:45 | 35.6024 | -120.9211 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101860186 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.9063 | 21:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1289 | 2017 | 7 | 24 | 21 | 45 | 17-0065191 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 21231 | 19.4445 | 203_107 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 21:45:00 | 1028 | 30.0108 | FALSE | 25-40mph | TABC1 | 3.74 | 2018-07-06T15:07:00Z | 3 | 1 | < 25mph | TABC1 | 3.74 | 2018-07-06T15:07:00Z | 3 | 1 | < 25mph | TABC1 | 3.74 | 2018-07-06T15:07:00Z | 3 | 2 | < 25mph | TABC1 | 3.74 | 2018-07-06T15:07:00Z | 3 | 2 | < 25mph
PG&E | 2019-06-15 | 14:08 | 38.8802 | -122.6125 | Tree - cutting, 3rd party | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 43361103 |  | 12000 | Pole | Overhead | Yes | 43631 | 14:08 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | Other/Unknown | 2019-19 | 2019 | 6 | 15 | 14 | 8 | 19-0068074 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 259562 | 11.2331 | 130_288 | <25mph | <15mph | HFTD - Distribution | 2019-06-15 14:08:00 | 1841 | 15.703 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5568 | 5.92 | 2015-04-03T11:44:00Z | 5.99 | 13 | < 25mph |  |  |  | 0 | 0 | No data | E5568 | 5.92 | 2015-04-03T13:29:00Z | 5.99 | 26 | < 25mph
PG&E | 2017-10-28 | 15:26 | 39.4516 | -123.3838 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102209084 | Unknown | 12000 | Conductor | Overhead | Yes | 43036 | 15:26 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | no-match | 1510 | 2017 | 10 | 28 | 15 | 26 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 10.3107 | 98_320 | <25mph | <15mph | HFTD - Distribution | 2017-10-28 15:26:00 | 1252 | 11.7696 | FALSE | <25mph | E4027 | 3.28 | 2018-06-19T23:03:00Z | 14 | 12 | < 25mph | E4027 | 3.28 | 2018-06-19T23:03:00Z | 14 | 12 | < 25mph | E4027 | 3.28 | 2018-06-19T23:03:00Z | 14 | 24 | < 25mph | E4027 | 3.28 | 2018-06-19T23:03:00Z | 14 | 24 | < 25mph
PG&E | 2018-08-20 | 9:34 | 39.8014 | -121.5813 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100400441 | Unknown | 12000 | Conductor | Overhead | Yes | 43332 | 9:34 | Contact From Object | N.A. | Other | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1849 | 2018 | 8 | 20 | 9 | 34 | 18-0071596 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 394259 | 5.4464 | 175_338 | <25mph | <15mph | HFTD - Distribution | 2018-08-20 09:34:00 | 1588 | 11.8754 | FALSE | <25mph | C4565 | 3.06 | 2017-01-24T11:23:00Z | 0 | 6 | < 25mph | JBGC1 | 6.67 | 2017-01-24T11:13:00Z | 8.99 | 20 | < 25mph | C4565 | 3.06 | 2017-01-24T12:23:00Z | 0 | 12 | < 25mph | JBGC1 | 6.67 | 2017-01-24T12:13:00Z | 13 | 40 | < 25mph
PG&E | 2019-07-13 | 13:13 | 34.7273 | -120.4357 |  | Shrub | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | Y44 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43659 | 13:13 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-154 | 2019 | 7 | 13 | 13 | 13 | 19-0077070 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 18256 | 12.2026 | 225_58 | <25mph | <15mph | HFTD - Distribution | 2019-07-13 13:13:00 | 1900 | 12.8932 | FALSE | <25mph | D4531 | 2.22 | 2015-03-04T02:13:00Z | 7 | 4 | < 25mph | E6531 | 6.63 | 2015-03-04T02:15:00Z | 8.99 | 17 | < 25mph | D4531 | 2.22 | 2015-03-04T03:43:00Z | 7 | 8 | < 25mph | E6531 | 6.63 | 2015-03-04T02:15:00Z | 8.99 | 33 | < 25mph
PG&E | 2017-07-16 11:59 | 11:59 | 36.6669 | -121.7515 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101761892 | None | 21000 | Fuse | Overhead | Yes | 42932.4994 | 11:59 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1259 | 2017 | 7 | 16 | 11 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 22.4318 | 166_166 | <25mph | <15mph | HFTD - Distribution | 2017-07-16 11:59:00 | 998 | 30.0095 | FALSE | 25-40mph | E6666 | 1.85 | 2017-05-17T00:35:00Z | 14 | 10 | < 25mph | KSNS | 7.95 | 2017-05-16T23:35:00Z | 20.71 | 14 | < 25mph | E6666 | 1.85 | 2017-05-17T01:15:00Z | 17 | 17 | < 25mph | KSNS | 7.95 | 2017-05-16T23:35:00Z | 20.71 | 25 | < 25mph
PG&E | 2019-08-12 | 17:42 | 38.6618 | -120.7451 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 101415488, 101404439 |  | 12000 | Pole | Overhead | Yes | 43689 | 17:42 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (slight defect) | 2019-241 | 2019 | 8 | 12 | 17 | 42 | 19-0087080 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 54604 | 8.3029 | 210_275 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 17:42:00 | 1968 | 11.2889 | FALSE | <25mph | E4543 | 3.82 | 2018-01-21T16:11:00Z | 1.01 | 4 | < 25mph | E4543 | 3.82 | 2018-01-21T16:11:00Z | 1.01 | 44 | < 25mph | E4543 | 3.82 | 2018-01-21T16:55:00Z | 1.01 | 9 | < 25mph | C6129 | 6.06 | 2018-01-21T17:14:00Z | 5.99 | 86 | < 25mph
PG&E | 2015-07-26 12:25 | 2015-07-26 12:25 | 39.1586 | -121.0634 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 15499 ALLISON RANCH RD |  | 12000 | Conductor | Overhead | Yes | 42211.5174 | 2015-07-26 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0485 | 2015 | 7 | 26 | 12 | 25 | 15-0050558 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2224 | 13.0644 | 197_303 | <25mph | <15mph | HFTD - Distribution | 2015-07-26 12:25:00 | 230 | 13.6917 | FALSE | <25mph | E1789 | 3.9 | 2015-05-29T05:00:00Z | 2.01 | 10 | < 25mph | E1789 | 3.9 | 2015-05-29T05:00:00Z | 2.01 | 82 | < 25mph | E1789 | 3.9 | 2015-05-29T05:30:00Z | 4 | 20 | < 25mph | E1789 | 3.9 | 2015-05-29T05:30:00Z | 4 | 162 | < 25mph
PG&E | 2017-10-20 | 6:18 | 39.2922 | -121.0157 | Vegetation | Rural | < 3 Meters | Fire Agency | PHILLIP NUNNINK INCIDENT # 27272 | 100087647 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43028 | 6:18 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1499 | 2017 | 10 | 20 | 6 | 18 | 17-0088957 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 102410 | 6.1464 | 199_310 | <25mph | <15mph | HFTD - Distribution | 2017-10-20 06:18:00 | 1242 | 23.0997 | FALSE | <25mph | E3651 | 3.59 | 2018-01-17T06:00:00Z | 3 | 17 | < 25mph | E3651 | 3.59 | 2018-01-17T06:00:00Z | 3 | 52 | < 25mph | E3651 | 3.59 | 2018-01-17T06:00:00Z | 3 | 36 | < 25mph | RRRC1 | 5.48 | 2018-01-17T06:13:00Z | 5.99 | 105 | < 25mph
PG&E | 2017-08-02 | 9:42 | 39.2274 | -123.1081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 5/0 | None | 60000 | Conductor | Overhead | Yes | 42949 | 9:42 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1307 | 2017 | 8 | 2 | 9 | 42 | INT-09925 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 4.0697 | 109_308 | <25mph | <15mph | HFTD - Transmission | 2017-08-02 09:42:00 | 1047 | 15.4312 | FALSE | <25mph |  |  |  | 0 | 0 | No data | COWC1 | 7.26 | 2016-10-16T07:01:00Z | 18.99 | 13 | < 25mph |  |  |  | 0 | 0 | No data | COWC1 | 7.26 | 2016-10-16T07:01:00Z | 18.99 | 26 | < 25mph
PG&E | 2016-10-23 18:44 | 18:10 | 38.021 | -120.5991 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101272943 |  | 115000 | Conductor | Overhead | Yes | 42666.7804 | 18:10 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1043 | 2016 | 10 | 23 | 18 | 10 | INT-08709 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 0 | 9.2045 | 217_240 | <25mph | <15mph | HFTD - Transmission | 2016-10-23 18:10:00 | 784 | 15.0974 | FALSE | <25mph | TT468 | 1.25 | 2019-12-23T11:14:00Z | 7 | 8 | < 25mph | PG266 | 6.14 | 2019-12-23T11:30:00Z | 8.05 | 57 | < 25mph | TT468 | 1.25 | 2019-12-23T11:14:00Z | 7 | 15 | < 25mph | PG161 | 7.22 | 2019-12-23T12:50:00Z | 10.09 | 112 | < 25mph
PG&E | 2016-07-16 08:19 | 2016-07-16 08:19 | 37.4828 | -119.87 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101079104 | None | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0856 | 2016 | 7 | 16 | 8 | 19 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 2.1905 | 249_211 | <25mph | <15mph | HFTD - Distribution | 2016-07-16 08:19:00 | 599 | 13.487 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MPOC1 | 6.57 | 2018-07-26T20:07:00Z | 12.01 | 11 | < 25mph |  |  |  | 0 | 0 | No data | MPOC1 | 6.57 | 2018-07-26T20:07:00Z | 12.01 | 22 | < 25mph
PG&E | 2016-08-01 | 2016-08-01 18:29 | 38.6956 | -120.9283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412720 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0898 | 2016 | 8 | 1 | 18 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2359 | 203_277 | <25mph | <15mph | HFTD - Distribution | 2016-08-01 18:29:00 | 641 | 12.0255 | FALSE | <25mph | D2736 | 1.29 | 2017-08-01T04:15:00Z | 1.01 | 16 | < 25mph | BENC1 | 7.25 | 2017-08-01T04:59:00Z | 4 | 68 | < 25mph | D4464 | 2.83 | 2017-08-01T05:19:00Z | 1.01 | 32 | < 25mph | BENC1 | 7.25 | 2017-08-01T05:59:00Z | 5.99 | 139 | < 25mph
PG&E | 2017-04-25 12:39 | 12:38 | 38.6583 | -120.9762 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101376746 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 42850.5271 | 12:38 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1072 | 2017 | 4 | 25 | 12 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 9.948 | 200_275 | <25mph | <15mph | HFTD - Distribution | 2017-04-25 12:38:00 | 812 | 10.5664 | FALSE | <25mph | D7401 | 2.53 | 2016-06-14T12:31:00Z | 4.99 | 8 | < 25mph | E8856 | 4.43 | 2016-06-14T12:34:00Z | 8.99 | 58 | < 25mph | D7401 | 2.53 | 2016-06-14T13:16:00Z | 8.01 | 16 | < 25mph | E8856 | 4.43 | 2016-06-14T13:54:00Z | 10 | 115 | < 25mph
PG&E | 2015-06-15 15:35 | 2015-06-15 15:35 | 37.1852 | -121.7595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Jose city | 100618215 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42170.6493 | 2015-06-15 15:35 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0384 | 2015 | 6 | 15 | 15 | 35 | 15-0041178 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 345 | 20.7397 | 166_194 | <25mph | <15mph | HFTD - Distribution | 2015-06-15 15:35:00 | 130 | 21.599 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C9520 | 5.63 | 2018-02-04T09:45:00Z | 2.01 | 69 | < 25mph |  |  |  | 0 | 0 | No data | E5617 | 5.37 | 2018-02-04T10:57:00Z | 3 | 136 | < 25mph
PG&E | 2018-10-14 | 19:39 | 38.446 | -120.5147 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | IC- Dillon Gissell- 209-295-7735 | 103384485 | Unknown | 12000 | Conductor | Overhead | Yes | 43387 | 19:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1939 | 2018 | 10 | 14 | 19 | 39 | 18-0090288 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3497327 | 25.4932 | 220_264 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-14 19:39:00 | 1678 | 30.9108 | FALSE | 25-40mph | AT450 | 3.11 | 2015-08-09T21:15:00Z | 14.99 | 16 | < 25mph | AT450 | 3.11 | 2015-08-09T21:15:00Z | 14.99 | 20 | < 25mph | AT450 | 3.11 | 2015-08-09T22:40:00Z | 14.99 | 32 | < 25mph | AT450 | 3.11 | 2015-08-09T22:40:00Z | 14.99 | 40 | < 25mph
PG&E | 2015-08-12 17:38 | 2015-08-12 17:38 | 40.2153 | -123.8681 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 1 SP LD SD METER 1007960761 |  | 12000 | Conductor | Overhead | Yes | 42228.7347 | 2015-08-12 17:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0525 | 2015 | 8 | 12 | 17 | 38 | 15-0054643 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 14640 | 10.9518 | 79_363 | <25mph | <15mph | HFTD - Distribution | 2015-08-12 17:38:00 | 269 | 13.2342 | FALSE | <25mph | PG273 | 1.3 | 2019-09-10T14:20:00Z | 5.99 | 12 | < 25mph | PG273 | 1.3 | 2019-09-10T14:20:00Z | 5.99 | 13 | < 25mph | PG273 | 1.3 | 2019-09-10T15:10:00Z | 6.13 | 24 | < 25mph | PG273 | 1.3 | 2019-09-10T15:10:00Z | 6.13 | 26 | < 25mph
PG&E | 2015-07-12 17:04 | 2015-07-12 17:04 | 37.4713 | -122.4256 | Vegetation | Rural | < 0.25 Acres | Fire Agency | COUNTY FIRE | 1 s w c509 |  | 12000 | Conductor | Overhead | Yes | 42197.7111 | 2015-07-12 17:04 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown | Jumper | Other/Unknown | 0456 | 2015 | 7 | 12 | 17 | 4 | 15-0047023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 117853 | 14.8289 | 137_210 | <25mph | <15mph | HFTD - Distribution | 2015-07-12 17:04:00 | 201 | 14.9925 | FALSE | <25mph | D9259 | 3.49 | 2015-07-15T00:31:00Z | 4 | 4 | < 25mph | HSPC1 | 6.33 | 2015-07-15T01:18:00Z | 34.99 | 53 | 25-40mph | D9259 | 3.49 | 2015-07-15T00:31:00Z | 4 | 8 | < 25mph | HSPC1 | 6.33 | 2015-07-15T01:18:00Z | 34.99 | 103 | 25-40mph
PG&E | 2015-11-09 05:55 | 2015-11-09 05:55 | 34.9984 | -120.3634 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42317.2465 | 2015-11-09 05:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0673 | 2015 | 11 | 9 | 5 | 55 | 15-0076534 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 205393 | 8.4294 | 228_73 | <25mph | <15mph | HFTD - Distribution | 2015-11-09 05:55:00 | 417 | 17.7768 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F0412 | 7.53 | 2018-04-03T14:35:00Z | 3 | 11 | < 25mph |  |  |  | 0 | 0 | No data | F0412 | 7.53 | 2018-04-03T15:25:00Z | 4.99 | 21 | < 25mph
PG&E | 2017-12-20 07:55 | 07:54 | 37.4012 | -122.3606 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100318864 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43089.3298 | 07:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1546 | 2017 | 12 | 20 | 7 | 54 | 17-0102756 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6602 | 16.1413 | 140_206 | <25mph | <15mph | HFTD - Distribution | 2017-12-20 07:54:00 | 1288 | 21.2088 | FALSE | <25mph | E4863 | 2.73 | 2015-12-30T06:54:00Z | 4 | 6 | < 25mph | E2649 | 6.54 | 2015-12-30T07:31:00Z | 8.99 | 23 | < 25mph | E4863 | 2.73 | 2015-12-30T08:14:00Z | 4 | 14 | < 25mph | PUGC1 | 6.04 | 2015-12-30T08:18:00Z | 12.01 | 48 | < 25mph
PG&E | 2016-07-15 05:19 | 2016-07-15 05:19 | 35.1839 | -120.5018 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101846594 |  | 12000 | Conductor | Overhead | Yes | 42566.2215 | 2016-07-15 05:19 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0851 | 2016 | 7 | 15 | 5 | 19 | 16-0050086 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 62404 | 2.6454 | 222_84 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 05:19:00 | 594 | 14.1102 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D6295 | 5.2 | 2016-01-13T17:08:00Z | 8.99 | 11 | < 25mph |  |  |  | 0 | 0 | No data | D6295 | 5.2 | 2016-01-13T17:08:00Z | 8.99 | 21 | < 25mph
PG&E | 2019-08-12 | 17:42 | 38.6618 | -120.7451 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 101415488, 101404439 |  | 12000 | Pole | Overhead | Yes | 43689 | 17:42 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (slight defect) | 2019-241 | 2019 | 8 | 12 | 17 | 42 | 19-0087080 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 54604 | 8.3029 | 210_275 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 17:42:00 | 1968 | 11.2889 | FALSE | <25mph | PG077 | 3.79 | 2018-08-28T06:10:00Z | 2.19 | 10 | < 25mph | PG068 | 5.78 | 2018-08-28T06:20:00Z | 2.64 | 53 | < 25mph | PG077 | 3.79 | 2018-08-28T07:30:00Z | 2.19 | 20 | < 25mph | PG068 | 5.78 | 2018-08-28T07:00:00Z | 2.64 | 106 | < 25mph
PG&E | 2018-06-30 | 22:36 | 39.1141 | -121.077 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Matt Wallen (530) 277-3312 Incident # NEU015486 | 100105380 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 22:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1717 | 2018 | 6 | 30 | 22 | 36 | 18-0056039 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 8004 | 7.8488 | 196_300 | <25mph | <15mph | HFTD - Distribution | 2018-06-30 22:36:00 | 1458 | 15.8656 | FALSE | <25mph | E1789 | 3.68 | 2019-01-27T00:18:00Z | 3 | 20 | < 25mph | E1789 | 3.68 | 2019-01-27T00:18:00Z | 3 | 62 | < 25mph | E1789 | 3.68 | 2019-01-27T01:42:00Z | 4 | 40 | < 25mph | E1789 | 3.68 | 2019-01-27T01:42:00Z | 4 | 125 | < 25mph
PG&E | 2015-07-26 12:25 | 2015-07-26 12:25 | 39.1586 | -121.0634 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 15499 ALLISON RANCH RD |  | 12000 | Conductor | Overhead | Yes | 42211.5174 | 2015-07-26 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0485 | 2015 | 7 | 26 | 12 | 25 | 15-0050558 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2224 | 13.0644 | 197_303 | <25mph | <15mph | HFTD - Distribution | 2015-07-26 12:25:00 | 230 | 13.6917 | FALSE | <25mph | E1789 | 3.9 | 2019-08-07T05:36:00Z | 4 | 10 | < 25mph | AV504 | 5.79 | 2019-08-07T05:25:00Z | 7 | 99 | < 25mph | E1789 | 3.9 | 2019-08-07T06:12:00Z | 7 | 20 | < 25mph | AV504 | 5.79 | 2019-08-07T06:35:00Z | 7 | 196 | < 25mph
PG&E | 2015-02-06 06:01 | 2015-02-06 06:01 | 38.6059 | -121.0221 | Vegetation | Rural | < 3 meters | Fire Agency |  | 6661 Ryan Ranch Road, El Dorado Hills |  | 21000 | Conductor | Overhead | Yes | 42041.2507 | 2015-02-06 06:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0259 | 2015 | 2 | 6 | 6 | 1 | 15-0009876 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 51996 | 16.7927 | 199_272 | <25mph | <15mph | HFTD - Distribution | 2015-02-06 06:01:00 | 6 | 30.3484 | FALSE | 25-40mph | E8856 | 3.45 | 2017-11-22T14:50:00Z | 4 | 12 | < 25mph | BENC1 | 4.89 | 2017-11-22T13:59:00Z | 4.99 | 53 | < 25mph | E8856 | 3.45 | 2017-11-22T14:50:00Z | 4 | 24 | < 25mph | BENC1 | 4.89 | 2017-11-22T13:59:00Z | 4.99 | 102 | < 25mph
PG&E | 2015-07-07 15:27 | 2015-07-07 15:27 | 35.155 | -120.5442 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 303corraltos cyn rd | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42192.6438 | 2015-07-07 15:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0449 | 2015 | 7 | 7 | 15 | 27 | 15-0046127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 98566 | 24.1391 | 220_82 | <25mph | <15mph | HFTD - Distribution | 2015-07-07 15:27:00 | 194 | 24.1391 | FALSE | <25mph | F0194 | 3.06 | 2017-08-26T12:45:00Z | 2.01 | 17 | < 25mph | E8214 | 6.32 | 2017-08-26T12:43:00Z | 3 | 21 | < 25mph | F0194 | 3.06 | 2017-08-26T13:45:00Z | 2.01 | 33 | < 25mph | E8214 | 6.32 | 2017-08-26T12:58:00Z | 3 | 41 | < 25mph
PG&E | 2015-02-23 13:25 | 2015-02-23 13:25 | 38.5046 | -122.7408 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RINCON VALLEY | BEHIND 4870 CARRIAGE LN SANTA ROSA |  | 12000 | Conductor | Overhead | Yes | 42058.559 | 2015-02-23 13:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0268 | 2015 | 2 | 23 | 13 | 25 | 15-0015168 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 85762 | 20.3218 | 124_267 | <25mph | <15mph | HFTD - Distribution | 2015-02-23 13:25:00 | 15 | 32.6885 | FALSE | 25-40mph | RSAC1 | 2.39 | 2019-12-27T22:29:00Z | 10 | 31 | < 25mph | E1553 | 5.33 | 2019-12-27T22:29:00Z | 11.01 | 127 | < 25mph | RSAC1 | 2.39 | 2019-12-27T23:29:00Z | 10 | 62 | < 25mph | E1553 | 5.33 | 2019-12-27T22:29:00Z | 11.01 | 254 | < 25mph
PG&E | 2016-04-30 | 17:59 | 38.3142 | -120.9015 | Vegetation | RURAL | < 3 meters | Fire Agency | Kern County FD |  |  | 12000 | Conductor | Overhead | Yes | 42490 | 17:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0719 | 2016 | 4 | 30 | 17 | 59 | 16-0032910 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 722 | 19.7396 | 204_256 | <25mph | <15mph | HFTD - Distribution | 2016-04-30 17:59:00 | 465 | 19.7396 | FALSE | <25mph | PG404 | 3.58 | 2019-11-30T14:40:00Z | 14.61 | 12 | < 25mph | CMAC1 | 6.54 | 2019-11-30T13:59:00Z | 17 | 16 | < 25mph | PG404 | 3.58 | 2019-11-30T15:20:00Z | 16.15 | 24 | < 25mph | CFAC1 | 4.81 | 2019-11-30T15:05:00Z | 18.99 | 32 | < 25mph
PG&E | 2016-07-15 14:09 | 2016-07-15 14:09 | 38.6965 | -120.8598 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412774 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.5896 | 2016-07-15 14:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0852 | 2016 | 7 | 15 | 14 | 9 | 16-0050274 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 11253 | 10.7453 | 205_277 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 14:09:00 | 595 | 14.2057 | FALSE | <25mph | E6490 | 1.76 | 2016-04-04T01:53:00Z | 7 | 29 | < 25mph | E6490 | 1.76 | 2016-04-04T01:53:00Z | 7 | 63 | < 25mph | E6490 | 1.76 | 2016-04-04T01:53:00Z | 7 | 59 | < 25mph | E6490 | 1.76 | 2016-04-04T01:53:00Z | 7 | 127 | < 25mph
PG&E | 2016-06-26 11:06 | 2016-06-26 11:06 | 40.4832 | -122.0466 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101483777 | FRONTIER | 12000 | Conductor | Overhead | Yes | 42547.4625 | 2016-06-26 11:06 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0826 | 2016 | 6 | 26 | 11 | 6 | 16-0045846 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 15520 | 6.1274 | 155_376 | <25mph | <15mph | HFTD - Distribution | 2016-06-26 11:06:00 | 566 | 14.8861 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2017-10-08 | 19:44 | 39.7446 | -121.597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100330456 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 19:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1464 | 2017 | 10 | 8 | 19 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 33.2724 | 174_335 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-08 19:44:00 | 1202 | 34.7906 | FALSE | 25-40mph | PDEC1 | 1.6 | 2015-09-14T11:00:00Z | 1.01 | 1 | < 25mph | JBGC1 | 5.77 | 2015-09-14T11:13:00Z | 14 | 5 | < 25mph | PDEC1 | 1.6 | 2015-09-14T12:00:00Z | 1.01 | 2 | < 25mph | JBGC1 | 5.77 | 2015-09-14T11:13:00Z | 14 | 10 | < 25mph
PG&E | 2016-04-21 09:25 | 2016-04-21 09:25 | 39.293 | -123.769 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 103312287 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0711 | 2016 | 4 | 21 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 8.8774 | 81_312 | <25mph | <15mph | HFTD - Distribution | 2016-04-21 09:25:00 | 455 | 20.2474 | FALSE | <25mph | E6025 | 0.21 | 2016-10-29T10:15:00Z | 0 | 4 | < 25mph | E6025 | 0.21 | 2016-10-29T10:15:00Z | 0 | 4 | < 25mph | E6025 | 0.21 | 2016-10-29T11:15:00Z | 0 | 8 | < 25mph | E6025 | 0.21 | 2016-10-29T11:15:00Z | 0 | 8 | < 25mph
PG&E | 2017-05-05 15:52 | 15:52 | 40.3776 | -123.0019 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101501566 | None | 12000 | Conductor | Overhead | Yes | 42860.6614 | 15:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1084 | 2017 | 5 | 5 | 15 | 52 | 17-0045707 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 56893 | 24.5621 | 115_371 | <25mph | <15mph | HFTD - Distribution | 2017-05-05 15:52:00 | 824 | 35.0644 | FALSE | 25-40mph | TT100 | 2.89 | 2019-09-20T14:27:00Z | 5.99 | 1 | < 25mph | PG299 | 6.16 | 2019-09-20T13:50:00Z | 20.67 | 8 | < 25mph | TT100 | 2.89 | 2019-09-20T15:27:00Z | 5.99 | 2 | < 25mph | PG299 | 6.16 | 2019-09-20T13:50:00Z | 20.67 | 16 | < 25mph
PG&E | 2017-07-22 12:26 | 12:25 | 40.8795 | -123.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Josh , comander chief of forest service. | 100980577 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.518 | 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1279 | 2017 | 7 | 22 | 12 | 25 | 17-0064721 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 23227 | 10.7493 | 84_399 | <25mph | <15mph | HFTD - Distribution | 2017-07-22 12:25:00 | 1018 | 13.5476 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BHTC1 | 5.5 | 2017-01-03T05:46:00Z | 14.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | BHTC1 | 5.5 | 2017-01-03T05:46:00Z | 14.99 | 2 | < 25mph
PG&E | 2017-09-05 | 6:58 | 39.6727 | -123.5128 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 102194697 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 42983 | 6:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1395 | 2017 | 9 | 5 | 6 | 58 | 17-0075976 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10528 | 9.1824 | 93_333 | <25mph | <15mph | HFTD - Distribution | 2017-09-05 06:58:00 | 1133 | 14.0364 | FALSE | <25mph | LAYC1 | 2.53 | 2017-01-19T20:29:00Z | 5.99 | 1 | < 25mph | LAYC1 | 2.53 | 2017-01-19T20:29:00Z | 5.99 | 1 | < 25mph | LAYC1 | 2.53 | 2017-01-19T21:29:00Z | 7 | 2 | < 25mph | LAYC1 | 2.53 | 2017-01-19T21:29:00Z | 7 | 2 | < 25mph
PG&E | 2016-09-22 | 13:53 | 40.224 | -122.3417 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101539450 | None | 12000 | Conductor | Overhead | Yes | 42635 | 13:53 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0996 | 2016 | 9 | 22 | 13 | 53 | 16-0066692 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 14706 | 14.6017 | 143_362 | <25mph | <15mph | HFTD - Distribution | 2016-09-22 13:53:00 | 739 | 20.1469 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 6.08 | 2017-12-31T19:13:00Z | 8.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 6.08 | 2017-12-31T20:14:00Z | 10 | 8 | < 25mph
PG&E | 2017-06-13 | 14:30 | 37.8526 | -122.1853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Tower 005/035c | Unknown | 115000 | Conductor | Overhead | Yes | 42899 | 14:30 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1143 | 2017 | 6 | 13 | 14 | 30 | INT-09744 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | Balloons | 0 | 10.6352 | 148_231 | <25mph | <15mph | HFTD - Transmission | 2017-06-13 14:30:00 | 882 | 14.5193 | FALSE | <25mph | LBNL1 | 3.84 | 2016-09-18T09:15:00Z | 6.87 | 49 | < 25mph | LBNL1 | 3.84 | 2016-09-18T09:15:00Z | 6.87 | 130 | < 25mph | LBNL1 | 3.84 | 2016-09-18T09:15:00Z | 6.87 | 98 | < 25mph | LTRC1 | 6.59 | 2016-09-18T10:28:00Z | 7 | 272 | < 25mph
PG&E | 2016-09-22 | 13:53 | 40.224 | -122.3417 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101539450 | None | 12000 | Conductor | Overhead | Yes | 42635 | 13:53 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0996 | 2016 | 9 | 22 | 13 | 53 | 16-0066692 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 14706 | 14.6017 | 143_362 | <25mph | <15mph | HFTD - Distribution | 2016-09-22 13:53:00 | 739 | 20.1469 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2018-05-11 | 10:13 | 38.387 | -122.9856 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101973909 | Unknown | 12000 | Conductor | Overhead | Yes | 43231 | 10:13 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1585 | 2018 | 5 | 11 | 10 | 13 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.6545 | 114_261 | <25mph | <15mph | HFTD - Distribution | 2018-05-11 10:13:00 | 1327 | 21.7544 | FALSE | <25mph | E5234 | 3.78 | 2015-05-21T00:27:00Z | 18.99 | 18 | < 25mph | E5234 | 3.78 | 2015-05-21T00:27:00Z | 18.99 | 47 | < 25mph | E5234 | 3.78 | 2015-05-21T00:27:00Z | 18.99 | 36 | < 25mph | E5234 | 3.78 | 2015-05-21T00:27:00Z | 18.99 | 89 | < 25mph
PG&E | 2017-06-15 04:31 | 2:58 | 40.299 | -122.4318 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101511631 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42901.1885 | 2:58 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | Other/Unknown | 1145 | 2017 | 6 | 15 | 2 | 58 | 17-0055359 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1762 | 9.755 | 139_366 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 02:58:00 | 884 | 19.4408 | FALSE | <25mph | E7114 | 1.68 | 2016-07-07T13:12:00Z | 5.99 | 4 | < 25mph | E7114 | 1.68 | 2016-07-07T13:12:00Z | 5.99 | 5 | < 25mph | E7114 | 1.68 | 2016-07-07T13:27:00Z | 7 | 8 | < 25mph | E7114 | 1.68 | 2016-07-07T13:27:00Z | 7 | 9 | < 25mph
PG&E | 2018-09-11 | 5:23 | 37.376 | -119.6304 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | TROY CHEEK 209-966-3621 | 101023184 | Unknown | 12000 | Conductor | Overhead | Yes | 43354 | 5:23 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1891 | 2018 | 9 | 11 | 5 | 23 | 18-0078387 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 288 | 4.3046 | 260_205 | <25mph | <15mph | HFTD - Distribution | 2018-09-11 05:23:00 | 1630 | 11.3584 | FALSE | <25mph | BSNC1 | 0.17 | 2017-11-21T14:48:00Z | 5.99 | 13 | < 25mph | BSNC1 | 0.17 | 2017-11-21T14:48:00Z | 5.99 | 32 | < 25mph | BSNC1 | 0.17 | 2017-11-21T15:48:00Z | 5.99 | 25 | < 25mph | MCFC1 | 7.89 | 2017-11-21T16:02:00Z | 8.01 | 63 | < 25mph
PG&E | 2016-08-05 | 2016-08-05 14:46 | 40.4797 | -123.7803 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103572261 |  | 12000 | Conductor | Overhead | Yes | 42587 | 2016-08-05 14:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0907 | 2016 | 8 | 5 | 14 | 46 | 16-0055425 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 7019 | 13.7408 | 83_377 | <25mph | <15mph | HFTD - Distribution | 2016-08-05 14:46:00 | 650 | 14.7579 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-06-15 | 2016-06-15 13:09 | 38.4433 | -120.7568 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103169620 |  | 12000 | Conductor | Overhead | Yes | 42536 | 2016-06-15 13:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0801 | 2016 | 6 | 15 | 13 | 9 | 16-0043476 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 23963 | 15.7348 | 210_263 | <25mph | <15mph | HFTD - Distribution | 2016-06-15 13:09:00 | 543 | 16.8625 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.74 | 2016-04-26T04:56:00Z | 8.01 | 2 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.74 | 2016-04-26T05:56:00Z | 8.01 | 4 | < 25mph
PG&E | 2019-07-23 | 16:55 | 37.2128 | -119.505 | Gun Shot | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | 252521103 |  | 12000 | Conductor | Overhead | Yes | 43669 | 16:55 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-434 | 2019 | 7 | 23 | 16 | 55 | 19-0080383 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 513358 | 13.6168 | 265_196 | <25mph | <15mph | HFTD - Distribution | 2019-07-23 16:55:00 | 1923 | 13.6168 | FALSE | <25mph | NFRC1 | 1.4 | 2015-12-01T17:55:00Z | 8.01 | 4 | < 25mph | NFRC1 | 1.4 | 2015-12-01T17:55:00Z | 8.01 | 4 | < 25mph | NFRC1 | 1.4 | 2015-12-01T17:55:00Z | 8.01 | 8 | < 25mph | NFRC1 | 1.4 | 2015-12-01T17:55:00Z | 8.01 | 8 | < 25mph
PG&E | 2017-08-08 04:23 | 4:10 | 38.4949 | -122.6685 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 102025742 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42955.1829 | 4:10 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1325 | 2017 | 8 | 8 | 4 | 10 | 17-0068642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 2750 | 5.2658 | 127_267 | <25mph | <15mph | HFTD - Distribution | 2017-08-08 04:10:00 | 1062 | 14.7124 | FALSE | <25mph | RSAC1 | 2.6 | 2019-02-05T09:29:00Z | 4 | 22 | < 25mph | PG005 | 4.89 | 2019-02-05T09:40:00Z | 5.7 | 58 | < 25mph | C3628 | 3.62 | 2019-02-05T10:46:00Z | 4 | 43 | < 25mph | PG005 | 4.89 | 2019-02-05T11:10:00Z | 6.8 | 115 | < 25mph
PG&E | 2018-10-20 | 14:31 | 40.5218 | -124.1137 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Str. 003/000 | None | 60000 | Conductor | Overhead | Yes | 43393 | 14:31 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1947 | 2018 | 10 | 20 | 14 | 31 | INT-11477 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 410982 | 9.6901 | 69_380 | <25mph | <15mph | HFTD - Transmission | 2018-10-20 14:31:00 | 1686 | 10.3412 | FALSE | <25mph | AT493 | 3.34 | 2015-02-16T11:08:00Z | 7 | 24 | < 25mph | AT493 | 3.34 | 2015-02-16T11:08:00Z | 7 | 24 | < 25mph | AT493 | 3.34 | 2015-02-16T11:38:00Z | 8.01 | 48 | < 25mph | AT493 | 3.34 | 2015-02-16T11:38:00Z | 8.01 | 48 | < 25mph
PG&E | 2017-07-31 14:42 | 14:41 | 38.7967 | -121.1329 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103782414 | Unknown | 12000 | Conductor | Overhead | Yes | 42947.6123 | 14:41 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1305 | 2017 | 7 | 31 | 14 | 41 | 17-0066797 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 210 | 10.6525 | 194_283 | <25mph | <15mph | HFTD - Distribution | 2017-07-31 14:41:00 | 1043 | 12.727 | FALSE | <25mph | D2336 | 3.3 | 2016-06-09T00:01:00Z | 7 | 4 | < 25mph | PLTC1 | 7.08 | 2016-06-08T23:56:00Z | 13 | 22 | < 25mph | D2336 | 3.3 | 2016-06-09T00:01:00Z | 7 | 7 | < 25mph | D0140 | 4.66 | 2016-06-09T01:00:00Z | 14 | 43 | < 25mph
PG&E | 2017-08-19 | 21:16 | 40.5752 | -122.2985 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464623 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42966 | 21:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1341 | 2017 | 8 | 19 | 21 | 16 | 17-0071522 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 19044 | 8.8981 | 145_381 | <25mph | <15mph | HFTD - Distribution | 2017-08-19 21:16:00 | 1079 | 13.341 | FALSE | <25mph | C5599 | 2.67 | 2018-12-21T17:56:00Z | 0 | 11 | < 25mph | RRAC1 | 4.12 | 2018-12-21T17:24:00Z | 5.99 | 12 | < 25mph | C5599 | 2.67 | 2018-12-21T18:56:00Z | 0 | 18 | < 25mph | RRAC1 | 4.12 | 2018-12-21T17:24:00Z | 5.99 | 20 | < 25mph
PG&E | 2016-07-28 13:19 | 2016-07-28 13:19 | 39.7127 | -123.4973 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102195566 |  | 12000 | Conductor | Overhead | Yes | 42579.5549 | 2016-07-28 13:19 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0886 | 2016 | 7 | 28 | 13 | 19 | 16-0053369 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 4447 | 11.1949 | 93_335 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 13:19:00 | 629 | 12.238 | FALSE | <25mph | LAYC1 | 0.97 | 2016-12-06T20:29:00Z | 8.99 | 1 | < 25mph | LAYC1 | 0.97 | 2016-12-06T20:29:00Z | 8.99 | 1 | < 25mph | LAYC1 | 0.97 | 2016-12-06T20:29:00Z | 8.99 | 2 | < 25mph | LAYC1 | 0.97 | 2016-12-06T20:29:00Z | 8.99 | 2 | < 25mph
PG&E | 2019-08-31 | 10:20 | 40.661 | -122.356 | Vehicle | Barren/Other | 3 meters - 0.25 Acres | Fire Dept | Shasta Lake FD | 103571671 | Yes | 12000 | Fuse | Overbuild | Yes | 43708 | 10:20 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-421 | 2019 | 8 | 31 | 10 | 20 | 19-0094332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3050 | 3.1396 | 143_386 | <25mph | <15mph | HFTD - Distribution | 2019-08-31 10:20:00 | 2007 | 12.9011 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AU138 | 7.86 | 2016-07-27T09:53:00Z | 4 | 7 | < 25mph |  |  |  | 0 | 0 | No data | AU138 | 7.86 | 2016-07-27T10:53:00Z | 4.99 | 14 | < 25mph
PG&E | 2015-04-30 00:26 | 2015-04-30 00:26 | 37.2401 | -122.2472 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 1145 VERDE R |  | 12000 | Conductor | Overhead | Yes | 42124.0181 | 2015-04-30 00:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0304 | 2015 | 4 | 30 | 0 | 26 | 15-0030607 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1256 | 5.7566 | 145_197 | <25mph | <15mph | HFTD - Distribution | 2015-04-30 00:26:00 | 50 | 15.5915 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6800 | 5.71 | 2018-05-07T14:53:00Z | 5.99 | 18 | < 25mph |  |  |  | 0 | 0 | No data | E6800 | 5.71 | 2018-05-07T14:53:00Z | 5.99 | 35 | < 25mph
PG&E | 2018-07-27 | 23:12 | 37.18 | -122.029 | Vegetation | Rural | < 3 meters | Fire Agency | Jeremy Wise 408-378-4010 Incident # C182080066 | 100518365 | Unknown | 12000 | Conductor | Overhead | Yes | 43308 | 23:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1793 | 2018 | 7 | 27 | 23 | 12 | 18-0064525 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 30475 | 3.2895 | 154_194 | <25mph | <15mph | HFTD - Distribution | 2018-07-27 23:12:00 | 1533 | 9.1823 | FALSE | <25mph | D9791 | 2.82 | 2017-09-04T10:11:00Z | 5.99 | 10 | < 25mph | E8391 | 7.91 | 2017-09-04T09:42:00Z | 13 | 132 | < 25mph | D9791 | 2.82 | 2017-09-04T10:11:00Z | 5.99 | 17 | < 25mph | E8391 | 7.91 | 2017-09-04T09:42:00Z | 13 | 245 | < 25mph
PG&E | 2016-08-22 | 2016-08-22 16:10 | 37.9666 | -120.2395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Toulumne City FD | 101043683 |  | 17000 | Conductor | Overhead | Yes | 42604 | 2016-08-22 16:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0941 | 2016 | 8 | 22 | 16 | 10 | 16-0059149 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 78534 | 13.4322 | 233_237 | <25mph | <15mph | HFTD - Distribution | 2016-08-22 16:10:00 | 684 | 13.7297 | FALSE | <25mph | PG067 | 2.98 | 2019-04-27T06:20:00Z | 8.99 | 18 | < 25mph | PG179 | 5.61 | 2019-04-27T06:10:00Z | 9.86 | 43 | < 25mph | PG067 | 2.98 | 2019-04-27T06:20:00Z | 8.99 | 36 | < 25mph | PG179 | 5.61 | 2019-04-27T06:50:00Z | 10.09 | 85 | < 25mph
PG&E | 2015-07-30 19:11 | 2015-07-30 19:11 | 37.8102 | -120.1287 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE |  |  | 17000 | Conductor | Overhead | Yes | 42215.7993 | 2015-07-30 19:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0500 | 2015 | 7 | 30 | 19 | 11 | 15-0051772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26776 | 10.007 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2015-07-30 19:11:00 | 245 | 11.7658 | FALSE | <25mph | SEWC1 | 1.66 | 2015-09-29T10:16:00Z | 8.99 | 1 | < 25mph | SEWC1 | 1.66 | 2015-09-29T10:16:00Z | 8.99 | 6 | < 25mph | SEWC1 | 1.66 | 2015-09-29T11:16:00Z | 8.99 | 2 | < 25mph | SEWC1 | 1.66 | 2015-09-29T11:16:00Z | 8.99 | 13 | < 25mph
PG&E | 2015-08-30 17:05 | 2015-08-30 17:05 | 38.4039 | -120.5559 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | centennial mine rd |  | 12000 | Conductor | Overhead | Yes | 42246.7118 | 2015-08-30 17:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0567 | 2015 | 8 | 30 | 17 | 5 | 15-0058273 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 40298 | 10.8566 | 219_261 | <25mph | <15mph | HFTD - Distribution | 2015-08-30 17:05:00 | 311 | 12.2451 | FALSE | <25mph | AT450 | 1.93 | 2017-10-05T09:53:00Z | 3 | 8 | < 25mph | C9148 | 6.15 | 2017-10-05T09:48:00Z | 4.99 | 24 | < 25mph | AT450 | 1.93 | 2017-10-05T11:18:00Z | 3 | 17 | < 25mph | C9148 | 6.15 | 2017-10-05T09:48:00Z | 4.99 | 48 | < 25mph
PG&E | 2017-09-08 | 21:14 | 37.9604 | -120.3764 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | John Lite 209-984-5623 | 101042521 | Unknown | 17000 | Conductor | Overhead | Yes | 42986 | 21:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1403 | 2017 | 9 | 8 | 21 | 14 | 17-0077137 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49858 | 11.2644 | 227_237 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 21:14:00 | 1141 | 11.9927 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C3161 | 5.93 | 2016-11-02T15:59:00Z | 1.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | C3161 | 5.93 | 2016-11-02T17:45:00Z | 4 | 8 | < 25mph
PG&E | 2016-09-12 | 12:38 | 38.7832 | -120.6006 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101421708 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42625 | 12:38 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0974 | 2016 | 9 | 12 | 12 | 38 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 15.5165 | 217_282 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 12:38:00 | 716 | 15.5342 | FALSE | <25mph | PG105 | 2.18 | 2019-07-06T14:00:00Z | 6.58 | 12 | < 25mph | PG104 | 6.88 | 2019-07-06T14:30:00Z | 14.47 | 37 | < 25mph | PG105 | 2.18 | 2019-07-06T14:00:00Z | 6.58 | 24 | < 25mph | PG104 | 6.88 | 2019-07-06T15:30:00Z | 14.47 | 74 | < 25mph
PG&E | 2018-07-25 | 0:42 | 39.7791 | -121.6173 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100327443 | Unknown | 12000 | Conductor | Overhead | Yes | 43306 | 0:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1788 | 2018 | 7 | 25 | 0 | 42 | 18-0063320 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6742 | 1.3279 | 173_337 | <25mph | <15mph | HFTD - Distribution | 2018-07-25 00:42:00 | 1528 | 11.7229 | FALSE | <25mph | E2076 | 2.2 | 2015-10-07T15:13:00Z | 2.01 | 16 | < 25mph | JBGC1 | 7.44 | 2015-10-07T15:13:00Z | 20 | 28 | < 25mph | E2076 | 2.2 | 2015-10-07T16:33:00Z | 2.01 | 32 | < 25mph | JBGC1 | 7.44 | 2015-10-07T16:13:00Z | 24 | 61 | < 25mph
PG&E | 2017-09-03 | 17:52 | 37.4956 | -119.8367 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101086621 | Unknown | 21000 | Transformer | Overhead | Yes | 42981 | 17:52 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 1389 | 2017 | 9 | 3 | 17 | 52 | 17-0075617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 4512 | 13.9592 | 250_212 | <25mph | <15mph | HFTD - Distribution | 2017-09-03 17:52:00 | 1127 | 22.0754 | FALSE | <25mph | JSDC1 | 3.33 | 2017-12-02T09:47:00Z | 8.01 | 1 | < 25mph | JSDC1 | 3.33 | 2017-12-02T09:47:00Z | 8.01 | 8 | < 25mph | JSDC1 | 3.33 | 2017-12-02T09:47:00Z | 8.01 | 2 | < 25mph | JSDC1 | 3.33 | 2017-12-02T09:47:00Z | 8.01 | 18 | < 25mph
PG&E | 2017-07-12 15:09 | 15:09 | 37.1491 | -122.0037 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 103565794 | Unknown | 21000 | Conductor | Overhead | Yes | 42928.6313 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1248 | 2017 | 7 | 12 | 15 | 9 | 17-0062439 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24690 | 9.5326 | 155_192 | <25mph | <15mph | HFTD - Distribution | 2017-07-12 15:09:00 | 986 | 9.5326 | FALSE | <25mph | D9791 | 1 | 2019-05-01T12:31:00Z | 2.01 | 26 | < 25mph | SJS04 | 6.44 | 2019-05-01T12:40:00Z | 20.4 | 167 | < 25mph | D9791 | 1 | 2019-05-01T13:41:00Z | 2.01 | 52 | < 25mph | SJS04 | 6.44 | 2019-05-01T13:00:00Z | 22.15 | 326 | < 25mph
5. Atlas (Southern LNU Complex) | 2017-10-08 | 21:52 | 38.3921 | -122.2437 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1991 | 2017 | 10 | 8 | 21 | 52 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 37.6357 | 146_261 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-08 21:52:00 | 1206 | 41.3099 | FALSE | 40-55mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.83 | 2016-09-14T10:29:00Z | 0 | 7 | < 25mph |  |  |  | 0 | 0 | No data | ATLC1 | 5.83 | 2016-09-14T11:29:00Z | 0 | 17 | < 25mph
PG&E | 2015-04-04 16:49 | 2015-04-04 16:49 | 38.8824 | -122.5914 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 20748 Jerusalem Grade Road, Middletown |  | 12000 | Other | Overhead | Yes | 42098.7007 | 2015-04-04 16:49 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0285 | 2015 | 4 | 4 | 16 | 49 | 15-0024208 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 20448 | 16.9925 | 131_288 | <25mph | <15mph | HFTD - Distribution | 2015-04-04 16:49:00 | 31 | 19.3597 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.51 | 2015-01-15T20:57:00Z | 5.99 | 14 | < 25mph |  |  |  | 0 | 0 | No data | KELC1 | 6.51 | 2015-01-15T21:57:00Z | 8.01 | 26 | < 25mph
PG&E | 2016-08-08 | 2016-08-08 15:44 | 37.1382 | -121.9672 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100519919 |  | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0912 | 2016 | 8 | 8 | 15 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 8.8992 | 157_192 | <25mph | <15mph | HFTD - Distribution | 2016-08-08 15:44:00 | 655 | 10.1741 | FALSE | <25mph | D9791 | 1.67 | 2019-10-09T01:31:00Z | 3 | 28 | < 25mph | SJS04 | 4.4 | 2019-10-09T02:15:00Z | 15.12 | 165 | < 25mph | PG057 | 2.38 | 2019-10-09T03:20:00Z | 6.22 | 57 | < 25mph | SJS04 | 4.4 | 2019-10-09T02:15:00Z | 15.12 | 334 | < 25mph
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 9:36 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 14.8685 | 222_261 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 09:36:00 | 925 | 23.4839 | FALSE | <25mph | AT450 | 2.61 | 2015-06-04T15:16:00Z | 4 | 12 | < 25mph | ESPC1 | 7.8 | 2015-06-04T15:13:00Z | 4.99 | 19 | < 25mph | AT450 | 2.61 | 2015-06-04T16:16:00Z | 7 | 28 | < 25mph | AT450 | 2.61 | 2015-06-04T16:16:00Z | 7 | 42 | < 25mph
PG&E | 2017-07-24 21:45 | 21:45 | 35.6024 | -120.9211 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101860186 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.9063 | 21:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1289 | 2017 | 7 | 24 | 21 | 45 | 17-0065191 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 21231 | 19.4445 | 203_107 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 21:45:00 | 1028 | 30.0108 | FALSE | 25-40mph | TABC1 | 3.74 | 2017-03-25T06:07:00Z | 7 | 1 | < 25mph | TABC1 | 3.74 | 2017-03-25T06:07:00Z | 7 | 1 | < 25mph | TABC1 | 3.74 | 2017-03-25T07:07:00Z | 7 | 2 | < 25mph | TABC1 | 3.74 | 2017-03-25T07:07:00Z | 7 | 2 | < 25mph
PG&E | 2017-08-15 19:29 | 19:28 | 39.5037 | -121.2783 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 100396172 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42962.8116 | 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1335 | 2017 | 8 | 15 | 19 | 28 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.8405 | 188_322 | <25mph | <15mph | HFTD - Distribution | 2017-08-15 19:28:00 | 1073 | 9.7276 | FALSE | <25mph | PG080 | 2.17 | 2019-03-22T17:10:00Z | 13.8 | 6 | < 25mph | PKCC1 | 4.51 | 2019-03-22T17:10:00Z | 14 | 8 | < 25mph | PG080 | 2.17 | 2019-03-22T17:10:00Z | 13.8 | 12 | < 25mph | PKCC1 | 4.51 | 2019-03-22T18:10:00Z | 14.99 | 16 | < 25mph
PG&E | 2015-06-28 02:50 | 2015-06-28 02:50 | 35.491 | -120.731 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 13505 Santa Lucia Rd. Atascadero |  | 12000 | Conductor | Overhead | Yes | 42183.1181 | 2015-06-28 02:50 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0418 | 2015 | 6 | 28 | 2 | 50 | 15-0043807 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 12323 | 9.9634 | 212_101 | <25mph | <15mph | HFTD - Distribution | 2015-06-28 02:50:00 | 163 | 24.8049 | FALSE | <25mph | E6394 | 1.17 | 2017-01-22T20:03:00Z | 18.01 | 4 | < 25mph | E6394 | 1.17 | 2017-01-22T20:03:00Z | 18.01 | 4 | < 25mph | E6394 | 1.17 | 2017-01-22T20:03:00Z | 18.01 | 8 | < 25mph | E6394 | 1.17 | 2017-01-22T20:03:00Z | 18.01 | 8 | < 25mph
PG&E | 2017-06-24 15:06 | 14:51 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 42910.6292 | 14:51 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1194 | 2017 | 6 | 24 | 14 | 51 | 17-0058332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 21296 | 10.4286 | 210_259 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 14:51:00 | 933 | 10.7263 | FALSE | <25mph | TS389 | 1.42 | 2018-01-27T14:53:00Z | 4.99 | 5 | < 25mph | TS389 | 1.42 | 2018-01-27T14:53:00Z | 4.99 | 6 | < 25mph | TS389 | 1.42 | 2018-01-27T15:53:00Z | 4.99 | 10 | < 25mph | MTZC1 | 6.33 | 2018-01-27T15:56:00Z | 5.99 | 12 | < 25mph
PG&E | 2018-10-16 | 10:44 | 40.5097 | -124.1624 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101004106 | Unknown | 12000 | Conductor | Overhead | Yes | 43389 | 10:44 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1942 | 2018 | 10 | 16 | 10 | 44 | 18-0090952 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 2081 | 4.5851 | 67_380 | <25mph | <15mph | HFTD - Distribution | 2018-10-16 10:44:00 | 1681 | 13.3626 | FALSE | <25mph | PG287 | 3.28 | 2019-06-15T06:10:00Z | 7 | 7 | < 25mph | PG249 | 5.35 | 2019-06-15T06:20:00Z | 15.77 | 43 | < 25mph | PG287 | 3.28 | 2019-06-15T06:10:00Z | 7 | 13 | < 25mph | PG249 | 5.35 | 2019-06-15T06:20:00Z | 15.77 | 81 | < 25mph
PG&E | 2017-09-24 | 16:42 | 38.3869 | -122.9667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DOUG JONES | 101973946 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43002 | 16:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1432 | 2017 | 9 | 24 | 16 | 42 | 17-0081329 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 22574 | 19.6154 | 114_261 | <25mph | <15mph | HFTD - Distribution | 2017-09-24 16:42:00 | 1170 | 19.6154 | FALSE | <25mph | E5234 | 2.8 | 2015-04-28T14:28:00Z | 3 | 19 | < 25mph | UCBM | 7.15 | 2015-04-28T13:50:00Z | 17.2 | 62 | < 25mph | E5234 | 2.8 | 2015-04-28T14:48:00Z | 3 | 37 | < 25mph | UCBM | 7.15 | 2015-04-28T13:50:00Z | 17.2 | 126 | < 25mph
PG&E | 2016-07-27 17:05 | 2016-07-27 17:05 | 38.5392 | -122.7656 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102029945 |  | 60000 | Conductor | Overhead | Yes | 42578.7118 | 2016-07-27 17:05 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0882 | 2016 | 7 | 27 | 17 | 5 | FU-2016-047 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 18.1446 | 123_269 | <25mph | <15mph | HFTD - Transmission | 2016-07-27 17:05:00 | 625 | 18.1446 | FALSE | <25mph | E6724 | 1.55 | 2016-11-13T09:50:00Z | 1.01 | 12 | < 25mph | RSAC1 | 5.1 | 2016-11-13T10:29:00Z | 4.99 | 70 | < 25mph | E6724 | 1.55 | 2016-11-13T09:50:00Z | 1.01 | 28 | < 25mph | E1553 | 4.66 | 2016-11-13T11:29:00Z | 5.99 | 144 | < 25mph
PG&E | 2016-08-12 | 2016-08-12 10:08 | 38.8751 | -122.4223 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 102168360 |  | 12000 | Conductor | Overhead | Yes | 42594 | 2016-08-12 10:08 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0922 | 2016 | 8 | 12 | 10 | 8 | 16-0056982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 1368 | 5.1025 | 138_288 | <25mph | <15mph | HFTD - Distribution | 2016-08-12 10:08:00 | 665 | 17.0718 | FALSE | <25mph | KNXC1 | 0.95 | 2016-07-08T04:09:00Z | 8.99 | 1 | < 25mph | KNXC1 | 0.95 | 2016-07-08T04:09:00Z | 8.99 | 9 | < 25mph | KNXC1 | 0.95 | 2016-07-08T04:09:00Z | 8.99 | 2 | < 25mph | KNXC1 | 0.95 | 2016-07-08T04:09:00Z | 8.99 | 18 | < 25mph
PG&E | 2018-08-07 | 17:15 | 37.1181 | -122.1093 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101670606 | AT&T | 12000 | Conductor | Overhead | Yes | 43319 | 17:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1827 | 2018 | 8 | 7 | 17 | 15 | 18-0067641 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1988 | 17.3453 | 151_191 | <25mph | <15mph | HFTD - Distribution | 2018-08-07 17:15:00 | 1567 | 17.3453 | FALSE | <25mph | BNDC1 | 3.6 | 2019-02-12T15:50:00Z | 13 | 26 | < 25mph | BNDC1 | 3.6 | 2019-02-12T15:50:00Z | 13 | 62 | < 25mph | BNDC1 | 3.6 | 2019-02-12T16:50:00Z | 21 | 52 | < 25mph | BNDC1 | 3.6 | 2019-02-12T16:50:00Z | 21 | 120 | < 25mph
PG&E | 2019-05-30 | 8:18 | 35.7005 | -120.8104 | Vehicle | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 101871463 |  | 12000 | Pole | Overhead | Yes | 43615 | 8:18 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-274 | 2019 | 5 | 30 | 8 | 18 | 19-0059906 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 171603 | 10.8019 | 208_112 | <25mph | <15mph | HFTD - Distribution | 2019-05-30 08:18:00 | 1791 | 17.2262 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TABC1 | 7.07 | 2015-01-14T14:07:00Z | 3 | 6 | < 25mph |  |  |  | 0 | 0 | No data | D4060 | 4.58 | 2015-01-14T14:49:00Z | 4 | 11 | < 25mph
PG&E | 2017-06-08 15:19 | 15:08 | 34.6058 | -120.0214 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SHAWN STEINER | 101947678 | Unknown | 12000 | Conductor | Overhead | Yes | 42894.6382 | 15:08 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1136 | 2017 | 6 | 8 | 15 | 8 | 17-0053783 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 41311 | 18.6266 | 244_52 | <25mph | <15mph | HFTD - Distribution | 2017-06-08 15:08:00 | 875 | 20.2983 | FALSE | <25mph |  |  |  | 0 | 0 | No data | SXWC1 | 5.38 | 2017-10-06T11:09:00Z | 4.99 | 12 | < 25mph |  |  |  | 0 | 0 | No data | SXWC1 | 5.38 | 2017-10-06T12:09:00Z | 7 | 23 | < 25mph
PG&E | 2019-04-09 | 14:07 | 34.6311 | -119.9813 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Fire Dept | Santa Barbra County FD | 101863014 |  | 12000 | Conductor | Overhead | Yes | 43564 | 14:07 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-263 | 2019 | 4 | 9 | 14 | 7 | 19-0040969 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 70756 | 38.5369 | 246_53 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-09 14:07:00 | 1737 | 43.1384 | FALSE | 40-55mph |  |  |  | 0 | 0 | No data | UCSE | 5.53 | 2018-07-11T17:20:00Z | 9.1 | 11 | < 25mph |  |  |  | 0 | 0 | No data | AP901 | 6.75 | 2018-07-11T18:10:00Z | 12.01 | 21 | < 25mph
PG&E | 2017-07-12 20:22 | 20:21 | 40.0808 | -123.8339 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103841917 | Unknown | 12000 | Conductor | Overhead | Yes | 42928.8485 | 20:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1249 | 2017 | 7 | 12 | 20 | 21 | 17-0062445 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 4616 | 11.5535 | 80_355 | <25mph | <15mph | HFTD - Distribution | 2017-07-12 20:21:00 | 988 | 18.1059 | FALSE | <25mph | AV037 | 2.72 | 2015-08-24T23:03:00Z | 10 | 6 | < 25mph | ERCC1 | 4.01 | 2015-08-24T22:28:00Z | 14 | 7 | < 25mph | AV037 | 2.72 | 2015-08-24T23:33:00Z | 10 | 10 | < 25mph | ERCC1 | 4.01 | 2015-08-24T23:28:00Z | 14.99 | 12 | < 25mph
PG&E | 2018-09-11 | 5:23 | 37.376 | -119.6304 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | TROY CHEEK 209-966-3621 | 101023184 | Unknown | 12000 | Conductor | Overhead | Yes | 43354 | 5:23 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1891 | 2018 | 9 | 11 | 5 | 23 | 18-0078387 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 288 | 4.3046 | 260_205 | <25mph | <15mph | HFTD - Distribution | 2018-09-11 05:23:00 | 1630 | 11.3584 | FALSE | <25mph | BSNC1 | 0.17 | 2019-08-01T12:48:00Z | 8.01 | 30 | < 25mph | MIAC1 | 6.99 | 2019-08-01T12:59:00Z | 10 | 81 | < 25mph | BSNC1 | 0.17 | 2019-08-01T13:48:00Z | 8.99 | 62 | < 25mph | MIAC1 | 6.99 | 2019-08-01T12:59:00Z | 10 | 155 | < 25mph
PG&E | 2019-07-17 | 7:49 | 34.5066 | -120.2247 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Santa Barbara County FD | 4Bx0717190747 |  | 12000 | Other | Overhead | Yes | 43663 | 7:49 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-425 | 2019 | 7 | 17 | 7 | 49 | 19-0078239 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 19608 | 17.3045 | 235_46 | <25mph | <15mph | HFTD - Distribution | 2019-07-17 07:49:00 | 1908 | 28.4942 | FALSE | 25-40mph | UP481 | 2.43 | 2015-09-18T02:00:00Z | 39.01 | 13 | 25-40mph | UP481 | 2.43 | 2015-09-18T02:00:00Z | 39.01 | 13 | 25-40mph | UP481 | 2.43 | 2015-09-18T02:00:00Z | 39.01 | 26 | 25-40mph | UP481 | 2.43 | 2015-09-18T02:00:00Z | 39.01 | 26 | 25-40mph
PG&E | 2015-08-07 06:32 | 2015-08-07 06:32 | 37.84 | -122.1823 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100498058 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42223.2722 | 2015-08-07 06:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0517 | 2015 | 8 | 7 | 6 | 32 | 15-0053493 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.7497 | 148_230 | <25mph | <15mph | HFTD - Distribution | 2015-08-07 06:32:00 | 261 | 20.6611 | FALSE | <25mph | ONOC1 | 2.72 | 2017-03-18T08:33:00Z | 4.99 | 53 | < 25mph | LTRC1 | 6.31 | 2017-03-18T08:28:00Z | 10 | 152 | < 25mph | C1634 | 3.52 | 2017-03-18T10:04:00Z | 4.99 | 103 | < 25mph | LTRC1 | 6.31 | 2017-03-18T08:28:00Z | 10 | 302 | < 25mph
PG&E | 2016-08-02 | 2016-08-02 16:15 | 37.0312 | -119.4395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Fresno County FD | 100675986 |  | 12000 | Conductor | Overhead | Yes | 42584 | 2016-08-02 16:15 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0900 | 2016 | 8 | 2 | 16 | 15 | 16-0054552 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 265566 | 14.0604 | 268_186 | <25mph | <15mph | HFTD - Distribution | 2016-08-02 16:15:00 | 643 | 14.6638 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTQC1 | 4.04 | 2015-12-13T03:52:00Z | 4 | 6 | < 25mph |  |  |  | 0 | 0 | No data | MTQC1 | 4.04 | 2015-12-13T04:52:00Z | 4 | 12 | < 25mph
PG&E | 2017-07-31 14:42 | 14:41 | 38.7967 | -121.1329 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103782414 | Unknown | 12000 | Conductor | Overhead | Yes | 42947.6123 | 14:41 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1305 | 2017 | 7 | 31 | 14 | 41 | 17-0066797 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 210 | 10.6525 | 194_283 | <25mph | <15mph | HFTD - Distribution | 2017-07-31 14:41:00 | 1043 | 12.727 | FALSE | <25mph | D2336 | 3.3 | 2016-11-30T05:46:00Z | 0 | 3 | < 25mph | FSLC1 | 7.26 | 2016-11-30T05:50:00Z | 8.32 | 32 | < 25mph | D2336 | 3.3 | 2016-11-30T06:34:00Z | 0 | 6 | < 25mph | FSLC1 | 7.26 | 2016-11-30T05:50:00Z | 8.32 | 64 | < 25mph
PG&E | 2016-05-15 15:54 | 2016-05-15 15:54 | 36.7948 | -119.3966 | Vegetation | RURAL | 100 - 299 Acres | Fire Agency | Cal Fire | 100729685 | None | 12000 | Conductor | Overhead | Yes | 42505.6625 | 2016-05-15 15:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0730 | 2016 | 5 | 15 | 15 | 54 | 16-0036136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 180310 | 10.5903 | 270_173 | <25mph | <15mph | HFTD - Distribution | 2016-05-15 15:54:00 | 474 | 14.7659 | FALSE | <25mph |  |  |  | 0 | 0 | No data | FCHC1 | 7.54 | 2015-09-03T12:00:00Z | 5.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | FCHC1 | 7.54 | 2015-09-03T12:00:00Z | 5.99 | 2 | < 25mph
PG&E | 2016-08-31 | 2016-08-31 14:52 | 35.1918 | -120.4697 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101942860 |  | 12000 | Conductor | Overhead | Yes | 42613 | 2016-08-31 14:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0955 | 2016 | 8 | 31 | 14 | 52 | 16-0061423 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 156294 | 16.7717 | 224_84 | <25mph | <15mph | HFTD - Distribution | 2016-08-31 14:52:00 | 697 | 16.7717 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C9687 | 6.31 | 2018-05-01T06:57:00Z | 4 | 22 | < 25mph |  |  |  | 0 | 0 | No data | C9687 | 6.31 | 2018-05-01T07:57:00Z | 5.99 | 49 | < 25mph
PG&E | 2016-09-26 | 10:40 | 38.0157 | -122.6889 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | marin county fire | 102252082 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42639 | 10:40 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1005 | 2016 | 9 | 26 | 10 | 40 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 4.5159 | 126_240 | <25mph | <15mph | HFTD - Distribution | 2016-09-26 10:40:00 | 747 | 11.2091 | FALSE | <25mph | WDAC1 | 2.97 | 2017-02-18T11:51:00Z | 18.99 | 2 | < 25mph | WDAC1 | 2.97 | 2017-02-18T11:51:00Z | 18.99 | 28 | < 25mph | WDAC1 | 2.97 | 2017-02-18T12:51:00Z | 21 | 4 | < 25mph | WDAC1 | 2.97 | 2017-02-18T12:51:00Z | 21 | 55 | < 25mph
PG&E | 2018-10-15 | 3:23 | 38.2897 | -120.5803 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103378003 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43388 | 3:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1941 | 2018 | 10 | 15 | 3 | 23 | 18-0090342 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1464 | 26.0611 | 218_255 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-15 03:23:00 | 1680 | 26.2858 | FALSE | 25-40mph | AT317 | 3.74 | 2016-09-03T14:37:00Z | 4 | 6 | < 25mph | MTZC1 | 7.96 | 2016-09-03T13:56:00Z | 10 | 8 | < 25mph | AT317 | 3.74 | 2016-09-03T14:57:00Z | 4 | 12 | < 25mph | MTZC1 | 7.96 | 2016-09-03T14:56:00Z | 10 | 16 | < 25mph
PG&E | 2018-10-20 | 14:31 | 40.5218 | -124.1137 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Str. 003/000 | None | 60000 | Conductor | Overhead | Yes | 43393 | 14:31 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1947 | 2018 | 10 | 20 | 14 | 31 | INT-11477 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 410982 | 9.6901 | 69_380 | <25mph | <15mph | HFTD - Transmission | 2018-10-20 14:31:00 | 1686 | 10.3412 | FALSE | <25mph | PG287 | 3.79 | 2019-08-02T14:30:00Z | 8.55 | 28 | < 25mph | PG283 | 6.99 | 2019-08-02T13:50:00Z | 15.57 | 34 | < 25mph | PG287 | 3.79 | 2019-08-02T14:30:00Z | 8.55 | 57 | < 25mph | PG283 | 6.99 | 2019-08-02T15:30:00Z | 15.77 | 69 | < 25mph
PG&E | 2016-07-29 | 18:16 | 38.5769 | -122.6187 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Selma Fire Department |  |  | 12000 | Conductor | Overhead | Yes | 42580 | 18:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0890 | 2016 | 7 | 29 | 18 | 16 | 16-0053726 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 177834 | 13.7145 | 130_271 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 18:16:00 | 635 | 15.1116 | FALSE | <25mph | PG229 | 2.9 | 2019-04-23T16:30:00Z | 10.29 | 14 | < 25mph | PG132 | 6.42 | 2019-04-23T16:10:00Z | 41.2 | 42 | 40-55mph | PG229 | 2.9 | 2019-04-23T18:00:00Z | 10.74 | 30 | < 25mph | PG132 | 6.42 | 2019-04-23T16:10:00Z | 41.2 | 92 | 40-55mph
PG&E | 2019-07-22 | 8:11 | 38.7687 | -120.9633 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | El Dorado County FD | 6Ht0722190809 |  | 21000 | Other | Overhead | Yes | 43668 | 8:11 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-49 | 2019 | 7 | 22 | 8 | 11 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.6529 | 201_281 | <25mph | <15mph | HFTD - Distribution | 2019-07-22 08:11:00 | 1920 | 11.9774 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 5.01 | 2017-10-25T23:56:00Z | 8.01 | 106 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 5.01 | 2017-10-25T23:56:00Z | 8.01 | 210 | < 25mph
PG&E | 2015-09-06 19:27 | 2015-09-06 19:27 | 34.6195 | -120.2534 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Santa Barbara County Fire | meter# 1008400678 | Verizon | 12000 | Conductor | Overhead | Yes | 42253.8104 | 2015-09-06 19:27 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0582 | 2015 | 9 | 6 | 19 | 27 | 15-0059612 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 863 | 14.7315 | 234_53 | <25mph | <15mph | HFTD - Distribution | 2015-09-06 19:27:00 | 326 | 17.7534 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TT480 | 6.18 | 2019-07-20T10:20:00Z | 8.99 | 13 | < 25mph |  |  |  | 0 | 0 | No data | TT480 | 6.18 | 2019-07-20T10:20:00Z | 8.99 | 26 | < 25mph
PG&E | 2018-06-23 | 9:31 | 40.8632 | -122.3962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | RYAN MEANS 530-238-2416 | 101472252 | AT&T | 12000 | Conductor | Overhead | Yes | 43274 | 9:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1688 | 2018 | 6 | 23 | 9 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2018-06-23 09:31:00 | NA | 0 | FALSE | <25mph | CTANT | 1.62 | 2015-01-12T05:00:00Z | 4.34 | 4 | < 25mph | CTANT | 1.62 | 2015-01-12T05:00:00Z | 4.34 | 9 | < 25mph | CTANT | 1.62 | 2015-01-12T06:00:00Z | 5.59 | 8 | < 25mph | CTANT | 1.62 | 2015-01-12T06:00:00Z | 5.59 | 18 | < 25mph
PG&E | 2016-04-08 13:14 | 2016-04-08 13:14 | 39.0429 | -121.1002 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100086751 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42468.5514 | 2016-04-08 13:14 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0705 | 2016 | 4 | 8 | 13 | 14 | 16-0027237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 11817 | 10.7666 | 195_296 | <25mph | <15mph | HFTD - Distribution | 2016-04-08 13:14:00 | 449 | 10.7666 | FALSE | <25mph | C0713 | 3.59 | 2018-07-18T04:55:00Z | 0 | 14 | < 25mph | E1789 | 7.22 | 2018-07-18T04:54:00Z | 3 | 38 | < 25mph | C0713 | 3.59 | 2018-07-18T05:54:00Z | 0 | 31 | < 25mph | E1789 | 7.22 | 2018-07-18T05:54:00Z | 3 | 79 | < 25mph
PG&E | 2016-07-28 08:12 | 2016-07-28 08:12 | 37.8207 | -120.1388 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101037043 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0884 | 2016 | 7 | 28 | 8 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 1.7128 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 08:12:00 | 627 | 11.4062 | FALSE | <25mph | SEWC1 | 2.5 | 2019-10-07T23:16:00Z | 14.99 | 29 | < 25mph | PG155 | 4.67 | 2019-10-07T23:40:00Z | 16.06 | 59 | < 25mph | SEWC1 | 2.5 | 2019-10-08T00:16:00Z | 14.99 | 57 | < 25mph | PG155 | 4.67 | 2019-10-07T23:40:00Z | 16.06 | 117 | < 25mph
PG&E | 2019-06-10 | 16:18 | 38.1107 | -122.9025 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 42291101 |  | 12000 | Conductor | Overhead | Yes | 43626 | 16:18 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-401 | 2019 | 6 | 10 | 16 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.6937 | 117_246 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 16:18:00 | 1826 | 12.047 | FALSE | <25mph | PTRCA | 2.82 | 2016-10-20T07:30:00Z | 8.01 | 13 | < 25mph | PTRCA | 2.82 | 2016-10-20T07:30:00Z | 8.01 | 13 | < 25mph | PTRCA | 2.82 | 2016-10-20T07:30:00Z | 8.01 | 26 | < 25mph | PTRCA | 2.82 | 2016-10-20T07:30:00Z | 8.01 | 26 | < 25mph
PG&E | 2017-08-14 | 23:52 | 37.1272 | -122.1689 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 015/127 | None | 60000 | Conductor | Overhead | Yes | 42961 | 23:52 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1333 | 2017 | 8 | 14 | 23 | 52 | INT-09976 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 1790869 | 16.3701 | 148_191 | <25mph | <15mph | HFTD - Transmission | 2017-08-14 23:52:00 | 1072 | 18.2518 | FALSE | <25mph | PG055 | 1.85 | 2019-02-17T14:20:00Z | 18.19 | 31 | < 25mph | PG055 | 1.85 | 2019-02-17T14:20:00Z | 18.19 | 47 | < 25mph | BNDC1 | 0.33 | 2019-02-17T14:50:00Z | 20 | 62 | < 25mph | BNDC1 | 0.33 | 2019-02-17T14:50:00Z | 20 | 94 | < 25mph
PG&E | 2018-12-12 | 12:09 | 38.727 | -120.7947 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 101404403 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43446 | 12:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1984 | 2018 | 12 | 12 | 12 | 9 | No ILIS or TOTL available | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.1462 | 208_279 | <25mph | <15mph | HFTD - Distribution | 2018-12-12 12:09:00 | 1724 | 13.5134 | FALSE | <25mph | E6490 | 3.26 | 2016-09-26T23:42:00Z | 10 | 38 | < 25mph | E6490 | 3.26 | 2016-09-26T23:42:00Z | 10 | 56 | < 25mph | E6490 | 3.26 | 2016-09-26T23:42:00Z | 10 | 73 | < 25mph | E6490 | 3.26 | 2016-09-26T23:42:00Z | 10 | 109 | < 25mph
PG&E | 2017-09-03 | 17:52 | 37.4956 | -119.8367 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101086621 | Unknown | 21000 | Transformer | Overhead | Yes | 42981 | 17:52 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 1389 | 2017 | 9 | 3 | 17 | 52 | 17-0075617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 4512 | 13.9592 | 250_212 | <25mph | <15mph | HFTD - Distribution | 2017-09-03 17:52:00 | 1127 | 22.0754 | FALSE | <25mph | JSDC1 | 3.33 | 2017-09-14T16:47:00Z | 8.99 | 1 | < 25mph | E9110 | 4.74 | 2017-09-14T17:10:00Z | 10 | 10 | < 25mph | JSDC1 | 3.33 | 2017-09-14T17:47:00Z | 8.99 | 2 | < 25mph | E9110 | 4.74 | 2017-09-14T17:40:00Z | 10 | 19 | < 25mph
PG&E | 2019-03-19 | 12:52 | 37.9956 | -120.3244 | Tree - cutting, 3rd party | Hardwood Forest | 1 meter - < 3 meters | Self Extinguished |  | 101045032 |  | 17000 | Conductor | Overhead | Yes | 43543 | 12:52 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-187 | 2019 | 3 | 19 | 12 | 52 | 19-0035101 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 70602 | 12.9023 | 229_239 | <25mph | <15mph | HFTD - Distribution | 2019-03-19 12:52:00 | 1736 | 14.3226 | FALSE | <25mph | WXSC1 | 2.36 | 2019-10-20T23:30:00Z | 11.77 | 22 | < 25mph | PG167 | 5.03 | 2019-10-20T23:10:00Z | 20.47 | 76 | < 25mph | WXSC1 | 2.36 | 2019-10-20T23:30:00Z | 11.77 | 44 | < 25mph | PG167 | 5.03 | 2019-10-20T23:10:00Z | 20.47 | 151 | < 25mph
PG&E | 2019-06-15 | 14:08 | 38.8802 | -122.6125 | Tree - cutting, 3rd party | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 43361103 |  | 12000 | Pole | Overhead | Yes | 43631 | 14:08 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | Other/Unknown | 2019-19 | 2019 | 6 | 15 | 14 | 8 | 19-0068074 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 259562 | 11.2331 | 130_288 | <25mph | <15mph | HFTD - Distribution | 2019-06-15 14:08:00 | 1841 | 15.703 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5568 | 5.92 | 2018-02-08T12:06:00Z | 5.99 | 9 | < 25mph |  |  |  | 0 | 0 | No data | E5568 | 5.92 | 2018-02-08T12:06:00Z | 5.99 | 18 | < 25mph
PG&E | 2017-08-28 | 9:14 | 38.7443 | -122.6491 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 103781085 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42975 | 9:14 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1356 | 2017 | 8 | 28 | 9 | 14 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 4.693 | 128_281 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 09:14:00 | 1094 | 16.6198 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E0674 | 6.69 | 2017-02-22T17:22:00Z | 8.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E0674 | 6.69 | 2017-02-22T18:07:00Z | 13 | 8 | < 25mph
PG&E | 2016-10-13 23:23 | 23:14 | 40.4901 | -122.3729 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | SHASTA COUNTY FIRE | 101502366 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42656.9745 | 23:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1029 | 2016 | 10 | 13 | 23 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 30.3025 | 142_377 | 25-40mph | 30-45mph | HFTD - Distribution | 2016-10-13 23:14:00 | 770 | 30.3025 | FALSE | 25-40mph | E6886 | 3.41 | 2016-02-21T15:29:00Z | 3 | 11 | < 25mph | E6886 | 3.41 | 2016-02-21T15:29:00Z | 3 | 17 | < 25mph | E6886 | 3.41 | 2016-02-21T16:29:00Z | 3 | 20 | < 25mph | E6886 | 3.41 | 2016-02-21T16:29:00Z | 3 | 32 | < 25mph
PG&E | 2015-09-10 05:42 | 2015-09-10 05:42 | 37.4609 | -121.8434 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100619766 | None | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0588 | 2015 | 9 | 10 | 5 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 1.7354 | 163_209 | <25mph | <15mph | HFTD - Distribution | 2015-09-10 05:42:00 | 333 | 13.8129 | FALSE | <25mph | PG016 | 3.28 | 2019-10-19T15:10:00Z | 5.84 | 10 | < 25mph | RSPC1 | 6.56 | 2019-10-19T15:28:00Z | 13 | 48 | < 25mph | PG016 | 3.28 | 2019-10-19T16:10:00Z | 7.45 | 20 | < 25mph | RSPC1 | 6.56 | 2019-10-19T15:28:00Z | 13 | 96 | < 25mph
PG&E | 2019-06-19 | 11:44 | 39.8612 | -121.6907 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100400933 |  | 12000 | Conductor | Overhead | Yes | 43635 | 11:44 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-224 | 2019 | 6 | 19 | 11 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.9144 | 170_342 | <25mph | <15mph | HFTD - Distribution | 2019-06-19 11:44:00 | 1855 | 12.1329 | FALSE | <25mph | C8878 | 2.27 | 2017-05-14T23:23:00Z | 0 | 11 | < 25mph | CSTC1 | 4.21 | 2017-05-14T22:51:00Z | 13 | 18 | < 25mph | C8878 | 2.27 | 2017-05-15T00:28:00Z | 0 | 23 | < 25mph | CSTC1 | 4.21 | 2017-05-14T22:51:00Z | 13 | 35 | < 25mph
PG&E | 2018-07-24 | 13:47 | 39.0606 | -123.4456 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102212216 | Unknown | 12000 | Conductor | Overhead | Yes | 43305 | 13:47 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1786 | 2018 | 7 | 24 | 13 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 16.5971 | 95_299 | <25mph | <15mph | HFTD - Distribution | 2018-07-24 13:47:00 | 1526 | 19.7448 | FALSE | <25mph | PG256 | 2.46 | 2019-08-23T18:30:00Z | 8.99 | 11 | < 25mph | PG252 | 4.99 | 2019-08-23T18:50:00Z | 9.22 | 31 | < 25mph | PG256 | 2.46 | 2019-08-23T19:30:00Z | 9.22 | 20 | < 25mph | BNVC1 | 7.27 | 2019-08-23T19:50:00Z | 10 | 57 | < 25mph
PG&E | 2017-09-27 | 12:12 | 39.4845 | -121.3545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | bill lopez cell 530 521-8052 | 100429924 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 43005 | 12:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1436 | 2017 | 9 | 27 | 12 | 12 | 17-0082180 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 6370 | 7.6613 | 184_321 | <25mph | <15mph | HFTD - Distribution | 2017-09-27 12:12:00 | 1174 | 27.61 | FALSE | 25-40mph | TT309 | 3.08 | 2017-08-27T10:45:00Z | 4 | 1 | < 25mph | TT309 | 3.08 | 2017-08-27T10:45:00Z | 4 | 2 | < 25mph | TT309 | 3.08 | 2017-08-27T11:45:00Z | 7 | 2 | < 25mph | TT309 | 3.08 | 2017-08-27T11:45:00Z | 7 | 4 | < 25mph
PG&E | 2018-11-16 | 17:02 | 38.7574 | -120.9012 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101409894 | AT&T | 21000 | Conductor | Overhead | Yes | 43420 | 17:02 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1976 | 2018 | 11 | 16 | 17 | 2 | 18-0100490 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 119860 | 5.5125 | 204_281 | <25mph | <15mph | HFTD - Distribution | 2018-11-16 17:02:00 | 1716 | 12.5682 | FALSE | <25mph | D2736 | 3.3 | 2017-08-16T03:40:00Z | 4 | 12 | < 25mph | PLTC1 | 7.76 | 2017-08-16T02:56:00Z | 8.01 | 73 | < 25mph | D2736 | 3.3 | 2017-08-16T03:55:00Z | 4 | 24 | < 25mph | PLTC1 | 7.76 | 2017-08-16T02:56:00Z | 8.01 | 146 | < 25mph
PG&E | 2017-07-12 20:22 | 20:21 | 40.0808 | -123.8339 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103841917 | Unknown | 12000 | Conductor | Overhead | Yes | 42928.8485 | 20:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1249 | 2017 | 7 | 12 | 20 | 21 | 17-0062445 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 4616 | 11.5535 | 80_355 | <25mph | <15mph | HFTD - Distribution | 2017-07-12 20:21:00 | 988 | 18.1059 | FALSE | <25mph | AV037 | 2.72 | 2016-12-18T18:03:00Z | 2.01 | 2 | < 25mph | ERCC1 | 4.01 | 2016-12-18T18:28:00Z | 4 | 3 | < 25mph | AV037 | 2.72 | 2016-12-18T19:23:00Z | 3 | 4 | < 25mph | ERCC1 | 4.01 | 2016-12-18T19:28:00Z | 4 | 6 | < 25mph
PG&E | 2016-08-30 | 2016-08-30 16:01 | 36.5941 | -121.9212 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Unknown | 101734977 |  | 21000 | Conductor | Overhead | Yes | 42612 | 2016-08-30 16:01 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0951 | 2016 | 8 | 30 | 16 | 1 | 16-0061130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 199327 | 14.6893 | 159_162 | <25mph | <15mph | HFTD - Distribution | 2016-08-30 16:01:00 | 694 | 14.6893 | FALSE | <25mph | E4129 | 2.06 | 2017-06-10T06:55:00Z | 13 | 25 | < 25mph | E8875 | 4.34 | 2017-06-10T06:51:00Z | 13 | 29 | < 25mph | E4129 | 2.06 | 2017-06-10T06:55:00Z | 13 | 55 | < 25mph | E8875 | 4.34 | 2017-06-10T06:51:00Z | 13 | 63 | < 25mph
PG&E | 2017-08-05 08:33 | 08:33 | 38.4583 | -120.8695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JEFF MICHEL- 530 409 2223 | 101236223 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42952.3565 | 08:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1317 | 2017 | 8 | 5 | 8 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 6.5905 | 205_264 | <25mph | <15mph | HFTD - Distribution | 2017-08-05 08:33:00 | 1055 | 14.6063 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 6.33 | 2018-03-20T16:05:00Z | 8.99 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 6.33 | 2018-03-20T17:05:00Z | 10 | 2 | < 25mph
PG&E | 2015-08-16 07:35 | 2015-08-16 07:35 | 35.4572 | -120.6567 | Vegetation | Rural | < 3 meters | Utility: PG&E |  | 8932 SAN GABRIEL RD. SW C/O OF LOT, Atascadero | None | 0 – 750 | Conductor | Overhead | Yes | 42232.316 | 2015-08-16 07:35 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0534 | 2015 | 8 | 16 | 7 | 35 | 15-0055284 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.0129 | 215_99 | <25mph | <15mph | HFTD - Distribution | 2015-08-16 07:35:00 | 278 | 16.9932 | FALSE | <25mph | E2260 | 2.13 | 2017-04-18T01:06:00Z | 10 | 11 | < 25mph | E2260 | 2.13 | 2017-04-18T01:06:00Z | 10 | 15 | < 25mph | E2260 | 2.13 | 2017-04-18T01:06:00Z | 10 | 19 | < 25mph | E2260 | 2.13 | 2017-04-18T01:06:00Z | 10 | 27 | < 25mph
PG&E | 2018-08-31 | 18:04 | 39.5785 | -123.3842 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102196393 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 18:04 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1873 | 2018 | 8 | 31 | 18 | 4 | 18-0075741 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18540 | 15.395 | 98_327 | <25mph | <15mph | HFTD - Distribution | 2018-08-31 18:04:00 | 1612 | 16.0884 | FALSE | <25mph |  |  |  | 0 | 0 | No data | RDVC1 | 7.03 | 2017-11-21T22:28:00Z | 17 | 1 | < 25mph |  |  |  | 0 | 0 | No data | RDVC1 | 7.03 | 2017-11-21T22:28:00Z | 17 | 2 | < 25mph
PG&E | 2019-05-24 | 15:03 | 35.1696 | -120.5103 |  | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 40589503 |  | 500000 | Pole | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-100 | 2019 | 5 | 24 | 15 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 14.866 | 222_83 | <25mph | <15mph | HFTD - Transmission | 2019-05-24 15:03:00 | 1780 | 15.7146 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C9814 | 5.59 | 2015-09-20T14:33:00Z | 3 | 10 | < 25mph |  |  |  | 0 | 0 | No data | C9814 | 5.59 | 2015-09-20T14:33:00Z | 3 | 20 | < 25mph
PG&E | 2019-06-10 | 16:34 | 38.821 | -120.846 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Garden Valley FD | 153082106 |  | 21000 | Conductor | Overhead | Yes | 43626 | 16:34 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-372 | 2019 | 6 | 10 | 16 | 34 | 19-0065481 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14169 | 8.5329 | 206_284 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 16:34:00 | 1827 | 15.7607 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5691 | 5.53 | 2016-08-01T02:08:00Z | 7 | 32 | < 25mph |  |  |  | 0 | 0 | No data | E5691 | 5.53 | 2016-08-01T02:08:00Z | 7 | 62 | < 25mph
PG&E | 2015-06-09 16:20 | 2015-06-09 16:20 | 38.3822 | -122.4316 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102269716 | Pacific Bell | 21000 | Unknown | Overhead | Yes | 42164.6806 | 2015-06-09 16:20 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0369 | 2015 | 6 | 9 | 16 | 20 | 15-0039860 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 4184 | 20.783 | 138_260 | <25mph | <15mph | HFTD - Distribution | 2015-06-09 16:20:00 | 115 | 24.1918 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AS725 | 7.12 | 2015-01-07T01:47:00Z | 0 | 8 | < 25mph |  |  |  | 0 | 0 | No data | AS725 | 7.12 | 2015-01-07T02:47:00Z | 0 | 17 | < 25mph
PG&E | 2018-07-27 | 23:12 | 37.18 | -122.029 | Vegetation | Rural | < 3 meters | Fire Agency | Jeremy Wise 408-378-4010 Incident # C182080066 | 100518365 | Unknown | 12000 | Conductor | Overhead | Yes | 43308 | 23:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1793 | 2018 | 7 | 27 | 23 | 12 | 18-0064525 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 30475 | 3.2895 | 154_194 | <25mph | <15mph | HFTD - Distribution | 2018-07-27 23:12:00 | 1533 | 9.1823 | FALSE | <25mph | AV005 | 3.55 | 2016-11-01T18:38:00Z | 4 | 4 | < 25mph | C1792 | 6.55 | 2016-11-01T18:52:00Z | 10 | 105 | < 25mph | AV005 | 3.55 | 2016-11-01T18:38:00Z | 4 | 8 | < 25mph | C1792 | 6.55 | 2016-11-01T18:52:00Z | 10 | 207 | < 25mph
PG&E | 2015-08-08 07:42 | 2015-08-08 07:42 | 39.2007 | -121.2137 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100076217 | Pacific Bell | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0519 | 2015 | 8 | 8 | 7 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 14.1661 | 190_305 | <25mph | <15mph | HFTD - Distribution | 2015-08-08 07:42:00 | 263 | 14.9803 | FALSE | <25mph | E2572 | 2.41 | 2015-10-02T03:23:00Z | 1.01 | 12 | < 25mph | E1789 | 5.79 | 2015-10-02T03:36:00Z | 4.99 | 48 | < 25mph | E2572 | 2.41 | 2015-10-02T04:53:00Z | 1.01 | 24 | < 25mph | E1789 | 5.79 | 2015-10-02T03:36:00Z | 4.99 | 94 | < 25mph
PG&E | 2015-09-12 09:51 | 2015-09-12 09:51 | 39.1164 | -121.0693 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | TOP OF AVALON PLACE, GRASS VALLEY TOWER NUMBER 19/152 40689729 |  | 115000 | Conductor | Overhead | Yes | 42259.4104 | 2015-09-12 09:51 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0594 | 2015 | 9 | 12 | 9 | 51 | VD-2015-079 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 6.5014 | 196_301 | <25mph | <15mph | HFTD - Transmission | 2015-09-12 09:51:00 | 339 | 14.0472 | FALSE | <25mph | E1789 | 3.95 | 2019-04-12T13:54:00Z | 10 | 21 | < 25mph | E1789 | 3.95 | 2019-04-12T13:54:00Z | 10 | 69 | < 25mph | E1789 | 3.95 | 2019-04-12T13:54:00Z | 10 | 37 | < 25mph | E1789 | 3.95 | 2019-04-12T13:54:00Z | 10 | 131 | < 25mph
PG&E | 2016-06-24 | 2016-06-24 14:38 | 40.22 | -122.283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101526647 | PACIFIC BELL | 0 – 750 | Unknown | Overhead | Yes | 42545 | 2016-06-24 14:38 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0821 | 2016 | 6 | 24 | 14 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 11.9685 | 145_362 | <25mph | <15mph | HFTD - Distribution | 2016-06-24 14:38:00 | 564 | 17.4582 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2017-07-28 | 14:02 | 40.9997 | -121.9579 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101512624 | Unknown | 12000 | Conductor | Overhead | Yes | 42944 | 14:02 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1293 | 2017 | 7 | 28 | 14 | 2 | 17-0066367 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 46581 | 11.7167 | 159_405 | <25mph | <15mph | HFTD - Distribution | 2017-07-28 14:02:00 | 1031 | 11.7167 | FALSE | <25mph | OMTC1 | 1.45 | 2015-11-27T19:26:00Z | 8.01 | 1 | < 25mph | OMTC1 | 1.45 | 2015-11-27T19:26:00Z | 8.01 | 1 | < 25mph | OMTC1 | 1.45 | 2015-11-27T20:26:00Z | 11.01 | 2 | < 25mph | OMTC1 | 1.45 | 2015-11-27T20:26:00Z | 11.01 | 2 | < 25mph
PG&E | 2018-06-23 | 9:31 | 40.8632 | -122.3962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | RYAN MEANS 530-238-2416 | 101472252 | AT&T | 12000 | Conductor | Overhead | Yes | 43274 | 9:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1688 | 2018 | 6 | 23 | 9 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 0 | NA | <25mph | <15mph | HFTD - Distribution | 2018-06-23 09:31:00 | NA | 0 | FALSE | <25mph | CTANT | 1.62 | 2015-09-29T21:15:00Z | 15.52 | 5 | < 25mph | SLFC1 | 4.17 | 2015-09-29T20:19:00Z | 18.01 | 10 | < 25mph | CTANT | 1.62 | 2015-09-29T21:15:00Z | 15.52 | 9 | < 25mph | SLFC1 | 4.17 | 2015-09-29T21:19:00Z | 18.01 | 19 | < 25mph
PG&E | 2019-05-17 | 15:12 | 38.4797 | -123.1486 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 42811111 |  | 12000 | Conductor | Overhead | Yes | 43602 | 15:12 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-200 | 2019 | 5 | 17 | 15 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 19.5511 | 107_266 | <25mph | <15mph | HFTD - Distribution | 2019-05-17 15:12:00 | 1775 | 20.334 | FALSE | <25mph | E8483 | 3.61 | 2017-02-12T05:52:00Z | 2.01 | 4 | < 25mph | E8483 | 3.61 | 2017-02-12T05:52:00Z | 2.01 | 10 | < 25mph | E8483 | 3.61 | 2017-02-12T06:22:00Z | 3 | 8 | < 25mph | E8483 | 3.61 | 2017-02-12T06:22:00Z | 3 | 21 | < 25mph
PG&E | 2018-07-29 | 17:29 | 38.5777 | -120.8556 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101383255 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43310 | 17:29 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1797 | 2018 | 7 | 29 | 17 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.882 | 206_271 | <25mph | <15mph | HFTD - Distribution | 2018-07-29 17:29:00 | 1537 | 11.0812 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BENC1 | 4.31 | 2016-03-04T04:59:00Z | 4.99 | 13 | < 25mph |  |  |  | 0 | 0 | No data | BENC1 | 4.31 | 2016-03-04T05:59:00Z | 5.99 | 26 | < 25mph
PG&E | 2015-01-16 07:07 | 2015-01-16 07:07 | 38.7753 | -122.7004 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 102167494 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0257 | 2015 | 1 | 16 | 7 | 7 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 19.4177 | 126_282 | <25mph | <15mph | HFTD - Distribution | 2015-01-16 07:07:00 | 4 | 24.2776 | FALSE | <25mph | PG114 | 3.14 | 2019-08-04T15:10:00Z | 8.12 | 18 | < 25mph | PG096 | 4.94 | 2019-08-04T15:10:00Z | 8.55 | 61 | < 25mph | PG114 | 3.14 | 2019-08-04T15:20:00Z | 9.22 | 36 | < 25mph | PG096 | 4.94 | 2019-08-04T15:30:00Z | 10.51 | 122 | < 25mph
PG&E | 2017-06-24 15:06 | 14:51 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 42910.6292 | 14:51 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1194 | 2017 | 6 | 24 | 14 | 51 | 17-0058332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 21296 | 10.4286 | 210_259 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 14:51:00 | 933 | 10.7263 | FALSE | <25mph | PG116 | 2.81 | 2018-11-28T23:10:00Z | 12.28 | 7 | < 25mph | PG116 | 2.81 | 2018-11-28T23:10:00Z | 12.28 | 8 | < 25mph | PG116 | 2.81 | 2018-11-28T23:40:00Z | 13.15 | 14 | < 25mph | PG116 | 2.81 | 2018-11-28T23:40:00Z | 13.15 | 16 | < 25mph
PG&E | 2017-08-28 | 9:14 | 38.7443 | -122.6491 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 103781085 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42975 | 9:14 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1356 | 2017 | 8 | 28 | 9 | 14 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 4.693 | 128_281 | <25mph | <15mph | HFTD - Distribution | 2017-08-28 09:14:00 | 1094 | 16.6198 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LKRC1 | 6.54 | 2017-04-27T08:05:00Z | 22.01 | 3 | < 25mph |  |  |  | 0 | 0 | No data | LKRC1 | 6.54 | 2017-04-27T08:05:00Z | 22.01 | 7 | < 25mph
PG&E | 2017-07-20 13:46 | 13:45 | 35.0804 | -120.5538 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | PAUL LEE 805 903-3416 INC # 8291 | 101941116 | Unknown | 12000 | Conductor | Overhead | Yes | 42936.5736 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1275 | 2017 | 7 | 20 | 13 | 45 | 17-0064321 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 45999 | 13.843 | 220_78 | <25mph | <15mph | HFTD - Distribution | 2017-07-20 13:45:00 | 1013 | 14.6968 | FALSE | <25mph | PG168 | 3.82 | 2019-03-05T01:40:00Z | 5.03 | 17 | < 25mph | PG168 | 3.82 | 2019-03-05T01:40:00Z | 5.03 | 47 | < 25mph | PG168 | 3.82 | 2019-03-05T01:40:00Z | 5.03 | 29 | < 25mph | KL52 | 4.14 | 2019-03-05T03:15:00Z | 11.5 | 90 | < 25mph
PG&E | 2017-07-01 04:43 | 3:12 | 38.1952 | -122.9197 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103855493 | Unknown | 12000 | Conductor | Overhead | Yes | 42917.1963 | 3:12 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1214 | 2017 | 7 | 1 | 3 | 12 | 17-0059935 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 41370 | 14.0388 | 116_251 | <25mph | <15mph | HFTD - Distribution | 2017-07-01 03:12:00 | 951 | 27.9197 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PREC1 | 6.43 | 2017-12-02T16:05:00Z | 3 | 13 | < 25mph |  |  |  | 0 | 0 | No data | PREC1 | 6.43 | 2017-12-02T16:05:00Z | 3 | 26 | < 25mph
PG&E | 2017-09-06 | 20:08 | 37.2925 | -122.294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100256917 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1400 | 2017 | 9 | 6 | 20 | 8 | 17-0076502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4914 | 6.7999 | 143_200 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 20:08:00 | 1138 | 13.6021 | FALSE | <25mph | LAHC1 | 2.3 | 2017-03-04T17:07:00Z | 5.99 | 1 | < 25mph | LAHC1 | 2.3 | 2017-03-04T17:07:00Z | 5.99 | 7 | < 25mph | LAHC1 | 2.3 | 2017-03-04T18:07:00Z | 7 | 2 | < 25mph | E4551 | 7.73 | 2017-03-04T18:10:00Z | 8.99 | 14 | < 25mph
PG&E | 2019-09-11 | 21:03 | 38.3132 | -120.9809 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 163341103 |  | 12000 | Conductor | Overhead | Yes | 43719 | 21:03 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-370 | 2019 | 9 | 11 | 21 | 3 | 19-0098003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25994 | 11.7888 | 200_256 | <25mph | <15mph | HFTD - Distribution | 2019-09-11 21:03:00 | 2035 | 13.1911 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 5.36 | 2017-05-24T09:05:00Z | 8.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 5.36 | 2017-05-24T09:05:00Z | 8.01 | 2 | < 25mph
PG&E | 2018-07-20 | 6:31 | 37.4318 | -119.9441 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ZACH RUTHERFORD 209-966-3621 | 103909942 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43301 | 6:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1771 | 2018 | 7 | 20 | 6 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.2004 | 246_208 | <25mph | <15mph | HFTD - Distribution | 2018-07-20 06:31:00 | 1511 | 13.5994 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E9110 | 6.48 | 2018-08-06T13:55:00Z | 8.01 | 8 | < 25mph |  |  |  | 0 | 0 | No data | E9110 | 6.48 | 2018-08-06T13:55:00Z | 8.01 | 15 | < 25mph
PG&E | 2018-07-17 | 11:58 | 37.2217 | -121.6778 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Luis Morado state arson fire fighter | 100601345 | Unknown | 12000 | Conductor | Overhead | Yes | 43298 | 11:58 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1756 | 2018 | 7 | 17 | 11 | 58 | 18-0060617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 5865 | 5.1834 | 170_196 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 11:58:00 | 1496 | 14.408 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C7794 | 7.07 | 2015-01-19T09:35:00Z | 1.01 | 25 | < 25mph |  |  |  | 0 | 0 | No data | C7168 | 7.31 | 2015-01-19T11:31:00Z | 2.01 | 46 | < 25mph
PG&E | 2017-10-02 | 16:05 | 38.7182 | -120.9756 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101375963 | Unknown | 21000 | Conductor | Overhead | Yes | 43010 | 16:05 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1448 | 2017 | 10 | 2 | 16 | 5 | 17-0083539 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4797 | 14.669 | 201_279 | <25mph | <15mph | HFTD - Distribution | 2017-10-02 16:05:00 | 1186 | 17.4155 | FALSE | <25mph | D7401 | 3.14 | 2015-11-28T23:50:00Z | 4.99 | 32 | < 25mph | D7413 | 4.69 | 2015-11-28T23:40:00Z | 8.99 | 50 | < 25mph | D7401 | 3.14 | 2015-11-28T23:50:00Z | 4.99 | 64 | < 25mph | D7413 | 4.69 | 2015-11-28T23:40:00Z | 8.99 | 100 | < 25mph
PG&E | 2017-09-17 | 17:38 | 38.9946 | -121.0261 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100029537 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42995 | 17:38 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Branch (OverHanging) | 1417 | 2017 | 9 | 17 | 17 | 38 | 17-0079585 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 28509 | 11.5169 | 198_294 | <25mph | <15mph | HFTD - Distribution | 2017-09-17 17:38:00 | 1155 | 15.8476 | FALSE | <25mph | C0713 | 1.74 | 2016-10-30T18:21:00Z | 21 | 17 | < 25mph | C5488 | 5.47 | 2016-10-30T18:44:00Z | 24.99 | 35 | < 25mph | C0713 | 1.74 | 2016-10-30T19:04:00Z | 27 | 32 | 25-40mph | KAUN | 4.22 | 2016-10-30T19:15:00Z | 32.21 | 65 | 25-40mph
1. Butte | 2015-09-09 | 14:26 | 38.3297 | -120.7042 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1987 | 2015 | 9 | 9 | 14 | 26 |  | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 1353755 | 12.0917 | 212_257 | <25mph | <15mph | HFTD - Distribution | 2015-09-09 14:26:00 | 332 | 14.8248 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG095 | 6.7 | 2018-09-08T18:10:00Z | 9.64 | 8 | < 25mph |  |  |  | 0 | 0 | No data | PG095 | 6.7 | 2018-09-08T18:50:00Z | 11.41 | 17 | < 25mph
PG&E | 2018-08-08 | 10:03 | 40.7933 | -124.0242 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CHIEF | 100983089 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 10:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1829 | 2018 | 8 | 8 | 10 | 3 | 18-0067921 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 27379 | 3.1403 | 73_395 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 10:03:00 | 1568 | 7.3376 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG285 | 5.45 | 2019-10-01T03:40:00Z | 6.35 | 36 | < 25mph |  |  |  | 0 | 0 | No data | PG285 | 5.45 | 2019-10-01T04:50:00Z | 6.71 | 69 | < 25mph
PG&E | 2018-09-03 | 18:29 | 39.4547 | -121.4955 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100395672 | Unknown | 12000 | Conductor | Overhead | Yes | 43346 | 18:29 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1880 | 2018 | 9 | 3 | 18 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 6.2719 | 178_319 | <25mph | <15mph | HFTD - Distribution | 2018-09-03 18:29:00 | 1619 | 14.7897 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KOVE | 7.3 | 2017-02-03T12:55:00Z | 23.02 | 5 | < 25mph |  |  |  | 0 | 0 | No data | KOVE | 7.3 | 2017-02-03T13:53:00Z | 25.32 | 8 | 25-40mph
PG&E | 2016-07-15 14:26 | 2016-07-15 14:26 | 38.1366 | -122.7092 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | NOVATO FIRE AND OTHERS | 102013570 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.6014 | 2016-07-15 14:26 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0853 | 2016 | 7 | 15 | 14 | 26 | 16-0050269 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 758 | 13.1533 | 125_247 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 14:26:00 | 596 | 15.659 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E0433 | 5.38 | 2018-06-27T14:01:00Z | 3 | 30 | < 25mph |  |  |  | 0 | 0 | No data | PG035 | 4.54 | 2018-06-27T14:40:00Z | 4.61 | 61 | < 25mph
PG&E | 2016-07-29 01:31 | 2016-07-29 01:31 | 41.0396 | -123.674 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Hoopa FD | 100962351 |  | 12000 | Conductor | Overhead | Yes | 42580.0632 | 2016-07-29 01:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0891 | 2016 | 7 | 29 | 1 | 31 | 16-0053478 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1418 | 4.1421 | 88_408 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 01:31:00 | 633 | 13.6696 | FALSE | <25mph | HOAC1 | 0.58 | 2019-11-26T06:40:00Z | 3 | 1 | < 25mph | BIIC1 | 4.46 | 2019-11-26T06:40:00Z | 10 | 8 | < 25mph | HOAC1 | 0.58 | 2019-11-26T07:40:00Z | 3 | 2 | < 25mph | BIIC1 | 4.46 | 2019-11-26T06:40:00Z | 10 | 16 | < 25mph
PG&E | 2018-10-14 | 20:08 | 38.8935 | -120.8497 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103674516 | Unknown | 21000 | Conductor | Overhead | Yes | 43387 | 20:08 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1940 | 2018 | 10 | 14 | 20 | 8 | 18-0090299 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 48095 | 8.663 | 206_288 | <25mph | <15mph | HFTD - Distribution | 2018-10-14 20:08:00 | 1679 | 24.0259 | FALSE | <25mph | PG033 | 2.11 | 2018-08-28T03:20:00Z | 2.19 | 19 | < 25mph | BDMC1 | 7.81 | 2018-08-28T03:36:00Z | 4.99 | 26 | < 25mph | PG033 | 2.11 | 2018-08-28T03:20:00Z | 2.19 | 39 | < 25mph | BDMC1 | 7.81 | 2018-08-28T04:36:00Z | 7 | 53 | < 25mph
PG&E | 2015-07-16 19:11 | 2015-07-16 19:11 | 37.1989 | -119.7712 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 20334 ROAD 400 |  | 12000 | Conductor | Overhead | Yes | 42201.7993 | 2015-07-16 19:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0465 | 2015 | 7 | 16 | 19 | 11 | 15-0048064 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 8.6422 | 254_195 | <25mph | <15mph | HFTD - Distribution | 2015-07-16 19:11:00 | 210 | 13.1745 | FALSE | <25mph | E5766 | 3.27 | 2017-01-26T13:03:00Z | 0 | 13 | < 25mph | E5766 | 3.27 | 2017-01-26T13:03:00Z | 0 | 13 | < 25mph | E5766 | 3.27 | 2017-01-26T14:03:00Z | 0 | 31 | < 25mph | E5766 | 3.27 | 2017-01-26T14:03:00Z | 0 | 31 | < 25mph
PG&E | 2018-09-21 | 23:02 | 38.6428 | -122.7453 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102218862 | Unknown | 12000 | Conductor | Overhead | Yes | 43364 | 23:02 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1909 | 2018 | 9 | 21 | 23 | 2 | 18-0082304 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 9470 | 7.2054 | 124_275 | <25mph | <15mph | HFTD - Distribution | 2018-09-21 23:02:00 | 1648 | 14.1592 | FALSE | <25mph | E3235 | 2.39 | 2017-03-05T01:31:00Z | 7 | 4 | < 25mph | E1553 | 5.85 | 2017-03-05T01:29:00Z | 20 | 30 | < 25mph | E3235 | 2.39 | 2017-03-05T01:31:00Z | 7 | 8 | < 25mph | E1553 | 5.85 | 2017-03-05T01:29:00Z | 20 | 60 | < 25mph
PG&E | 2016-08-22 | 2016-08-22 16:10 | 37.9666 | -120.2395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Toulumne City FD | 101043683 |  | 17000 | Conductor | Overhead | Yes | 42604 | 2016-08-22 16:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0941 | 2016 | 8 | 22 | 16 | 10 | 16-0059149 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 78534 | 13.4322 | 233_237 | <25mph | <15mph | HFTD - Distribution | 2016-08-22 16:10:00 | 684 | 13.7297 | FALSE | <25mph | PG031 | 3.85 | 2018-11-18T16:10:00Z | 6.35 | 18 | < 25mph | PG179 | 5.61 | 2018-11-18T15:20:00Z | 15.12 | 41 | < 25mph | PG031 | 3.85 | 2018-11-18T16:20:00Z | 8.12 | 36 | < 25mph | PG179 | 5.61 | 2018-11-18T16:40:00Z | 16.44 | 83 | < 25mph
PG&E | 2018-06-13 | 22:40 | 38.4901 | -122.6661 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SRS181640125 | 101966547 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 22:40 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1656 | 2018 | 6 | 13 | 22 | 40 | 18-0050782 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 295146 | 2.5247 | 128_267 | <25mph | <15mph | HFTD - Distribution | 2018-06-13 22:40:00 | 1398 | 17.8767 | FALSE | <25mph | RSAC1 | 2.6 | 2019-01-19T03:29:00Z | 7 | 21 | < 25mph | RSAC1 | 2.6 | 2019-01-19T03:29:00Z | 7 | 62 | < 25mph | RSAC1 | 2.6 | 2019-01-19T04:29:00Z | 12.01 | 42 | < 25mph | PG005 | 5.24 | 2019-01-19T04:00:00Z | 13.6 | 125 | < 25mph
PG&E | 2017-09-17 | 17:38 | 38.9946 | -121.0261 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100029537 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42995 | 17:38 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Branch (OverHanging) | 1417 | 2017 | 9 | 17 | 17 | 38 | 17-0079585 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 28509 | 11.5169 | 198_294 | <25mph | <15mph | HFTD - Distribution | 2017-09-17 17:38:00 | 1155 | 15.8476 | FALSE | <25mph | C0713 | 1.74 | 2016-12-15T09:55:00Z | 13 | 14 | < 25mph | C5488 | 5.47 | 2016-12-15T10:19:00Z | 13 | 28 | < 25mph | C0713 | 1.74 | 2016-12-15T11:05:00Z | 17 | 26 | < 25mph | KAUN | 4.22 | 2016-12-15T11:15:00Z | 18.41 | 55 | < 25mph
PG&E | 2016-06-11 | 2016-06-11 19:45 | 39.3265 | -121.3921 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101292512 |  | 0 – 750 | Transformer | Overhead | Yes | 42532 | 2016-06-11 19:45 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0790 | 2016 | 6 | 11 | 19 | 45 | 16-0042611 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 642 | 8.1809 | 183_312 | <25mph | <15mph | HFTD - Distribution | 2016-06-11 19:45:00 | 533 | 16.0839 | FALSE | <25mph | BNGC1 | 3.76 | 2016-07-19T02:51:00Z | 13 | 1 | < 25mph | BNGC1 | 3.76 | 2016-07-19T02:51:00Z | 13 | 1 | < 25mph | BNGC1 | 3.76 | 2016-07-19T02:51:00Z | 13 | 2 | < 25mph | BNGC1 | 3.76 | 2016-07-19T02:51:00Z | 13 | 2 | < 25mph
PG&E | 2018-11-10 | 13:31 | 37.0467 | -121.9853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101671641 | Unknown | 21000 | Conductor | Overhead | Yes | 43414 | 13:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1966 | 2018 | 11 | 10 | 13 | 31 | 18-0098856 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 1482 | 7.3629 | 156_187 | <25mph | <15mph | HFTD - Distribution | 2018-11-10 13:31:00 | 1706 | 13.8913 | FALSE | <25mph | D8700 | 1.89 | 2016-01-08T12:30:00Z | 3 | 49 | < 25mph | C8539 | 5.67 | 2016-01-08T12:46:00Z | 7 | 163 | < 25mph | D8700 | 1.89 | 2016-01-08T12:30:00Z | 3 | 91 | < 25mph | C8539 | 5.67 | 2016-01-08T12:46:00Z | 7 | 321 | < 25mph
PG&E | 2017-06-22 10:07 | 9:36 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 9:36 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 14.8685 | 222_261 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 09:36:00 | 925 | 23.4839 | FALSE | <25mph | AT450 | 2.61 | 2016-09-07T23:00:00Z | 12.01 | 16 | < 25mph | ESPC1 | 7.8 | 2016-09-07T23:13:00Z | 17 | 23 | < 25mph | AT450 | 2.61 | 2016-09-07T23:00:00Z | 12.01 | 32 | < 25mph | ESPC1 | 7.8 | 2016-09-08T00:13:00Z | 17 | 46 | < 25mph
PG&E | 2019-07-01 | 2:15 | 38.2955 | -120.8335 |  | Shrub | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-252 | 2019 | 7 | 1 | 2 | 15 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.9479 | 207_255 | <25mph | <15mph | HFTD - Distribution | 2019-07-01 02:15:00 | 1878 | 14.184 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.85 | 2017-11-24T04:05:00Z | 8.99 | 3 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.85 | 2017-11-24T04:05:00Z | 8.99 | 6 | < 25mph
PG&E | 2015-08-17 08:37 | 2015-08-17 08:37 | 37.0757 | -122.023 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101800237 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0537 | 2015 | 8 | 17 | 8 | 37 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 1.4249 | 154_188 | <25mph | <15mph | HFTD - Distribution | 2015-08-17 08:37:00 | 281 | 11.7495 | FALSE | <25mph | E5965 | 3.61 | 2017-06-19T01:45:00Z | 7 | 28 | < 25mph | E5965 | 3.61 | 2017-06-19T01:45:00Z | 7 | 135 | < 25mph | E5965 | 3.61 | 2017-06-19T01:45:00Z | 7 | 61 | < 25mph | E5965 | 3.61 | 2017-06-19T01:45:00Z | 7 | 284 | < 25mph
PG&E | 2017-08-08 04:23 | 4:10 | 38.4949 | -122.6685 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 102025742 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42955.1829 | 4:10 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1325 | 2017 | 8 | 8 | 4 | 10 | 17-0068642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 2750 | 5.2658 | 127_267 | <25mph | <15mph | HFTD - Distribution | 2017-08-08 04:10:00 | 1062 | 14.7124 | FALSE | <25mph | RSAC1 | 2.6 | 2015-09-27T03:29:00Z | 7 | 15 | < 25mph | RSAC1 | 2.6 | 2015-09-27T03:29:00Z | 7 | 58 | < 25mph | RSAC1 | 2.6 | 2015-09-27T03:29:00Z | 7 | 30 | < 25mph | RSAC1 | 2.6 | 2015-09-27T03:29:00Z | 7 | 113 | < 25mph
PG&E | 2017-05-14 | 11:59 | 38.0798 | -122.8665 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102247059 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42869 | 11:59 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1095 | 2017 | 5 | 14 | 11 | 59 | 17-0047802 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 377483 | 24.3878 | 118_244 | <25mph | <15mph | HFTD - Distribution | 2017-05-14 11:59:00 | 835 | 24.3878 | FALSE | <25mph | PG046 | 0 | 2018-09-15T07:00:00Z | 27.63 | 6 | 25-40mph | PG046 | 0 | 2018-09-15T07:00:00Z | 27.63 | 25 | 25-40mph | PG046 | 0 | 2018-09-15T07:20:00Z | 27.63 | 12 | 25-40mph | PG046 | 0 | 2018-09-15T07:20:00Z | 27.63 | 50 | 25-40mph
PG&E | 2019-07-01 | 2:15 | 38.2955 | -120.8335 |  | Shrub | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-252 | 2019 | 7 | 1 | 2 | 15 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.9479 | 207_255 | <25mph | <15mph | HFTD - Distribution | 2019-07-01 02:15:00 | 1878 | 14.184 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CMAC1 | 5.28 | 2015-06-23T15:59:00Z | 7 | 2 | < 25mph |  |  |  | 0 | 0 | No data | CMAC1 | 5.28 | 2015-06-23T16:59:00Z | 8.01 | 4 | < 25mph
PG&E | 2016-07-25 15:32 | 2016-07-25 15:32 | 38.3522 | -120.7107 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42576.6472 | 2016-07-25 15:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0878 | 2016 | 7 | 25 | 15 | 32 | 16-0052398 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 19951 | 10.4912 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2016-07-25 15:32:00 | 621 | 14.4675 | FALSE | <25mph | PG116 | 3.99 | 2019-01-31T19:50:00Z | 19.73 | 6 | < 25mph | PG116 | 3.99 | 2019-01-31T19:50:00Z | 19.73 | 20 | < 25mph | PG116 | 3.99 | 2019-01-31T19:50:00Z | 19.73 | 12 | < 25mph | PG116 | 3.99 | 2019-01-31T19:50:00Z | 19.73 | 41 | < 25mph
PG&E | 2017-09-20 | 2:06 | 37.2597 | -122.3222 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100322388 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42998 | 2:06 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1424 | 2017 | 9 | 20 | 2 | 6 | 17-0080179 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 36593 | 8.989 | 141_198 | <25mph | <15mph | HFTD - Distribution | 2017-09-20 02:06:00 | 1162 | 20.1127 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.84 | 2015-03-01T10:07:00Z | 5.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 4.84 | 2015-03-01T11:07:00Z | 5.99 | 9 | < 25mph
PG&E | 2016-08-22 | 2016-08-22 16:10 | 37.9666 | -120.2395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Toulumne City FD | 101043683 |  | 17000 | Conductor | Overhead | Yes | 42604 | 2016-08-22 16:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0941 | 2016 | 8 | 22 | 16 | 10 | 16-0059149 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 78534 | 13.4322 | 233_237 | <25mph | <15mph | HFTD - Distribution | 2016-08-22 16:10:00 | 684 | 13.7297 | FALSE | <25mph | PG029 | 2.6 | 2018-07-06T00:50:00Z | 10.09 | 18 | < 25mph | MOUC1 | 6.67 | 2018-07-06T01:02:00Z | 13 | 37 | < 25mph | PG029 | 2.6 | 2018-07-06T00:50:00Z | 10.09 | 36 | < 25mph | MOUC1 | 6.67 | 2018-07-06T01:02:00Z | 13 | 72 | < 25mph
PG&E | 2018-07-02 | 5:12 | 38.6092 | -122.4595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 707-967-1467 | 102252558 | AT&T | 21000 | Conductor | Overhead | Yes | 43283 | 5:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1722 | 2018 | 7 | 2 | 5 | 12 | 18-0056178 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 403 | 6.1424 | 137_273 | <25mph | <15mph | HFTD - Distribution | 2018-07-02 05:12:00 | 1463 | 24.2981 | FALSE | <25mph | AT925 | 2.55 | 2017-08-14T19:30:00Z | 4.99 | 10 | < 25mph | E2050 | 7.61 | 2017-08-14T19:16:00Z | 8.01 | 14 | < 25mph | AT925 | 2.55 | 2017-08-14T20:00:00Z | 4.99 | 22 | < 25mph | E2050 | 7.61 | 2017-08-14T20:31:00Z | 8.99 | 30 | < 25mph
PG&E | 2018-05-19 | 19:44 | 40.2665 | -122.2727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103899310 | Unknown | 12000 | Conductor | Overhead | Yes | 43239 | 19:44 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1599 | 2018 | 5 | 19 | 19 | 44 | 18-0042559 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 31980 | 15.59 | 146_364 | <25mph | <15mph | HFTD - Distribution | 2018-05-19 19:44:00 | 1341 | 18.253 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 7.1 | 2018-05-17T06:54:00Z | 20 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 7.1 | 2018-05-17T06:54:00Z | 20 | 8 | < 25mph
PG&E | 2015-10-30 17:13 | 2015-10-30 17:13 | 38.3166 | -120.7226 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 7600 HWY 49, Jackson | None | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0662 | 2015 | 10 | 30 | 17 | 13 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 8.0122 | 211_256 | <25mph | <15mph | HFTD - Distribution | 2015-10-30 17:13:00 | 406 | 12.822 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.34 | 2016-04-19T01:56:00Z | 7 | 3 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 6.34 | 2016-04-19T03:56:00Z | 7 | 5 | < 25mph
PG&E | 2015-11-09 05:55 | 2015-11-09 05:55 | 34.9984 | -120.3634 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42317.2465 | 2015-11-09 05:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0673 | 2015 | 11 | 9 | 5 | 55 | 15-0076534 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 205393 | 8.4294 | 228_73 | <25mph | <15mph | HFTD - Distribution | 2015-11-09 05:55:00 | 417 | 17.7768 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AU609 | 7.47 | 2016-11-17T19:49:00Z | 14 | 2 | < 25mph |  |  |  | 0 | 0 | No data | AU609 | 7.47 | 2016-11-17T19:49:00Z | 14 | 5 | < 25mph
PG&E | 2015-06-15 15:35 | 2015-06-15 15:35 | 37.1852 | -121.7595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Jose city | 100618215 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42170.6493 | 2015-06-15 15:35 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0384 | 2015 | 6 | 15 | 15 | 35 | 15-0041178 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 345 | 20.7397 | 166_194 | <25mph | <15mph | HFTD - Distribution | 2015-06-15 15:35:00 | 130 | 21.599 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C9520 | 5.63 | 2017-10-28T20:00:00Z | 7 | 45 | < 25mph |  |  |  | 0 | 0 | No data | C7794 | 7.73 | 2017-10-28T21:00:00Z | 8.01 | 95 | < 25mph
PG&E | 2019-07-06 | 14:22 | 34.6388 | -119.9695 |  | Herbaceous | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | 182721104 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43652 | 14:22 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-153 | 2019 | 7 | 6 | 14 | 22 | 19-0074960 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 14213 | 21.2189 | 246_54 | <25mph | <15mph | HFTD - Distribution | 2019-07-06 14:22:00 | 1888 | 23.8361 | FALSE | <25mph |  |  |  | 0 | 0 | No data | UCSE | 5.59 | 2019-05-01T20:00:00Z | 13.2 | 17 | < 25mph |  |  |  | 0 | 0 | No data | PG214 | 6.78 | 2019-05-01T20:50:00Z | 15.12 | 34 | < 25mph
PG&E | 2018-10-20 | 14:31 | 40.5218 | -124.1137 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Str. 003/000 | None | 60000 | Conductor | Overhead | Yes | 43393 | 14:31 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1947 | 2018 | 10 | 20 | 14 | 31 | INT-11477 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 410982 | 9.6901 | 69_380 | <25mph | <15mph | HFTD - Transmission | 2018-10-20 14:31:00 | 1686 | 10.3412 | FALSE | <25mph | AT493 | 3.34 | 2017-06-14T11:01:00Z | 0 | 7 | < 25mph | AT493 | 3.34 | 2017-06-14T11:01:00Z | 0 | 7 | < 25mph | C5061 | 3.19 | 2017-06-14T12:50:00Z | 2.01 | 12 | < 25mph | C5061 | 3.19 | 2017-06-14T12:50:00Z | 2.01 | 12 | < 25mph
PG&E | 2017-09-15 | 14:55 | 39.7461 | -121.4885 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100335239 | Unknown | 12000 | Conductor | Overhead | Yes | 42993 | 14:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1415 | 2017 | 9 | 15 | 14 | 55 | 17-0079388 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 8834 | 10.5756 | 179_335 | <25mph | <15mph | HFTD - Distribution | 2017-09-15 14:55:00 | 1153 | 16.2937 | FALSE | <25mph | PG328 | 3.7 | 2019-12-21T08:50:00Z | 21.85 | 19 | < 25mph | PG326 | 5.77 | 2019-12-21T08:30:00Z | 27.11 | 80 | 25-40mph | PG328 | 3.7 | 2019-12-21T08:50:00Z | 21.85 | 38 | < 25mph | PG326 | 5.77 | 2019-12-21T09:10:00Z | 27.11 | 160 | 25-40mph
PG&E | 2016-09-25 10:35 | 2016-09-25 10:35 | 38.8019 | -122.8176 | Vegetation | RURAL | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103613996 |  | 115000 | Other | Overhead | Yes | 2016-09-25 10:35 | 2016-09-25 10:35 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1004 | 2016 | 9 | 25 | 10 | 35 | INT-08572 | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Equip Failure - Other | 0 | 28.1055 | 121_284 | 25-40mph | 15-30mph | HFTD - Transmission | 2016-09-25 10:35:00 | 743 | 28.9174 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | LKRC1 | 4.16 | 2016-09-18T20:05:00Z | 11.01 | 2 | < 25mph |  |  |  | 0 | 0 | No data | HWKC1 | 4.73 | 2016-09-18T20:56:00Z | 13 | 4 | < 25mph
5. Atlas (Southern LNU Complex) | 2017-10-08 | 21:52 | 38.3921 | -122.2437 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1991 | 2017 | 10 | 8 | 21 | 52 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 37.6357 | 146_261 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-08 21:52:00 | 1206 | 41.3099 | FALSE | 40-55mph | PG053 | 2.92 | 2018-09-02T05:30:00Z | 6.8 | 28 | < 25mph | ATLC1 | 5.83 | 2018-09-02T05:29:00Z | 11.01 | 36 | < 25mph | PG053 | 2.92 | 2018-09-02T05:30:00Z | 6.8 | 56 | < 25mph | ATLC1 | 5.83 | 2018-09-02T06:29:00Z | 11.01 | 71 | < 25mph
PG&E | 2015-05-02 16:51 | 2015-05-02 16:51 | 37.3284 | -119.643 | Vegetation | Rural | < 0.25 Acres | Fire Agency | MADERA COUNTY | 103768995 |  | 12000 | Conductor | Overhead | Yes | 42126.7021 | 2015-05-02 16:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0305 | 2015 | 5 | 2 | 16 | 51 | 15-0031285 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 79805 | 9.7158 | 259_202 | <25mph | <15mph | HFTD - Distribution | 2015-05-02 16:51:00 | 51 | 12.4769 | FALSE | <25mph | D7171 | 2.96 | 2016-08-04T02:05:00Z | 8.01 | 23 | < 25mph | TR172 | 7.55 | 2016-08-04T01:45:00Z | 11.01 | 53 | < 25mph | D7171 | 2.96 | 2016-08-04T02:05:00Z | 8.01 | 48 | < 25mph | TR172 | 7.55 | 2016-08-04T01:45:00Z | 11.01 | 107 | < 25mph
PG&E | 2016-09-21 | 10:01 | 39.1173 | -121.071 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100014315 | PACIFIC BELL | 115000 | Conductor | Overhead | Yes | 42634 | 10:01 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0991 | 2016 | 9 | 21 | 10 | 1 | INT-08560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 18.3543 | 196_301 | <25mph | <15mph | HFTD - Transmission | 2016-09-21 10:01:00 | 734 | 24.3978 | FALSE | <25mph | E1789 | 3.84 | 2019-03-29T16:30:00Z | 4.99 | 20 | < 25mph | E1789 | 3.84 | 2019-03-29T16:30:00Z | 4.99 | 64 | < 25mph | E1789 | 3.84 | 2019-03-29T16:48:00Z | 7 | 40 | < 25mph | E1789 | 3.84 | 2019-03-29T16:48:00Z | 7 | 126 | < 25mph
PG&E | 2018-09-16 | 8:26 | 35.3046 | -120.6389 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | Pole 4/23A | None | 70000 | Conductor | Overhead | Yes | 43359 | 8:26 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1903 | 2018 | 9 | 16 | 8 | 26 | INT-11371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 29925 | 32.6873 | 216_90 | 25-40mph | 30-45mph | HFTD - Transmission | 2018-09-16 08:26:00 | 1642 | 35.3808 | FALSE | 25-40mph | ARGC1 | 2.25 | 2018-09-16T00:54:00Z | 10 | 1 | < 25mph | KSBP | 4.73 | 2018-09-16T00:25:00Z | 27.63 | 8 | 25-40mph | ARGC1 | 2.25 | 2018-09-16T00:54:00Z | 10 | 2 | < 25mph | KSBP | 4.73 | 2018-09-16T00:25:00Z | 27.63 | 13 | 25-40mph
PG&E | 2015-06-08 14:18 | 2015-06-08 14:18 | 38.1796 | -120.959 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 102048579 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42163.5958 | 2015-06-08 14:18 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0360 | 2015 | 6 | 8 | 14 | 18 | 15-0039368 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 65168 | 7.0021 | 201_249 | <25mph | <15mph | HFTD - Distribution | 2015-06-08 14:18:00 | 106 | 9.7763 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CMAC1 | 5.88 | 2018-04-11T09:59:00Z | 3 | 1 | < 25mph |  |  |  | 0 | 0 | No data | CMAC1 | 5.88 | 2018-04-11T10:59:00Z | 3 | 2 | < 25mph
PG&E | 2016-06-21 | 20:49 | 35.5352 | -120.8457 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101900832 |  | 12000 | Conductor | Overhead | Yes | 42542 | 20:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0812 | 2016 | 6 | 21 | 20 | 49 | 16-0044904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7806 | 8.2716 | 207_103 | <25mph | <15mph | HFTD - Distribution | 2016-06-21 20:49:00 | 558 | 17.6234 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6394 | 6.56 | 2015-12-11T04:36:00Z | 7 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E6394 | 6.56 | 2015-12-11T04:51:00Z | 8.99 | 8 | < 25mph
PG&E | 2019-07-22 | 8:11 | 38.7687 | -120.9633 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | El Dorado County FD | 6Ht0722190809 |  | 21000 | Other | Overhead | Yes | 43668 | 8:11 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-49 | 2019 | 7 | 22 | 8 | 11 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 5.6529 | 201_281 | <25mph | <15mph | HFTD - Distribution | 2019-07-22 08:11:00 | 1920 | 11.9774 | FALSE | <25mph | PG027 | 3.71 | 2018-08-06T10:50:00Z | 4.83 | 12 | < 25mph | PG073 | 4.09 | 2018-08-06T11:10:00Z | 7.25 | 82 | < 25mph | PG027 | 3.71 | 2018-08-06T10:50:00Z | 4.83 | 24 | < 25mph | PG073 | 4.09 | 2018-08-06T11:20:00Z | 7.45 | 163 | < 25mph
PG&E | 2017-10-16 | 12:26 | 36.6641 | -121.0995 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Nick Shawkey E4462 209-402-1645 Cover Engine from Tuolumne Calaveras Unit | 101689865 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43024 | 12:26 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1495 | 2017 | 10 | 16 | 12 | 26 | 17-0087754 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 519 | 1.3904 | 195_165 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:26:00 | 1238 | 14.8173 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1697 | 6.85 | 2017-06-28T05:21:00Z | 2.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E1697 | 6.85 | 2017-06-28T05:21:00Z | 2.01 | 8 | < 25mph
PG&E | 2016-08-17 | 2016-08-17 18:37 | 37.3078 | -119.6511 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101020932 |  | 21000 | Conductor | Overhead | Yes | 42599 | 2016-08-17 18:37 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0934 | 2016 | 8 | 17 | 18 | 37 | 16-0058019 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 59379 | 5.4346 | 259_201 | <25mph | <15mph | HFTD - Distribution | 2016-08-17 18:37:00 | 677 | 11.1875 | FALSE | <25mph | D7778 | 1.33 | 2016-11-28T18:13:00Z | 1.01 | 25 | < 25mph | BSNC1 | 5.02 | 2016-11-28T17:48:00Z | 2.01 | 55 | < 25mph | D7778 | 1.33 | 2016-11-28T19:07:00Z | 4 | 51 | < 25mph | BSNC1 | 5.02 | 2016-11-28T18:48:00Z | 4.99 | 106 | < 25mph
PG&E | 2017-04-28 16:21 | 15:49 | 38.7679 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chris paper fire investigator, 530/677-1868. incident #caaeuo11821 | 101409833 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42853.6815 | 15:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1077 | 2017 | 4 | 28 | 15 | 49 | 17-0043771 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 82614 | 19.7837 | 201_281 | <25mph | <15mph | HFTD - Distribution | 2017-04-28 15:49:00 | 817 | 25.4223 | FALSE | 25-40mph | PG024 | 1.01 | 2019-11-15T04:10:00Z | 1.74 | 12 | < 25mph | PLTC1 | 5.08 | 2019-11-15T03:56:00Z | 8.01 | 114 | < 25mph | PG027 | 3.64 | 2019-11-15T05:00:00Z | 2.13 | 24 | < 25mph | PLTC1 | 5.08 | 2019-11-15T03:56:00Z | 8.01 | 227 | < 25mph
PG&E | 2018-06-16 | 20:33 | 38.0494 | -122.206 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Contra Costa FD | 101423963 | Unknown | 21000 | Conductor | Overhead | Yes | 43267 | 20:33 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 1671 | 2018 | 6 | 16 | 20 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 31.0273 | 147_242 | 25-40mph | 30-45mph | HFTD - Distribution | 2018-06-16 20:33:00 | 1413 | 35.6333 | FALSE | 25-40mph | DPXC1 | 2.96 | 2019-08-09T10:06:00Z | 17.98 | 17 | < 25mph | PG064 | 7.4 | 2019-08-09T10:10:00Z | 21.25 | 99 | < 25mph | DPXC1 | 2.96 | 2019-08-09T11:18:00Z | 18.99 | 32 | < 25mph | PG064 | 7.4 | 2019-08-09T10:30:00Z | 24.34 | 188 | < 25mph
PG&E | 2017-09-27 | 19:06 | 40.7592 | -123.995 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103660812 | Unknown | 12000 | Conductor | Overhead | Yes | 43005 | 19:06 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1437 | 2017 | 9 | 27 | 19 | 6 | 17-0082303 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 35394 | 10.6184 | 74_393 | <25mph | <15mph | HFTD - Distribution | 2017-09-27 19:06:00 | 1175 | 13.0154 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KNNC1 | 4.42 | 2015-09-20T13:55:00Z | 7 | 7 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 4.42 | 2015-09-20T13:55:00Z | 7 | 13 | < 25mph
PG&E | 2019-09-05 | 23:02 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire | California Department of Forestry | 101670112 |  | 12000 | Fuse | Overhead | Yes | 43713 | 23:02 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-388 | 2019 | 9 | 5 | 23 | 2 | 19-0095858 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 17920 | 6.8605 | 147_193 | <25mph | <15mph | HFTD - Distribution | 2019-09-05 23:02:00 | 2016 | 8.0768 | FALSE | <25mph | BNDC1 | 2.84 | 2018-08-04T14:50:00Z | 10 | 7 | < 25mph | BNDC1 | 2.84 | 2018-08-04T14:50:00Z | 10 | 43 | < 25mph | BNDC1 | 2.84 | 2018-08-04T15:50:00Z | 11.01 | 14 | < 25mph | BNDC1 | 2.84 | 2018-08-04T15:50:00Z | 11.01 | 85 | < 25mph
PG&E | 2015-10-16 09:43 | 2015-10-16 09:43 | 39.187 | -123.2015 | Vegetation | Rural | < 3 meters | Unknown |  | 102196855 |  | 12000 | Conductor | Overhead | Yes | 42293.4049 | 2015-10-16 09:43 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0653 | 2015 | 10 | 16 | 9 | 43 | 15-0070948 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 65228 | 2.2696 | 105_305 | <25mph | <15mph | HFTD - Distribution | 2015-10-16 09:43:00 | 397 | 16.8813 | FALSE | <25mph | E7513 | 1.34 | 2016-04-25T17:33:00Z | 17 | 12 | < 25mph | KUKI | 4.09 | 2016-04-25T17:56:00Z | 21.85 | 23 | < 25mph | E7513 | 1.34 | 2016-04-25T17:33:00Z | 17 | 23 | < 25mph | KUKI | 4.09 | 2016-04-25T17:56:00Z | 21.85 | 42 | < 25mph
PG&E | 2018-10-20 | 14:31 | 40.5218 | -124.1137 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Str. 003/000 | None | 60000 | Conductor | Overhead | Yes | 43393 | 14:31 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1947 | 2018 | 10 | 20 | 14 | 31 | INT-11477 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 410982 | 9.6901 | 69_380 | <25mph | <15mph | HFTD - Transmission | 2018-10-20 14:31:00 | 1686 | 10.3412 | FALSE | <25mph | C5061 | 3.19 | 2018-04-08T10:29:00Z | 4.99 | 22 | < 25mph | C5061 | 3.19 | 2018-04-08T10:29:00Z | 4.99 | 22 | < 25mph | C5061 | 3.19 | 2018-04-08T11:39:00Z | 8.99 | 42 | < 25mph | C5061 | 3.19 | 2018-04-08T11:39:00Z | 8.99 | 42 | < 25mph
PG&E | 2016-06-20 | 2016-06-20 16:45 | 41.0697 | -123.6789 | Vegetation | RURAL | < 3 meters | Fire Agency | Hoopa FD | 101011420 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42541 | 2016-06-20 16:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0811 | 2016 | 6 | 20 | 16 | 45 | 16-0044577 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7361 | 15.1157 | 88_410 | <25mph | <15mph | HFTD - Distribution | 2016-06-20 16:45:00 | 554 | 15.1157 | FALSE | <25mph | BIIC1 | 2.95 | 2017-11-21T06:40:00Z | 24 | 2 | < 25mph | BIIC1 | 2.95 | 2017-11-21T06:40:00Z | 24 | 2 | < 25mph | BIIC1 | 2.95 | 2017-11-21T06:40:00Z | 24 | 4 | < 25mph | BIIC1 | 2.95 | 2017-11-21T06:40:00Z | 24 | 4 | < 25mph
PG&E | 2018-06-11 | 17:49 | 34.7329 | -120.0861 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103015183 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43262 | 17:49 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1649 | 2018 | 6 | 11 | 17 | 49 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 16.7571 | 241_59 | <25mph | <15mph | HFTD - Distribution | 2018-06-11 17:49:00 | 1391 | 18.839 | FALSE | <25mph | PG209 | 2.63 | 2019-04-29T04:30:00Z | 11.18 | 21 | < 25mph | PG209 | 2.63 | 2019-04-29T04:30:00Z | 11.18 | 31 | < 25mph | PG209 | 2.63 | 2019-04-29T04:30:00Z | 11.18 | 39 | < 25mph | PG209 | 2.63 | 2019-04-29T04:30:00Z | 11.18 | 58 | < 25mph
PG&E | 2016-05-29 14:19 | 2016-05-29 14:19 | 40.5795 | -122.4694 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103156596 | Yes | 12000 | Conductor | Overhead | Yes | 42519.5965 | 2016-05-29 14:19 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0751 | 2016 | 5 | 29 | 14 | 19 | 16-0039619 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3860 | 1.6611 | 138_382 | <25mph | <15mph | HFTD - Distribution | 2016-05-29 14:19:00 | 494 | 20.6013 | FALSE | <25mph | MMOC1 | 1.91 | 2019-07-21T06:00:00Z | 20 | 36 | < 25mph | MMOC1 | 1.91 | 2019-07-21T06:00:00Z | 20 | 43 | < 25mph | MMOC1 | 1.91 | 2019-07-21T06:00:00Z | 20 | 72 | < 25mph | MMOC1 | 1.91 | 2019-07-21T06:00:00Z | 20 | 89 | < 25mph
PG&E | 2019-07-13 | 13:13 | 34.7273 | -120.4357 |  | Shrub | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | Y44 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43659 | 13:13 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-154 | 2019 | 7 | 13 | 13 | 13 | 19-0077070 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 18256 | 12.2026 | 225_58 | <25mph | <15mph | HFTD - Distribution | 2019-07-13 13:13:00 | 1900 | 12.8932 | FALSE | <25mph | VDBC1 | 3.58 | 2015-06-13T14:22:00Z | 5.99 | 5 | < 25mph | VDBC1 | 3.58 | 2015-06-13T14:22:00Z | 5.99 | 5 | < 25mph | VDBC1 | 3.58 | 2015-06-13T15:22:00Z | 7 | 10 | < 25mph | VDBC1 | 3.58 | 2015-06-13T15:22:00Z | 7 | 10 | < 25mph
PG&E | 2017-08-12 09:09 | 09:08 | 34.6689 | -120.0286 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103391912 | Unknown | 12000 | Conductor | Overhead | Yes | 42959.3812 | 09:08 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | wire cut | Other/Unknown | 1330 | 2017 | 8 | 12 | 9 | 8 | 17-0069829 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 26070 | 3.5662 | 244_55 | <25mph | <15mph | HFTD - Distribution | 2017-08-12 09:08:00 | 1068 | 23.4799 | FALSE | <25mph | UCSE | 1.88 | 2016-10-26T07:20:00Z | 4.21 | 6 | < 25mph | FGMC1 | 4.7 | 2016-10-26T07:35:00Z | 4.99 | 13 | < 25mph | UCSE | 1.88 | 2016-10-26T08:50:00Z | 5.3 | 12 | < 25mph | UCSE | 1.88 | 2016-10-26T08:50:00Z | 5.3 | 25 | < 25mph
PG&E | 2018-08-07 | 17:15 | 37.1181 | -122.1093 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101670606 | AT&T | 12000 | Conductor | Overhead | Yes | 43319 | 17:15 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1827 | 2018 | 8 | 7 | 17 | 15 | 18-0067641 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1988 | 17.3453 | 151_191 | <25mph | <15mph | HFTD - Distribution | 2018-08-07 17:15:00 | 1567 | 17.3453 | FALSE | <25mph | BNDC1 | 3.6 | 2019-03-25T03:50:00Z | 7 | 33 | < 25mph | E6800 | 7.86 | 2019-03-25T03:40:00Z | 7 | 74 | < 25mph | BNDC1 | 3.6 | 2019-03-25T04:50:00Z | 14 | 64 | < 25mph | BNDC1 | 3.6 | 2019-03-25T04:50:00Z | 14 | 148 | < 25mph
PG&E | 2018-08-13 | 15:33 | 38.708 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101377799 | Unknown | 21000 | Conductor | Overhead | Yes | 43325 | 15:33 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1840 | 2018 | 8 | 13 | 15 | 33 | 18-0069470 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1004 | 11.7134 | 201_278 | <25mph | <15mph | HFTD - Distribution | 2018-08-13 15:33:00 | 1579 | 13.7748 | FALSE | <25mph | D7401 | 3.18 | 2015-03-08T18:30:00Z | 4.99 | 34 | < 25mph | D7413 | 4.96 | 2015-03-08T18:25:00Z | 7 | 71 | < 25mph | D7401 | 3.18 | 2015-03-08T19:30:00Z | 5.99 | 66 | < 25mph | D7413 | 4.96 | 2015-03-08T19:35:00Z | 8.01 | 139 | < 25mph
PG&E | 2017-06-10 07:38 | 07:37 | 35.4359 | -120.4957 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101890429 | Unknown | 21000 | Conductor | Overhead | Yes | 42896.3177 | 07:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1140 | 2017 | 6 | 10 | 7 | 37 | 17-0054182 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 34397 | 9.2577 | 222_98 | <25mph | <15mph | HFTD - Distribution | 2017-06-10 07:37:00 | 879 | 18.05 | FALSE | <25mph | TT469 | 3.26 | 2019-10-01T01:14:00Z | 15.99 | 19 | < 25mph | F4444 | 7 | 2019-10-01T01:01:00Z | 15.99 | 60 | < 25mph | TT469 | 3.26 | 2019-10-01T01:14:00Z | 15.99 | 38 | < 25mph | PG205 | 7.78 | 2019-10-01T02:50:00Z | 23.6 | 120 | < 25mph
PG&E | 2018-06-15 | 10:05 | 38.6238 | -121.0221 | Vegetation | Rural | < 3 meters | Customer | N.A. | 101376538 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43266 | 10:05 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1661 | 2018 | 6 | 15 | 10 | 5 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 10.3423 | 199_273 | <25mph | <15mph | HFTD - Distribution | 2018-06-15 10:05:00 | 1403 | 17.1425 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BENC1 | 5.3 | 2016-10-01T11:59:00Z | 7 | 41 | < 25mph |  |  |  | 0 | 0 | No data | BENC1 | 5.3 | 2016-10-01T12:59:00Z | 8.01 | 80 | < 25mph
PG&E | 2019-08-14 | 10:16 | 35.379 | -120.4232 | Vegetation | Hardwood Woodland | < 1 meter | Cal Fire |  | 512769069280 |  | 21000 | Conductor | Overhead | Yes | 43691 | 10:16 | Vegetation | [5 empty] | no-match |  | 2019 | 8 | 14 | 10 | 16 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.0314 | 226_94 | <25mph | <15mph | HFTD - Distribution | 2019-08-14 10:16:00 | 1976 | 14.3934 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2015-07-04 01:14 | 2015-07-04 01:14 | 38.9566 | -121.0434 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100037226 |  | 12000 | Other | Overhead | Yes | 42189.0514 | 2015-07-04 01:14 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0441 | 2015 | 7 | 4 | 1 | 14 | 15-0045440 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 53865 | 7.3476 | 198_292 | <25mph | <15mph | HFTD - Distribution | 2015-07-04 01:14:00 | 186 | 12.3228 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D9434 | 7.1 | 2016-03-08T06:39:00Z | 0 | 23 | < 25mph |  |  |  | 0 | 0 | No data | D9434 | 7.1 | 2016-03-08T07:38:00Z | 3 | 44 | < 25mph
PG&E | 2018-02-12 | 20:20 | 39.9395 | -121.6494 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430947 | Unknown | 12000 | Conductor | Overhead | Yes | 43143 | 20:20 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1561 | 2018 | 2 | 12 | 20 | 20 | 18-0013604 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 149212 | 10.1876 | 172_346 | <25mph | <15mph | HFTD - Distribution | 2018-02-12 20:20:00 | 1303 | 14.6044 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CSTC1 | 7.88 | 2018-02-05T19:51:00Z | 11.01 | 19 | < 25mph |  |  |  | 0 | 0 | No data | CSTC1 | 7.88 | 2018-02-05T20:51:00Z | 14.99 | 38 | < 25mph
PG&E | 2019-07-15 | 7:51 | 38.3266 | -122.568 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 42721104 |  | 12000 | Conductor | Overhead | Yes | 43661 | 7:51 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-343 | 2019 | 7 | 15 | 7 | 51 | 19-0077351 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2348 | 31.0114 | 132_257 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-07-15 07:51:00 | 1903 | 35.3209 | FALSE | 25-40mph | F11WW | 3.53 | 2018-05-07T19:00:00Z | 5.39 | 1 | < 25mph | KENWW | 5.78 | 2018-05-07T19:00:00Z | 9.89 | 26 | < 25mph | F11WW | 3.53 | 2018-05-07T20:00:00Z | 6.11 | 2 | < 25mph | KENWW | 5.78 | 2018-05-07T20:00:00Z | 9.89 | 51 | < 25mph
PG&E | 2019-09-10 | 7:13 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 82841102 |  | 12000 | Conductor | Overhead | Yes | 43718 | 7:13 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-369 | 2019 | 9 | 10 | 7 | 13 | 19-0097264 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 23500 | 14.6244 | 147_193 | <25mph | <15mph | HFTD - Distribution | 2019-09-10 07:13:00 | 2029 | 17.7422 | FALSE | <25mph | BNDC1 | 2.84 | 2018-09-28T10:50:00Z | 4 | 7 | < 25mph | BNDC1 | 2.84 | 2018-09-28T10:50:00Z | 4 | 50 | < 25mph | BNDC1 | 2.84 | 2018-09-28T11:50:00Z | 4.99 | 14 | < 25mph | BNDC1 | 2.84 | 2018-09-28T11:50:00Z | 4.99 | 101 | < 25mph
PG&E | 2017-05-25 17:36 | 16:55 | 38.3986 | -122.9876 | Vegetation | Rural | < 3 Meters | Utility: PG&E | N.A. | 101974034 | Unknown | 12000 | Conductor | Overhead | Yes | 42880.7334 | 16:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1114 | 2017 | 5 | 25 | 16 | 55 | 17-0050815 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 2644 | 12.6436 | 114_262 | <25mph | <15mph | HFTD - Distribution | 2017-05-25 16:55:00 | 854 | 13.2306 | FALSE | <25mph | D2849 | 1.17 | 2017-03-31T11:35:00Z | 5.99 | 13 | < 25mph | BDZC1 | 7.05 | 2017-03-31T11:24:00Z | 16.37 | 77 | < 25mph | D2849 | 1.17 | 2017-03-31T11:35:00Z | 5.99 | 25 | < 25mph | BDZC1 | 7.05 | 2017-03-31T12:34:00Z | 17.31 | 150 | < 25mph
PG&E | 2018-06-13 | 22:40 | 38.4901 | -122.6661 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SRS181640125 | 101966547 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 22:40 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1656 | 2018 | 6 | 13 | 22 | 40 | 18-0050782 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 295146 | 2.5247 | 128_267 | <25mph | <15mph | HFTD - Distribution | 2018-06-13 22:40:00 | 1398 | 17.8767 | FALSE | <25mph | E1582 | 2.84 | 2018-10-28T14:33:00Z | 4 | 15 | < 25mph | PG091 | 7.98 | 2018-10-28T14:20:00Z | 22.37 | 59 | < 25mph | E1582 | 2.84 | 2018-10-28T15:13:00Z | 4 | 30 | < 25mph | PG091 | 7.98 | 2018-10-28T14:20:00Z | 22.37 | 120 | < 25mph
PG&E | 2017-06-22 17:54 | 18:07 | 38.7583 | -120.7176 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101401088 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.7461 | 18:07 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1188 | 2017 | 6 | 22 | 18 | 7 | 17-0057857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 8517 | 11.5365 | 212_281 | <25mph | <15mph | HFTD - Distribution | 2017-06-22 18:07:00 | 927 | 16.1873 | FALSE | <25mph | AV185 | 2.54 | 2017-05-06T22:30:00Z | 7 | 22 | < 25mph | E6490 | 7.72 | 2017-05-06T22:25:00Z | 10 | 33 | < 25mph | AV185 | 2.54 | 2017-05-06T22:30:00Z | 7 | 43 | < 25mph | E6490 | 7.72 | 2017-05-06T22:25:00Z | 10 | 65 | < 25mph
PG&E | 2018-07-14 | 14:44 | 38.9524 | -121.2467 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100035452 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 14:44 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1748 | 2018 | 7 | 14 | 14 | 44 | 18-0059847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2430 | 9.5304 | 189_291 | <25mph | <15mph | HFTD - Distribution | 2018-07-14 14:44:00 | 1488 | 13.6375 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LICC1 | 5.05 | 2015-11-21T13:13:00Z | 4 | 5 | < 25mph |  |  |  | 0 | 0 | No data | LICC1 | 5.05 | 2015-11-21T14:13:00Z | 5.99 | 10 | < 25mph
PG&E | 2018-11-01 | 20:45 | 38.372 | -123.0507 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103852431 | AT&T | 12000 | Conductor | Overhead | Yes | 43405 | 20:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1958 | 2018 | 11 | 1 | 20 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.9426 | 111_260 | <25mph | <15mph | HFTD - Distribution | 2018-11-01 20:45:00 | 1697 | 13.8199 | FALSE | <25mph | BBYC1 | 3.77 | 2018-01-03T11:10:00Z | 16.53 | 1 | < 25mph | UCBM | 4.05 | 2018-01-03T11:00:00Z | 25.1 | 31 | 25-40mph | BBYC1 | 3.77 | 2018-01-03T11:10:00Z | 16.53 | 2 | < 25mph | UCBM | 4.05 | 2018-01-03T11:00:00Z | 25.1 | 62 | 25-40mph
PG&E | 2015-11-09 05:55 | 2015-11-09 05:55 | 34.9984 | -120.3634 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42317.2465 | 2015-11-09 05:55 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0673 | 2015 | 11 | 9 | 5 | 55 | 15-0076534 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 205393 | 8.4294 | 228_73 | <25mph | <15mph | HFTD - Distribution | 2015-11-09 05:55:00 | 417 | 17.7768 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F0412 | 7.53 | 2018-05-10T06:30:00Z | 3 | 10 | < 25mph |  |  |  | 0 | 0 | No data | F0412 | 7.53 | 2018-05-10T06:30:00Z | 3 | 20 | < 25mph
PG&E | 2015-10-25 05:50 | 2015-10-25 05:50 | 37.7843 | -121.7683 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | cutouts 9504 |  | 21000 | Conductor | Overhead | Yes | 42302.2431 | 2015-10-25 05:50 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0657 | 2015 | 10 | 25 | 5 | 50 | 15-0073203 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 10710 | 23.3456 | 166_227 | <25mph | <15mph | HFTD - Distribution | 2015-10-25 05:50:00 | 401 | 23.3456 | FALSE | <25mph | VAQC1 | 1.86 | 2015-10-18T16:45:00Z | 23 | 2 | < 25mph | VAQC1 | 1.86 | 2015-10-18T16:45:00Z | 23 | 2 | < 25mph | VAQC1 | 1.86 | 2015-10-18T17:45:00Z | 25.99 | 4 | 25-40mph | VAQC1 | 1.86 | 2015-10-18T17:45:00Z | 25.99 | 4 | 25-40mph
4. Nuns (Central LNU Complex) | 2017-10-08 | 22:00 | 38.4041 | -122.5209 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1990 | 2017 | 10 | 8 | 22 | 0 |  | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 45.6439 | 134_262 | 40-55mph | >=45mph | HFTD - Distribution | 2017-10-08 22:00:00 | 1207 | 46.2981 | FALSE | 40-55mph |  |  |  | 0 | 0 | No data | E1582 | 7.05 | 2016-04-30T10:53:00Z | 8.99 | 6 | < 25mph |  |  |  | 0 | 0 | No data | E1582 | 7.05 | 2016-04-30T12:33:00Z | 13 | 12 | < 25mph
PG&E | 2019-07-06 | 14:22 | 34.6388 | -119.9695 |  | Herbaceous | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | 182721104 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43652 | 14:22 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-153 | 2019 | 7 | 6 | 14 | 22 | 19-0074960 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 14213 | 21.2189 | 246_54 | <25mph | <15mph | HFTD - Distribution | 2019-07-06 14:22:00 | 1888 | 23.8361 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG214 | 6.78 | 2019-05-17T22:00:00Z | 34.2 | 22 | 25-40mph |  |  |  | 0 | 0 | No data | SXWC1 | 5.29 | 2019-05-17T22:09:00Z | 37 | 42 | 25-40mph
PG&E | 2019-07-23 | 16:55 | 37.2128 | -119.505 | Gun Shot | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | 252521103 |  | 12000 | Conductor | Overhead | Yes | 43669 | 16:55 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-434 | 2019 | 7 | 23 | 16 | 55 | 19-0080383 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 513358 | 13.6168 | 265_196 | <25mph | <15mph | HFTD - Distribution | 2019-07-23 16:55:00 | 1923 | 13.6168 | FALSE | <25mph | NFRC1 | 1.4 | 2015-07-17T03:55:00Z | 4.99 | 4 | < 25mph | NFRC1 | 1.4 | 2015-07-17T03:55:00Z | 4.99 | 4 | < 25mph | C6459 | 1.76 | 2015-07-17T05:20:00Z | 4.99 | 8 | < 25mph | C6459 | 1.76 | 2015-07-17T05:20:00Z | 4.99 | 8 | < 25mph
PG&E | 2015-09-19 09:51 | 2015-09-19 09:51 | 38.4755 | -122.9069 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FORESTVILLE | 103334444 |  | 12000 | Conductor | Overhead | Yes | 42266.4104 | 2015-09-19 09:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0603 | 2015 | 9 | 19 | 9 | 51 | 15-0062267 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 488 | 1.1332 | 117_266 | <25mph | <15mph | HFTD - Distribution | 2015-09-19 09:51:00 | 348 | 13.7107 | FALSE | <25mph | SHOWW | 2.45 | 2018-02-12T21:00:00Z | 15.39 | 20 | < 25mph | DENWW | 4.23 | 2018-02-12T21:00:00Z | 16.4 | 120 | < 25mph | SHOWW | 2.45 | 2018-02-12T21:00:00Z | 15.39 | 38 | < 25mph | KSTS | 5.17 | 2018-02-12T21:55:00Z | 18.41 | 237 | < 25mph
PG&E | 2016-07-15 05:19 | 2016-07-15 05:19 | 35.1839 | -120.5018 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101846594 |  | 12000 | Conductor | Overhead | Yes | 42566.2215 | 2016-07-15 05:19 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0851 | 2016 | 7 | 15 | 5 | 19 | 16-0050086 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 62404 | 2.6454 | 222_84 | <25mph | <15mph | HFTD - Distribution | 2016-07-15 05:19:00 | 594 | 14.1102 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F0194 | 6.17 | 2017-11-02T10:53:00Z | 2.01 | 21 | < 25mph |  |  |  | 0 | 0 | No data | C9687 | 4.56 | 2017-11-02T11:21:00Z | 3 | 42 | < 25mph
PG&E | 2015-06-27 12:48 | 2015-06-27 12:48 | 37.9474 | -120.4274 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101034512 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.5333 | 2015-06-27 12:48 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0414 | 2015 | 6 | 27 | 12 | 48 | 15-0043755 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 150075 | 11.0891 | 224_236 | <25mph | <15mph | HFTD - Distribution | 2015-06-27 12:48:00 | 159 | 19.6587 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2017-09-05 | 6:58 | 39.6727 | -123.5128 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 102194697 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 42983 | 6:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1395 | 2017 | 9 | 5 | 6 | 58 | 17-0075976 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10528 | 9.1824 | 93_333 | <25mph | <15mph | HFTD - Distribution | 2017-09-05 06:58:00 | 1133 | 14.0364 | FALSE | <25mph | LAYC1 | 2.53 | 2017-07-07T04:29:00Z | 3 | 1 | < 25mph | LAYC1 | 2.53 | 2017-07-07T04:29:00Z | 3 | 7 | < 25mph | LAYC1 | 2.53 | 2017-07-07T04:29:00Z | 3 | 2 | < 25mph | LAYC1 | 2.53 | 2017-07-07T04:29:00Z | 3 | 14 | < 25mph
PG&E | 2015-10-07 15:04 | 2015-10-07 15:04 | 35.3079 | -120.8328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101924901 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42284.6277 | 2015-10-07 15:04 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0640 | 2015 | 10 | 7 | 15 | 3 | 15-0068730 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 77896 | 15.4357 | 207_90 | <25mph | <15mph | HFTD - Distribution | 2015-10-07 15:03:00 | 384 | 16.4418 | FALSE | <25mph | E1668 | 0.48 | 2017-02-08T00:24:00Z | 21 | 8 | < 25mph | E1668 | 0.48 | 2017-02-08T00:24:00Z | 21 | 9 | < 25mph | E1668 | 0.48 | 2017-02-08T00:24:00Z | 21 | 16 | < 25mph | E1668 | 0.48 | 2017-02-08T00:24:00Z | 21 | 17 | < 25mph
PG&E | 2017-09-06 | 19:26 | 40.8392 | -122.3635 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103643183 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 19:26 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1399 | 2017 | 9 | 6 | 19 | 26 | 17-0076501 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 23830 | 6.5088 | 142_396 | <25mph | <15mph | HFTD - Distribution | 2017-09-06 19:26:00 | 1137 | 12.365 | FALSE | <25mph | CTANT | 1.93 | 2018-06-10T08:30:00Z | 3.74 | 4 | < 25mph | SLFC1 | 6.48 | 2018-06-10T08:19:00Z | 14 | 9 | < 25mph | CTANT | 1.93 | 2018-06-10T10:00:00Z | 3.74 | 8 | < 25mph | SLFC1 | 6.48 | 2018-06-10T09:19:00Z | 15.99 | 18 | < 25mph
PG&E | 2017-08-19 | 21:16 | 40.5752 | -122.2985 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464623 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42966 | 21:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1341 | 2017 | 8 | 19 | 21 | 16 | 17-0071522 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 19044 | 8.8981 | 145_381 | <25mph | <15mph | HFTD - Distribution | 2017-08-19 21:16:00 | 1079 | 13.341 | FALSE | <25mph | C5599 | 2.67 | 2018-03-01T21:47:00Z | 32.01 | 4 | 25-40mph | KRDD | 4.19 | 2018-03-01T22:05:00Z | 39.12 | 9 | 25-40mph | C5599 | 2.67 | 2018-03-01T21:47:00Z | 32.01 | 7 | 25-40mph | KRDD | 4.19 | 2018-03-01T22:20:00Z | 42.57 | 20 | 40-55mph
PG&E | 2016-08-01 | 2016-08-01 12:50 | 38.9044 | -121.1274 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100078299 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42583 | 2016-08-01 12:50 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0896 | 2016 | 8 | 1 | 12 | 50 | 16-0054142 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 855 | 9.1677 | 194_289 | <25mph | <15mph | HFTD - Distribution | 2016-08-01 12:50:00 | 639 | 14.2258 | FALSE | <25mph | D8862 | 3.4 | 2016-07-28T09:14:00Z | 8.99 | 4 | < 25mph | D8862 | 3.4 | 2016-07-28T09:14:00Z | 8.99 | 5 | < 25mph | D8862 | 3.4 | 2016-07-28T09:14:00Z | 8.99 | 8 | < 25mph | D8862 | 3.4 | 2016-07-28T09:14:00Z | 8.99 | 10 | < 25mph
PG&E | 2015-11-21 10:36 | 2015-11-21 10:36 | 38.0679 | -120.1872 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101045952 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42329.4417 | 2015-11-21 10:36 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0677 | 2015 | 11 | 21 | 10 | 36 | 15-0079868 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18350 | 7.816 | 235_243 | <25mph | <15mph | HFTD - Distribution | 2015-11-21 10:36:00 | 421 | 16.6927 | FALSE | <25mph | MOUC1 | 3.29 | 2017-10-20T18:02:00Z | 8.99 | 1 | < 25mph | MOUC1 | 3.29 | 2017-10-20T18:02:00Z | 8.99 | 1 | < 25mph | MOUC1 | 3.29 | 2017-10-20T19:02:00Z | 10 | 2 | < 25mph | MOUC1 | 3.29 | 2017-10-20T19:02:00Z | 10 | 2 | < 25mph
PG&E | 2018-10-20 | 14:31 | 40.5218 | -124.1137 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Str. 003/000 | None | 60000 | Conductor | Overhead | Yes | 43393 | 14:31 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1947 | 2018 | 10 | 20 | 14 | 31 | INT-11477 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 410982 | 9.6901 | 69_380 | <25mph | <15mph | HFTD - Transmission | 2018-10-20 14:31:00 | 1686 | 10.3412 | FALSE | <25mph | AT493 | 3.34 | 2015-06-06T20:53:00Z | 15.99 | 24 | < 25mph | AT493 | 3.34 | 2015-06-06T20:53:00Z | 15.99 | 24 | < 25mph | KFOT | 2.39 | 2015-06-06T21:35:00Z | 19.57 | 49 | < 25mph | KFOT | 2.39 | 2015-06-06T21:35:00Z | 19.57 | 49 | < 25mph
PG&E | 2017-10-16 | 12:26 | 36.6641 | -121.0995 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Nick Shawkey E4462 209-402-1645 Cover Engine from Tuolumne Calaveras Unit | 101689865 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43024 | 12:26 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1495 | 2017 | 10 | 16 | 12 | 26 | 17-0087754 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 519 | 1.3904 | 195_165 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:26:00 | 1238 | 14.8173 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1697 | 6.85 | 2017-09-04T07:41:00Z | 5.99 | 3 | < 25mph |  |  |  | 0 | 0 | No data | E1697 | 6.85 | 2017-09-04T07:41:00Z | 5.99 | 6 | < 25mph
PG&E | 2017-08-19 | 21:16 | 40.5752 | -122.2985 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464623 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42966 | 21:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1341 | 2017 | 8 | 19 | 21 | 16 | 17-0071522 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 19044 | 8.8981 | 145_381 | <25mph | <15mph | HFTD - Distribution | 2017-08-19 21:16:00 | 1079 | 13.341 | FALSE | <25mph | C5599 | 2.67 | 2017-06-27T17:47:00Z | 4 | 4 | < 25mph | RRAC1 | 4.12 | 2017-06-27T17:24:00Z | 8.01 | 5 | < 25mph | C5599 | 2.67 | 2017-06-27T18:46:00Z | 7 | 8 | < 25mph | RRAC1 | 4.12 | 2017-06-27T17:24:00Z | 8.01 | 10 | < 25mph
PG&E | 2016-07-31 12:11 | 2016-07-31 12:11 | 38.7827 | -120.9168 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101417359 |  | 21000 | Conductor | Overhead | Yes | 42582.5076 | 2016-07-31 12:11 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0895 | 2016 | 7 | 31 | 12 | 11 | 16-0053949 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 10.9662 | 203_282 | <25mph | <15mph | HFTD - Distribution | 2016-07-31 12:11:00 | 638 | 14.1387 | FALSE | <25mph | PG027 | 3.25 | 2019-10-03T17:30:00Z | 8.05 | 18 | < 25mph | C6129 | 7.06 | 2019-10-03T17:44:00Z | 14.99 | 102 | < 25mph | PG027 | 3.25 | 2019-10-03T18:50:00Z | 12.71 | 36 | < 25mph | C6129 | 7.06 | 2019-10-03T18:39:00Z | 20 | 203 | < 25mph
PG&E | 2018-08-01 | 17:58 | 38.9155 | -122.799 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102156435 | Unknown | 12000 | Conductor | Overhead | Yes | 43313 | 17:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1805 | 2018 | 8 | 1 | 17 | 58 | 18-0065921 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2744 | 14.8702 | 122_290 | <25mph | <15mph | HFTD - Distribution | 2018-08-01 17:58:00 | 1545 | 14.8702 | FALSE | <25mph | E4393 | 3.97 | 2015-06-10T16:42:00Z | 16.98 | 4 | < 25mph | KELC1 | 4.99 | 2015-06-10T16:57:00Z | 21 | 5 | < 25mph | E4393 | 3.97 | 2015-06-10T16:42:00Z | 16.98 | 8 | < 25mph | KELC1 | 4.99 | 2015-06-10T16:57:00Z | 21 | 10 | < 25mph
PG&E | 2019-06-19 | 11:44 | 39.8612 | -121.6907 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100400933 |  | 12000 | Conductor | Overhead | Yes | 43635 | 11:44 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-224 | 2019 | 6 | 19 | 11 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.9144 | 170_342 | <25mph | <15mph | HFTD - Distribution | 2019-06-19 11:44:00 | 1855 | 12.1329 | FALSE | <25mph | C8878 | 2.27 | 2019-05-10T10:34:00Z | 13 | 21 | < 25mph | CSTC1 | 4.21 | 2019-05-10T09:51:00Z | 14.99 | 41 | < 25mph | C8878 | 2.27 | 2019-05-10T10:34:00Z | 13 | 42 | < 25mph | CSTC1 | 4.21 | 2019-05-10T09:51:00Z | 14.99 | 79 | < 25mph
PG&E | 2018-06-19 | 0:27 | 38.7604 | -120.8224 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101388356 | Unknown | 12000 | Conductor | Overhead | Yes | 43270 | 0:27 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1675 | 2018 | 6 | 19 | 0 | 27 | 18-0052111 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 141652 | 7.2853 | 207_281 | <25mph | <15mph | HFTD - Distribution | 2018-06-19 00:27:00 | 1417 | 13.5304 | FALSE | <25mph | E5691 | 1.82 | 2015-08-27T22:21:00Z | 14 | 12 | < 25mph | KPVF | 4.49 | 2015-08-27T21:55:00Z | 17.27 | 41 | < 25mph | E5691 | 1.82 | 2015-08-27T22:21:00Z | 14 | 24 | < 25mph | KPVF | 4.49 | 2015-08-27T21:55:00Z | 17.27 | 81 | < 25mph
PG&E | 2016-06-12 01:45 | 1:45 | 37.4643 | -122.3459 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Unknown | 100265854 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42533.0729 | 1:45 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0796 | 2016 | 6 | 12 | 1 | 45 | 16-0042637 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 19836 | 11.0705 | 141_210 | <25mph | <15mph | HFTD - Distribution | 2016-06-12 01:45:00 | 534 | 17.9563 | FALSE | <25mph | PUGC1 | 2.7 | 2015-06-02T22:18:00Z | 21 | 5 | < 25mph | AU824 | 4.06 | 2015-06-02T22:14:00Z | 23.98 | 78 | < 25mph | PUGC1 | 2.7 | 2015-06-02T23:18:00Z | 22.01 | 10 | < 25mph | AU824 | 4.06 | 2015-06-02T23:14:00Z | 25.99 | 153 | 25-40mph
PG&E | 2017-07-03 20:28 | 20:26 | 38.7923 | -120.9438 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101388730 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42919.853 | 20:26 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1218 | 2017 | 7 | 3 | 20 | 26 | 17-0060336 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 8134 | 10.0527 | 202_283 | <25mph | <15mph | HFTD - Distribution | 2017-07-03 20:26:00 | 957 | 12.5378 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 4.45 | 2016-06-18T17:56:00Z | 10 | 30 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 4.45 | 2016-06-18T18:56:00Z | 11.01 | 59 | < 25mph
PG&E | 2018-08-08 | 16:02 | 36.4703 | -121.7143 | Vegetation | Rural | < 3 meters | Customer | N.A. | 103910535 | None | 12000 | Conductor | Overhead | Yes | 43320 | 16:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1830 | 2018 | 8 | 8 | 16 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 14.7322 | 168_155 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:02:00 | 1569 | 15.5625 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F1964 | 7.27 | 2018-09-25T13:18:00Z | 1.01 | 4 | < 25mph |  |  |  | 0 | 0 | No data | F1964 | 7.27 | 2018-09-25T13:33:00Z | 3 | 8 | < 25mph
PG&E | 2017-08-12 09:09 | 09:08 | 34.6689 | -120.0286 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103391912 | Unknown | 12000 | Conductor | Overhead | Yes | 42959.3812 | 09:08 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | wire cut | Other/Unknown | 1330 | 2017 | 8 | 12 | 9 | 8 | 17-0069829 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 26070 | 3.5662 | 244_55 | <25mph | <15mph | HFTD - Distribution | 2017-08-12 09:08:00 | 1068 | 23.4799 | FALSE | <25mph | SXWC1 | 1.34 | 2017-09-22T00:09:00Z | 31 | 7 | 25-40mph | SXWC1 | 1.34 | 2017-09-22T00:09:00Z | 31 | 20 | 25-40mph | SXWC1 | 1.34 | 2017-09-22T00:09:00Z | 31 | 14 | 25-40mph | SXWC1 | 1.34 | 2017-09-22T00:09:00Z | 31 | 35 | 25-40mph
PG&E | 2017-10-31 | 21:02 | 39.1119 | -122.9163 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Structure 020/003 | Unknown | 60000 | Conductor | Overhead | Yes | 43039 | 21:02 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | no-match | 1513 | 2017 | 10 | 31 | 21 | 2 | INT-10325 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | 50730 | 1.8727 | 117_301 | <25mph | <15mph | HFTD - Transmission | 2017-10-31 21:02:00 | 1255 | 9.8895 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E5780 | 6.35 | 2018-07-16T12:23:00Z | 3 | 12 | < 25mph |  |  |  | 0 | 0 | No data | E5780 | 6.35 | 2018-07-16T13:33:00Z | 3 | 24 | < 25mph
PG&E | 2017-08-30 | 22:37 | 38.9993 | -120.9887 | Vegetation | Rural | < 3 Meters | Fire Agency | Andy 530-889-0111 | 100026238 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42977 | 22:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1370 | 2017 | 8 | 30 | 22 | 37 | 17-0074333 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 3750 | 7.3126 | 200_294 | <25mph | <15mph | HFTD - Distribution | 2017-08-30 22:37:00 | 1108 | 12.9461 | FALSE | <25mph | C0713 | 3.13 | 2016-06-18T08:49:00Z | 3 | 20 | < 25mph | AT999 | 7.28 | 2016-06-18T09:16:00Z | 3 | 33 | < 25mph | C0713 | 3.13 | 2016-06-18T08:49:00Z | 3 | 40 | < 25mph | AT999 | 7.28 | 2016-06-18T09:16:00Z | 3 | 69 | < 25mph
PG&E | 2017-10-20 | 13:45 | 34.5532 | -120.5303 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 101921492 | Unknown | 12000 | Conductor | Overhead | Yes | 43028 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1502 | 2017 | 10 | 20 | 13 | 45 | 17-0089249 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 173 | 31.847 | 221_49 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-20 13:45:00 | 1245 | 35.5655 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | E2332 | 4.19 | 2015-05-07T16:11:00Z | 16.98 | 8 | < 25mph |  |  |  | 0 | 0 | No data | E2332 | 4.19 | 2015-05-07T17:12:00Z | 17.98 | 20 | < 25mph
PG&E | 2017-06-15 04:31 | 2:58 | 40.299 | -122.4318 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101511631 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42901.1885 | 2:58 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | Other/Unknown | 1145 | 2017 | 6 | 15 | 2 | 58 | 17-0055359 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1762 | 9.755 | 139_366 | <25mph | <15mph | HFTD - Distribution | 2017-06-15 02:58:00 | 884 | 19.4408 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2019-08-20 | 9:03 | 41.1088 | -121.5034 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-297 | 2019 | 8 | 20 | 9 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 2.4258 | 178_411 | <25mph | <15mph | HFTD - Distribution | 2019-08-20 09:03:00 | 1990 | 15.6046 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2015-05-21 09:23 | 2015-05-21 09:23 | 38.5996 | -122.9935 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 4 SPANS LOAD SIDE 2993 |  | 12000 | Conductor | Overhead | Yes | 42145.391 | 2015-05-21 09:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0324 | 2015 | 5 | 21 | 9 | 23 | 15-0035686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2850 | 1.6525 | 114_273 | <25mph | <15mph | HFTD - Distribution | 2015-05-21 09:23:00 | 70 | 15.124 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AR798 | 6.08 | 2016-02-25T22:44:00Z | 4.99 | 24 | < 25mph |  |  |  | 0 | 0 | No data | AR798 | 6.08 | 2016-02-25T23:00:00Z | 5.99 | 46 | < 25mph
PG&E | 2016-01-21 21:32 | 2016-01-21 21:32 | 40.553 | -124.1116 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100994021 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42390.8972 | 2016-01-21 21:32 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0690 | 2016 | 1 | 21 | 21 | 32 | 16-0007239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 6468 | 26.2481 | 69_382 | 25-40mph | 15-30mph | HFTD - Distribution | 2016-01-21 21:32:00 | 434 | 29.6828 | FALSE | 25-40mph | AT493 | 1.6 | 2019-06-07T05:23:00Z | 13 | 23 | < 25mph | PG287 | 5.92 | 2019-06-07T05:00:00Z | 17.09 | 29 | < 25mph | AT493 | 1.6 | 2019-06-07T05:23:00Z | 13 | 44 | < 25mph | PG287 | 5.92 | 2019-06-07T06:10:00Z | 22.15 | 56 | < 25mph
PG&E | 2018-07-17 | 19:40 | 40.5927 | -122.4886 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101477082 | AT&T | 12000 | Conductor | Overhead | Yes | 43298 | 19:40 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1760 | 2018 | 7 | 17 | 19 | 40 | 18-0060840 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 30162 | 14.3022 | 137_382 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 19:40:00 | 1500 | 21.6282 | FALSE | <25mph | MMOC1 | 1.8 | 2016-03-19T11:00:00Z | 4.99 | 7 | < 25mph | WYTC1 | 7.38 | 2016-03-19T10:00:00Z | 6.76 | 19 | < 25mph | MMOC1 | 1.8 | 2016-03-19T12:00:00Z | 7 | 12 | < 25mph | WYTC1 | 7.38 | 2016-03-19T12:00:00Z | 7.31 | 33 | < 25mph
PG&E | 2016-02-08 03:55 | 2016-02-08 03:55 | 39.7852 | -121.5056 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100337507 |  | 12000 | Conductor | Overhead | Yes | 42408.1632 | 2016-02-08 03:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0694 | 2016 | 2 | 8 | 3 | 55 | 16-0011201 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 87046 | 36.3276 | 178_337 | 25-40mph | 30-45mph | HFTD - Distribution | 2016-02-08 03:55:00 | 438 | 40.0336 | FALSE | 40-55mph | JBGC1 | 3.52 | 2016-01-17T01:13:00Z | 5.99 | 1 | < 25mph | JBGC1 | 3.52 | 2016-01-17T01:13:00Z | 5.99 | 18 | < 25mph | JBGC1 | 3.52 | 2016-01-17T02:13:00Z | 8.01 | 2 | < 25mph | JBGC1 | 3.52 | 2016-01-17T02:13:00Z | 8.01 | 35 | < 25mph
PG&E | 2015-05-02 16:51 | 2015-05-02 16:51 | 37.3284 | -119.643 | Vegetation | Rural | < 0.25 Acres | Fire Agency | MADERA COUNTY | 103768995 |  | 12000 | Conductor | Overhead | Yes | 42126.7021 | 2015-05-02 16:51 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0305 | 2015 | 5 | 2 | 16 | 51 | 15-0031285 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 79805 | 9.7158 | 259_202 | <25mph | <15mph | HFTD - Distribution | 2015-05-02 16:51:00 | 51 | 12.4769 | FALSE | <25mph | D7171 | 2.96 | 2018-07-29T03:50:00Z | 7 | 26 | < 25mph | D7171 | 2.96 | 2018-07-29T03:50:00Z | 7 | 50 | < 25mph | D7171 | 2.96 | 2018-07-29T03:50:00Z | 7 | 60 | < 25mph | D7171 | 2.96 | 2018-07-29T03:50:00Z | 7 | 109 | < 25mph
PG&E | 2019-08-14 | 10:16 | 35.379 | -120.4232 | Vegetation | Hardwood Woodland | < 1 meter | Cal Fire |  | 512769069280 |  | 21000 | Conductor | Overhead | Yes | 43691 | 10:16 | Vegetation | [5 empty] | no-match |  | 2019 | 8 | 14 | 10 | 16 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.0314 | 226_94 | <25mph | <15mph | HFTD - Distribution | 2019-08-14 10:16:00 | 1976 | 14.3934 | FALSE | <25mph | PG236 | 3.82 | 2019-10-14T09:50:00Z | 5.99 | 24 | < 25mph | PG236 | 3.82 | 2019-10-14T09:50:00Z | 5.99 | 48 | < 25mph | PG236 | 3.82 | 2019-10-14T09:50:00Z | 5.99 | 48 | < 25mph | PG236 | 3.82 | 2019-10-14T09:50:00Z | 5.99 | 96 | < 25mph
PG&E | 2018-10-14 | 19:39 | 38.446 | -120.5147 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | IC- Dillon Gissell- 209-295-7735 | 103384485 | Unknown | 12000 | Conductor | Overhead | Yes | 43387 | 19:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1939 | 2018 | 10 | 14 | 19 | 39 | 18-0090288 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3497327 | 25.4932 | 220_264 | 25-40mph | 15-30mph | HFTD - Distribution | 2018-10-14 19:39:00 | 1678 | 30.9108 | FALSE | 25-40mph | AT450 | 3.11 | 2017-07-28T17:34:00Z | 5.99 | 13 | < 25mph | AT450 | 3.11 | 2017-07-28T17:34:00Z | 5.99 | 17 | < 25mph | AT450 | 3.11 | 2017-07-28T18:24:00Z | 8.99 | 27 | < 25mph | AT450 | 3.11 | 2017-07-28T18:24:00Z | 8.99 | 35 | < 25mph
PG&E | 2017-07-24 14:02 | 14:01 | 37.2635 | -122.3364 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike klink 650-879-0121 | 100322130 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42940.5845 | 14:01 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1286 | 2017 | 7 | 24 | 14 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 18.4533 | 141_199 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 14:01:00 | 1025 | 18.6394 | FALSE | <25mph |  |  |  | 0 | 0 | No data | LAHC1 | 5.31 | 2018-04-24T05:07:00Z | 4 | 1 | < 25mph |  |  |  | 0 | 0 | No data | LAHC1 | 5.31 | 2018-04-24T06:07:00Z | 4 | 2 | < 25mph
PG&E | 2018-08-01 | 17:58 | 38.9155 | -122.799 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102156435 | Unknown | 12000 | Conductor | Overhead | Yes | 43313 | 17:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1805 | 2018 | 8 | 1 | 17 | 58 | 18-0065921 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2744 | 14.8702 | 122_290 | <25mph | <15mph | HFTD - Distribution | 2018-08-01 17:58:00 | 1545 | 14.8702 | FALSE | <25mph | E4393 | 3.97 | 2015-10-28T11:40:00Z | 4.99 | 4 | < 25mph | KELC1 | 4.99 | 2015-10-28T11:57:00Z | 10 | 5 | < 25mph | E4393 | 3.97 | 2015-10-28T11:40:00Z | 4.99 | 8 | < 25mph | KELC1 | 4.99 | 2015-10-28T11:57:00Z | 10 | 10 | < 25mph
PG&E | 2019-08-12 | 20:06 | 39.0952 | -123.4937 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 102177212 |  | 12000 | Conductor | Overhead | Yes | 43689 | 20:06 | Vegetation |  | Veg. contact |  |  |  | Fell into (No defect) | 2019-400 | 2019 | 8 | 12 | 20 | 6 | 19-0087090 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2508 | 13.5331 | 93_301 | <25mph | <15mph | HFTD - Distribution | 2019-08-12 20:06:00 | 1970 | 19.4805 | FALSE | <25mph | E1763 | 1.72 | 2017-12-07T14:18:00Z | 7 | 4 | < 25mph | E1763 | 1.72 | 2017-12-07T14:18:00Z | 7 | 4 | < 25mph | E1763 | 1.72 | 2017-12-07T14:18:00Z | 7 | 8 | < 25mph | E1763 | 1.72 | 2017-12-07T14:18:00Z | 7 | 8 | < 25mph
PG&E | 2016-10-02 16:41 | 16:41 | 39.8888 | -121.6648 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103358082 |  | 12000 | Other | Overhead | Yes | 42645.6954 | 16:41 | Other | N.A. | N.A. | N.A. | Weather | lightning strike | Other/Unknown | 1013 | 2016 | 10 | 2 | 16 | 41 | 16-0069050 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 339550 | 8.5152 | 171_343 | <25mph | <15mph | HFTD - Distribution | 2016-10-02 16:41:00 | 755 | 17.2989 | FALSE | <25mph | C8878 | 1.4 | 2017-07-14T23:23:00Z | 0 | 11 | < 25mph | CSTC1 | 5.65 | 2017-07-14T22:51:00Z | 15.99 | 15 | < 25mph | C8878 | 1.4 | 2017-07-15T00:23:00Z | 0 | 23 | < 25mph | CSTC1 | 5.65 | 2017-07-14T22:51:00Z | 15.99 | 33 | < 25mph
PG&E | 2018-08-08 | 16:02 | 36.4703 | -121.7143 | Vegetation | Rural | < 3 meters | Customer | N.A. | 103910535 | None | 12000 | Conductor | Overhead | Yes | 43320 | 16:02 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1830 | 2018 | 8 | 8 | 16 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 14.7322 | 168_155 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:02:00 | 1569 | 15.5625 | FALSE | <25mph |  |  |  | 0 | 0 | No data | F1964 | 7.27 | 2018-06-21T05:23:00Z | 7 | 4 | < 25mph |  |  |  | 0 | 0 | No data | F1964 | 7.27 | 2018-06-21T05:23:00Z | 7 | 8 | < 25mph
PG&E | 2017-09-08 | 4:47 | 38.7478 | -120.859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101391575 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42986 | 4:47 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1401 | 2017 | 9 | 8 | 4 | 47 | 17-0076889 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 39736 | 2.1381 | 205_280 | <25mph | <15mph | HFTD - Distribution | 2017-09-08 04:47:00 | 1139 | 10.5203 | FALSE | <25mph | D2736 | 3.92 | 2017-09-19T03:04:00Z | 10 | 77 | < 25mph | D4464 | 7.65 | 2017-09-19T02:11:00Z | 12.01 | 112 | < 25mph | D2736 | 3.92 | 2017-09-19T03:04:00Z | 10 | 149 | < 25mph | D4464 | 7.65 | 2017-09-19T02:11:00Z | 12.01 | 214 | < 25mph
PG&E | 2018-06-09 | 0:46 | 35.0745 | -120.5167 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101927520 | Unknown | 12000 | Conductor | Overhead | Yes | 43260 | 0:46 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1645 | 2018 | 6 | 9 | 0 | 46 | 18-0049171 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 16825 | 5.84 | 221_78 | <25mph | <15mph | HFTD - Distribution | 2018-06-09 00:46:00 | 1387 | 22.9582 | FALSE | <25mph | D6295 | 3.81 | 2016-05-30T21:45:00Z | 14 | 8 | < 25mph | D6295 | 3.81 | 2016-05-30T21:45:00Z | 14 | 18 | < 25mph | D6295 | 3.81 | 2016-05-30T21:45:00Z | 14 | 16 | < 25mph | D6295 | 3.81 | 2016-05-30T21:45:00Z | 14 | 36 | < 25mph
PG&E | 2019-07-25 | 7:39 | 39.1735 | -123.5763 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Oj 2 P/Ss Of Cgc# 215532055340 |  | 12000 | Other | Overhead | Yes | 43671 | 7:39 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-380 | 2019 | 7 | 25 | 7 | 39 | 19-0080947 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 790 | 2.0398 | 89_305 | <25mph | <15mph | HFTD - Distribution | 2019-07-25 07:39:00 | 1928 | 13.3511 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PG248 | 4.83 | 2019-07-11T10:30:00Z | 6.58 | 16 | < 25mph |  |  |  | 0 | 0 | No data | PG248 | 4.83 | 2019-07-11T10:30:00Z | 6.58 | 32 | < 25mph
PG&E | 2016-06-30 | 0:03 | 39.8157 | -121.5994 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42551 | 0:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0832 | 2016 | 6 | 30 | 0 | 3 | 16-0046763 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 299100 | 7.8781 | 174_339 | <25mph | <15mph | HFTD - Distribution | 2016-06-30 00:03:00 | 575 | 11.8323 | FALSE | <25mph | E4833 | 0.69 | 2015-11-22T19:46:00Z | 3 | 21 | < 25mph | C8878 | 4.73 | 2015-11-22T19:28:00Z | 7 | 34 | < 25mph | E4833 | 0.69 | 2015-11-22T21:07:00Z | 3 | 40 | < 25mph | C8878 | 4.73 | 2015-11-22T19:28:00Z | 7 | 66 | < 25mph
PG&E | 2015-07-01 12:57 | 2015-07-01 12:57 | 39.4146 | -121.379 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42186.5396 | 2015-07-01 12:57 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0434 | 2015 | 7 | 1 | 12 | 57 | 15-0044609 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 12.6482 | 183_317 | <25mph | <15mph | HFTD - Distribution | 2015-07-01 12:57:00 | 179 | 18.7031 | FALSE | <25mph | BNGC1 | 2.37 | 2018-06-14T00:51:00Z | 12.01 | 1 | < 25mph | BNGC1 | 2.37 | 2018-06-14T00:51:00Z | 12.01 | 2 | < 25mph | BNGC1 | 2.37 | 2018-06-14T01:51:00Z | 12.01 | 2 | < 25mph | BNGC1 | 2.37 | 2018-06-14T01:51:00Z | 12.01 | 4 | < 25mph
PG&E | 2016-06-03 | 2016-06-03 12:16 | 38.6435 | -120.6959 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | cal-fire and usfs | 103119737 |  | 21000 | Conductor | Overhead | Yes | 42524 | 2016-06-03 12:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0764 | 2016 | 6 | 3 | 12 | 16 | 16-0040808 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 101354 | 7.6436 | 213_274 | <25mph | <15mph | HFTD - Distribution | 2016-06-03 12:16:00 | 507 | 11.74 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E6490 | 7.82 | 2016-12-28T18:24:00Z | 4.99 | 17 | < 25mph |  |  |  | 0 | 0 | No data | AV185 | 6.2 | 2016-12-28T19:21:00Z | 5.99 | 38 | < 25mph
PG&E | 2016-06-10 15:51 | 2016-06-10 15:51 | 39.9934 | -123.7883 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100992291 |  | 12000 | Conductor | Overhead | Yes | 42531.6604 | 2016-06-10 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0788 | 2016 | 6 | 10 | 15 | 51 | 16-0042501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | N.A. | 22.4156 | 82_351 | <25mph | <15mph | HFTD - Distribution | 2016-06-10 15:51:00 | 531 | 22.7996 | FALSE | <25mph |  |  |  | 0 | 0 | No data | AV037 | 5.5 | 2018-10-29T19:43:00Z | 7 | 4 | < 25mph |  |  |  | 0 | 0 | No data | AV037 | 5.5 | 2018-10-29T20:53:00Z | 11.01 | 9 | < 25mph
PG&E | 2016-09-12 | 12:38 | 38.7832 | -120.6006 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101421708 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42625 | 12:38 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0974 | 2016 | 9 | 12 | 12 | 38 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 15.5165 | 217_282 | <25mph | <15mph | HFTD - Distribution | 2016-09-12 12:38:00 | 716 | 15.5342 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E3165 | 7.91 | 2015-05-01T02:05:00Z | 2.01 | 6 | < 25mph |  |  |  | 0 | 0 | No data | E3165 | 7.91 | 2015-05-01T03:55:00Z | 2.01 | 12 | < 25mph
PG&E | 2017-07-24 19:31 | 19:31 | 38.3519 | -120.7103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.8134 | 19:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1288 | 2017 | 7 | 24 | 19 | 31 | 17-0065145 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14281 | 10.3402 | 212_258 | <25mph | <15mph | HFTD - Distribution | 2017-07-24 19:31:00 | 1027 | 12.2366 | FALSE | <25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2015-10-09T20:56:00Z | 11.01 | 1 | < 25mph |  |  |  | 0 | 0 | No data | MTZC1 | 4.1 | 2015-10-09T20:56:00Z | 11.01 | 2 | < 25mph
PG&E | 2018-10-16 | 16:30 | 38.7754 | -122.8976 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MARK GRADEK (707) 889-4303 | 101962692 | AT&T | 12000 | Conductor | Overhead | Yes | 43389 | 16:30 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1943 | 2018 | 10 | 16 | 16 | 30 | 18-0091127 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 744 | 10.3513 | 118_282 | <25mph | <15mph | HFTD - Distribution | 2018-10-16 16:30:00 | 1682 | 19.9126 | FALSE | <25mph |  |  |  | 0 | 0 | No data | HWKC1 | 4.29 | 2015-12-20T19:56:00Z | 21 | 1 | < 25mph |  |  |  | 0 | 0 | No data | HWKC1 | 4.29 | 2015-12-20T20:56:00Z | 21 | 2 | < 25mph
PG&E | 2017-12-14 | 17:16 | 34.5878 | -120.3566 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101911004 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 43083 | 17:16 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1538 | 2017 | 12 | 14 | 17 | 16 | 17-0101672 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2896 | 2.7073 | 229_51 | <25mph | <15mph | HFTD - Distribution | 2017-12-14 17:16:00 | 1280 | 11.3138 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E2332 | 7.61 | 2016-07-29T07:56:00Z | 14.99 | 7 | < 25mph |  |  |  | 0 | 0 | No data | E2332 | 7.61 | 2016-07-29T07:56:00Z | 14.99 | 11 | < 25mph
PG&E | 2018-08-08 | 16:03 | 37.2974 | -122.2651 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 100307515 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 16:03 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1831 | 2018 | 8 | 8 | 16 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.1654 | 144_201 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 16:03:00 | 1570 | 9.1654 | FALSE | <25mph | LAHC1 | 0.77 | 2015-03-19T16:07:00Z | 4.99 | 4 | < 25mph | LAHC1 | 0.77 | 2015-03-19T16:07:00Z | 4.99 | 27 | < 25mph | LAHC1 | 0.77 | 2015-03-19T17:07:00Z | 4.99 | 9 | < 25mph | E4825 | 6.3 | 2015-03-19T17:45:00Z | 4.99 | 61 | < 25mph
PG&E | 2017-09-04 | 3:29 | 39.8317 | -121.8444 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102300100 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1392 | 2017 | 9 | 4 | 3 | 29 | 17-0075723 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 214974 | 9.8341 | 164_340 | <25mph | <15mph | HFTD - Distribution | 2017-09-04 03:29:00 | 1130 | 13.8789 | FALSE | <25mph |  |  |  | 0 | 0 | No data | D8204 | 5.42 | 2018-04-11T19:10:00Z | 18.99 | 21 | < 25mph | KCIC | 2.39 | 2018-04-11T19:47:00Z | 23.02 | 1 | < 25mph | KCIC | 2.39 | 2018-04-11T19:47:00Z | 23.02 | 43 | < 25mph
PG&E | 2018-11-13 | 15:41 | 37.0644 | -121.9578 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101680441 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43417 | 15:41 | Other | N.A. | N.A. | N.A. | Human Error | Grow house | Other/Unknown | 1973 | 2018 | 11 | 13 | 15 | 41 | 18-0099492 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 21484 | 1.9347 | 157_188 | <25mph | <15mph | HFTD - Distribution | 2018-11-13 15:41:00 | 1713 | 13.1257 | FALSE | <25mph | AP191 | 2.69 | 2015-01-18T00:24:00Z | 5.99 | 41 | < 25mph | C8539 | 7.44 | 2015-01-18T00:51:00Z | 8.01 | 159 | < 25mph | AP191 | 2.69 | 2015-01-18T00:24:00Z | 5.99 | 86 | < 25mph | D8979 | 4.33 | 2015-01-18T02:17:00Z | 10.98 | 313 | < 25mph
PG&E | 2019-06-06 | 20:30 | 38.4969 | -122.6435 |  | Barren/Other | < 1 meter | Self Extinguished |  | Unknown |  | 230000 | Circuit Breaker | Overhead | Yes | 43622 | 20:30 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | no-match | 2019-102 | 2019 | 6 | 6 | 20 | 30 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 16.883 | 129_267 | <25mph | <15mph | HFTD - Transmission | 2019-06-06 20:30:00 | 1804 | 23.129 | FALSE | <25mph | PG558 | 2.52 | 2019-12-14T02:20:00Z | 12.86 | 24 | < 25mph | PG162 | 5.7 | 2019-12-14T01:40:00Z | 28.43 | 100 | 25-40mph | RSAC1 | 3.91 | 2019-12-14T02:29:00Z | 17 | 47 | < 25mph | PG162 | 5.7 | 2019-12-14T01:40:00Z | 28.43 | 197 | 25-40mph
PG&E | 2018-01-16 | 14:25 | 34.5703 | -119.9645 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101921689 | Verizon | 12000 | Conductor | Overhead | Yes | 43116 | 14:25 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1556 | 2018 | 1 | 16 | 14 | 25 | 18-0006506 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 23519 | 5.0963 | 247_50 | <25mph | <15mph | HFTD - Distribution | 2018-01-16 14:25:00 | 1298 | 9.8389 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KIZA | 6.8 | 2015-06-02T00:35:00Z | 21.85 | 6 | < 25mph |  |  |  | 0 | 0 | No data | KIZA | 6.8 | 2015-06-02T00:55:00Z | 21.85 | 14 | < 25mph
PG&E | 2017-08-15 19:29 | 19:28 | 39.5037 | -121.2783 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 100396172 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42962.8116 | 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1335 | 2017 | 8 | 15 | 19 | 28 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 6.8405 | 188_322 | <25mph | <15mph | HFTD - Distribution | 2017-08-15 19:28:00 | 1073 | 9.7276 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PKCC1 | 4.51 | 2015-10-02T17:10:00Z | 18.99 | 2 | < 25mph |  |  |  | 0 | 0 | No data | PKCC1 | 4.51 | 2015-10-02T17:10:00Z | 18.99 | 4 | < 25mph
PG&E | 2017-06-13 | 14:30 | 37.8526 | -122.1853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Tower 005/035c | Unknown | 115000 | Conductor | Overhead | Yes | 42899 | 14:30 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1143 | 2017 | 6 | 13 | 14 | 30 | INT-09744 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | Balloons | 0 | 10.6352 | 148_231 | <25mph | <15mph | HFTD - Transmission | 2017-06-13 14:30:00 | 882 | 14.5193 | FALSE | <25mph | LBNL1 | 3.84 | 2019-11-11T07:45:00Z | 8.48 | 92 | < 25mph | LTRC1 | 6.59 | 2019-11-11T07:28:00Z | 10 | 260 | < 25mph | ONOC1 | 2.12 | 2019-11-11T08:33:00Z | 11.01 | 182 | < 25mph | ONOC1 | 2.12 | 2019-11-11T08:33:00Z | 11.01 | 514 | < 25mph
PG&E | 2018-09-02 | 15:36 | 37.4714 | -122.4248 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Arie Delay 659-740-4636 | 103808872 | Unknown | 12000 | Capacitor Bank | Overhead | Yes | 43345 | 15:36 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1876 | 2018 | 9 | 2 | 15 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 11.73 | 137_210 | <25mph | <15mph | HFTD - Distribution | 2018-09-02 15:36:00 | 1615 | 13.6047 | FALSE | <25mph | D9259 | 3.46 | 2017-12-28T23:06:00Z | 4.99 | 4 | < 25mph | E4863 | 5.74 | 2017-12-28T22:58:00Z | 17 | 58 | < 25mph | D9259 | 3.46 | 2017-12-28T23:06:00Z | 4.99 | 8 | < 25mph | MBWC1 | 6.8 | 2017-12-29T00:00:00Z | 17 | 116 | < 25mph
PG&E | 2017-06-24 10:32 | 10:31 | 38.9438 | -121.0447 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100090318 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42910.439 | 10:31 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1193 | 2017 | 6 | 24 | 10 | 31 | 17-0058318 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 582 | 9.5424 | 198_291 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 10:31:00 | 932 | 10.7882 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.98 | 2018-05-25T16:56:00Z | 10 | 31 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.98 | 2018-05-25T16:56:00Z | 10 | 60 | < 25mph
PG&E | 2017-07-08 19:23 | 18:49 | 40.2935 | -122.4089 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | TOM STROING, RED BLUFF | 101526269 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42924.8076 | 18:49 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1234 | 2017 | 7 | 8 | 18 | 49 | 17-0061469 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 157484 | 8.2983 | 140_366 | <25mph | <15mph | HFTD - Distribution | 2017-07-08 18:49:00 | 973 | 15.6109 | FALSE | <25mph | E7114 | 0.65 | 2017-08-03T20:13:00Z | 14.99 | 4 | < 25mph | E7114 | 0.65 | 2017-08-03T20:13:00Z | 14.99 | 4 | < 25mph | E7114 | 0.65 | 2017-08-03T20:13:00Z | 14.99 | 8 | < 25mph | E7114 | 0.65 | 2017-08-03T20:13:00Z | 14.99 | 8 | < 25mph
PG&E | 2018-08-08 | 10:03 | 40.7933 | -124.0242 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CHIEF | 100983089 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 10:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1829 | 2018 | 8 | 8 | 10 | 3 | 18-0067921 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 27379 | 3.1403 | 73_395 | <25mph | <15mph | HFTD - Distribution | 2018-08-08 10:03:00 | 1568 | 7.3376 | FALSE | <25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.13 | 2018-03-18T20:55:00Z | 17 | 30 | < 25mph |  |  |  | 0 | 0 | No data | KNNC1 | 7.13 | 2018-03-18T21:55:00Z | 17 | 59 | < 25mph
PG&E | 2017-10-11 | 11:57 | 38.5015 | -123.0237 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101974930 | Unknown | 12000 | Conductor | Overhead | Yes | 43019 | 11:57 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1484 | 2017 | 10 | 11 | 11 | 57 | 17-0086350 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 226925 | 16.5068 | 112_268 | <25mph | <15mph | HFTD - Distribution | 2017-10-11 11:57:00 | 1227 | 19.0479 | FALSE | <25mph | D3481 | 2.38 | 2015-04-09T01:27:00Z | 5.99 | 35 | < 25mph | D3481 | 2.38 | 2015-04-09T01:27:00Z | 5.99 | 35 | < 25mph | D3481 | 2.38 | 2015-04-09T01:27:00Z | 5.99 | 70 | < 25mph | D3481 | 2.38 | 2015-04-09T01:27:00Z | 5.99 | 70 | < 25mph
PG&E | 2018-06-08 | 19:03 | 35.154 | -120.594 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101852092 | AT&T | 12000 | Conductor | Overhead | Yes | 43259 | 19:03 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1644 | 2018 | 6 | 8 | 19 | 3 | 18-0049130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2473 | 24.0333 | 218_82 | <25mph | <15mph | HFTD - Distribution | 2018-06-08 19:03:00 | 1386 | 25.9327 | FALSE | 25-40mph | D6295 | 3.26 | 2016-09-21T12:47:00Z | 0 | 9 | < 25mph | E8214 | 6.18 | 2016-09-21T12:20:00Z | 2.01 | 17 | < 25mph | D6295 | 3.26 | 2016-09-21T13:32:00Z | 0 | 17 | < 25mph | E8214 | 6.18 | 2016-09-21T13:37:00Z | 2.01 | 33 | < 25mph
PG&E | 2017-06-08 15:19 | 15:08 | 34.6058 | -120.0214 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SHAWN STEINER | 101947678 | Unknown | 12000 | Conductor | Overhead | Yes | 42894.6382 | 15:08 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1136 | 2017 | 6 | 8 | 15 | 8 | 17-0053783 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 41311 | 18.6266 | 244_52 | <25mph | <15mph | HFTD - Distribution | 2017-06-08 15:08:00 | 875 | 20.2983 | FALSE | <25mph | KIZA | 3.08 | 2017-02-19T00:15:00Z | 19.57 | 3 | < 25mph | RHWC1 | 6.88 | 2017-02-19T00:06:00Z | 38.01 | 27 | 25-40mph | KIZA | 3.08 | 2017-02-19T00:15:00Z | 19.57 | 4 | < 25mph | RHWC1 | 6.88 | 2017-02-19T01:06:00Z | 47 | 47 | 40-55mph
PG&E | 2017-07-28 19:21 | 19:20 | 35.7276 | -120.9903 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Luis Obispo CDF | 101945496 | None | 21000 | Conductor | Overhead | Yes | 42944.8062 | 19:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1295 | 2017 | 7 | 28 | 19 | 20 | 17-0066392 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 8300 | 11.4004 | 200_114 | <25mph | <15mph | HFTD - Distribution | 2017-07-28 19:20:00 | 1033 | 13.3732 | FALSE | <25mph | E9175 | 1.53 | 2019-01-12T03:50:00Z | 10 | 12 | < 25mph | PG169 | 6.35 | 2019-01-12T03:50:00Z | 16.67 | 29 | < 25mph | E9175 | 1.53 | 2019-01-12T03:50:00Z | 10 | 24 | < 25mph | PG171 | 6.51 | 2019-01-12T04:50:00Z | 22.37 | 58 | < 25mph
PG&E | 2015-09-24 13:56 | 2015-09-24 13:56 | 39.3508 | -121.2454 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 9692 Rices-Texas Hill rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42271.5806 | 2015-09-24 13:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0614 | 2015 | 9 | 24 | 13 | 56 | 15-0063159 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 51917 | 10.3419 | 189_313 | <25mph | <15mph | HFTD - Distribution | 2015-09-24 13:56:00 | 359 | 13.3743 | FALSE | <25mph | PG424 | 3.37 | 2019-10-06T18:20:00Z | 6.93 | 12 | < 25mph | BNGC1 | 7.8 | 2019-10-06T17:51:00Z | 8.01 | 50 | < 25mph | PG424 | 3.37 | 2019-10-06T19:20:00Z | 9.73 | 24 | < 25mph | PG424 | 3.37 | 2019-10-06T19:20:00Z | 9.73 | 100 | < 25mph
PG&E | 2019-04-20 | 6:57 | 37.8686 | -121.6843 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | East County FD | Unknown |  | 17000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-321 | 2019 | 4 | 20 | 6 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 39.0116 | 170_232 | 25-40mph | 30-45mph | HFTD - Distribution | 2019-04-20 06:57:00 | 1744 | 39.0116 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | VAQC1 | 6.19 | 2016-01-04T05:45:00Z | 12.01 | 7 | < 25mph |  |  |  | 0 | 0 | No data | VAQC1 | 6.19 | 2016-01-04T06:45:00Z | 13 | 14 | < 25mph
PG&E | 2017-05-15 | 3:05 | 35.6261 | -120.8962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101873299 | Unknown | 21000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1097 | 2017 | 5 | 15 | 3 | 5 | 17-0047837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 337188 | 4.016 | 204_108 | <25mph | <15mph | HFTD - Distribution | 2017-05-15 03:05:00 | 837 | 18.5139 | FALSE | <25mph | TABC1 | 2.62 | 2018-06-06T14:07:00Z | 2.01 | 1 | < 25mph | TABC1 | 2.62 | 2018-06-06T14:07:00Z | 2.01 | 1 | < 25mph | TABC1 | 2.62 | 2018-06-06T15:07:00Z | 4 | 2 | < 25mph | TABC1 | 2.62 | 2018-06-06T15:07:00Z | 4 | 2 | < 25mph
PG&E | 2015-05-09 21:37 | 2015-05-09 21:37 | 39.2848 | -121.0219 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100004095 | Pacific Bell | 12000 | Fuse | Overhead | Yes | 42133.9007 | 2015-05-09 21:37 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0312 | 2015 | 5 | 9 | 21 | 37 | 15-0033109 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 11 | 9.2188 | 198_310 | <25mph | <15mph | HFTD - Distribution | 2015-05-09 21:37:00 | 58 | 15.4234 | FALSE | <25mph | E5439 | 3.42 | 2018-02-13T12:00:00Z | 13 | 31 | < 25mph | KGOO | 4.32 | 2018-02-13T11:40:00Z | 20.71 | 63 | < 25mph | E5439 | 3.42 | 2018-02-13T12:00:00Z | 13 | 63 | < 25mph | KGOO | 4.32 | 2018-02-13T11:40:00Z | 20.71 | 126 | < 25mph
PG&E | 2019-06-10 | 16:34 | 38.821 | -120.846 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Garden Valley FD | 153082106 |  | 21000 | Conductor | Overhead | Yes | 43626 | 16:34 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-372 | 2019 | 6 | 10 | 16 | 34 | 19-0065481 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14169 | 8.5329 | 206_284 | <25mph | <15mph | HFTD - Distribution | 2019-06-10 16:34:00 | 1827 | 15.7607 | FALSE | <25mph | PG180 | 3.67 | 2019-07-27T21:40:00Z | 12.48 | 12 | < 25mph | PG027 | 6.76 | 2019-07-27T21:30:00Z | 14.7 | 73 | < 25mph | PG180 | 3.67 | 2019-07-27T22:30:00Z | 14.25 | 24 | < 25mph | PG364 | 5.22 | 2019-07-27T22:30:00Z | 17.09 | 146 | < 25mph
PG&E | 2017-10-16 | 12:26 | 36.6641 | -121.0995 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Nick Shawkey E4462 209-402-1645 Cover Engine from Tuolumne Calaveras Unit | 101689865 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43024 | 12:26 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1495 | 2017 | 10 | 16 | 12 | 26 | 17-0087754 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 519 | 1.3904 | 195_165 | <25mph | <15mph | HFTD - Distribution | 2017-10-16 12:26:00 | 1238 | 14.8173 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E1697 | 6.85 | 2015-12-30T02:42:00Z | 4 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E1697 | 6.85 | 2015-12-30T03:12:00Z | 4 | 8 | < 25mph
PG&E | 2016-08-08 | 2016-08-08 15:44 | 37.1382 | -121.9672 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100519919 |  | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0912 | 2016 | 8 | 8 | 15 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 8.8992 | 157_192 | <25mph | <15mph | HFTD - Distribution | 2016-08-08 15:44:00 | 655 | 10.1741 | FALSE | <25mph | D8979 | 1.09 | 2017-04-07T06:41:00Z | 20 | 23 | < 25mph | LSGC1 | 4.65 | 2017-04-07T06:32:00Z | 77 | 97 | 55mph+ | D8979 | 1.09 | 2017-04-07T06:41:00Z | 20 | 46 | < 25mph | LSGC1 | 4.65 | 2017-04-07T06:32:00Z | 77 | 204 | 55mph+
PG&E | 2017-08-29 | 15:54 | 38.302 | -122.5431 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 911 | 102026119 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 42976 | 15:54 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1367 | 2017 | 8 | 29 | 15 | 54 | 17-0073928 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 485 | 16.1777 | 133_256 | <25mph | <15mph | HFTD - Distribution | 2017-08-29 15:54:00 | 1105 | 18.0049 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7525 | 5.91 | 2016-08-29T01:48:00Z | 13 | 10 | < 25mph |  |  |  | 0 | 0 | No data | KO69 | 4.55 | 2016-08-29T02:35:00Z | 19.57 | 27 | < 25mph
PG&E | 2017-06-24 15:06 | 14:51 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 42910.6292 | 14:51 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1194 | 2017 | 6 | 24 | 14 | 51 | 17-0058332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 21296 | 10.4286 | 210_259 | <25mph | <15mph | HFTD - Distribution | 2017-06-24 14:51:00 | 933 | 10.7263 | FALSE | <25mph | ANUC1 | 1.37 | 2016-01-23T19:53:00Z | 12.01 | 2 | < 25mph | ANUC1 | 1.37 | 2016-01-23T19:53:00Z | 12.01 | 3 | < 25mph | ANUC1 | 1.37 | 2016-01-23T20:53:00Z | 13 | 3 | < 25mph | ANUC1 | 1.37 | 2016-01-23T20:53:00Z | 13 | 5 | < 25mph
PG&E | 2018-08-14 | 15:46 | 38.0878 | -122.6002 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103916882 | Verizon | 0 – 750 | Conductor | Overhead | Yes | 43326 | 15:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1844 | 2018 | 8 | 14 | 15 | 46 | 18-0069929 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 546 | 20.6189 | 130_244 | <25mph | <15mph | HFTD - Distribution | 2018-08-14 15:46:00 | 1583 | 26.2074 | FALSE | 25-40mph | PG123 | 2.32 | 2019-05-16T04:00:00Z | 72.34 | 44 | 55mph+ | PG123 | 2.32 | 2019-05-16T04:00:00Z | 72.34 | 94 | 55mph+ | PG123 | 2.32 | 2019-05-16T04:00:00Z | 72.34 | 88 | 55mph+ | PG123 | 2.32 | 2019-05-16T04:00:00Z | 72.34 | 189 | 55mph+
PG&E | 2018-08-20 | 9:34 | 39.8014 | -121.5813 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100400441 | Unknown | 12000 | Conductor | Overhead | Yes | 43332 | 9:34 | Contact From Object | N.A. | Other | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1849 | 2018 | 8 | 20 | 9 | 34 | 18-0071596 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 394259 | 5.4464 | 175_338 | <25mph | <15mph | HFTD - Distribution | 2018-08-20 09:34:00 | 1588 | 11.8754 | FALSE | <25mph | E4833 | 1.36 | 2015-09-15T09:43:00Z | 2.01 | 10 | < 25mph | PDEC1 | 4.03 | 2015-09-15T09:00:00Z | 12.01 | 24 | < 25mph | E4833 | 1.36 | 2015-09-15T10:19:00Z | 2.01 | 20 | < 25mph | PDEC1 | 4.03 | 2015-09-15T09:00:00Z | 12.01 | 48 | < 25mph
PG&E | 2017-07-01 04:43 | 3:12 | 38.1952 | -122.9197 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103855493 | Unknown | 12000 | Conductor | Overhead | Yes | 42917.1963 | 3:12 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1214 | 2017 | 7 | 1 | 3 | 12 | 17-0059935 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 41370 | 14.0388 | 116_251 | <25mph | <15mph | HFTD - Distribution | 2017-07-01 03:12:00 | 951 | 27.9197 | FALSE | 25-40mph |  |  |  | 0 | 0 | No data | PRWC1 | 7.17 | 2017-03-12T06:00:00Z | 16.89 | 13 | < 25mph |  |  |  | 0 | 0 | No data | PRWC1 | 7.17 | 2017-03-12T06:30:00Z | 17.83 | 26 | < 25mph
PG&E | 2016-07-29 01:31 | 2016-07-29 01:31 | 41.0396 | -123.674 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Hoopa FD | 100962351 |  | 12000 | Conductor | Overhead | Yes | 42580.0632 | 2016-07-29 01:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0891 | 2016 | 7 | 29 | 1 | 31 | 16-0053478 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1418 | 4.1421 | 88_408 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 01:31:00 | 633 | 13.6696 | FALSE | <25mph |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data |  |  |  | 0 | 0 | No data
PG&E | 2016-04-21 09:25 | 2016-04-21 09:25 | 39.293 | -123.769 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 103312287 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0711 | 2016 | 4 | 21 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 8.8774 | 81_312 | <25mph | <15mph | HFTD - Distribution | 2016-04-21 09:25:00 | 455 | 20.2474 | FALSE | <25mph | F1771 | 2.04 | 2018-09-09T08:43:00Z | 0 | 9 | < 25mph | F1771 | 2.04 | 2018-09-09T08:43:00Z | 0 | 9 | < 25mph | E6025 | 0.21 | 2018-09-09T09:00:00Z | 2.01 | 19 | < 25mph | E6025 | 0.21 | 2018-09-09T09:00:00Z | 2.01 | 19 | < 25mph
PG&E | 2016-10-11 23:17 | 23:16 | 39.0201 | -120.8294 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire.foresthill fire | 100025501 |  | 60000 | Conductor | Overhead | Yes | 42654.9701 | 23:16 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error |  | no-match | 1028 | 2016 | 10 | 11 | 23 | 16 | INT-08640 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 0 | 7.6312 | 207_295 | <25mph | <15mph | HFTD - Transmission | 2016-10-11 23:16:00 | 769 | 11.1078 | FALSE | <25mph | AU268 | 0.89 | 2018-04-14T06:46:00Z | 0 | 5 | < 25mph | FSHC1 | 7.19 | 2018-04-14T06:33:00Z | 3 | 9 | < 25mph | AU268 | 0.89 | 2018-04-14T07:49:00Z | 2.01 | 9 | < 25mph | FSHC1 | 7.19 | 2018-04-14T07:33:00Z | 3 | 19 | < 25mph
PG&E | 2015-01-26 03:51 | 2015-01-26 03:51 | 37.0539 | -122.1587 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42030.1604 | 2015-01-26 03:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0258 | 2015 | 1 | 26 | 3 | 51 | 15-0007000 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7602 | 14.3078 | 149_187 | <25mph | <15mph | HFTD - Distribution | 2015-01-26 03:51:00 | 5 | 14.9656 | FALSE | <25mph |  |  |  | 0 | 0 | No data | BNDC1 | 5.38 | 2016-12-26T05:50:00Z | 14.99 | 46 | < 25mph |  |  |  | 0 | 0 | No data | BNDC1 | 5.38 | 2016-12-26T06:50:00Z | 17 | 93 | < 25mph
PG&E | 2016-07-29 | 18:16 | 38.5769 | -122.6187 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Selma Fire Department |  |  | 12000 | Conductor | Overhead | Yes | 42580 | 18:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0890 | 2016 | 7 | 29 | 18 | 16 | 16-0053726 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 177834 | 13.7145 | 130_271 | <25mph | <15mph | HFTD - Distribution | 2016-07-29 18:16:00 | 635 | 15.1116 | FALSE | <25mph | E1553 | 3.84 | 2018-03-31T14:29:00Z | 3 | 4 | < 25mph | C1766 | 4.56 | 2018-03-31T15:17:00Z | 4 | 18 | < 25mph | E1553 | 3.84 | 2018-03-31T15:59:00Z | 3 | 8 | < 25mph | C1766 | 4.56 | 2018-03-31T15:32:00Z | 4.99 | 36 | < 25mph
PG&E | 2015-07-30 19:11 | 2015-07-30 19:11 | 37.8102 | -120.1287 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE |  |  | 17000 | Conductor | Overhead | Yes | 42215.7993 | 2015-07-30 19:11 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0500 | 2015 | 7 | 30 | 19 | 11 | 15-0051772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26776 | 10.007 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2015-07-30 19:11:00 | 245 | 11.7658 | FALSE | <25mph | SEWC1 | 1.66 | 2017-10-14T05:16:00Z | 14.99 | 6 | < 25mph | SEWC1 | 1.66 | 2017-10-14T05:16:00Z | 14.99 | 6 | < 25mph | SEWC1 | 1.66 | 2017-10-14T06:16:00Z | 14.99 | 10 | < 25mph | SEWC1 | 1.66 | 2017-10-14T06:16:00Z | 14.99 | 10 | < 25mph
PG&E | 2017-12-20 07:55 | 07:54 | 37.4012 | -122.3606 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100318864 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43089.3298 | 07:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1546 | 2017 | 12 | 20 | 7 | 54 | 17-0102756 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6602 | 16.1413 | 140_206 | <25mph | <15mph | HFTD - Distribution | 2017-12-20 07:54:00 | 1288 | 21.2088 | FALSE | <25mph | E4863 | 2.73 | 2015-01-27T05:33:00Z | 3 | 13 | < 25mph | E2649 | 6.54 | 2015-01-27T05:57:00Z | 8.01 | 34 | < 25mph | E4863 | 2.73 | 2015-01-27T06:53:00Z | 4 | 27 | < 25mph | E2649 | 6.54 | 2015-01-27T05:57:00Z | 8.01 | 69 | < 25mph
PG&E | 2018-09-29 | 16:16 | 41.0219 | -123.655 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Hoopa Fire Dept | 100962165 | Unknown | 12000 | Conductor | Overhead | Yes | 43372 | 16:16 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1923 | 2018 | 9 | 29 | 16 | 16 | 18-0084877 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 16028 | 7.8421 | 89_407 | <25mph | <15mph | HFTD - Distribution | 2018-09-29 16:16:00 | 1662 | 11.5265 | FALSE | <25mph | HOAC1 | 1.98 | 2018-08-20T18:40:00Z | 4.99 | 1 | < 25mph | BIIC1 | 5.31 | 2018-08-20T18:40:00Z | 11.01 | 7 | < 25mph | HOAC1 | 1.98 | 2018-08-20T19:40:00Z | 5.99 | 2 | < 25mph | BIIC1 | 5.31 | 2018-08-20T18:40:00Z | 11.01 | 14 | < 25mph
PG&E | 2015-08-17 08:37 | 2015-08-17 08:37 | 37.0757 | -122.023 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101800237 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0537 | 2015 | 8 | 17 | 8 | 37 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 1.4249 | 154_188 | <25mph | <15mph | HFTD - Distribution | 2015-08-17 08:37:00 | 281 | 11.7495 | FALSE | <25mph | C5272 | 1.08 | 2015-04-06T06:02:00Z | 5.99 | 32 | < 25mph | E6085 | 7.55 | 2015-04-06T06:03:00Z | 10 | 156 | < 25mph | C5272 | 1.08 | 2015-04-06T06:02:00Z | 5.99 | 64 | < 25mph | E6085 | 7.55 | 2015-04-06T07:03:00Z | 10 | 309 | < 25mph
PG&E | 2019-06-27 | 2:23 | 36.8198 | -119.3334 | Bird Found | Hardwood Woodland | 0.25 - 10 Acres | Self Extinguished |  | Kings River-Sanger-Reedley 115Kv At 16/089 |  | 115000 | Insulator | Overhead | Yes | 43643 | 2:23 | Equipment - PG&E | Insulator |  |  |  |  | no-match | 2019-104 | 2019 | 6 | 27 | 2 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | N.A. | 13.572 | 273_175 | <25mph | <15mph | HFTD - Transmission | 2019-06-27 02:23:00 | 1872 | 13.572 | FALSE | <25mph |  |  |  | 0 | 0 | No data | TRMC1 | 6.47 | 2016-10-28T23:52:00Z | 4 | 7 | < 25mph |  |  |  | 0 | 0 | No data | TRMC1 | 6.47 | 2016-10-29T00:52:00Z | 4 | 14 | < 25mph
PG&E | 2017-05-25 17:36 | 16:55 | 38.3986 | -122.9876 | Vegetation | Rural | < 3 Meters | Utility: PG&E | N.A. | 101974034 | Unknown | 12000 | Conductor | Overhead | Yes | 42880.7334 | 16:55 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1114 | 2017 | 5 | 25 | 16 | 55 | 17-0050815 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 2644 | 12.6436 | 114_262 | <25mph | <15mph | HFTD - Distribution | 2017-05-25 16:55:00 | 854 | 13.2306 | FALSE | <25mph | D2849 | 1.17 | 2016-10-02T16:11:00Z | 4 | 13 | < 25mph | D3838 | 5.48 | 2016-10-02T16:17:00Z | 5.99 | 49 | < 25mph | D2849 | 1.17 | 2016-10-02T17:21:00Z | 4.99 | 25 | < 25mph | BDZC1 | 7.05 | 2016-10-02T16:24:00Z | 9.13 | 97 | < 25mph
PG&E | 2015-07-26 12:25 | 2015-07-26 12:25 | 39.1586 | -121.0634 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 15499 ALLISON RANCH RD |  | 12000 | Conductor | Overhead | Yes | 42211.5174 | 2015-07-26 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0485 | 2015 | 7 | 26 | 12 | 25 | 15-0050558 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2224 | 13.0644 | 197_303 | <25mph | <15mph | HFTD - Distribution | 2015-07-26 12:25:00 | 230 | 13.6917 | FALSE | <25mph | E1789 | 3.9 | 2019-06-22T14:12:00Z | 13 | 10 | < 25mph | E1789 | 3.9 | 2019-06-22T14:12:00Z | 13 | 118 | < 25mph | E1789 | 3.9 | 2019-06-22T15:30:00Z | 13 | 20 | < 25mph | PG429 | 7.31 | 2019-06-22T16:00:00Z | 16.22 | 229 | < 25mph
PG&E | 2016-09-28 | 14:00 | 35.2145 | -118.5625 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire |  |  | 0 – 750 | Conductor | Overhead | Yes | 42641 | 14:00 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1008 | 2016 | 9 | 28 | 14 | 0 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.8467 | 310_87 | <25mph | <15mph | HFTD - Distribution | 2016-09-28 14:00:00 | 750 | 26.957 | FALSE | 25-40mph | UP691 | 1.1 | 2017-07-29T14:20:00Z | 8.05 | 2 | < 25mph | UP691 | 1.1 | 2017-07-29T14:20:00Z | 8.05 | 25 | < 25mph | UP691 | 1.1 | 2017-07-29T14:20:00Z | 8.05 | 4 | < 25mph | UP691 | 1.1 | 2017-07-29T14:20:00Z | 8.05 | 41 | < 25mph
PG&E | 2018-08-01 | 17:58 | 38.9155 | -122.799 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102156435 | Unknown | 12000 | Conductor | Overhead | Yes | 43313 | 17:58 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1805 | 2018 | 8 | 1 | 17 | 58 | 18-0065921 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2744 | 14.8702 | 122_290 | <25mph | <15mph | HFTD - Distribution | 2018-08-01 17:58:00 | 1545 | 14.8702 | FALSE | <25mph | E4393 | 3.97 | 2015-08-25T09:06:00Z | 4.99 | 4 | < 25mph | KELC1 | 4.99 | 2015-08-25T08:57:00Z | 10 | 5 | < 25mph | E4393 | 3.97 | 2015-08-25T09:21:00Z | 4.99 | 8 | < 25mph | KELC1 | 4.99 | 2015-08-25T08:57:00Z | 10 | 10 | < 25mph
PG&E | 2015-12-03 12:10 | 2015-12-03 12:10 | 40.0277 | -120.9652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | usfs | spanish creek campground |  | 12000 | Conductor | Overhead | Yes | 42341.5069 | 2015-12-03 12:10 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0683 | 2015 | 12 | 3 | 12 | 10 | 15-0082505 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 196854 | 26.293 | 201_351 | 25-40mph | 15-30mph | HFTD - Distribution | 2015-12-03 12:10:00 | 427 | 26.9543 | FALSE | 25-40mph | CHAC1 | 3.2 | 2016-04-25T12:47:00Z | 8.99 | 2 | < 25mph | CHAC1 | 3.2 | 2016-04-25T12:47:00Z | 8.99 | 3 | < 25mph | CHAC1 | 3.2 | 2016-04-25T13:47:00Z | 17 | 4 | < 25mph | CHAC1 | 3.2 | 2016-04-25T13:47:00Z | 17 | 6 | < 25mph
PG&E | 2017-07-16 11:59 | 11:59 | 36.6669 | -121.7515 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101761892 | None | 21000 | Fuse | Overhead | Yes | 42932.4994 | 11:59 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1259 | 2017 | 7 | 16 | 11 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 22.4318 | 166_166 | <25mph | <15mph | HFTD - Distribution | 2017-07-16 11:59:00 | 998 | 30.0095 | FALSE | 25-40mph | E4669 | 2.51 | 2015-12-25T05:30:00Z | 10 | 18 | < 25mph | E4669 | 2.51 | 2015-12-25T05:30:00Z | 10 | 18 | < 25mph | E4669 | 2.51 | 2015-12-25T05:30:00Z | 10 | 33 | < 25mph | E4669 | 2.51 | 2015-12-25T05:30:00Z | 10 | 33 | < 25mph
PG&E | 2017-10-02 | 14:56 | 38.9102 | -120.9185 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100110800 | None | 21000 | Other | Overhead | Yes | 43010 | 14:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1447 | 2017 | 10 | 2 | 14 | 56 | 17-0083516 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 160 | 17.2967 | 203_289 | <25mph | <15mph | HFTD - Distribution | 2017-10-02 14:56:00 | 1185 | 22.7009 | FALSE | <25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.3 | 2016-02-25T01:56:00Z | 7 | 19 | < 25mph |  |  |  | 0 | 0 | No data | PLTC1 | 7.3 | 2016-02-25T01:56:00Z | 7 | 38 | < 25mph
PG&E | 2017-09-18 | 23:50 | 37.9088 | -120.4865 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | incident comander geoff marshall 209-419-4407 | 101040882 | Unknown | 17000 | Conductor | Overhead | Yes | 42996 | 23:50 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1422 | 2017 | 9 | 18 | 23 | 50 | 17-0079858 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 382303 | 9.0814 | 222_234 | <25mph | <15mph | HFTD - Distribution | 2017-09-18 23:50:00 | 1160 | 16.9339 | FALSE | <25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.23 | 2018-12-26T01:03:00Z | 17 | 26 | < 25mph |  |  |  | 0 | 0 | No data | GNSC1 | 5.23 | 2018-12-26T01:03:00Z | 17 | 52 | < 25mph
PG&E | 2017-07-02 | 13:28 | 39.8605 | -121.6274 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 000/017c | Unknown | 60000 | Conductor | Overhead | Yes | 42918 | 13:28 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1216 | 2017 | 7 | 2 | 13 | 28 | INT-09794 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 10.1141 | 173_342 | <25mph | <15mph | HFTD - Transmission | 2017-07-02 13:28:00 | 956 | 11.4462 | FALSE | <25mph | C4565 | 1.76 | 2016-08-06T00:50:00Z | 2.01 | 3 | < 25mph | CSTC1 | 7.55 | 2016-08-06T00:51:00Z | 13 | 5 | < 25mph | C4565 | 1.76 | 2016-08-06T00:50:00Z | 2.01 | 5 | < 25mph | CSTC1 | 7.55 | 2016-08-06T00:51:00Z | 13 | 9 | < 25mph
PG&E | 2018-09-09 | 4:25 | 38.6534 | -122.8538 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 13/1 | None | 60000 | Conductor | Overhead | Yes | 43352 | 4:25 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1887 | 2018 | 9 | 9 | 4 | 25 | INT-11353 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 7.8888 | 120_276 | <25mph | <15mph | HFTD - Transmission | 2018-09-09 04:25:00 | 1626 | 22.3261 | FALSE | <25mph | DRYWW | 3.16 | 2018-08-01T07:00:00Z | 7.7 | 11 | < 25mph | HWKC1 | 5.72 | 2018-08-01T06:56:00Z | 13 | 24 | < 25mph | DRYWW | 3.16 | 2018-08-01T07:00:00Z | 7.7 | 22 | < 25mph | HWKC1 | 5.72 | 2018-08-01T06:56:00Z | 13 | 48 | < 25mph
PG&E | 2018-07-17 | 11:58 | 37.2217 | -121.6778 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Luis Morado state arson fire fighter | 100601345 | Unknown | 12000 | Conductor | Overhead | Yes | 43298 | 11:58 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1756 | 2018 | 7 | 17 | 11 | 58 | 18-0060617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 5865 | 5.1834 | 170_196 | <25mph | <15mph | HFTD - Distribution | 2018-07-17 11:58:00 | 1496 | 14.408 | FALSE | <25mph |  |  |  | 0 | 0 | No data | C7794 | 7.07 | 2015-11-14T22:40:00Z | 8.01 | 80 | < 25mph |  |  |  | 0 | 0 | No data | C7794 | 7.07 | 2015-11-14T22:40:00Z | 8.01 | 163 | < 25mph
PG&E | 2016-09-23 05:23 | 15:23 | 39.3784 | -121.0922 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100091491 | None | 12000 | Conductor | Overhead | Yes | 42636.2243 | 15:23 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0999 | 2016 | 9 | 23 | 15 | 23 | 16-0067089 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 80185 | 10.9717 | 195_315 | <25mph | <15mph | HFTD - Distribution | 2016-09-23 15:23:00 | 741 | 11.3047 | FALSE | <25mph | E3651 | 3.67 | 2017-03-24T23:10:00Z | 4 | 12 | < 25mph | RRRC1 | 5.34 | 2017-03-24T23:13:00Z | 14 | 13 | < 25mph | E3651 | 3.67 | 2017-03-24T23:10:00Z | 4 | 24 | < 25mph | RRRC1 | 5.34 | 2017-03-24T23:13:00Z | 14 | 26 | < 25mph
PG&E | 2018-11-13 | 15:41 | 37.0644 | -121.9578 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101680441 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43417 | 15:41 | Other | N.A. | N.A. | N.A. | Human Error | Grow house | Other/Unknown | 1973 | 2018 | 11 | 13 | 15 | 41 | 18-0099492 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 21484 | 1.9347 | 157_188 | <25mph | <15mph | HFTD - Distribution | 2018-11-13 15:41:00 | 1713 | 13.1257 | FALSE | <25mph | PG062 | 0.72 | 2019-07-10T15:20:00Z | 7.9 | 36 | < 25mph | D8979 | 4.33 | 2019-07-10T15:35:00Z | 11.01 | 200 | < 25mph | PG062 | 0.72 | 2019-07-10T15:20:00Z | 7.9 | 76 | < 25mph | D8979 | 4.33 | 2019-07-10T15:35:00Z | 11.01 | 408 | < 25mph
PG&E | 2019-07-22 | 21:39 | 38.8618 | -121.1044 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 152561103 |  | 12000 | Conductor | Overhead | Yes | 43668 | 21:39 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-336 | 2019 | 7 | 22 | 21 | 39 | 19-0080025 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 9842 | 9.5984 | 195_286 | <25mph | <15mph | HFTD - Distribution | 2019-07-22 21:39:00 | 1921 | 13.5446 | FALSE | <25mph | D7393 | 2.11 | 2018-07-02T21:13:00Z | 11.01 | 10 | < 25mph | D7393 | 2.11 | 2018-07-02T21:13:00Z | 11.01 | 15 | < 25mph | D7393 | 2.11 | 2018-07-02T21:13:00Z | 11.01 | 20 | < 25mph | D7393 | 2.11 | 2018-07-02T21:13:00Z | 11.01 | 28 | < 25mph
PG&E | 2016-07-28 14:24 | 2016-07-28 14:24 | 37.8232 | -120.1356 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101037045 |  | 17000 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Guy/Span Wire | N.A. | N.A. | Unknown |  | no-match | 0888 | 2016 | 7 | 28 | 14 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Guy/Span Wire | N.A. | 10.9021 | 237_229 | <25mph | <15mph | HFTD - Distribution | 2016-07-28 14:24:00 | 631 | 11.4062 | FALSE | <25mph | SEWC1 | 2.46 | 2017-11-25T19:16:00Z | 17 | 5 | < 25mph | SEWC1 | 2.46 | 2017-11-25T19:16:00Z | 17 | 5 | < 25mph | SEWC1 | 2.46 | 2017-11-25T20:16:00Z | 22.01 | 10 | < 25mph | SEWC1 | 2.46 | 2017-11-25T20:16:00Z | 22.01 | 10 | < 25mph
PG&E | 2017-06-13 | 14:30 | 37.8526 | -122.1853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Tower 005/035c | Unknown | 115000 | Conductor | Overhead | Yes | 42899 | 14:30 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1143 | 2017 | 6 | 13 | 14 | 30 | INT-09744 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | Balloons | 0 | 10.6352 | 148_231 | <25mph | <15mph | HFTD - Transmission | 2017-06-13 14:30:00 | 882 | 14.5193 | FALSE | <25mph | ONOC1 | 2.12 | 2017-05-19T16:33:00Z | 18.99 | 47 | < 25mph | LTRC1 | 6.59 | 2017-05-19T16:28:00Z | 20 | 133 | < 25mph | ONOC1 | 2.12 | 2017-05-19T17:33:00Z | 18.99 | 92 | < 25mph | LTRC1 | 6.59 | 2017-05-19T16:28:00Z | 20 | 264 | < 25mph
PG&E | 2018-03-06 | 17:57 | 38.2811 | -120.8965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-647-5220 | 101238429 | AT&T | 12000 | Conductor | Overhead | Yes | 43165 | 17:57 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1566 | 2018 | 3 | 6 | 17 | 57 | 18-0020396 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 142000 | 3.9357 | 204_254 | <25mph | <15mph | HFTD - Distribution | 2018-03-06 17:57:00 | 1308 | 12.1612 | FALSE | <25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.07 | 2016-10-20T09:05:00Z | 8.99 | 3 | < 25mph |  |  |  | 0 | 0 | No data | CFAC1 | 7.07 | 2016-10-20T10:05:00Z | 8.99 | 6 | < 25mph
PG&E | 2015-09-04 07:49 | 2015-09-04 07:49 | 40.2318 | -122.3643 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | E/O FRONTIER RD & N/O WAGON WAY |  | 12000 | Conductor | Overhead | Yes | 42251.3257 | 2015-09-04 07:49 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0577 | 2015 | 9 | 4 | 7 | 49 | 15-0059323 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 9563 | 2.343 | 142_362 | <25mph | <15mph | HFTD - Distribution | 2015-09-04 07:49:00 | 321 | 17.9748 | FALSE | <25mph |  |  |  | 0 | 0 | No data | E7114 | 5.07 | 2018-04-10T23:02:00Z | 15.99 | 4 | < 25mph |  |  |  | 0 | 0 | No data | E7114 | 5.07 | 2018-04-10T23:02:00Z | 15.99 | 8 | < 25mph
PG&E | 2017-06-30 23:55 | 23:54 | 38.5794 | -122.8835 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 101958804 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42916.9965 | 23:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1211 | 2017 | 6 | 30 | 23 | 54 | 17-0059922 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2025 | 14.1552 | 118_272 | <25mph | <15mph | HFTD - Distribution | 2017-06-30 23:54:00 | 950 | 23.4555 | FALSE | <25mph | D2144 | 3.78 | 2016-01-31T00:48:00Z | 2.01 | 16 | < 25mph | E6724 | 5.41 | 2016-01-31T00:19:00Z | 4.99 | 38 | < 25mph | D2144 | 3.78 | 2016-01-31T01:48:00Z | 2.01 | 32 | < 25mph | E6724 | 5.41 | 2016-01-31T00:19:00Z | 4.99 | 75 | < 25mph
PG&E | 2017-09-24 | 16:42 | 38.3869 | -122.9667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DOUG JONES | 101973946 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43002 | 16:42 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1432 | 2017 | 9 | 24 | 16 | 42 | 17-0081329 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 22574 | 19.6154 | 114_261 | <25mph | <15mph | HFTD - Distribution | 2017-09-24 16:42:00 | 1170 | 19.6154 | FALSE | <25mph | E5234 | 2.8 | 2015-01-03T19:50:00Z | 5.99 | 18 | < 25mph | BGAC1 | 6.8 | 2015-01-03T19:05:00Z | 14.99 | 63 | < 25mph | E5234 | 2.8 | 2015-01-03T20:10:00Z | 5.99 | 36 | < 25mph | BGAC1 | 6.8 | 2015-01-03T19:05:00Z | 14.99 | 124 | < 25mph
5. Atlas (Southern LNU Complex) | 2017-10-08 | 21:52 | 38.3921 | -122.2437 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1991 | 2017 | 10 | 8 | 21 | 52 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 37.6357 | 146_261 | 25-40mph | 30-45mph | HFTD - Distribution | 2017-10-08 21:52:00 | 1206 | 41.3099 | FALSE | 40-55mph | F0187 | 3.03 | 2017-06-19T13:47:00Z | 1.01 | 4 | < 25mph | ATLC1 | 5.83 | 2017-06-19T13:29:00Z | 10 | 7 | < 25mph | F0187 | 3.03 | 2017-06-19T14:47:00Z | 2.01 | 8 | < 25mph | ATLC1 | 5.83 | 2017-06-19T13:29:00Z | 10 | 16 | < 25mph