## RuralHFTD - Chart
Size | Count of Size - HFTD | Count of Size - UI
Less Than .25 Acres | 83
.26 - 9.99 Acres | 30
10 - 99 Acres | 7 | 4
100 - 299 Acres | 2 | 2
300 - 999 Acres | 1 | 3
1000 - 4999 Acres |  | 4
Greater than 5000 Acres | 2 | 6

## RuralHFTD
ID | Name | Circuit | Date | Year | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Size - HFTD | Size - UI | Suppressed by | Suppressing Agency | Facility Identification | FLOC | HFRA | cGIS HFRA | HFTD | Other Companies | Voltage (Volts) | Business Line | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor
1 |  | Birchim | 2015-02-06 | 2015 | 13:15 | 37.454 | -118.5842 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Various Fire Agencies | Between Poles 1854107E & 1854106E | OH-1854107E | Tier 2 | T2 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-02-06 | 13:15 | Unknown |  |  |  | Unknown
2 |  | Sexton | 2015-02-22 | 2015 | 9:52 | 34.2849 | -119.2173 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura Fire Department | Pole 1718768E | OH-1718768E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-02-22 | 10:49 | Unknown |  |  |  | None
3 |  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown
4 |  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown
5 |  | Maguire | 2015-04-17 | 2015 | 16:41 | 34.0851 | -118.8044 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles County Fire | Maguire 16kV out of Latigo Sub | OH-1199311E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2015-04-17 | 16:41 | Contact From Object |  | Vehicle | Pole | None
6 |  | Zone | 2015-04-27 | 2015 | 19:09 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | 9372 STOCKTON RD PMP MOORPARK | OH-4734128E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-04-27 | 19:09 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
7 |  | Zone | 2015-04-27 | 2015 | 19:10 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 4734128E | OH-4734128E | Tier 3 | T3 | Y |  | 16 | Distribution | Other | Overhead | Yes | 2015-04-27 | 19:10 | Equipment/Facility Failure | Other |  |  | Unknown
8 |  | Atlanta | 2015-05-05 | 2015 | 16:00 | 33.711 | -117.7089 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 4229158E | OH-4229158E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vehicle | Electric Facility | None
9 |  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None
10 |  | Soda Springs | 2015-05-14 | 2015 | 22:24 | 36.1318 | -118.7784 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | Soda Springs 12kV out of Boxwood Sub | OH-4464511E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-14 | 22:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown
11 |  | Lopez | 2015-05-23 | 2015 | 11:57 | 34.3006 | -118.3613 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | Pole 1261671E | OH-1261671E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Conductor | Overhead | Yes | 2015-05-23 | 11:05 | Unknown |  |  |  | Unknown
12 |  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown
13 |  | Pawley | 2015-05-29 | 2015 | 7:29 | 36.387 | -118.9536 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare County Fire | Lemon Cove and Three Rivers Sub. Venida 66kV | OH-4434944E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-05-29 | 7:29 | Contact From Object |  | Animal | Electric Facility | None
14 |  | Atento | 2015-05-30 | 2015 | 15:26 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | Unknown
15 |  | Atento | 2015-05-30 | 2015 | 15:30 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | None
16 |  | Python | 2015-06-06 | 2015 | 10:00 | 34.4043 | -118.4234 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | 16450 Alamo Canyon Rd, Canyon Country | OH-4779534E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-06-06 | 10:13 | Contact From Object |  | Animal | Electric Facility | None
17 |  | Keller | 2015-06-09 | 2015 | 5:46 | 33.5986 | -117.1311 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 4401960E | OH-2297077E | Tier 2 | T2 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2015-06-09 | 5:46 | Contact From Object |  | Animal | Electric Facility | None
18 |  | SPRINGVILLE-LINDSAY-VENIDA/ET-07230,SPRINGVILLE-STRATHMORE/ET-07256 | 2015-06-17 | 2015 | 17:29 | 36.1086 | -118.9425 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 722603E | OH-722604E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-06-17 | 17:29 | Contact From Object |  | Animal | Electric Facility | None
19 |  | Zone | 2015-06-23 | 2015 | 17:21 | 34.279 | -118.9072 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura Fire Department | Primary splice box at base of pole 2115918e | OH-2115918E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Subsurface | No | <Null> |  | Equipment/Facility Failure | Other |  |  | Unknown
20 |  | Taiwan | 2015-07-13 | 2015 | 11:15 | 33.7678 | -117.7207 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | Cal Fire | Pole 960439E | OH-960439E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-07-13 | 13:30 | Unknown |  |  |  | Unknown
21 |  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error
22 |  | BIG CREEK 3-RECTOR NO.1/ET-01046 | 2015-09-03 | 2015 | 17:00 | 36.8936 | -119.4571 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | East of Watts Valley Rd and Pittman Hill Rd, East of Clovis | OH-7020930 | Tier 2 | T2 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2015-09-03 | 16:15 | Contact From Object |  | Balloons | Electric Facility | None
23 |  | PALOMINO | 2015-10-09 | 2015 | 14:00 | 33.5752 | -117.17 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | BEHIND ADDRESS 28151 CELIA RD / PROPERTY LINE., STR 212903S | OH-212903S | Tier 2 | T2 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown
24 |  | GUITAR | 2016-01-16 | 2016 | 15:20 | 34.4096 | -118.6816 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-848266E | OH-848266E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-01-16 | 15:20 | Equipment/Facility Failure | Other |  |  | Unknown
25 |  | SHEFFIELD | 2016-02-22 | 2016 | 17:04 | 34.4492 | -119.5845 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Montecito Fire Department | OH-1082380E | OH-1082380E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-02-22 | 17:04 | Equipment/Facility Failure | Conductor |  |  | Unknown
26 |  | POPPET FLATS | 2016-02-27 | 2016 | 0:49 | 33.9134 | -116.8003 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1989045E | OH-1989045E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-02-27 | 0:49 | Contact From Object |  | Vehicle | Pole | Unknown
27 |  | SANTA CLARA-TAYSHELL/ET-00423 | 2016-04-21 | 2016 | 12:20 | 34.3339 | -119.2748 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4434916E | OH-4434916E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2016-04-21 | 12:20 | Contact From Object |  | Animal | Electric Facility | Unknown
28 |  | WELCH | 2016-04-25 | 2016 | 15:23 | 35.8387 | -118.9147 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1078325E | OH-1078325E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 15:23 | Equipment/Facility Failure | Insulator |  |  | Unknown
29 |  | ELSTER | 2016-04-25 | 2016 | 19:15 | 36.1372 | -118.8615 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-X16345E | OH-X16345E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 120/240 V | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 19:15 | Equipment/Facility Failure | Conductor |  |  | Unknown
30 |  | TICO | 2016-04-28 | 2016 | 14:00 | 34.357 | -119.314 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura County FD | OH-1604151E | OH-1604151E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-04-28 | 14:00 | Equipment/Facility Failure | Other |  |  | Unknown
31 |  | CONCEPCION | 2016-05-02 | 2016 | 7:03 | 34.4736 | -120.2153 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-4041841E | OH-4041841E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-02 | 7:03 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
32 |  | CONCEPCION | 2016-05-12 | 2016 | 8:55 | 34.4736 | -120.216 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-708452E | OH-708452E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-12 | 8:55 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
33 |  | SKINKLE | 2016-05-29 | 2016 | 22:25 | 36.0091 | -118.9563 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-4566417E | OH-4566417E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-05-29 | 22:25 | Contact From Object |  | Other | Electric Facility | Unknown
34 |  | BRUMFIELD | 2016-06-04 | 2016 | 10:17 | 33.5947 | -117.1387 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-2206630E | OH-2206630E | Tier 2 | T2 | Y |  | 12 | Distribution | Transformer | Overhead | Yes | 2016-06-04 | 10:17 | Equipment/Facility Failure | Transformer |  |  | Unknown
35 |  | PYTHON | 2016-06-05 | 2016 | 15:59 | 34.4208 | -118.4218 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4154960E | OH-4154960E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-06-05 | 15:59 | Unknown |  |  |  | Unknown
36 |  | VIENTO | 2016-06-06 | 2016 | 17:44 | 35.1355 | -118.4771 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1373165E | OH-1373165E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-06 | 17:44 | Contact From Object |  | Other | Pole | Unknown
37 |  | SHOWDOWN | 2016-06-09 | 2016 | 11:28 | 34.5862 | -118.196 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4267121E | OH-4267121E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-09 | 11:28 | Contact From Object |  | Balloons | Electric Facility | Unknown
38 |  | SODA SPRINGS | 2016-06-21 | 2016 | 21:47 | 36.2515 | -118.7809 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4391218E | OH-4391218E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-21 | 21:47 | Contact From Object |  | Vegetation | Electric Facility | Unknown
39 |  | KINSEY | 2016-07-08 | 2016 | 11:15 | 34.7906 | -118.8256 | Vegetation | Rural | 300 - 999 Acres | 300 - 999 Acres |  | Fire Agency | Kern County Fire Department | 1-5, Gorman | OH-4539401E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown
40 |  | CACHUMA | 2016-08-18 | 2016 | 14:52 | 34.5356 | -119.8523 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-1413051E | OH-1413051E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-18 | 14:52 | Contact From Object |  | Vegetation | Communication Facility | Unknown
41 |  | VALLECITO | 2016-08-18 | 2016 | 19:00 | 34.4214 | -119.5964 | Other | Rural | Structure Only | Structure Only |  | Fire Agency | Santa Barbara County Fire Department | 2400 block of Whitney Avenue in Summerland | OH-1523986E | Tier 2 | T2 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown
42 |  | MIST | 2016-08-24 | 2016 | 16:37 | 34.4665 | -120.0701 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Santa Barbara County Fire Department | Refiugio Canyon, Santa Barbara | OH-4538468E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-24 | 18:50 | Contact From Object |  | Animal | Electric Facility | Unknown
43 |  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown
44 |  | PATRICIA | 2016-09-16 | 2016 | 19:02 | 34.4851 | -119.3001 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ojai City Fire Department | OH-4797071E | OH-4797071E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-09-16 | 19:02 | Contact From Object |  | Vehicle | Pole | Unknown
45 |  | TUNA | 2016-09-19 | 2016 | 6:11 | 34.04 | -118.6687 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-1638513E | OH-1638513E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown
46 |  | CARVER | 2016-09-24 | 2016 | 14:20 | 35.7381 | -118.9546 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4784763E | OH-4784763E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-09-24 | 14:20 | Contact From Object |  | Animal | Electric Facility | Unknown
47 |  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown
48 |  | DRISKILL | 2016-10-18 | 2016 | 18:41 | 34.4687 | -119.7722 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Santa Barbara Fire Department | OH-2178476E | OH-2178476E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-18 | 18:41 | Equipment/Facility Failure | Fuse |  |  | Unknown
49 |  | PYTHON | 2016-10-22 | 2016 | 15:17 | 34.3812 | -118.4132 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | RAR 0038 | OH-4860064E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-22 | 15:17 | Contact From Object |  | Balloons | Electric Facility | Unknown
50 |  | PATRICIA | 2016-10-23 | 2016 | 9:40 | 34.4603 | -119.2853 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | 900 Rice Road Ojai | OH-786960E | Tier 3 | T3 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown
51 |  | HUGHES LAKE | 2016-10-26 | 2016 | 12:19 | 34.7081 | -118.5367 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | ELIZABETH LAKE ROAD AND KINGS CANYON ROAD, LAKE HUGHES | OH-1586523E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-26 | 12:19 | Contact From Object |  | Vegetation | Electric Facility | Unknown
52 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown
53 |  | PYTHON | 2016-12-02 | 2016 | 21:26 | 34.3812 | -118.4132 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | OH-4572770E | OH-4572770E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vegetation | Electric Facility | Unknown
54 |  | RHODA | 2016-12-30 | 2016 | 11:42 | 34.1231 | -118.723 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-1927507E | OH-1927507E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-12-30 | 11:42 | Contact From Object |  | Balloons | Electric Facility | Unknown
55 |  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown
56 |  | OAK GLEN | 2017-03-15 | 2017 | 13:23 | 34.0534 | -116.971 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-2326555E | OH-2326555E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-15 | 13:23 | Contact From Object |  | Animal | Electric Facility | Unknown
57 |  | HUCKLEBERRY | 2017-03-17 | 2017 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4493863E | OH-4493863E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown
58 |  | PATRICIA | 2017-04-16 | 2017 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4495331E | OH-4495331E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown
59 |  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown
60 |  | LEE VINING-LUNDY NO. 1/ET-01774 | 2017-05-01 | 2017 | 5:40 | 38.0209 | -119.1608 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | CAlFIre | OH-1580964E | OH-1580964E | Tier 2 | T2 | Y |  | 55 | Distribution | Conductor | Overhead | No | <Null> |  | Contamination |  |  |  | Unknown
61 |  | GUITAR | 2017-05-11 | 2017 | 12:27 | 34.4127 | -118.6702 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-848255E | OH-848255E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-05-11 | 12:27 | Contact From Object |  | Balloons | Electric Facility | Unknown
62 |  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown
63 |  | METTLER | 2017-06-02 | 2017 | 10:50 | 35.1021 | -118.5328 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4416566E | OH-4416566E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown
64 |  | ANZAR | 2017-06-04 | 2017 | 13:14 | 33.8373 | -117.4863 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-1757417E | OH-1757417E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2017-06-04 | 13:14 | Wire-Wire Contact |  |  |  | Unknown
65 |  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown
66 |  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown
67 |  | PICK | 2017-06-19 | 2017 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | 30278 Arrastre Canyon Rd., Acton | OH-699610E | Tier 3 | T3 | Y |  | 33 | Distribution | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown
68 |  | MAYBELL | 2017-07-02 | 2017 | 8:24 | 34.0804 | -117.8552 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | OH-144184E | OH-1255315E | T2 200Ft Outer Buffer | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-07-02 | 8:24 | Contact From Object |  | Animal | Electric Facility | Unknown
69 |  | DALBA | 2017-07-11 | 2017 | 18:06 | 34.2054 | -117.1143 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-919465E | OH-919465E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 2.4 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown
70 |  | CUDDEBACK | 2017-08-08 | 2017 | 17:52 | 35.1342 | -118.5607 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4179753E | OH-4179753E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-08-08 | 17:52 | Contact From Object |  | Vehicle | Electric Facility | Unknown
71 |  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown
72 |  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown
73 |  | CABANA | 2017-10-16 | 2017 | 6:11 | 34.0217 | -117.5069 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1670014E | OH-1670014E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-10-16 | 6:11 | Contact From Object |  | Balloons | Electric Facility | Unknown
74 |  | DEACON | 2017-10-18 | 2017 | 13:34 | 33.7702 | -117.2157 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1564666E | OH-1564666E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown
75 |  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown
76 |  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
77 |  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown
78 |  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown
79 |  | BENCH | 2018-06-26 | 2018 | 20:48 | 34.0158 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Holmes St/Wildwood Canyon Rd, Yucaipa | OH-4367391E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-26 | 20:48 | Contact From Object |  | Vehicle | Pole | Unknown
80 |  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown
81 |  | HUGHES LAKE/ED-08810 | 2018-07-06 | 2018 | 5:38 | 34.6744 | -118.4517 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | 465140E | OH-1938477E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-07-06 | 5:38 | Contact From Object |  | Vehicle | Pole | Unknown
82 |  | BIG CREEK 1-RECTOR/ET-01082 | 2018-08-04 | 2018 | 0:43 | 37.1895 | -119.2738 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | OH-7021454 | OH-7021454 | Tier 3 | T3 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2018-08-04 | 2:21 | Equipment/Facility Failure | Other |  |  | Unknown
83 |  | JORDAN | 2018-08-29 | 2018 | 17:32 | 35.7358 | -118.7192 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | Jack Ranch Rd/White River Rd, Kernville | OH-4635091E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-08-29 | 19:06 | Contact From Object |  | Vegetation | Electric Facility | Unknown
84 |  | POULTRY | 2018-09-21 | 2018 | 8:28 | 34.0728 | -117.0397 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Juniper St. Yucaipa | OH-129241E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown
85 |  | OAK GLEN | 2018-11-08 | 2018 | 12:09 | 34.0397 | -116.9362 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 11833 Oak Glen Rd. Yucaipa | OH-4611601E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-08 | 12:09 | Equipment/Facility Failure | Transformer |  |  | Unknown
86 |  | ARCHIE | 2018-11-13 | 2018 | 7:11 | 33.4928 | -117.2796 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | NORTH OF CARANCHO ON VIA CIELO | OH-4149859E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-13 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Unknown
87 |  | Peninsula | 2019-03-16 | 2019 | 17:58 | 33.6182 | -117.8025 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1729510E | OH-1729510E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-03-16 | 17:58 | Equipment/Facility Failure | Crossarm |  |  | Unknown
88 |  | Taggert | 2019-04-23 | 2019 | 21:06 | 34.2147 | -117.0973 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1027559E | OH-1027559E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution |  | Overhead | No |  |  | Unknown |  |  |  | Unknown
89 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error
90 |  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error
91 |  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force
92 |  | Northpark | 2019-06-20 | 2019 | 14:08 | 34.2298 | -117.4048 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | San Bern. FD | OH-201371S | OH-201371S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Human Error
93 |  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force
94 |  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather
95 |  | Saugus-Santa Susana | 2019-08-06 | 2019 | 15:03 | 34.3918 | -118.6596 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | VFD & LACFD | M6-T1 | M6-T1 | Tier 3 | T3 | Y | NA | 66 | Transmission | Other | Overhead | Yes | 2019-08-06 | 12:51 | Contact From Object |  | Animal | Electric Facility | Other
96 |  | Zone | 2019-08-10 | 2019 | 13:00 | 34.3089 | -118.9413 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | VFD | OH-4734128E | OH-4734128E | Tier 3 | T3 | Y | AT&T Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
97 |  | Enchanted | 2019-08-25 | 2019 | 8:03 | 34.301 | -118.8308 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4754475E | OH-4754475E | Tier 3 | T3 | Y | NA | 16 | Distribution | Lightning Arrestor | Overhead | Yes | 2019-08-25 | 8:03 | Contact From Object |  | Animal | Electric Facility | Other
98 |  | Hughes Lake | 2019-09-02 | 2019 | 14:02 | 34.7026 | -118.342 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4782978E | OH-4782978E | Tier 2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-02 | 14:02 | Contact From Object |  | Balloons | Electric Facility | Other
99 |  | Plateau | 2019-09-11 | 2019 | 8:08 | 34.0991 | -118.6793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4424792E | OH-4424792E | Tier 3 | T3 | Y | Verizon / AT&T / Crown Castle | 16 | Distribution | Conductor | Overhead | Yes | 2019-09-11 | 8:08 | Equipment/Facility Failure | Conductor |  | Electric Facility | Human Error
100 |  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown
101 |  | Penstock | 2019-09-18 | 2019 | 2:52 | 34.3143 | -117.3793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4066969E | OH-4066969E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Human Error
102 |  | Wildomar | 2019-09-19 | 2019 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside County FD | OH-2225310E | OH-2225310E | Tier 3 | T3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other
103 |  | Elster | 2019-09-21 | 2019 | 10:53 | 36.1026 | -118.8659 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4252581E | OH-4252581E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-21 | 10:53 | Contact From Object |  | Vehicle | Electric Facility | Human Error
104 |  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown
105 |  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other
106 |  | Medusa | 2020-03-06 | 2020 | 17:05 | 34.0802 | -117.254 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1811355E | OH-1811355E | T2 | T2 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Other
107 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
108 |  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other
109 |  | VALLEY-MAYBERRY-MORENO-VISTA | 2020-05-18 | 2020 | 12:10 | 33.8587 | -117.0203 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire Perris | OH-1979539E | OH-1979539E | T3 | T3 | Y | None | 115 | Transmission | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Other
110 |  | Bonanza | 2020-06-05 | 2020 | 17:33 | 35.7635 | -118.4218 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Kern County Fire Department | OH-4451126E | OH-4451126E | T3 | T3 | Y | None | 12 | Distribution | Other | Overhead | Yes | 2020-06-05 | 17:33 | Contact From Object |  | Animal | Electric Facility | Other
111 |  | Conestoga | 2020-06-13 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Other
112 |  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other
113 |  | La Mancha | 2020-07-05 | 2020 | 3:57 | 34.1325 | -118.8532 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1848406E | OH-1848406E | T3 | T3 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-07-05 | 3:57 | Equipment/Facility Failure | Insulator |  |  | Unknown
114 |  | Capanero | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | T2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Unknown
115 |  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
116 |  | Mettler | 2020-08-10 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | OH-2093506E | OH-2093506E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Unknown
117 |  | Flying D | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County | OH-1761180E | OH-1761180E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown
118 |  | Calgrove | 2020-10-03 | 2020 | 17:45 | 34.357 | -118.5659 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | OH-2101062E | OH-2101062E | T3 | T3 |  | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
119 |  | Kickapoo Trail | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1941931E | OH-1941931E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Unknown
120 |  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
121 |  | Vicasa | 2020-11-30 | 2020 | 21:02 | 34.0723 | -118.588 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles Fire Department | OH-4535641E | OH-4535641E | T3 | T3 |  | Verizon Wireless, AT&T Mobility, Frontier Communications, Crown Castle NG West, Inc | 16 | Distribution | Other | Overhead | Yes | 2020-11-30 | 21:02 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
122 |  | Viento | 2020-06-09 | 2020 | 16:42 | 35.1384 | -118.4809 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4707894E | OH-4707894E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
123 |  | Lasker | 2020-07-26 | 2020 | 12:50 | 34.5326 | -118.0541 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4619162E | OH-4619162E | T3 | T3 |  | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
124 |  | Morongo | 2020-08-03 | 2020 | 10:33 | 34.0758 | -116.5548 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-2107480E | OH-2107480E | T2 | T2 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-08-03 | 19:15 | Contact From Object |  | Balloons | Electric Facility | Outside Force
125 |  | Bidder | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire | OH-2023941E | OH-2023941E | T3 | T3 |  | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force
126 |  | Vicasa | 2020-10-26 | 2020 | 11:56 | 34.0998 | -118.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | OH-795990E | OH-795990E | T3 | T3 |  | Frontier Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Weather
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather
10002 | CABIN |  | 2015-08-14 | 2015 | 13:07 | 34.0299 | -118.0726 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather
10003 | EDISON |  | 2016-05-12 | 2016 | -4 | 34.3135 | -119.1865 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather
10004 | ERSKINE |  | 2016-06-23 | 2016 | 16:00 | 34.2676 | -117.844 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | BLM | [13 empty] | Contact From Object |  | Vegetation
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather
10006 | RYE |  | 2017-12-05 | 2017 | 15:00 | 34.2676 | -117.844 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather
10007 | ELLIS |  | 2017-10-18 | 2017 | 11:18 | 33.7721 | -117.2173 | Vegetation | Rural | Unknown |  | Unknown | Fire Agency | Cal Fire | [17 empty] | Weather
10008 | THOMAS |  | 2017-12-04 | 2017 | 18:28 | 34.4152 | -119.0912 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | USFS | [17 empty] | Weather
10009 | RYE |  | 2017-12-05 | 2017 | 11:31 | 34.4528 | -118.5819 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather
10010 | MEYERS |  | 2017-12-05 | 2017 | 14:00 | 34.2183 | -117.4062 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Cal Fire | [17 empty] | Weather
10011 | LIBERTY |  | 2017-12-07 | 2017 | 13:00 | 33.5926 | -117.1498 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | Murrieta Fire Department | [17 empty] | Weather
10012 | HOLIDAY |  | 2018-07-06 | 2018 | 20:40 | 34.4639 | -119.8314 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Santa Barbara Fire Department | [17 empty] | Weather
10013 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather
10014 | STAR |  | 2019-07-28 | 2019 | 14:00 | 33.9975 | -117.7698 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Chino Valley Fire Department | [13 empty] | Contact From Object |  | Bird |  | Weather
10015 | TENAJA |  | 2019-09-04 | 2019 | 16:43 | 33.5285 | -117.2732 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Cal Fire | [17 empty] | Weather
10016 | SADDLE RIDGE |  | 2019-10-10 | 2019 | 21:09 | 34.3299 | -118.4816 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather
10017 | OAK |  | 2019-10-28 | 2019 | 8:42 | 34.1489 | -118.6954 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather
10018 | EASY |  | 2019-10-30 | 2019 | 6:00 | 34.2822 | -118.8034 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather
10019 | MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather
10020 | MARIA |  | 2019-10-31 | 2019 | 20:58 | 34.3022 | -118.9971 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather
Note on D1: Date the event started (Use MM/DD/YY when inputting dates)
Note on F1: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on G1: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on H1: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on I1: Material involved in the initial fueling of the fire;
Note on J1: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on K1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on L1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on M1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on N1: Is who suppressed the fire
Note on O1: If the fire was suppressed by a fire agency or agencies, insert the lead agency when one or more agency was involved
Note on P1: Utility’s description of the pole and/or equipment involved.
Note on U1: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on V1: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on X1: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on Y1: The equipment involved in the event (overhead, padmounted or subsurface);
Note on Z1: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AA1: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AB1: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AC1: The suspected cause of the ignition;
Note on AD1: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on AE1: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on AF1: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on AG1: Factors that contributed to the ignition;

## UnderInvestigation
ID | Name | Circuit | Date | Year | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Size - HFTD | Size - UI | Suppressed by | Suppressing Agency | Facility Identification | FLOC | HFRA | cGIS HFRA | HFTD | Other Companies | Voltage (Volts) | Business Line | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather
10002 | CABIN |  | 2015-08-14 | 2015 | 13:07 | 34.0299 | -118.0726 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather
10003 | EDISON |  | 2016-05-12 | 2016 | -4 | 34.3135 | -119.1865 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather
10004 | ERSKINE |  | 2016-06-23 | 2016 | 16:00 | 34.2676 | -117.844 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | BLM | [13 empty] | Contact From Object |  | Vegetation
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather
10006 | RYE |  | 2017-12-05 | 2017 | 15:00 | 34.2676 | -117.844 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather
10007 | ELLIS |  | 2017-10-18 | 2017 | 11:18 | 33.7721 | -117.2173 | Vegetation | Rural | Unknown |  | Unknown | Fire Agency | Cal Fire | [17 empty] | Weather
10008 | THOMAS |  | 2017-12-04 | 2017 | 18:28 | 34.4152 | -119.0912 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | USFS | [17 empty] | Weather
10009 | RYE |  | 2017-12-05 | 2017 | 11:31 | 34.4528 | -118.5819 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather
10010 | MEYERS |  | 2017-12-05 | 2017 | 14:00 | 34.2183 | -117.4062 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Cal Fire | [17 empty] | Weather
10011 | LIBERTY |  | 2017-12-07 | 2017 | 13:00 | 33.5926 | -117.1498 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | Murrieta Fire Department | [17 empty] | Weather
10012 | HOLIDAY |  | 2018-07-06 | 2018 | 20:40 | 34.4639 | -119.8314 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Santa Barbara Fire Department | [17 empty] | Weather
10013 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather
10014 | STAR |  | 2019-07-28 | 2019 | 14:00 | 33.9975 | -117.7698 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Chino Valley Fire Department | [13 empty] | Contact From Object |  | Bird |  | Weather
10015 | TENAJA |  | 2019-09-04 | 2019 | 16:43 | 33.5285 | -117.2732 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Cal Fire | [17 empty] | Weather
10016 | SADDLE RIDGE |  | 2019-10-10 | 2019 | 21:09 | 34.3299 | -118.4816 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather
10017 | OAK |  | 2019-10-28 | 2019 | 8:42 | 34.1489 | -118.6954 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather
10018 | EASY |  | 2019-10-30 | 2019 | 6:00 | 34.2822 | -118.8034 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather
10019 | MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather
10020 | MARIA |  | 2019-10-31 | 2019 | 20:58 | 34.3022 | -118.9971 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather
Note on D1: Date the event started (Use MM/DD/YY when inputting dates)
Note on F1: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on G1: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on H1: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on I1: Material involved in the initial fueling of the fire;
Note on J1: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on K1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on L1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on M1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on N1: Is who suppressed the fire
Note on O1: If the fire was suppressed by a fire agency or agencies, insert the lead agency when one or more agency was involved
Note on P1: Utility’s description of the pole and/or equipment involved.
Note on U1: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on V1: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on X1: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on Y1: The equipment involved in the event (overhead, padmounted or subsurface);
Note on Z1: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AA1: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AB1: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AC1: The suspected cause of the ignition;
Note on AD1: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on AE1: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on AF1: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on AG1: Factors that contributed to the ignition;

## IgnitionsWind
[33 empty] | 8m/1h stid | 8m/1h dist | 8m/1h time | 8m/1h gust mph | 8m/1h count | 8m/1h Category
1 |  | Birchim | 2015-02-06 | 2015 | 13:15 | 37.454 | -118.5842 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Various Fire Agencies | Between Poles 1854107E & 1854106E | OH-1854107E | Tier 2 | T2 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-02-06 | 13:15 | Unknown |  |  |  | Unknown | OVRC1 | 4.68 | 2015-02-06T07:54:00Z | 12.01 | 1 | < 25mph
2 |  | Sexton | 2015-02-22 | 2015 | 9:52 | 34.2849 | -119.2173 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura Fire Department | Pole 1718768E | OH-1718768E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-02-22 | 10:49 | Unknown |  |  |  | None | AT185 | 8 | 2015-02-22T08:27:00Z | 7 | 22 | < 25mph
3 |  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | AU958 | 2.06 | 2015-03-26T07:23:00Z | 4.99 | 65 | < 25mph
4 |  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown | CNSC1 | 7.75 | 2015-04-17T07:16:00Z | 14 | 21 | < 25mph
5 |  | Maguire | 2015-04-17 | 2015 | 16:41 | 34.0851 | -118.8044 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles County Fire | Maguire 16kV out of Latigo Sub | OH-1199311E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2015-04-17 | 16:41 | Contact From Object |  | Vehicle | Pole | None | CRXC1 | 7.72 | 2015-04-17T06:57:00Z | 13 | 24 | < 25mph
6 |  | Zone | 2015-04-27 | 2015 | 19:09 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | 9372 STOCKTON RD PMP MOORPARK | OH-4734128E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-04-27 | 19:09 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | WLYC1 | 7.19 | 2015-04-27T06:49:00Z | 14.99 | 52 | < 25mph
7 |  | Zone | 2015-04-27 | 2015 | 19:10 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 4734128E | OH-4734128E | Tier 3 | T3 | Y |  | 16 | Distribution | Other | Overhead | Yes | 2015-04-27 | 19:10 | Equipment/Facility Failure | Other |  |  | Unknown | WLYC1 | 7.19 | 2015-04-27T06:49:00Z | 14.99 | 52 | < 25mph
8 |  | Atlanta | 2015-05-05 | 2015 | 16:00 | 33.711 | -117.7089 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 4229158E | OH-4229158E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.92 | 2015-05-05T06:51:00Z | 14.99 | 67 | < 25mph
9 |  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.54 | 2015-05-06T06:51:00Z | 11.01 | 56 | < 25mph
10 |  | Soda Springs | 2015-05-14 | 2015 | 22:24 | 36.1318 | -118.7784 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | Soda Springs 12kV out of Boxwood Sub | OH-4464511E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-14 | 22:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown | OORC1 | 5.23 | 2015-05-14T07:12:00Z | 11.01 | 1 | < 25mph
11 |  | Lopez | 2015-05-23 | 2015 | 11:57 | 34.3006 | -118.3613 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | Pole 1261671E | OH-1261671E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Conductor | Overhead | Yes | 2015-05-23 | 11:05 | Unknown |  |  |  | Unknown | CNIC1 | 4.89 | 2015-05-23T06:55:00Z | 18.99 | 20 | < 25mph
12 |  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | LCBC1 | 6.83 | 2015-05-26T06:55:00Z | 7 | 28 | < 25mph
13 |  | Pawley | 2015-05-29 | 2015 | 7:29 | 36.387 | -118.9536 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare County Fire | Lemon Cove and Three Rivers Sub. Venida 66kV | OH-4434944E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-05-29 | 7:29 | Contact From Object |  | Animal | Electric Facility | None | D0117 | 5.17 | 2015-05-29T07:00:00Z | 2.01 | 8 | < 25mph
14 |  | Atento | 2015-05-30 | 2015 | 15:26 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | Unknown | FRCC1 | 7.87 | 2015-05-30T06:51:00Z | 10 | 36 | < 25mph
15 |  | Atento | 2015-05-30 | 2015 | 15:30 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | None | FRCC1 | 7.87 | 2015-05-30T06:51:00Z | 10 | 36 | < 25mph
16 |  | Python | 2015-06-06 | 2015 | 10:00 | 34.4043 | -118.4234 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | 16450 Alamo Canyon Rd, Canyon Country | OH-4779534E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-06-06 | 10:13 | Contact From Object |  | Animal | Electric Facility | None | NHPC1 | 7.23 | 2015-06-06T06:56:00Z | 14 | 27 | < 25mph
17 |  | Keller | 2015-06-09 | 2015 | 5:46 | 33.5986 | -117.1311 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 4401960E | OH-2297077E | Tier 2 | T2 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2015-06-09 | 5:46 | Contact From Object |  | Animal | Electric Facility | None | SRUC1 | 7.92 | 2015-06-09T06:54:00Z | 13 | 18 | < 25mph
18 |  | SPRINGVILLE-LINDSAY-VENIDA/ET-07230,SPRINGVILLE-STRATHMORE/ET-07256 | 2015-06-17 | 2015 | 17:29 | 36.1086 | -118.9425 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 722603E | OH-722604E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-06-17 | 17:29 | Contact From Object |  | Animal | Electric Facility | None | C1000 | 6.57 | 2015-06-17T07:30:00Z | 0 | 13 | < 25mph
19 |  | Zone | 2015-06-23 | 2015 | 17:21 | 34.279 | -118.9072 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura Fire Department | Primary splice box at base of pole 2115918e | OH-2115918E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Subsurface | No | <Null> |  | Equipment/Facility Failure | Other |  |  | Unknown | AT184 | 7.68 | 2015-06-23T06:31:00Z | 4.99 | 44 | < 25mph
20 |  | Taiwan | 2015-07-13 | 2015 | 11:15 | 33.7678 | -117.7207 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | Cal Fire | Pole 960439E | OH-960439E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-07-13 | 13:30 | Unknown |  |  |  | Unknown | FRCC1 | 3.07 | 2015-07-13T06:51:00Z | 7 | 55 | < 25mph
21 |  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error | AU563 | 7.19 | 2015-08-12T07:29:00Z | 18.01 | 16 | < 25mph
22 |  | BIG CREEK 3-RECTOR NO.1/ET-01046 | 2015-09-03 | 2015 | 17:00 | 36.8936 | -119.4571 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | East of Watts Valley Rd and Pittman Hill Rd, East of Clovis | OH-7020930 | Tier 2 | T2 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2015-09-03 | 16:15 | Contact From Object |  | Balloons | Electric Facility | None | FCHC1 | 1.24 | 2015-09-03T07:00:00Z | 5.99 | 1 | < 25mph
23 |  | PALOMINO | 2015-10-09 | 2015 | 14:00 | 33.5752 | -117.17 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | BEHIND ADDRESS 28151 CELIA RD / PROPERTY LINE., STR 212903S | OH-212903S | Tier 2 | T2 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | SDFRV | 4.96 | 2015-10-09T06:49:00Z | 8.99 | 25 | < 25mph
24 |  | GUITAR | 2016-01-16 | 2016 | 15:20 | 34.4096 | -118.6816 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-848266E | OH-848266E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-01-16 | 15:20 | Equipment/Facility Failure | Other |  |  | Unknown | E3126 | 7.2 | 2016-01-16T07:59:00Z | 8.99 | 9 | < 25mph
25 |  | SHEFFIELD | 2016-02-22 | 2016 | 17:04 | 34.4492 | -119.5845 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Montecito Fire Department | OH-1082380E | OH-1082380E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-02-22 | 17:04 | Equipment/Facility Failure | Conductor |  |  | Unknown | AU816 | 5.58 | 2016-02-22T07:30:00Z | 4 | 14 | < 25mph
26 |  | POPPET FLATS | 2016-02-27 | 2016 | 0:49 | 33.9134 | -116.8003 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1989045E | OH-1989045E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-02-27 | 0:49 | Contact From Object |  | Vehicle | Pole | Unknown | BAZC1 | 1.3 | 2016-02-27T08:14:00Z | 13 | 7 | < 25mph
27 |  | SANTA CLARA-TAYSHELL/ET-00423 | 2016-04-21 | 2016 | 12:20 | 34.3339 | -119.2748 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4434916E | OH-4434916E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2016-04-21 | 12:20 | Contact From Object |  | Animal | Electric Facility | Unknown | CSVC1 | 7.52 | 2016-04-21T07:09:00Z | 5.99 | 34 | < 25mph
28 |  | WELCH | 2016-04-25 | 2016 | 15:23 | 35.8387 | -118.9147 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1078325E | OH-1078325E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 15:23 | Equipment/Facility Failure | Insulator |  |  | Unknown | FTNC1 | 3.62 | 2016-04-25T07:00:00Z | 14.99 | 1 | < 25mph
29 |  | ELSTER | 2016-04-25 | 2016 | 19:15 | 36.1372 | -118.8615 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-X16345E | OH-X16345E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 120/240 V | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 19:15 | Equipment/Facility Failure | Conductor |  |  | Unknown | MOLC1 | 6.51 | 2016-04-25T07:27:00Z | 12.01 | 1 | < 25mph
30 |  | TICO | 2016-04-28 | 2016 | 14:00 | 34.357 | -119.314 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura County FD | OH-1604151E | OH-1604151E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-04-28 | 14:00 | Equipment/Facility Failure | Other |  |  | Unknown | E8097 | 7.74 | 2016-04-28T06:36:00Z | 44.98 | 26 | 40-55mph
31 |  | CONCEPCION | 2016-05-02 | 2016 | 7:03 | 34.4736 | -120.2153 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-4041841E | OH-4041841E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-02 | 7:03 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | C6499 | 0.63 | 2016-05-02T07:28:00Z | 3 | 13 | < 25mph
32 |  | CONCEPCION | 2016-05-12 | 2016 | 8:55 | 34.4736 | -120.216 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-708452E | OH-708452E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-12 | 8:55 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | C6499 | 0.67 | 2016-05-12T07:18:00Z | 4 | 12 | < 25mph
33 |  | SKINKLE | 2016-05-29 | 2016 | 22:25 | 36.0091 | -118.9563 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-4566417E | OH-4566417E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-05-29 | 22:25 | Contact From Object |  | Other | Electric Facility | Unknown | C1000 | 7.9 | 2016-05-29T07:30:00Z | 0 | 11 | < 25mph
34 |  | BRUMFIELD | 2016-06-04 | 2016 | 10:17 | 33.5947 | -117.1387 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-2206630E | OH-2206630E | Tier 2 | T2 | Y |  | 12 | Distribution | Transformer | Overhead | Yes | 2016-06-04 | 10:17 | Equipment/Facility Failure | Transformer |  |  | Unknown | E3052 | 7.64 | 2016-06-04T07:09:00Z | 8.99 | 25 | < 25mph
35 |  | PYTHON | 2016-06-05 | 2016 | 15:59 | 34.4208 | -118.4218 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4154960E | OH-4154960E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-06-05 | 15:59 | Unknown |  |  |  | Unknown | CNIC1 | 4.67 | 2016-06-05T06:55:00Z | 20 | 28 | < 25mph
36 |  | VIENTO | 2016-06-06 | 2016 | 17:44 | 35.1355 | -118.4771 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1373165E | OH-1373165E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-06 | 17:44 | Contact From Object |  | Other | Pole | Unknown | E3266 | 3.96 | 2016-06-06T06:38:00Z | 24 | 28 | < 25mph
37 |  | SHOWDOWN | 2016-06-09 | 2016 | 11:28 | 34.5862 | -118.196 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4267121E | OH-4267121E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-09 | 11:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | LPDC1 | 6.32 | 2016-06-09T06:55:00Z | 22.01 | 24 | < 25mph
38 |  | SODA SPRINGS | 2016-06-21 | 2016 | 21:47 | 36.2515 | -118.7809 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4391218E | OH-4391218E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-21 | 21:47 | Contact From Object |  | Vegetation | Electric Facility | Unknown | MOLC1 | 5.11 | 2016-06-21T07:27:00Z | 8.01 | 2 | < 25mph
39 |  | KINSEY | 2016-07-08 | 2016 | 11:15 | 34.7906 | -118.8256 | Vegetation | Rural | 300 - 999 Acres | 300 - 999 Acres |  | Fire Agency | Kern County Fire Department | 1-5, Gorman | OH-4539401E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | E5906 | 7.95 | 2016-07-08T07:27:00Z | 3 | 3 | < 25mph
40 |  | CACHUMA | 2016-08-18 | 2016 | 14:52 | 34.5356 | -119.8523 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-1413051E | OH-1413051E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-18 | 14:52 | Contact From Object |  | Vegetation | Communication Facility | Unknown | AS303 | 7.85 | 2016-08-18T06:35:00Z | 13 | 106 | < 25mph
41 |  | VALLECITO | 2016-08-18 | 2016 | 19:00 | 34.4214 | -119.5964 | Other | Rural | Structure Only | Structure Only |  | Fire Agency | Santa Barbara County Fire Department | 2400 block of Whitney Avenue in Summerland | OH-1523986E | Tier 2 | T2 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | NTBC1 | 5.13 | 2016-08-18T07:18:00Z | 5.99 | 24 | < 25mph
42 |  | MIST | 2016-08-24 | 2016 | 16:37 | 34.4665 | -120.0701 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Santa Barbara County Fire Department | Refiugio Canyon, Santa Barbara | OH-4538468E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-24 | 18:50 | Contact From Object |  | Animal | Electric Facility | Unknown | RHWC1 | 3.48 | 2016-08-24T07:06:00Z | 34.99 | 13 | 25-40mph
43 |  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | OJ | 0.4 | 2016-09-03T07:00:00Z | 2.68 | 14 | < 25mph
44 |  | PATRICIA | 2016-09-16 | 2016 | 19:02 | 34.4851 | -119.3001 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ojai City Fire Department | OH-4797071E | OH-4797071E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-09-16 | 19:02 | Contact From Object |  | Vehicle | Pole | Unknown | CSVC1 | 6.69 | 2016-09-16T07:09:00Z | 4.99 | 6 | < 25mph
45 |  | TUNA | 2016-09-19 | 2016 | 6:11 | 34.04 | -118.6687 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-1638513E | OH-1638513E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | MBCC1 | 3.63 | 2016-09-19T06:56:00Z | 13 | 17 | < 25mph
46 |  | CARVER | 2016-09-24 | 2016 | 14:20 | 35.7381 | -118.9546 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4784763E | OH-4784763E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-09-24 | 14:20 | Contact From Object |  | Animal | Electric Facility | Unknown | WOCC1 | 7.2 | 2016-09-24T07:13:00Z | 5.99 | 1 | < 25mph
47 |  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown | E1966 | 2.94 | 2016-10-02T07:15:00Z | 15.99 | 12 | < 25mph
48 |  | DRISKILL | 2016-10-18 | 2016 | 18:41 | 34.4687 | -119.7722 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Santa Barbara Fire Department | OH-2178476E | OH-2178476E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-18 | 18:41 | Equipment/Facility Failure | Fuse |  |  | Unknown | MTIC1 | 7.03 | 2016-10-18T06:47:00Z | 50 | 134 | 40-55mph
49 |  | PYTHON | 2016-10-22 | 2016 | 15:17 | 34.3812 | -118.4132 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | RAR 0038 | OH-4860064E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-22 | 15:17 | Contact From Object |  | Balloons | Electric Facility | Unknown | CNIC1 | 1.96 | 2016-10-22T06:55:00Z | 23 | 33 | < 25mph
50 |  | PATRICIA | 2016-10-23 | 2016 | 9:40 | 34.4603 | -119.2853 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | 900 Rice Road Ojai | OH-786960E | Tier 3 | T3 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | CSVC1 | 6.08 | 2016-10-23T07:09:00Z | 4 | 5 | < 25mph
51 |  | HUGHES LAKE | 2016-10-26 | 2016 | 12:19 | 34.7081 | -118.5367 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | ELIZABETH LAKE ROAD AND KINGS CANYON ROAD, LAKE HUGHES | OH-1586523E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-26 | 12:19 | Contact From Object |  | Vegetation | Electric Facility | Unknown | C4614 | 6.71 | 2016-10-26T06:40:00Z | 4.99 | 11 | < 25mph
52 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | E6898 | 7.67 | 2016-11-20T07:38:00Z | 4 | 58 | < 25mph
53 |  | PYTHON | 2016-12-02 | 2016 | 21:26 | 34.3812 | -118.4132 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | OH-4572770E | OH-4572770E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vegetation | Electric Facility | Unknown | CNIC1 | 1.96 | 2016-12-02T07:55:00Z | 30 | 31 | 25-40mph
54 |  | RHODA | 2016-12-30 | 2016 | 11:42 | 34.1231 | -118.723 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-1927507E | OH-1927507E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-12-30 | 11:42 | Contact From Object |  | Balloons | Electric Facility | Unknown | MBUC1 | 6.16 | 2016-12-30T07:56:00Z | 18.99 | 48 | < 25mph
55 |  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | MSJC1 | 4.82 | 2017-01-13T07:53:00Z | 17 | 34 | < 25mph
56 |  | OAK GLEN | 2017-03-15 | 2017 | 13:23 | 34.0534 | -116.971 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-2326555E | OH-2326555E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-15 | 13:23 | Contact From Object |  | Animal | Electric Facility | Unknown | MMKC1 | 4.7 | 2017-03-15T06:34:00Z | 12.01 | 65 | < 25mph
57 |  | HUCKLEBERRY | 2017-03-17 | 2017 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4493863E | OH-4493863E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown | E1966 | 2.92 | 2017-03-17T06:55:00Z | 12.01 | 15 | < 25mph
58 |  | PATRICIA | 2017-04-16 | 2017 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4495331E | OH-4495331E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown | CSVC1 | 7.35 | 2017-04-16T07:09:00Z | 5.99 | 9 | < 25mph
59 |  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | E1966 | 3.22 | 2017-04-23T06:52:00Z | 18.99 | 12 | < 25mph
60 |  | LEE VINING-LUNDY NO. 1/ET-01774 | 2017-05-01 | 2017 | 5:40 | 38.0209 | -119.1608 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | CAlFIre | OH-1580964E | OH-1580964E | Tier 2 | T2 | Y |  | 55 | Distribution | Conductor | Overhead | No | <Null> |  | Contamination |  |  |  | Unknown | ERYC1 | 7.12 | 2017-05-01T07:00:00Z | 6.51 | 1 | < 25mph
61 |  | GUITAR | 2017-05-11 | 2017 | 12:27 | 34.4127 | -118.6702 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-848255E | OH-848255E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-05-11 | 12:27 | Contact From Object |  | Balloons | Electric Facility | Unknown | PU | 7.98 | 2017-05-11T07:00:00Z | 9.15 | 6 | < 25mph
62 |  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | F0145 | 4.82 | 2017-05-20T07:21:00Z | 3 | 36 | < 25mph
63 |  | METTLER | 2017-06-02 | 2017 | 10:50 | 35.1021 | -118.5328 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4416566E | OH-4416566E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | E3266 | 6.22 | 2017-06-02T06:57:00Z | 14.99 | 38 | < 25mph
64 |  | ANZAR | 2017-06-04 | 2017 | 13:14 | 33.8373 | -117.4863 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-1757417E | OH-1757417E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2017-06-04 | 13:14 | Wire-Wire Contact |  |  |  | Unknown | C7445 | 5.5 | 2017-06-04T07:28:00Z | 7 | 45 | < 25mph
65 |  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown | LYQC1 | 4.98 | 2017-06-10T07:18:00Z | 23 | 1 | < 25mph
66 |  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | AT643 | 4.77 | 2017-06-14T06:59:00Z | 4.99 | 41 | < 25mph
67 |  | PICK | 2017-06-19 | 2017 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | 30278 Arrastre Canyon Rd., Acton | OH-699610E | Tier 3 | T3 | Y |  | 33 | Distribution | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown | MLCC1 | 7.72 | 2017-06-19T06:53:00Z | 7 | 1 | < 25mph
68 |  | MAYBELL | 2017-07-02 | 2017 | 8:24 | 34.0804 | -117.8552 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | OH-144184E | OH-1255315E | T2 200Ft Outer Buffer | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-07-02 | 8:24 | Contact From Object |  | Animal | Electric Facility | Unknown | D6285 | 6.41 | 2017-07-02T06:55:00Z | 5.99 | 78 | < 25mph
69 |  | DALBA | 2017-07-11 | 2017 | 18:06 | 34.2054 | -117.1143 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-919465E | OH-919465E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 2.4 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | HHPC1 | 2.47 | 2017-07-11T07:15:00Z | 15.99 | 61 | < 25mph
70 |  | CUDDEBACK | 2017-08-08 | 2017 | 17:52 | 35.1342 | -118.5607 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4179753E | OH-4179753E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-08-08 | 17:52 | Contact From Object |  | Vehicle | Electric Facility | Unknown | C8288 | 3.79 | 2017-08-08T07:18:00Z | 8.99 | 34 | < 25mph
71 |  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TNRC1 | 2.34 | 2017-08-28T06:57:00Z | 12.01 | 115 | < 25mph
72 |  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | D2363 | 4.16 | 2017-08-28T06:38:00Z | 24 | 74 | < 25mph
73 |  | CABANA | 2017-10-16 | 2017 | 6:11 | 34.0217 | -117.5069 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1670014E | OH-1670014E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-10-16 | 6:11 | Contact From Object |  | Balloons | Electric Facility | Unknown | E7239 | 2.66 | 2017-10-16T06:42:00Z | 4 | 16 | < 25mph
74 |  | DEACON | 2017-10-18 | 2017 | 13:34 | 33.7702 | -117.2157 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1564666E | OH-1564666E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SDPRR | 3.64 | 2017-10-18T06:49:00Z | 4.99 | 29 | < 25mph
75 |  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | MTIC1 | 4.81 | 2017-10-27T06:47:00Z | 4.99 | 15 | < 25mph
76 |  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UCMO | 4.71 | 2017-11-13T07:40:00Z | 7.09 | 31 | < 25mph
77 |  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown | FTNC1 | 0.32 | 2018-06-02T07:00:00Z | 4.99 | 1 | < 25mph
78 |  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown | F0490 | 5.32 | 2018-06-15T07:16:00Z | 23 | 24 | < 25mph
79 |  | BENCH | 2018-06-26 | 2018 | 20:48 | 34.0158 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Holmes St/Wildwood Canyon Rd, Yucaipa | OH-4367391E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-26 | 20:48 | Contact From Object |  | Vehicle | Pole | Unknown | BNJC1 | 6.9 | 2018-06-26T07:13:00Z | 22.01 | 47 | < 25mph
80 |  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | MBCC1 | 6.95 | 2018-06-29T06:56:00Z | 18.99 | 113 | < 25mph
81 |  | HUGHES LAKE/ED-08810 | 2018-07-06 | 2018 | 5:38 | 34.6744 | -118.4517 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | 465140E | OH-1938477E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-07-06 | 5:38 | Contact From Object |  | Vehicle | Pole | Unknown | PPPC1 | 4.96 | 2018-07-06T06:56:00Z | 32.99 | 6 | 25-40mph
82 |  | BIG CREEK 1-RECTOR/ET-01082 | 2018-08-04 | 2018 | 0:43 | 37.1895 | -119.2738 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | OH-7021454 | OH-7021454 | Tier 3 | T3 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2018-08-04 | 2:21 | Equipment/Facility Failure | Other |  |  | Unknown | SHVC1 | 3.7 | 2018-08-04T06:56:00Z | 1.01 | 1 | < 25mph
83 |  | JORDAN | 2018-08-29 | 2018 | 17:32 | 35.7358 | -118.7192 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | Jack Ranch Rd/White River Rd, Kernville | OH-4635091E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-08-29 | 19:06 | Contact From Object |  | Vegetation | Electric Facility | Unknown | WOCC1 | 6.68 | 2018-08-29T07:13:00Z | 4 | 1 | < 25mph
84 |  | POULTRY | 2018-09-21 | 2018 | 8:28 | 34.0728 | -117.0397 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Juniper St. Yucaipa | OH-129241E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SE083 | 6.59 | 2018-09-21T06:30:00Z | 7.34 | 64 | < 25mph
85 |  | OAK GLEN | 2018-11-08 | 2018 | 12:09 | 34.0397 | -116.9362 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 11833 Oak Glen Rd. Yucaipa | OH-4611601E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-08 | 12:09 | Equipment/Facility Failure | Transformer |  |  | Unknown | E5008 | 7.19 | 2018-11-08T08:30:00Z | 20 | 83 | < 25mph
86 |  | ARCHIE | 2018-11-13 | 2018 | 7:11 | 33.4928 | -117.2796 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | NORTH OF CARANCHO ON VIA CIELO | OH-4149859E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-13 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Unknown | HP012 | 6.73 | 2018-11-13T07:34:00Z | 32.21 | 48 | 25-40mph
87 |  | Peninsula | 2019-03-16 | 2019 | 17:58 | 33.6182 | -117.8025 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1729510E | OH-1729510E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-03-16 | 17:58 | Equipment/Facility Failure | Crossarm |  |  | Unknown | F0107 | 5.38 | 2019-03-16T07:10:00Z | 17 | 153 | < 25mph
88 |  | Taggert | 2019-04-23 | 2019 | 21:06 | 34.2147 | -117.0973 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1027559E | OH-1027559E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution |  | Overhead | No |  |  | Unknown |  |  |  | Unknown | HHPC1 | 2.75 | 2019-04-23T07:15:00Z | 28.01 | 67 | 25-40mph
89 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error | LPDC1 | 6.51 | 2019-06-01T06:55:00Z | 24.99 | 71 | < 25mph
90 |  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error | SE273 | 3.85 | 2019-06-06T06:50:00Z | 5.48 | 81 | < 25mph
91 |  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force | TSHC1 | 6.99 | 2019-06-06T07:04:00Z | 13 | 14 | < 25mph
92 |  | Northpark | 2019-06-20 | 2019 | 14:08 | 34.2298 | -117.4048 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | San Bern. FD | OH-201371S | OH-201371S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Human Error | E3127 | 5.2 | 2019-06-20T06:30:00Z | 14 | 102 | < 25mph
93 |  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force | SDMEA | 5.11 | 2019-06-23T06:49:00Z | 10 | 68 | < 25mph
94 |  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather | SRXC1 | 7.9 | 2019-06-25T06:56:00Z | 7 | 71 | < 25mph
95 |  | Saugus-Santa Susana | 2019-08-06 | 2019 | 15:03 | 34.3918 | -118.6596 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | VFD & LACFD | M6-T1 | M6-T1 | Tier 3 | T3 | Y | NA | 66 | Transmission | Other | Overhead | Yes | 2019-08-06 | 12:51 | Contact From Object |  | Animal | Electric Facility | Other | SE086 | 4 | 2019-08-06T07:30:00Z | 10.51 | 70 | < 25mph
96 |  | Zone | 2019-08-10 | 2019 | 13:00 | 34.3089 | -118.9413 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | VFD | OH-4734128E | OH-4734128E | Tier 3 | T3 | Y | AT&T Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | WLYC1 | 7.19 | 2019-08-10T06:49:00Z | 13 | 176 | < 25mph
97 |  | Enchanted | 2019-08-25 | 2019 | 8:03 | 34.301 | -118.8308 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4754475E | OH-4754475E | Tier 3 | T3 | Y | NA | 16 | Distribution | Lightning Arrestor | Overhead | Yes | 2019-08-25 | 8:03 | Contact From Object |  | Animal | Electric Facility | Other | SE146 | 7 | 2019-08-25T06:30:00Z | 10.96 | 140 | < 25mph
98 |  | Hughes Lake | 2019-09-02 | 2019 | 14:02 | 34.7026 | -118.342 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4782978E | OH-4782978E | Tier 2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-02 | 14:02 | Contact From Object |  | Balloons | Electric Facility | Other | PPPC1 | 3.45 | 2019-09-02T06:56:00Z | 17 | 46 | < 25mph
99 |  | Plateau | 2019-09-11 | 2019 | 8:08 | 34.0991 | -118.6793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4424792E | OH-4424792E | Tier 3 | T3 | Y | Verizon / AT&T / Crown Castle | 16 | Distribution | Conductor | Overhead | Yes | 2019-09-11 | 8:08 | Equipment/Facility Failure | Conductor |  | Electric Facility | Human Error | SE003 | 1.93 | 2019-09-11T06:50:00Z | 7.67 | 162 | < 25mph
100 |  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown | WTPC1 | 2.77 | 2019-09-12T06:57:00Z | 25.99 | 37 | 25-40mph
101 |  | Penstock | 2019-09-18 | 2019 | 2:52 | 34.3143 | -117.3793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4066969E | OH-4066969E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Human Error | SE355 | 5.09 | 2019-09-18T07:30:00Z | 18.5 | 136 | < 25mph
102 |  | Wildomar | 2019-09-19 | 2019 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside County FD | OH-2225310E | OH-2225310E | Tier 3 | T3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other | DLZSD | 4.22 | 2019-09-19T06:30:00Z | 8.99 | 61 | < 25mph
103 |  | Elster | 2019-09-21 | 2019 | 10:53 | 36.1026 | -118.8659 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4252581E | OH-4252581E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-21 | 10:53 | Contact From Object |  | Vehicle | Electric Facility | Human Error | SE279 | 2.27 | 2019-09-21T07:20:00Z | 8.99 | 35 | < 25mph
104 |  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown | UCSH | 2.26 | 2019-04-24T06:30:00Z | 14.81 | 12 | < 25mph
105 |  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | MLCC1 | 7.93 | 2020-01-03T07:53:00Z | 30 | 48 | 25-40mph
106 |  | Medusa | 2020-03-06 | 2020 | 17:05 | 34.0802 | -117.254 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1811355E | OH-1811355E | T2 | T2 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Other | SE152 | 5.81 | 2020-03-06T08:00:00Z | 14.76 | 73 | < 25mph
107 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | SE130 | 4.93 | 2020-04-22T06:50:00Z | 18.05 | 64 | < 25mph
108 |  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other | SE608 | 5.27 | 2020-05-01T07:30:00Z | 27.34 | 106 | 25-40mph
109 |  | VALLEY-MAYBERRY-MORENO-VISTA | 2020-05-18 | 2020 | 12:10 | 33.8587 | -117.0203 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire Perris | OH-1979539E | OH-1979539E | T3 | T3 | Y | None | 115 | Transmission | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Other | SE746 | 7.38 | 2020-05-18T07:00:00Z | 12.48 | 147 | < 25mph
110 |  | Bonanza | 2020-06-05 | 2020 | 17:33 | 35.7635 | -118.4218 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Kern County Fire Department | OH-4451126E | OH-4451126E | T3 | T3 | Y | None | 12 | Distribution | Other | Overhead | Yes | 2020-06-05 | 17:33 | Contact From Object |  | Animal | Electric Facility | Other | SE319 | 7.73 | 2020-06-05T07:20:00Z | 15.86 | 41 | < 25mph
111 |  | Conestoga | 2020-06-13 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Other | SNPC1 | 6.73 | 2020-06-13T07:20:00Z | 17.99 | 119 | < 25mph
112 |  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other | PPPC1 | 1.78 | 2020-06-14T06:56:00Z | 47 | 25 | 40-55mph
113 |  | La Mancha | 2020-07-05 | 2020 | 3:57 | 34.1325 | -118.8532 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1848406E | OH-1848406E | T3 | T3 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-07-05 | 3:57 | Equipment/Facility Failure | Insulator |  |  | Unknown | LCBC1 | 7.67 | 2020-07-05T06:55:00Z | 14.01 | 186 | < 25mph
114 |  | Capanero | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | T2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE290 | 4.95 | 2020-07-05T06:30:00Z | 10.59 | 35 | < 25mph
115 |  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force | LYQC1 | 1.86 | 2020-07-25T07:18:00Z | 27 | 75 | 25-40mph
116 |  | Mettler | 2020-08-10 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | OH-2093506E | OH-2093506E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Unknown | SE467 | 2.98 | 2020-08-10T06:30:00Z | 13.96 | 136 | < 25mph
117 |  | Flying D | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County | OH-1761180E | OH-1761180E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown | BKGC1 | 4.48 | 2020-09-24T06:51:00Z | 14.99 | 44 | < 25mph
118 |  | Calgrove | 2020-10-03 | 2020 | 17:45 | 34.357 | -118.5659 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | OH-2101062E | OH-2101062E | T3 | T3 |  | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | PHCC1 | 3.76 | 2020-10-03T06:48:00Z | 30 | 249 | 25-40mph
119 |  | Kickapoo Trail | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1941931E | OH-1941931E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE575 | 4.94 | 2020-11-09T08:20:00Z | 12.06 | 117 | < 25mph
120 |  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other | SE286 | 7.46 | 2020-05-26T07:10:00Z | 17.17 | 126 | < 25mph
121 |  | Vicasa | 2020-11-30 | 2020 | 21:02 | 34.0723 | -118.588 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles Fire Department | OH-4535641E | OH-4535641E | T3 | T3 |  | Verizon Wireless, AT&T Mobility, Frontier Communications, Crown Castle NG West, Inc | 16 | Distribution | Other | Overhead | Yes | 2020-11-30 | 21:02 | Contact From Object |  | Vehicle | Electric Facility | Outside Force | MBUC1 | 3.36 | 2020-11-30T07:56:00Z | 17 | 285 | < 25mph
122 |  | Viento | 2020-06-09 | 2020 | 16:42 | 35.1384 | -118.4809 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4707894E | OH-4707894E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | SE681 | 7.74 | 2020-06-09T06:30:00Z | 13.08 | 151 | < 25mph
123 |  | Lasker | 2020-07-26 | 2020 | 12:50 | 34.5326 | -118.0541 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4619162E | OH-4619162E | T3 | T3 |  | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | SE652 | 3.1 | 2020-07-26T06:30:00Z | 23.25 | 112 | < 25mph
124 |  | Morongo | 2020-08-03 | 2020 | 10:33 | 34.0758 | -116.5548 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-2107480E | OH-2107480E | T2 | T2 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-08-03 | 19:15 | Contact From Object |  | Balloons | Electric Facility | Outside Force | SE287 | 5.93 | 2020-08-03T07:20:00Z | 12.78 | 85 | < 25mph
125 |  | Bidder | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire | OH-2023941E | OH-2023941E | T3 | T3 |  | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force | SE054 | 5.44 | 2020-11-09T07:30:00Z | 19 | 243 | < 25mph
126 |  | Vicasa | 2020-10-26 | 2020 | 11:56 | 34.0998 | -118.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | OH-795990E | OH-795990E | T3 | T3 |  | Frontier Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Weather | MBUC1 | 4.01 | 2020-10-26T06:56:00Z | 16 | 305 | < 25mph
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | CBVA | 1.36 | 2015-02-06T08:20:00Z | 39.19 | 13 | 25-40mph
10002 | CABIN |  | 2015-08-14 | 2015 | 13:07 | 34.0299 | -118.0726 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | WTHC1 | 4.82 | 2015-08-14T06:57:00Z | 4 | 71 | < 25mph
10003 | EDISON |  | 2016-05-12 | 2016 | -4 | 34.3135 | -119.1865 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | E8097 | 6.25 | 2016-05-12T06:31:00Z | 10 | 89 | < 25mph
10004 | ERSKINE |  | 2016-06-23 | 2016 | 16:00 | 34.2676 | -117.844 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | BLM | [13 empty] | Contact From Object |  | Vegetation |  |  | TANC1 | 6.35 | 2016-06-23T07:01:00Z | 4.99 | 1 | < 25mph
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | ERYC1 | 5.82 | 2016-06-24T07:00:00Z | 18.9 | 9 | < 25mph
10006 | RYE |  | 2017-12-05 | 2017 | 15:00 | 34.2676 | -117.844 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | TANC1 | 6.35 | 2017-12-05T08:01:00Z | 37 | 1 | 25-40mph
10007 | ELLIS |  | 2017-10-18 | 2017 | 11:18 | 33.7721 | -117.2173 | Vegetation | Rural | Unknown |  | Unknown | Fire Agency | Cal Fire | [17 empty] | Weather | SDPRR | 3.55 | 2017-10-18T06:49:00Z | 4.99 | 29 | < 25mph
10008 | THOMAS |  | 2017-12-04 | 2017 | 18:28 | 34.4152 | -119.0912 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | USFS | [17 empty] | Weather | AT184 | 6.91 | 2017-12-04T08:14:00Z | 27 | 98 | 25-40mph
10009 | RYE |  | 2017-12-05 | 2017 | 11:31 | 34.4528 | -118.5819 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | SAUC1 | 4.1 | 2017-12-05T07:57:00Z | 32.99 | 15 | 25-40mph
10010 | MEYERS |  | 2017-12-05 | 2017 | 14:00 | 34.2183 | -117.4062 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | E3127 | 5.41 | 2017-12-05T08:01:00Z | 55.99 | 11 | 55mph+
10011 | LIBERTY |  | 2017-12-07 | 2017 | 13:00 | 33.5926 | -117.1498 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | Murrieta Fire Department | [17 empty] | Weather | SRUC1 | 6.88 | 2017-12-07T07:54:00Z | 14.99 | 27 | < 25mph
10012 | HOLIDAY |  | 2018-07-06 | 2018 | 20:40 | 34.4639 | -119.8314 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Santa Barbara Fire Department | [17 empty] | Weather | MPWC1 | 2.75 | 2018-07-06T07:06:00Z | 28.99 | 140 | 25-40mph
10013 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | CEEC1 | 3.51 | 2018-11-08T07:38:00Z | 8.99 | 86 | < 25mph
10014 | STAR |  | 2019-07-28 | 2019 | 14:00 | 33.9975 | -117.7698 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Chino Valley Fire Department | [13 empty] | Contact From Object |  | Bird |  | Weather | SE133 | 2.02 | 2019-07-28T07:30:00Z | 10.09 | 138 | < 25mph
10015 | TENAJA |  | 2019-09-04 | 2019 | 16:43 | 33.5285 | -117.2732 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | DLZSD | 5.04 | 2019-09-04T06:50:00Z | 8.99 | 62 | < 25mph
10016 | SADDLE RIDGE |  | 2019-10-10 | 2019 | 21:09 | 34.3299 | -118.4816 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | SE079 | 5.82 | 2019-10-10T06:30:00Z | 20.89 | 115 | < 25mph
10017 | OAK |  | 2019-10-28 | 2019 | 8:42 | 34.1489 | -118.6954 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | MBUC1 | 6.68 | 2019-10-28T06:56:00Z | 41 | 205 | 40-55mph
10018 | EASY |  | 2019-10-30 | 2019 | 6:00 | 34.2822 | -118.8034 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | SE277 | 5.28 | 2019-10-30T07:20:00Z | 32.95 | 156 | 25-40mph
10019 | MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | SE003 | 5.19 | 2019-10-30T06:50:00Z | 20.4 | 215 | < 25mph
10020 | MARIA |  | 2019-10-31 | 2019 | 20:58 | 34.3022 | -118.9971 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | SE277 | 7.26 | 2019-10-31T06:50:00Z | 60.42 | 169 | 55mph+