## Index
Table of Contents for Wildfire Bowtie Analysis file
| Tab # | Tab Name | Tab Description
| 1 | Index | Tab with Table of Contents
| 2 | All Ignition Data Set | CPUC Reportable Ignitions from 2015-2019 + 7 fires
| 3 | Risk Input Sheet | Pivot Tables based on tab 'All Ignition Dataset' from 2015 - 2019
| 4 | HFTD-Distribution Pivots | Pivot Tables based on tab 'All Ignition Dataset' from 2015 - 2019 for HFTD-Distribution Tranche
| 5 | LookUps | Lookup Tables used in tab 'All Ignition Dataset'
| 6 | Large Fires (PGETerritory) | CalFire wildfires that were greater than 300 acres that occurred in PG&E territory (2015 - 2019)
| 7 | EventTree | Large Fires Summary by HFTD / Red Flag Warning / Destructive
| 8 | Fire-driven Outages | Non-restorable Outages for 2015-2018
| 9 | Fire Names & ILIS | Mapping of Outage (ILIS) IDs to Fire Name

## HFTD Ignitions
Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations | [7 empty] | Used in the pivot | [7 empty] | Used in Pivot | Used for Tranche | Used in the Risk Input Sheet | Used in Pivot | Used in the Risk Input Sheet | Used in the Risk Input | Used in EO-WF-14
Utility Name | Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | Notes (Optional): | Veg Subdriver | 0_Ignition ID | 0_Year | 0_Month | 0_Day | 0_Hour | 0_Minute | 0_Outage ID | 0_HFTD Zone | 0_HFTD | 0_RFW Applicable | 0_Transmission/Distribution | 0_Tranche | 0_Fire Greater than 300 Acres | 0_Driver | 0_Subdriver | 0_Customer Minutes Interrupted | 1_wg_mph | 1_we_sn | 1_Wind Categorization | 1_Wind Category | 1_Tranche | 4m/1h stid | 4m/1h time | 4m/1h dist | 4m/1h gust mph | 4m/1h count | 8m/1h stid | 8m/1h time | 8m/1h dist | 8m/1h gust mph | 8m/1h count | 4m/2h stid | 4m/2h time | 4m/2h dist | 4m/2h gust mph | 4m/2h count | 8m/2h stid | 8m/2h time | 8m/2h dist | 8m/2h gust mph | 8m/2h count
PG&E | 42020.2965 | 42020.2965 | 38.7753 | -122.7004 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 102167494 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0257 | 2015 | 1 | 16 | 7 | 7 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 15.1992 | 126_282 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42030.1604 | 42030.1604 | 37.0539 | -122.1587 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42030.1604 | 42030.1604 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0258 | 2015 | 1 | 26 | 3 | 51 | 15-0007000 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7602 | 4.1659 | 149_187 | <25mph | <15mph | HFTD - Distribution
PG&E | 42041.2507 | 42041.2507 | 38.6059 | -121.0221 | Vegetation | Rural | < 3 meters | Fire Agency |  | 6661 Ryan Ranch Road, El Dorado Hills |  | 21000 | Conductor | Overhead | Yes | 42041.2507 | 42041.2507 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0259 | 2015 | 2 | 6 | 6 | 1 | 15-0009876 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 51996 | 1.788 | 199_272 | <25mph | <15mph | HFTD - Distribution
PG&E | 42042.7764 | 42042.7764 | 40.4674 | -123.6545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | mile marker 36.61, hwy 36, bridgeville |  | 12000 | Conductor | Overhead | Yes | 42042.7764 | 42042.7764 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0262 | 2015 | 2 | 7 | 18 | 38 | 15-0011390 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 7691 | 13.8601 | 88_377 | <25mph | <15mph | HFTD - Distribution
PG&E | 42058.0868 | 42058.0868 | 39.3027 | -121.0175 | Vegetation | Rural | < 3 meters | Fire Agency | NEVADA CITY FIRE | 100086316 |  | 12000 | Conductor | Overhead | Yes | 42058.0868 | 42058.0868 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0267 | 2015 | 2 | 23 | 2 | 5 | 15-0014910 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 93279 | 10.0636 | 199_311 | <25mph | <15mph | HFTD - Distribution
PG&E | 42058.559 | 42058.559 | 38.5046 | -122.7408 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RINCON VALLEY | BEHIND 4870 CARRIAGE LN SANTA ROSA |  | 12000 | Conductor | Overhead | Yes | 42058.559 | 42058.559 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0268 | 2015 | 2 | 23 | 13 | 25 | 15-0015168 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 85762 | 12.3213 | 124_267 | <25mph | <15mph | HFTD - Distribution
PG&E | 42067.7806 | 42067.7806 | 38.9995 | -122.7545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kelseyville FD | 102156367 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42067.7806 | 42067.7806 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0271 | 2015 | 3 | 4 | 18 | 44 | 15-0017374 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29532 | 8.0458 | 124_295 | <25mph | <15mph | HFTD - Distribution
PG&E | 42070.566 | 42070.566 | 38.7091 | -122.6484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 14417 western mine rd, Middletown |  | 12000 | Conductor | Overhead | Yes | 42070.566 | 42070.566 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0272 | 2015 | 3 | 7 | 13 | 35 | 15-0018003 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2263 | 12.3057 | 128_279 | <25mph | <15mph | HFTD - Distribution
PG&E | 42072.4 | 42072.4 | 38.7328 | -120.7524 | Building | Urban | Structure Only | Unknown |  | 101399208 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42072.4 | 42072.4 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0273 | 2015 | 3 | 9 | 9 | 36 | 15-0018212 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 35991 | 13.2535 | 210_279 | <25mph | <15mph | HFTD - Distribution
PG&E | 42077.1042 | 42077.1042 | 38.9038 | -122.7579 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 9210 Wildcat Road, Kelseyville |  | 12000 | Conductor | Overhead | Yes | 42077.1042 | 42077.1042 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0274 | 2015 | 3 | 14 | 2 | 30 | 15-0019556 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2280 | 6.6558 | 124_289 | <25mph | <15mph | HFTD - Distribution
PG&E | 42078.9493 | 42078.9493 | 38.3346 | -120.5325 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 103106530 |  | 12000 | Conductor | Overhead | Yes | 42078.9493 | 42078.9493 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0279 | 2015 | 3 | 15 | 22 | 47 | 15-0019709 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 14520 | 18.0364 | 220_257 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42084.4486 | 42084.4486 | 40.1645 | -122.2894 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101546309 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42084.4486 | 42084.4486 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0281 | 2015 | 3 | 21 | 10 | 46 | 15-0021120 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 10355 | 6.9716 | 145_359 | <25mph | <15mph | HFTD - Distribution
PG&E | 42096.4056 | 42096.4056 | 39.6772 | -121.492 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100338726 |  | 12000 | Conductor | Overhead | Yes | 42096.4056 | 42096.4056 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0284 | 2015 | 4 | 2 | 9 | 44 | 15-0023747 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 100204 | 13.8343 | 178_332 | <25mph | <15mph | HFTD - Distribution
PG&E | 42098.7007 | 42098.7007 | 38.8824 | -122.5914 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 20748 Jerusalem Grade Road, Middletown |  | 12000 | Other | Overhead | Yes | 42098.7007 | 42098.7007 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0285 | 2015 | 4 | 4 | 16 | 49 | 15-0024208 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 20448 | 15.6149 | 131_288 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42105.7194 | 42105.7194 | 40.5462 | -122.2343 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101491414 |  | 12000 | Conductor | Overhead | Yes | 42105.7194 | 42105.7194 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0286 | 2015 | 4 | 11 | 17 | 16 | 15-0026023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 11914 | 1.6378 | 148_380 | <25mph | <15mph | HFTD - Distribution
PG&E | 42112.1299 | 42112.1299 | 38.6858 | -121.0084 | Vegetation | Urban | < 3 meters | Fire Agency | carmeron park F.D. | around t-7464 |  | 21000 | Conductor | Overhead | Yes | 42112.1299 | 42112.1299 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0293 | 2015 | 4 | 18 | 3 | 7 | 15-0027556 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 49438 | 4.8579 | 199_277 | <25mph | <15mph | HFTD - Distribution
PG&E | 42121.5375 | 42121.5375 | 35.4871 | -120.6756 | Vegetation | Rural | < 3 meters | Unknown |  | 103310601 |  | 21000 | Conductor | Overhead | Yes | 42121.5375 | 42121.5375 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0301 | 2015 | 4 | 27 | 12 | 54 | 15-0029875 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 5836 | 3.3323 | 214_100 | <25mph | <15mph | HFTD - Distribution
PG&E | 42124.0181 | 42124.0181 | 37.2401 | -122.2472 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 1145 VERDE R |  | 12000 | Conductor | Overhead | Yes | 42124.0181 | 42124.0181 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0304 | 2015 | 4 | 30 | 0 | 26 | 15-0030607 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1256 | 10.5301 | 145_197 | <25mph | <15mph | HFTD - Distribution
PG&E | 42126.7021 | 42126.7021 | 37.3284 | -119.643 | Vegetation | Rural | < 0.25 Acres | Fire Agency | MADERA COUNTY | 103768995 |  | 12000 | Conductor | Overhead | Yes | 42126.7021 | 42126.7021 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0305 | 2015 | 5 | 2 | 16 | 51 | 15-0031285 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 79805 | 7.1357 | 259_202 | <25mph | <15mph | HFTD - Distribution
PG&E | 42130.7201 | 42130.7201 | 37.4273 | -119.8803 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | BOOSTER 8179 INDIAN PEEK N/O MIWUK | None | 21000 | Other | Overhead | Yes | 42130.7201 | 42130.7201 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0307 | 2015 | 5 | 6 | 17 | 17 | 15-0032311 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 81600 | 10.2211 | 249_208 | <25mph | <15mph | HFTD - Distribution
PG&E | 42133.5486 | 42133.5486 | 39.2343 | -121.2468 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100000103 | None | 21000 | Conductor | Overhead | Yes | 42133.5486 | 42133.5486 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0311 | 2015 | 5 | 9 | 13 | 10 | 15-0033085 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 382926 | 8.0659 | 189_307 | <25mph | <15mph | HFTD - Distribution
PG&E | 42133.9007 | 42133.9007 | 39.2848 | -121.0219 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100004095 | Pacific Bell | 12000 | Fuse | Overhead | Yes | 42133.9007 | 42133.9007 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0312 | 2015 | 5 | 9 | 21 | 37 | 15-0033109 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 11 | 15.0569 | 198_310 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42145.391 | 42145.391 | 38.5996 | -122.9935 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 4 SPANS LOAD SIDE 2993 |  | 12000 | Conductor | Overhead | Yes | 42145.391 | 42145.391 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0324 | 2015 | 5 | 21 | 9 | 23 | 15-0035686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2850 | 6.2166 | 114_273 | <25mph | <15mph | HFTD - Distribution
PG&E | 42151.9056 | 42151.9056 | 39.169 | -120.9612 | Vegetation | Rural | < 0.25 Acres | Fire Agency | PEARDALE F.D. | 100077687 |  | 12000 | Conductor | Overhead | Yes | 42151.9056 | 42151.9056 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0329 | 2015 | 5 | 27 | 21 | 44 | 15-0036850 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10828 | 11.7191 | 201_303 | <25mph | <15mph | HFTD - Distribution
PG&E | 42154.5361 | 42154.5361 | 38.7371 | -120.8122 | Vegetation | Urban | < 3 meters | Fire Agency | el dorado co fire district | across from 2669 hwy 49 |  | 12000 | Fuse | Overhead | Yes | 42154.5361 | 42154.5361 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0334 | 2015 | 5 | 30 | 12 | 52 | 15-0037405 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 115 | 10.597 | 208_280 | <25mph | <15mph | HFTD - Distribution
PG&E | 42158.3979 | 42158.3979 | 39.6896 | -121.6216 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42158.3979 | 42158.3979 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0341 | 2015 | 6 | 3 | 9 | 33 | 15-0038091 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 28146 | 10.298 | 173_332 | <25mph | <15mph | HFTD - Distribution
PG&E | 42159.5535 | 42159.5535 | 39.2694 | -123.7841 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42159.5535 | 42159.5535 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0344 | 2015 | 6 | 4 | 13 | 17 | 15-0038501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20525 | 19.0954 | 81_311 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42159.8333 | 42159.8333 | 38.6916 | -120.8606 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101412760 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42159.8333 | 42159.8333 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0347 | 2015 | 6 | 4 | 20 | 0 | 15-0038597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 9640 | 10.3503 | 205_277 | <25mph | <15mph | HFTD - Distribution
PG&E | 42160.059 | 42160.059 | 38.3461 | -122.3998 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | 4870 REDWOOD |  | 21000 | Conductor | Overhead | Yes | 42160.059 | 42160.059 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0348 | 2015 | 6 | 5 | 1 | 25 | 15-0038607 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 53842 | 15.9469 | 139_258 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42160.6111 | 42160.6111 | 37.9578 | -120.4519 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101012484 |  | 17000 | Conductor | Overhead | Yes | 42160.6111 | 42160.6111 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0350 | 2015 | 6 | 5 | 14 | 40 | 15-0038686 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 14319 | 7.0168 | 223_237 | <25mph | <15mph | HFTD - Distribution
PG&E | 42161.6514 | 42161.6514 | 39.0409 | -123.4019 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 11480 ANDERSON VALLEY WAY @ BRIDGE |  | 12000 | Conductor | Overhead | Yes | 42161.6514 | 42161.6514 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0355 | 2015 | 6 | 6 | 15 | 38 | 15-0039056 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 1748 | 3.7796 | 97_298 | <25mph | <15mph | HFTD - Distribution
PG&E | 42163.5958 | 42163.5958 | 38.1796 | -120.959 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 102048579 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42163.5958 | 42163.5958 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0360 | 2015 | 6 | 8 | 14 | 18 | 15-0039368 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 65168 | 4.5038 | 201_249 | <25mph | <15mph | HFTD - Distribution
PG&E | 42163.6771 | 42163.6771 | 39.8236 | -123.6093 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 2 spans loadside 1741 |  | 12000 | Conductor | Overhead | Yes | 42163.6771 | 42163.6771 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0362 | 2015 | 6 | 8 | 16 | 15 | 15-0039481 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1740 | 1.0148 | 132_246 | <25mph | <15mph | HFTD - Distribution
PG&E | 42164.6417 | 42164.6417 | 38.3651 | -122.2541 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | load side 2987 | Yes | 21000 | Conductor | Overhead | Yes | 42164.6417 | 42164.6417 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0368 | 2015 | 6 | 9 | 15 | 24 | 15-0039825 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 651298 | 7.1362 | 145_259 | <25mph | <15mph | HFTD - Distribution
PG&E | 42164.6806 | 42164.6806 | 38.3822 | -122.4316 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102269716 | Pacific Bell | 21000 | Unknown | Overhead | Yes | 42164.6806 | 42164.6806 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0369 | 2015 | 6 | 9 | 16 | 20 | 15-0039860 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 4184 | 4.5208 | 138_260 | <25mph | <15mph | HFTD - Distribution
PG&E | 42167.5465 | 42167.5465 | 40.4077 | -122.4104 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS STREET FROM 4139 OLD HAPPY VALLEY RD |  | 12000 | Lightning Arrestor | Overhead | No |  |  | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | no-match | 0378 | 2015 | 6 | 12 | 13 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Lightning Arrestor | N.A. | 9.5962 | 140_372 | <25mph | <15mph | HFTD - Distribution
PG&E | 42167.9806 | 42167.9806 | 39.2308 | -121.1559 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 10903 PROSPECTOR RD ROUGH AND READY | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42167.9806 | 42167.9806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0380 | 2015 | 6 | 12 | 23 | 32 | 15-0040789 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 20 | 13.2853 | 193_307 | <25mph | <15mph | HFTD - Distribution
PG&E | 42170.6493 | 42170.6493 | 37.1852 | -121.7595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Jose city | 100618215 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42170.6493 | 42170.6493 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0384 | 2015 | 6 | 15 | 15 | 35 | 15-0041178 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 345 | 7.5345 | 166_194 | <25mph | <15mph | HFTD - Distribution
PG&E | 42176.5632 | 42176.5632 | 37.375 | -119.6116 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103204866 |  | 0 – 750 | Conductor | Overhead | No |  |  | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0399 | 2015 | 6 | 21 | 13 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 9.3936 | 260_205 | <25mph | <15mph | HFTD - Distribution
PG&E | 42177.4986 | 42177.4986 | 39.1737 | -121.0667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | SENTINAL WY |  | 12000 | Conductor | Overhead | Yes | 42177.4986 | 42177.4986 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0400 | 2015 | 6 | 22 | 11 | 58 | 15-0042502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 148438 | 8.3404 | 197_304 | <25mph | <15mph | HFTD - Distribution
PG&E | 42179.7951 | 42179.7951 | 39.9921 | -123.9258 | Vegetation | Rural | < 3 meters | Customer |  | 4 spans load side 8207 |  | 12000 | Conductor | Overhead | Yes | 42179.7951 | 42179.7951 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0406 | 2015 | 6 | 24 | 19 | 5 | 15-0043176 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1080 | 15.1757 | 76_351 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42182.5333 | 42182.5333 | 37.9474 | -120.4274 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101034512 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.5333 | 42182.5333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0414 | 2015 | 6 | 27 | 12 | 48 | 15-0043755 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 150075 | 6.5103 | 224_236 | <25mph | <15mph | HFTD - Distribution
PG&E | 42182.7854 | 42182.7854 | 37.9911 | -120.438 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | MORMON CREEK 100' FROM S/OF HWY 49 |  | 17000 | Conductor | Overhead | Yes | 42182.7854 | 42182.7854 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0415 | 2015 | 6 | 27 | 18 | 51 | 15-0043784 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 5249 | 10.5236 | 224_239 | <25mph | <15mph | HFTD - Distribution
PG&E | 42182.8854 | 42182.8854 | 39.2699 | -121.0403 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 16151 INDAIN FLAT RD |  | 12000 | Conductor | Overhead | Yes | 42182.8854 | 42182.8854 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0416 | 2015 | 6 | 27 | 21 | 15 | 15-0043789 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4210 | 10.7773 | 198_309 | <25mph | <15mph | HFTD - Distribution
PG&E | 42182.9361 | 42182.9361 | 38.1194 | -120.6218 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 101281699 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.9361 | 42182.9361 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0417 | 2015 | 6 | 27 | 22 | 28 | 15-0043798 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 517 | 11.6492 | 216_246 | <25mph | <15mph | HFTD - Distribution
PG&E | 42183.1181 | 42183.1181 | 35.491 | -120.731 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 13505 Santa Lucia Rd. Atascadero |  | 12000 | Conductor | Overhead | Yes | 42183.1181 | 42183.1181 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0418 | 2015 | 6 | 28 | 2 | 50 | 15-0043807 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 12323 | 9.8825 | 108_293 | <25mph | <15mph | HFTD - Distribution
PG&E | 42183.8799 | 42183.8799 | 39.7405 | -121.4974 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | DEADWOOD RD, JARBO GAP |  | 12000 | Conductor | Overhead | Yes | 42183.8799 | 42183.8799 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0424 | 2015 | 6 | 28 | 21 | 7 | 15-0043869 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 45683 | 8.9868 | 178_335 | <25mph | <15mph | HFTD - Distribution
PG&E | 42185.7625 | 42185.7625 | 36.2199 | -121.7534 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | loadside of 88973 | unknown | 12000 | Conductor | Overhead | Yes | 42185.7625 | 42185.7625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0432 | 2015 | 6 | 30 | 18 | 18 | 15-0044405 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 158 | 4.041 | 166_141 | <25mph | <15mph | HFTD - Distribution
PG&E | 42186.3868 | 42186.3868 | 38.5715 | -122.5443 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42186.3868 | 42186.3868 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0433 | 2015 | 7 | 1 | 9 | 17 | 15-0044529 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 85168 | 1.0096 | 133_271 | <25mph | <15mph | HFTD - Distribution
PG&E | 42186.5396 | 42186.5396 | 39.4146 | -121.379 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42186.5396 | 42186.5396 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0434 | 2015 | 7 | 1 | 12 | 57 | 15-0044609 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 11.1661 | 183_317 | <25mph | <15mph | HFTD - Distribution
PG&E | 42188.141 | 42188.141 | 35.6785 | -120.9567 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 1 soan 1 conducter 1 span loade side transformer formtr 1008493290 |  | 21000 | Conductor | Overhead | Yes | 42188.141 | 42188.141 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0438 | 2015 | 7 | 3 | 3 | 23 | 15-0045239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 978 | 8.0641 | 202_111 | <25mph | <15mph | HFTD - Distribution
PG&E | 42189.0514 | 42189.0514 | 38.9566 | -121.0434 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100037226 |  | 12000 | Other | Overhead | Yes | 42189.0514 | 42189.0514 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0441 | 2015 | 7 | 4 | 1 | 14 | 15-0045440 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 53865 | 8.7379 | 198_292 | <25mph | <15mph | HFTD - Distribution
PG&E | 42190.4042 | 42190.4042 | 35.5323 | -120.7371 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 0 – 750 | Conductor | Overhead | No |  |  | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0444 | 2015 | 7 | 5 | 9 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 11.411 | 211_103 | <25mph | <15mph | HFTD - Distribution
PG&E | 42190.8896 | 42190.8896 | 38.6524 | -120.6278 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | one span east of c/o 1055 |  | 21000 | Conductor | Overhead | Yes | 42190.8896 | 42190.8896 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0445 | 2015 | 7 | 5 | 21 | 21 | 15-0045605 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 22374 | 12.1034 | 215_275 | <25mph | <15mph | HFTD - Distribution
PG&E | 42192.4458 | 42192.4458 | 39.1138 | -121.0655 | Vegetation | Rural | < 0.25 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42192.4458 | 42192.4458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0448 | 2015 | 7 | 7 | 10 | 42 | 15-0045985 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 46738 | 7.2813 | 197_300 | <25mph | <15mph | HFTD - Distribution
PG&E | 42192.6438 | 42192.6438 | 35.155 | -120.5442 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 303corraltos cyn rd | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42192.6438 | 42192.6438 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0449 | 2015 | 7 | 7 | 15 | 27 | 15-0046127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 98566 | 7.6944 | 220_82 | <25mph | <15mph | HFTD - Distribution
PG&E | 42193.4743 | 42193.4743 | 39.224 | -121.0635 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 100094468 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42193.4743 | 42193.4743 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0451 | 2015 | 7 | 8 | 11 | 23 | 15-0046274 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 22064 | 1.9773 | 197_306 | <25mph | <15mph | HFTD - Distribution
PG&E | 42197.7111 | 42197.7111 | 37.4713 | -122.4256 | Vegetation | Rural | < 0.25 Acres | Fire Agency | COUNTY FIRE | 1 s w c509 |  | 12000 | Conductor | Overhead | Yes | 42197.7111 | 42197.7111 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown | Jumper | Other/Unknown | 0456 | 2015 | 7 | 12 | 17 | 4 | 15-0047023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 117853 | 8.7739 | 137_210 | <25mph | <15mph | HFTD - Distribution
PG&E | 42200.375 | 42200.375 | 36.997 | -121.7381 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101795728 |  | 21000 | Conductor | Overhead | Yes | 42200.375 | 42200.375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0463 | 2015 | 7 | 15 | 9 | 0 | 15-0047650 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3800 | 7.3003 | 167_184 | <25mph | <15mph | HFTD - Distribution
PG&E | 42201.7993 | 42201.7993 | 37.1989 | -119.7712 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 20334 ROAD 400 |  | 12000 | Conductor | Overhead | Yes | 42201.7993 | 42201.7993 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0465 | 2015 | 7 | 16 | 19 | 11 | 15-0048064 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 11.2562 | 207_226 | <25mph | <15mph | HFTD - Distribution
PG&E | 42203.7083 | 42203.7083 | 38.8383 | -123.6297 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | off HWY 1 PA |  | 12000 | Conductor | Overhead | Yes | 42203.7083 | 42203.7083 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0470 | 2015 | 7 | 18 | 17 | 0 | 15-0048394 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 51806 | 20.752 | 86_287 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42207.5979 | 42207.5979 | 38.7935 | -120.714 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | s\ 3204 stope dr |  | 12000 | Conductor | Overhead | Yes | 42207.5979 | 42207.5979 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0478 | 2015 | 7 | 22 | 14 | 21 | 15-0049908 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 149206 | 3.7513 | 212_283 | <25mph | <15mph | HFTD - Distribution
PG&E | 42209.6042 | 42209.6042 | 36.6913 | -119.0312 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46970 DUNLAP RD | YES | 0 – 750 | Transformer | Overhead | Yes | 42209.6042 | 42209.6042 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0482 | 2015 | 7 | 24 | 14 | 30 | 15-0050401 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 281 | 2.316 | 287_168 | <25mph | <15mph | HFTD - Distribution
PG&E | 42211.5174 | 42211.5174 | 39.1586 | -121.0634 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 15499 ALLISON RANCH RD |  | 12000 | Conductor | Overhead | Yes | 42211.5174 | 42211.5174 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0485 | 2015 | 7 | 26 | 12 | 25 | 15-0050558 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2224 | 8.9153 | 197_303 | <25mph | <15mph | HFTD - Distribution
PG&E | 42215.7472 | 42215.7472 | 37.9021 | -120.4739 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101019808 |  | 17000 | Conductor | Overhead | Yes | 42215.7472 | 42215.7472 | Contact From Object | N.A. | Other | Electric Facility | Unknown | osprey nest | Other/Unknown | 0499 | 2015 | 7 | 30 | 17 | 56 | 15-0051764 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 615 | 7.9687 | 222_234 | <25mph | <15mph | HFTD - Distribution
PG&E | 42215.7993 | 42215.7993 | 37.8102 | -120.1287 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE |  |  | 17000 | Conductor | Overhead | Yes | 42215.7993 | 42215.7993 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0500 | 2015 | 7 | 30 | 19 | 11 | 15-0051772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26776 | 8.9312 | 237_229 | <25mph | <15mph | HFTD - Distribution
PG&E | 42216.9479 | 42216.9479 | 38.3805 | -120.5628 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS FROM 1958 QUAIL LN WEST POINT | None | 12000 | Conductor | Overhead | Yes | 42216.9479 | 42216.9479 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0503 | 2015 | 7 | 31 | 22 | 45 | 15-0052033 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 33559 | 14.2556 | 218_260 | <25mph | <15mph | HFTD - Distribution
PG&E | 42217.6042 | 42217.6042 | 34.9524 | -120.2952 | Vegetation | Rural | 10 - 99 Acres | Unknown |  | 101868639 |  | 12000 | Conductor | Overhead | Yes | 42217.6042 | 42217.6042 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0505 | 2015 | 8 | 1 | 14 | 30 | 15-0052506 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 1528 | 8.881 | 232_71 | <25mph | <15mph | HFTD - Distribution
PG&E | 42218.6833 | 42218.6833 | 37.6317 | -120.1547 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101076992 |  | 21000 | Conductor | Overhead | Yes | 42218.6833 | 42218.6833 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0508 | 2015 | 8 | 2 | 16 | 24 | 15-0064792 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 3.9691 | 236_219 | <25mph | <15mph | HFTD - Distribution
PG&E | 42219.0049 | 42219.0049 | 40.5056 | -122.347 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | COTTONWOOD FIRE DEPT | 101503428 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42219.0049 | 42219.0049 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0509 | 2015 | 8 | 3 | 0 | 7 | 15-0052184 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 10427 | 13.2206 | 143_378 | <25mph | <15mph | HFTD - Distribution
PG&E | 42219.7451 | 42219.7451 | 39.3361 | -121.1894 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Pole 000/008 |  | 60000 | Conductor | Overhead | Yes | 42219.7451 | 42219.7451 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0510 | 2015 | 8 | 3 | 17 | 53 | TM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 7.5021 | 191_313 | <25mph | <15mph | HFTD - Transmission
PG&E | 42220.6701 | 42220.6701 | 40.0822 | -121.1538 | Vegetation | Rural | < 0.25 Acres | Fire Agency | USFS | 100441220 | None | 0 – 750 | Fuse | Overhead | Yes | 42220.6701 | 42220.6701 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0511 | 2015 | 8 | 4 | 16 | 5 | 15-0052743 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 4591 | 1.7808 | 193_354 | <25mph | <15mph | HFTD - Distribution
PG&E | 42220.7479 | 42220.7479 | 37.5879 | -120.229 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Str. 007/019 |  | 70000 | Conductor | Overhead | Yes | 42220.7479 | 42220.7479 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0512 | 2015 | 8 | 4 | 17 | 57 | LB-2015-028 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 8.863 | 233_216 | <25mph | <15mph | HFTD - Transmission
PG&E | 42223.2722 | 42223.2722 | 37.84 | -122.1823 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100498058 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42223.2722 | 42223.2722 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0517 | 2015 | 8 | 7 | 6 | 32 | 15-0053493 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 13.1042 | 151_212 | <25mph | <15mph | HFTD - Distribution
PG&E | 42224.3208 | 42224.3208 | 39.2007 | -121.2137 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100076217 | Pacific Bell | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0519 | 2015 | 8 | 8 | 7 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 7.7252 | 190_305 | <25mph | <15mph | HFTD - Distribution
PG&E | 42228.7347 | 42228.7347 | 40.2153 | -123.8681 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 1 SP LD SD METER 1007960761 |  | 12000 | Conductor | Overhead | Yes | 42228.7347 | 42228.7347 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0525 | 2015 | 8 | 12 | 17 | 38 | 15-0054643 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 14640 | 0.6842 | 79_363 | <25mph | <15mph | HFTD - Distribution
PG&E | 42229.1569 | 42229.1569 | 37.2072 | -119.7343 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 44365 SAVAGE RD COARSEGOLD |  | 21000 | Conductor | Overhead | Yes | 42229.1569 | 42229.1569 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0526 | 2015 | 8 | 13 | 3 | 46 | 15-0054655 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 7600 | 15.6363 | 163_282 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42230.6312 | 42230.6312 | 40.9829 | -121.7802 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101514540 |  | 21000 | Conductor | Overhead | Yes | 42230.6312 | 42230.6312 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0530 | 2015 | 8 | 14 | 15 | 9 | 15-0055136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3072 | 10.0331 | 167_404 | <25mph | <15mph | HFTD - Distribution
PG&E | 42230.7389 | 42230.7389 | 37.8894 | -120.4933 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | ENTRANCE TO 14650 HWY 108, JAMESTOWN |  | 17000 | Conductor | Overhead | Yes | 42230.7389 | 42230.7389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0531 | 2015 | 8 | 14 | 17 | 44 | 15-0055160 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 1726 | 9.2286 | 222_233 | <25mph | <15mph | HFTD - Distribution
PG&E | 42231.5701 | 42231.5701 | 37.9607 | -122.5709 | Vegetation | Urban | < 0.25 Acres | Fire Agency | COUNTY FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42231.5701 | 42231.5701 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0533 | 2015 | 8 | 15 | 13 | 41 | 15-0055217 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 5973 | 6.9969 | 131_237 | <25mph | <15mph | HFTD - Distribution
PG&E | 42232.316 | 42232.316 | 35.4572 | -120.6567 | Vegetation | Rural | < 3 meters | Utility: PG&E |  | 8932 SAN GABRIEL RD. SW C/O OF LOT, Atascadero | None | 0 – 750 | Conductor | Overhead | Yes | 42232.316 | 42232.316 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0534 | 2015 | 8 | 16 | 7 | 35 | 15-0055284 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 7.6585 | 215_99 | <25mph | <15mph | HFTD - Distribution
PG&E | 42233.359 | 42233.359 | 37.0757 | -122.023 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101800237 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0537 | 2015 | 8 | 17 | 8 | 37 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 5.0262 | 154_188 | <25mph | <15mph | HFTD - Distribution
PG&E | 42233.7312 | 42233.7312 | 38.8337 | -123.5533 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 14 spans load side 2345 |  | 12000 | Conductor | Overhead | Yes | 42233.7312 | 42233.7312 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0539 | 2015 | 8 | 17 | 17 | 33 | 15-0055664 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 676 | 5.4473 | 90_286 | <25mph | <15mph | HFTD - Distribution
PG&E | 42233.8729 | 42233.8729 | 36.6867 | -119.0612 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46371 ORCHARD DRIVE |  | 12000 | Conductor | Overhead | Yes | 42233.8729 | 42233.8729 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0540 | 2015 | 8 | 17 | 20 | 57 | 15-0055696 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 34398 | 10.2483 | 285_168 | <25mph | <15mph | HFTD - Distribution
PG&E | 42235.2639 | 42235.2639 | 39.2831 | -123.2931 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | MTR#50001225 | None | 12000 | Conductor | Overhead | Yes | 42235.2639 | 42235.2639 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0545 | 2015 | 8 | 19 | 6 | 20 | 15-0055982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5403 | 6.0572 | 102_311 | <25mph | <15mph | HFTD - Distribution
PG&E | 42238.8597 | 42238.8597 | 38.7748 | -120.8564 | Vegetation | Rural | < 3 meters | Self Extinguished |  | at base of co pole 21721 - 720 Woodridge Rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42238.8597 | 42238.8597 | Contact From Object | N.A. | Vegetation | Communication Facility | Unknown | tree hit phone lines | Fell into (Moderate-Severe defect) | 0549 | 2015 | 8 | 22 | 20 | 38 | 15-0056766 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26513 | 9.4458 | 206_282 | <25mph | <15mph | HFTD - Distribution
PG&E | 42240.95 | 42240.95 | 37.896 | -122.6011 | Vegetation | Rural | < 3 meters | Fire Agency | marin county fire | 200' east of pan toll rd 50' north of panoramic hwy |  | 12000 | Unknown | Overhead | Yes | 42240.95 | 42240.95 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0552 | 2015 | 8 | 24 | 22 | 48 | 15-0057082 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 1128 | 13.1626 | 130_234 | <25mph | <15mph | HFTD - Distribution
PG&E | 42242.5028 | 42242.5028 | 37.9638 | -122.5243 | Vegetation | Urban | < 0.25 Acres | Fire Agency | srfd | 102242504 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42242.5028 | 42242.5028 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0555 | 2015 | 8 | 26 | 12 | 4 | 15-0057475 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 28873 | 2.3344 | 133_237 | <25mph | <15mph | HFTD - Distribution
PG&E | 42242.9924 | 42242.9924 | 36.3897 | -121.3653 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101756678 | None | 21000 | Conductor | Overhead | Yes | 42242.9924 | 42242.9924 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0557 | 2015 | 8 | 26 | 23 | 49 | 15-0057613 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 8445 | 26.8734 | 183_150 | 25-40mph | >=15mph | HFTD - Distribution
PG&E | 42243.1458 | 42243.1458 | 37.8448 | -122.1992 | Vegetation | Urban | < 0.25 Acres | Unknown |  | 100487196 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42243.1458 | 42243.1458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0558 | 2015 | 8 | 27 | 3 | 30 | 15-0057619 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 176351 | 4.6001 | 147_231 | <25mph | <15mph | HFTD - Distribution
PG&E | 42244.4917 | 42244.4917 | 38.8513 | -121.1469 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100055373 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0562 | 2015 | 8 | 28 | 11 | 48 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 10.3663 | 193_286 | <25mph | <15mph | HFTD - Distribution
PG&E | 42244.5014 | 42244.5014 | 37.9047 | -122.2058 | Vegetation | Rural | < 0.25 Acres | Fire Agency | EB MUD | 103623279 |  | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0563 | 2015 | 8 | 28 | 12 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 8.9364 | 147_234 | <25mph | <15mph | HFTD - Distribution
PG&E | 42245.1458 | 42245.1458 | 38.6302 | -122.8327 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Dirt road across from 3204 Rio Lindo Rd, Healdsburg |  | 12000 | Conductor | Overhead | Yes | 42245.1458 | 42245.1458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0566 | 2015 | 8 | 29 | 3 | 30 | 15-0058127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4780 | 5.6914 | 120_274 | <25mph | <15mph | HFTD - Distribution
PG&E | 42246.7118 | 42246.7118 | 38.4039 | -120.5559 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | centennial mine rd |  | 12000 | Conductor | Overhead | Yes | 42246.7118 | 42246.7118 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0567 | 2015 | 8 | 30 | 17 | 5 | 15-0058273 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 40298 | 9.3233 | 219_261 | <25mph | <15mph | HFTD - Distribution
PG&E | 42247.6028 | 42247.6028 | 36.5325 | -121.1462 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 29401 Hwy 25 |  | 21000 | Conductor | Overhead | Yes | 42247.6028 | 42247.6028 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0568 | 2015 | 8 | 31 | 14 | 28 | 15-0058455 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25668 | 11.3997 | 193_158 | <25mph | <15mph | HFTD - Distribution
PG&E | 42251.3257 | 42251.3257 | 40.2318 | -122.3643 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | E/O FRONTIER RD & N/O WAGON WAY |  | 12000 | Conductor | Overhead | Yes | 42251.3257 | 42251.3257 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0577 | 2015 | 9 | 4 | 7 | 49 | 15-0059323 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 9563 | 10.12 | 142_362 | <25mph | <15mph | HFTD - Distribution
PG&E | 42253.8104 | 42253.8104 | 34.6195 | -120.2534 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Santa Barbara County Fire | meter# 1008400678 | Verizon | 12000 | Conductor | Overhead | Yes | 42253.8104 | 42253.8104 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0582 | 2015 | 9 | 6 | 19 | 27 | 15-0059612 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 863 | 7.384 | 158_212 | <25mph | <15mph | HFTD - Distribution
PG&E | 42256.4493 | 42256.4493 | 37.1041 | -121.8853 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100520291 |  | 12000 | Conductor | Overhead | Yes | 42256.4493 | 42256.4493 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0587 | 2015 | 9 | 9 | 10 | 47 | 15-0060074 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 142401 | 10.1251 | 161_190 | <25mph | <15mph | HFTD - Distribution
PG&E | 42257.2375 | 42257.2375 | 37.4609 | -121.8434 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100619766 | None | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0588 | 2015 | 9 | 10 | 5 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 14.0503 | 212_257 | <25mph | <15mph | HFTD - Distribution
PG&E | 42257.6833 | 42257.6833 | 38.5049 | -122.3535 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103159970 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42257.6833 | 42257.6833 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0589 | 2015 | 9 | 10 | 16 | 24 | 15-0060610 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 130124 | 3.6761 | 163_209 | <25mph | <15mph | HFTD - Distribution
PG&E | 42257.7771 | 42257.7771 | 40.7569 | -123.7958 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 096/004 |  | 115000 | Conductor | Overhead | Yes | 42257.7771 | 42257.7771 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0590 | 2015 | 9 | 10 | 18 | 39 | RM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 9.2278 | 141_267 | <25mph | <15mph | HFTD - Transmission
PG&E | 42258.3438 | 42258.3438 | 38.1094 | -122.87 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102293992 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42258.3438 | 42258.3438 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0592 | 2015 | 9 | 11 | 8 | 15 | 15-0060698 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 32419 | 4.233 | 144_213 | <25mph | <15mph | HFTD - Distribution
PG&E | 42259.4104 | 42259.4104 | 39.1164 | -121.0693 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | TOP OF AVALON PLACE, GRASS VALLEY TOWER NUMBER 19/152 40689729 |  | 115000 | Conductor | Overhead | Yes | 42259.4104 | 42259.4104 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0594 | 2015 | 9 | 12 | 9 | 51 | VD-2015-079 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 15.4664 | 188_228 | <25mph | >=15mph | HFTD - Transmission
PG&E | 42259.4646 | 42259.4646 | 38.603 | -120.6741 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101394996 |  | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0595 | 2015 | 9 | 12 | 11 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 12.6722 | 196_301 | <25mph | <15mph | HFTD - Distribution
PG&E | 42265.7118 | 42265.7118 | 37.8992 | -120.4551 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101019893 |  | 17000 | Conductor | Overhead | Yes | 42265.7118 | 42265.7118 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0602 | 2015 | 9 | 18 | 17 | 5 | 15-0062207 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 35222 | 9.1735 | 191_232 | <25mph | <15mph | HFTD - Distribution
PG&E | 42266.4104 | 42266.4104 | 38.4755 | -122.9069 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FORESTVILLE | 103334444 |  | 12000 | Conductor | Overhead | Yes | 42266.4104 | 42266.4104 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0603 | 2015 | 9 | 19 | 9 | 51 | 15-0062267 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 488 | 1.2724 | 223_234 | <25mph | <15mph | HFTD - Distribution
PG&E | 42267.7868 | 42267.7868 | 39.8638 | -121.6599 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42267.7868 | 42267.7868 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0604 | 2015 | 9 | 20 | 18 | 53 | 15-0062407 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 3479 | 3.8017 | 117_266 | <25mph | <15mph | HFTD - Distribution
PG&E | 42268.1708 | 42268.1708 | 38.6587 | -121.0404 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 1of3@13833 |  | 21000 | Conductor | Overhead | Yes | 42268.1708 | 42268.1708 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0605 | 2015 | 9 | 21 | 4 | 6 | 15-0062450 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | 162824 | 5.4184 | 171_342 | <25mph | <15mph | HFTD - Distribution
PG&E | 42268.5993 | 42268.5993 | 40.4786 | -123.771 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | mile marker 29.1, e of hairpin turn |  | 12000 | Conductor | Overhead | Yes | 42268.5993 | 42268.5993 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0606 | 2015 | 9 | 21 | 14 | 23 | 15-0062556 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 13197 | 7.5594 | 198_275 | <25mph | <15mph | HFTD - Distribution
PG&E | 42271.1875 | 42271.1875 | 38.6769 | -123.314 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Str. 041/007 |  | 60000 | Conductor | Overhead | Yes | 42271.1875 | 42271.1875 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0613 | 2015 | 9 | 24 | 4 | 30 | FU-2015-057 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 22680 | 6.9914 | 141_345 | <25mph | <15mph | HFTD - Transmission
PG&E | 42271.5806 | 42271.5806 | 39.3508 | -121.2454 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 9692 Rices-Texas Hill rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42271.5806 | 42271.5806 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0614 | 2015 | 9 | 24 | 13 | 56 | 15-0063159 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 51917 | 8.169 | 100_277 | <25mph | <15mph | HFTD - Distribution
PG&E | 42272.7278 | 42272.7278 | 38.7169 | -120.7693 | Vegetation | Rural | < 0.25 Acres | Fire Agency | el dorado F D | 101405928 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42272.7278 | 42272.7278 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0616 | 2015 | 9 | 25 | 17 | 28 | 15-0063666 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 111180 | 10.4745 | 211_198 | <25mph | <15mph | HFTD - Distribution
PG&E | 42275.4042 | 42275.4042 | 37.9623 | -122.1765 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100458692 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42275.4042 | 42275.4042 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0619 | 2015 | 9 | 28 | 9 | 42 | 15-0066062 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 2125 | 6.386 | 190_282 | <25mph | <15mph | HFTD - Distribution
PG&E | 42277.7257 | 42277.7257 | 38.5747 | -120.682 | Vegetation | Rural | < 0.25 Acres | Fire Agency | el dorado county | 7901 shenandoah ln |  | 21000 | Conductor | Overhead | Yes | 42277.7257 | 42277.7257 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0625 | 2015 | 9 | 30 | 17 | 25 | 15-0066934 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 28912 | 3.2693 | 149_204 | <25mph | <15mph | HFTD - Distribution
PG&E | 42280.3104 | 42280.3104 | 39.0633 | -122.6237 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 2323 new long valley rd | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0631 | 2015 | 10 | 3 | 7 | 27 | No ILIS or TOTL available | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 10.2588 | 251_181 | <25mph | <15mph | HFTD - Distribution
PG&E | 42280.8826 | 42280.8826 | 39.7358 | -121.6855 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | honey run rd at cutouts 16015 |  | 12000 | Conductor | Overhead | Yes | 42280.8826 | 42280.8826 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0632 | 2015 | 10 | 3 | 21 | 11 | 15-0067708 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 10499 | 6.7716 | 130_298 | <25mph | <15mph | HFTD - Distribution
PG&E | 42281.0437 | 42281.0437 | 39.7923 | -121.5803 | Vegetation | Urban | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42281.0437 | 42281.0437 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0634 | 2015 | 10 | 4 | 1 | 3 | 15-0067711 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2697 | 17.8391 | 119_301 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42281.0639 | 42281.0639 | 39.2279 | -121.3774 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | in field at 6275 sandstonel ln |  | 12000 | Conductor | Overhead | Yes | 42281.0639 | 42281.0639 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0635 | 2015 | 10 | 4 | 1 | 32 | 15-0067743 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 4021 | 6.2139 | 175_338 | <25mph | <15mph | HFTD - Distribution
PG&E | 42284.6277 | 42284.6277 | 35.3079 | -120.8328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101924901 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42284.6277 | 42284.6277 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0640 | 2015 | 10 | 7 | 15 | 3 | 15-0068730 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 77896 | 2.8464 | 148_378 | <25mph | <15mph | HFTD - Distribution
PG&E | 42286.2722 | 42286.2722 | 38.364 | -122.9173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 320 Freestone St, Frestone | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0642 | 2015 | 10 | 9 | 6 | 32 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 7.488 | 210_104 | <25mph | <15mph | HFTD - Distribution
PG&E | 42293.4049 | 42293.4049 | 39.187 | -123.2015 | Vegetation | Rural | < 3 meters | Unknown |  | 102196855 |  | 12000 | Conductor | Overhead | Yes | 42293.4049 | 42293.4049 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0653 | 2015 | 10 | 16 | 9 | 43 | 15-0070948 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 65228 | 2.6808 | 253_157 | <25mph | <15mph | HFTD - Distribution
PG&E | 42302.2431 | 42302.2431 | 37.7843 | -121.7683 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | cutouts 9504 |  | 21000 | Conductor | Overhead | Yes | 42302.2431 | 42302.2431 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0657 | 2015 | 10 | 25 | 5 | 50 | 15-0073203 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 10710 | 7.7814 | 190_281 | <25mph | <15mph | HFTD - Distribution
PG&E | 42307.1868 | 42307.1868 | 39.5059 | -123.7672 | Vegetation | Rural | < 3 meters | Fire Agency | local fire | in field next to hwy / 1 span SS of Fuse 4617 |  | 12000 | Conductor | Overhead | Yes | 42307.1868 | 42307.1868 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0661 | 2015 | 10 | 30 | 4 | 29 | 15-0074188 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 273183 | 6.0304 | 151_219 | <25mph | <15mph | HFTD - Distribution
PG&E | 42307.7174 | 42307.7174 | 38.3166 | -120.7226 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 7600 HWY 49, Jackson | None | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0662 | 2015 | 10 | 30 | 17 | 13 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 8.2726 | 82_324 | <25mph | <15mph | HFTD - Distribution
PG&E | 42308.3229 | 42308.3229 | 38.1157 | -120.8931 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal FIRE | 103763040 |  | 12000 | Conductor | Overhead | Yes | 42308.3229 | 42308.3229 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0663 | 2015 | 10 | 31 | 7 | 45 | 15-0074424 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 314565 | 3.1706 | 211_256 | <25mph | <15mph | HFTD - Distribution
PG&E | 42317.2465 | 42317.2465 | 34.9984 | -120.3634 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42317.2465 | 42317.2465 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0673 | 2015 | 11 | 9 | 5 | 55 | 15-0076534 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 205393 | 9.4792 | 175_300 | <25mph | <15mph | HFTD - Distribution
PG&E | 42323.6875 | 42323.6875 | 37.0007 | -121.885 | Vegetation | Rural | < 3 meters | Customer |  | 101691004 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42323.6875 | 42323.6875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0676 | 2015 | 11 | 15 | 16 | 30 | 15-0077978 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 25920 | 16.4134 | 159_198 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42329.4417 | 42329.4417 | 38.0679 | -120.1872 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101045952 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42329.4417 | 42329.4417 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0677 | 2015 | 11 | 21 | 10 | 36 | 15-0079868 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18350 | 4.5257 | 161_184 | <25mph | <15mph | HFTD - Distribution
PG&E | 42339.5021 | 42339.5021 | 35.6744 | -120.9932 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal FIRE | 101860660 |  | 21000 | Conductor | Overhead | Yes | 42339.5021 | 42339.5021 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0680 | 2015 | 12 | 1 | 12 | 3 | 15-0081983 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 42427 | 9.2617 | 160_329 | <25mph | <15mph | HFTD - Distribution
PG&E | 42341.5069 | 42341.5069 | 40.0277 | -120.9652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | usfs | spanish creek campground |  | 12000 | Conductor | Overhead | Yes | 42341.5069 | 42341.5069 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0683 | 2015 | 12 | 3 | 12 | 10 | 15-0082505 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 196854 | 4.6483 | 155_201 | <25mph | <15mph | HFTD - Distribution
PG&E | 42346.5285 | 42346.5285 | 38.2489 | -120.5228 | Other | Rural | Structure Only | Unknown |  | 7026 Railroad Flat Road, Mountain Ranch |  | 12000 | Conductor | Overhead | Yes | 42346.5285 | 42346.5285 | Contact From Object | N.A. | Other | Electric Facility | Human Error | AT&T work error | Other/Unknown | 0684 | 2015 | 12 | 8 | 12 | 41 | 15-0083435 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1120 | 11.1655 | 201_351 | <25mph | <15mph | HFTD - Distribution
PG&E | 42369.8 | 42369.8 | 37.1568 | -121.9868 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LOS GATOS MONTE SERENO SARATOGA | 100518215 | Verizon | 21000 | Conductor | Overhead | Yes | 42369.8 | 42369.8 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0689 | 2015 | 12 | 31 | 19 | 12 | 15-0087962 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7979 | 8.4855 | 224_72 | <25mph | <15mph | HFTD - Distribution
PG&E | 42390.8972 | 42390.8972 | 40.553 | -124.1116 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100994021 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42390.8972 | 42390.8972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0690 | 2016 | 1 | 21 | 21 | 32 | 16-0007239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 6468 | 9.9649 | 156_193 | <25mph | <15mph | HFTD - Distribution
PG&E | 42392.6535 | 42392.6535 | 39.9486 | -122.3728 | Vegetation | RURAL | < 0.25 Acres | Self Extinguished | N.A. | 101524077 |  | 12000 | Conductor | Overhead | Yes | 42392.6535 | 42392.6535 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0691 | 2016 | 1 | 23 | 15 | 41 | 16-0007778 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 133520 | 22.3041 | 69_382 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42405.8681 | 42405.8681 | 40.0156 | -122.4333 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | TEHAMA COUNTY & LOCAL VOLUNTEER | 101529688 | None | 12000 | Conductor | Overhead | Yes | 42405.8681 | 42405.8681 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0693 | 2016 | 2 | 5 | 20 | 50 | 16-0011034 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 11424 | 14.1578 | 137_227 | <25mph | <15mph | HFTD - Distribution
PG&E | 42408.1632 | 42408.1632 | 39.7852 | -121.5056 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100337507 |  | 12000 | Conductor | Overhead | Yes | 42408.1632 | 42408.1632 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0694 | 2016 | 2 | 8 | 3 | 55 | 16-0011201 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 87046 | 5.6741 | 139_351 | <25mph | <15mph | HFTD - Distribution
PG&E | 42463.5007 | 42463.5007 | 38.6804 | -123.125 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101968191 |  | 12000 | Conductor | Overhead | Yes | 42463.5007 | 42463.5007 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0702 | 2016 | 4 | 3 | 12 | 1 | 16-0025794 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 3528 | 6.9875 | 148_373 | <25mph | <15mph | HFTD - Distribution
PG&E | 42468.5514 | 42468.5514 | 39.0429 | -121.1002 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100086751 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42468.5514 | 42468.5514 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0705 | 2016 | 4 | 8 | 13 | 14 | 16-0027237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 11817 | 2.5181 | 289_93 | <25mph | <15mph | HFTD - Distribution
PG&E | 42473.8111 | 42473.8111 | 40.4954 | -124.1219 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103659313 |  | 12000 | Conductor | Overhead | Yes | 42473.8111 | 42473.8111 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0706 | 2016 | 4 | 13 | 19 | 28 | 16-0028421 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 688 | 8.5227 | 195_296 | <25mph | <15mph | HFTD - Distribution
PG&E | 42481.3924 | 42481.3924 | 39.293 | -123.769 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 103312287 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0711 | 2016 | 4 | 21 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 9.0201 | 145_250 | <25mph | <15mph | HFTD - Distribution
PG&E | 42490 | 0.74931 | 38.3142 | -120.9015 | Vegetation | RURAL | < 3 meters | Fire Agency | Kern County FD |  |  | 12000 | Conductor | Overhead | Yes | 42490 | 0.74931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0719 | 2016 | 4 | 30 | 17 | 59 | 16-0032910 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 722 | 8.5677 | 277_158 | <25mph | <15mph | HFTD - Distribution
PG&E | 42502.8438 | 42502.8438 | 35.1922 | -120.4563 | Vegetation | RURAL | < 3 meters | Self Extinguished | N.A. | 101857280 |  | 12000 | Conductor | Overhead | Yes | 42502.8438 | 42502.8438 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0727 | 2016 | 5 | 12 | 20 | 15 | 16-0035728 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 54088 | 3.4097 | 71_376 | <25mph | <15mph | HFTD - Distribution
PG&E | 42505.6625 | 42505.6625 | 36.7948 | -119.3966 | Vegetation | RURAL | 100 - 299 Acres | Fire Agency | Cal Fire | 100729685 | None | 12000 | Conductor | Overhead | Yes | 42505.6625 | 42505.6625 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0730 | 2016 | 5 | 15 | 15 | 54 | 16-0036136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 180310 | 10.2803 | 175_303 | <25mph | <15mph | HFTD - Distribution
PG&E | 42508 | 0.76667 | 39.7381 | -123.1587 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42508 | 0.76667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0735 | 2016 | 5 | 18 | 18 | 24 | 16-0036911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1482 | 1.95 | 289_96 | <25mph | <15mph | HFTD - Distribution
PG&E | 42509.0708 | 42509.0708 | 34.6645 | -120.4 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Santa Barbara County FD | 101916587 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42509.0708 | 42509.0708 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | no-match | 0738 | 2016 | 5 | 19 | 1 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 5.916 | 140_376 | <25mph | <15mph | HFTD - Distribution
PG&E | 42509.7875 | 42509.7875 | 38.8168 | -123.5843 | Vegetation | RURAL | < 3 meters | Fire Agency | Gualala Firw | 102183917 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42509.7875 | 42509.7875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0740 | 2016 | 5 | 19 | 18 | 54 | 16-0037247 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 4510 | 40.5937 | 88_285 | 40-55mph | >=15mph | HFTD - Distribution
PG&E | 42510.6257 | 0.62569 | 39.0559 | -123.4581 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102198323 |  | 12000 | Conductor | Overhead | Yes | 42510.6257 | 0.62569 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0741 | 2016 | 5 | 20 | 15 | 1 | 16-0037479 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2720 | 14.9654 | 208_225 | <25mph | <15mph | HFTD - Distribution
PG&E | 42514.525 | 42514.525 | 38.0811 | -120.668 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101278239 |  | 12000 | Conductor | Overhead | Yes | 42514.525 | 42514.525 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0747 | 2016 | 5 | 24 | 12 | 36 | 16-0038096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 10678 | 11.9408 | 171_236 | <25mph | <15mph | HFTD - Distribution
PG&E | 42519.5965 | 42519.5965 | 40.5795 | -122.4694 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103156596 | Yes | 12000 | Conductor | Overhead | Yes | 42519.5965 | 42519.5965 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0751 | 2016 | 5 | 29 | 14 | 19 | 16-0039619 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3860 | 11.1608 | 256_169 | <25mph | <15mph | HFTD - Distribution
PG&E | 42521.1681 | 42521.1681 | 35.7984 | -120.9743 | Vegetation | RURAL | < 0.25 Acres | Utility: PG&E | N.A. | 101863413 |  | 12000 | Conductor | Overhead | Yes | 42521.1681 | 42521.1681 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0754 | 2016 | 5 | 31 | 4 | 2 | 16-0039748 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 51888 | 14.9631 | 293_100 | <25mph | <15mph | HFTD - Distribution
PG&E | 42524 | 42524.5111 | 38.6435 | -120.6959 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | cal-fire and usfs | 103119737 |  | 21000 | Conductor | Overhead | Yes | 42524 | 42524.5111 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0764 | 2016 | 6 | 3 | 12 | 16 | 16-0040808 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 101354 | 4.1999 | 173_161 | <25mph | <15mph | HFTD - Distribution
PG&E | 42525 | 0.92708 | 38.5117 | -122.9373 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42525 | 0.92708 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0768 | 2016 | 6 | 4 | 22 | 15 | 16-0041119 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7220 | 9.2554 | 161_208 | <25mph | <15mph | HFTD - Distribution
PG&E | 42526.6556 | 42526.6556 | 40.3441 | -123.71 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101009790 |  | 60000 | Conductor | Overhead | Yes | 42526.6556 | 42526.6556 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0774 | 2016 | 6 | 5 | 15 | 44 | HM-2016-016 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 4.5459 | 85_370 | <25mph | <15mph | HFTD - Transmission
PG&E | 42527 | 42527.825 | 38.9129 | -121.1192 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire/placer fire | 100050264 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42527 | 42527.825 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0775 | 2016 | 6 | 6 | 19 | 48 | 16-0041497 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 2039 | 7.5231 | 261_162 | <25mph | <15mph | HFTD - Distribution
PG&E | 42531.6604 | 42531.6604 | 39.9934 | -123.7883 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100992291 |  | 12000 | Conductor | Overhead | Yes | 42531.6604 | 42531.6604 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0788 | 2016 | 6 | 10 | 15 | 51 | 16-0042501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | N.A. | 14.26 | 257_169 | <25mph | <15mph | HFTD - Distribution
PG&E | 42531.6646 | 42531.6646 | 38.1792 | -120.6657 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103809655 |  | 12000 | Conductor | Overhead | Yes | 42531.6646 | 42531.6646 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0789 | 2016 | 6 | 10 | 15 | 57 | 16-0042508 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 17.8656 | 82_351 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42532 | 42532.8229 | 39.3265 | -121.3921 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101292512 |  | 0 – 750 | Transformer | Overhead | Yes | 42532 | 42532.8229 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0790 | 2016 | 6 | 11 | 19 | 45 | 16-0042611 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 642 | 6.2372 | 214_249 | <25mph | <15mph | HFTD - Distribution
PG&E | 42533 | 42533.4319 | 38.0491 | -120.3976 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101042514 |  | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0792 | 2016 | 6 | 12 | 10 | 22 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 16.9807 | 141_210 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42533 | 42533.5514 | 37.5096 | -120.0462 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101083986 |  | 0 – 750 | Conductor | Overhead | Yes | 42533 | 42533.5514 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0795 | 2016 | 6 | 12 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 22.6022 | 143_332 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42533.0729 | 0.072917 | 37.4643 | -122.3459 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Unknown | 100265854 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42533.0729 | 0.072917 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0796 | 2016 | 6 | 12 | 1 | 45 | 16-0042637 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 19836 | 19.954 | 153_253 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42536 | 42536.5479 | 38.4433 | -120.7568 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103169620 |  | 12000 | Conductor | Overhead | Yes | 42536 | 42536.5479 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0801 | 2016 | 6 | 15 | 13 | 9 | 16-0043476 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 23963 | 7.7425 | 127_264 | <25mph | <15mph | HFTD - Distribution
PG&E | 42540 | 42540.5049 | 39.3811 | -123.7737 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102187888 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42540 | 42540.5049 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0807 | 2016 | 6 | 19 | 12 | 7 | 16-0044317 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6100 | 14.1625 | 226_169 | <25mph | <15mph | HFTD - Distribution
PG&E | 42540 | 42540.7215 | 38.4508 | -122.3546 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire--napa fire | 102256859 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42540 | 42540.7215 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0808 | 2016 | 6 | 19 | 17 | 19 | 16-0044337 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 672 | 7.3683 | 81_317 | <25mph | <15mph | HFTD - Distribution
PG&E | 42541 | 42541.6979 | 41.0697 | -123.6789 | Vegetation | RURAL | < 3 meters | Fire Agency | Hoopa FD | 101011420 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42541 | 42541.6979 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0811 | 2016 | 6 | 20 | 16 | 45 | 16-0044577 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7361 | 7.0385 | 271_159 | <25mph | <15mph | HFTD - Distribution
PG&E | 42542 | 0.86736 | 35.5352 | -120.8457 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101900832 |  | 12000 | Conductor | Overhead | Yes | 42542 | 0.86736 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0812 | 2016 | 6 | 21 | 20 | 49 | 16-0044904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7806 | 2.4781 | 88_410 | <25mph | <15mph | HFTD - Distribution
PG&E | 42542 | 42542.4229 | 39.0294 | -121.2927 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100024816 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | no-match | 0813 | 2016 | 6 | 21 | 10 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 10.9438 | 187_296 | <25mph | <15mph | HFTD - Distribution
PG&E | 42542 | 42542.7035 | 38.4233 | -122.5448 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | KENWOOD FIRE XST | 102036904 | Yes | 0 – 750 | Conductor | Overhead | Yes | 42542 | 42542.7035 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0814 | 2016 | 6 | 21 | 16 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 2.3548 | 133_263 | <25mph | <15mph | HFTD - Distribution
PG&E | 42545 | 42545.6097 | 40.22 | -122.283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101526647 | PACIFIC BELL | 0 – 750 | Unknown | Overhead | Yes | 42545 | 42545.6097 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0821 | 2016 | 6 | 24 | 14 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 15.3241 | 197_279 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42547 | 42547.6931 | 39.5042 | -121.4475 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100375810 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42547 | 42547.6931 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0823 | 2016 | 6 | 26 | 16 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 8.0953 | 173_336 | <25mph | <15mph | HFTD - Distribution
PG&E | 42547.4625 | 42547.4625 | 40.4832 | -122.0466 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101483777 | FRONTIER | 12000 | Conductor | Overhead | Yes | 42547.4625 | 42547.4625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0826 | 2016 | 6 | 26 | 11 | 6 | 16-0045846 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 15520 | 13.515 | 214_111 | <25mph | <15mph | HFTD - Distribution
PG&E | 42551 | 0.0020833 | 39.8157 | -121.5994 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42551 | 0.0020833 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0832 | 2016 | 6 | 30 | 0 | 3 | 16-0046763 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 299100 | 7.6229 | 180_156 | <25mph | <15mph | HFTD - Distribution
PG&E | 42551 | 42551.7181 | 40.0353 | -122.5694 | Vegetation | RURAL | 300 - 999 Acres | Fire Agency | Cal Fire | 101528146 |  | 12000 | Conductor | Overhead | Yes | 42551 | 42551.7181 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0833 | 2016 | 6 | 30 | 17 | 14 | 16-0047210 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Fell into (slight defect) | 4520 | 9.209 | 174_339 | <25mph | <15mph | HFTD - Distribution
PG&E | 42551.5972 | 42551.5972 | 37.9927 | -120.3996 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Cal Fire | 102327111 | PACIFIC BELL | 17000 | Conductor | Overhead | Yes | 42551.5972 | 42551.5972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0834 | 2016 | 6 | 30 | 14 | 20 | 16-0047073 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 278 | 9.6736 | 226_239 | <25mph | <15mph | HFTD - Distribution
PG&E | 42554.625 | 42554.625 | 38.0348 | -120.3809 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101050507 |  | 17000 | Conductor | Overhead | Yes | 42554.625 | 42554.625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0837 | 2016 | 7 | 3 | 15 | 0 | 16-0047689 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38812 | 10.2237 | 178_227 | <25mph | <15mph | HFTD - Distribution
PG&E | 42559.4507 | 42559.4507 | 38.3373 | -122.1211 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 102291118 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42559.4507 | 42559.4507 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0842 | 2016 | 7 | 8 | 10 | 49 | 16-0048647 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 19469 | 7.9878 | 164_311 | <25mph | <15mph | HFTD - Distribution
PG&E | 42563.5958 | 42563.5958 | 35.3471 | -120.3813 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101879190 |  | 21000 | Conductor | Overhead | Yes | 42563.5958 | 42563.5958 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0848 | 2016 | 7 | 12 | 14 | 18 | 16-0049403 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 18883 | 14.2521 | 163_201 | <25mph | <15mph | HFTD - Distribution
PG&E | 42566.2215 | 42566.2215 | 35.1839 | -120.5018 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101846594 |  | 12000 | Conductor | Overhead | Yes | 42566.2215 | 42566.2215 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0851 | 2016 | 7 | 15 | 5 | 19 | 16-0050086 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 62404 | 4.7111 | 293_96 | <25mph | <15mph | HFTD - Distribution
PG&E | 42566.5896 | 42566.5896 | 38.6965 | -120.8598 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412774 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.5896 | 42566.5896 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0852 | 2016 | 7 | 15 | 14 | 9 | 16-0050274 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 11253 | 4.6799 | 222_84 | <25mph | <15mph | HFTD - Distribution
PG&E | 42566.6014 | 42566.6014 | 38.1366 | -122.7092 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | NOVATO FIRE AND OTHERS | 102013570 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.6014 | 42566.6014 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0853 | 2016 | 7 | 15 | 14 | 26 | 16-0050269 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 758 | 4.6138 | 125_247 | <25mph | <15mph | HFTD - Distribution
PG&E | 42567.0403 | 42567.0403 | 36.4379 | -121.9198 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101669758 |  | 12000 | Other | Overhead | Yes | 42567.0403 | 42567.0403 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0855 | 2016 | 7 | 16 | 0 | 58 | 16-0050335 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 8976 | 2.0878 | 288_94 | <25mph | <15mph | HFTD - Distribution
PG&E | 42567.3465 | 42567.3465 | 37.4828 | -119.87 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101079104 | None | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0856 | 2016 | 7 | 16 | 8 | 19 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 17.2897 | 159_153 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42567.8514 | 42567.8514 | 38.4944 | -122.4944 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Cal Fire | 102265740 | None | 12000 | Conductor | Overhead | Yes | 42567.8514 | 42567.8514 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0857 | 2016 | 7 | 16 | 20 | 26 | 16-0050320 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 13240 | 10.3059 | 249_211 | <25mph | <15mph | HFTD - Distribution
PG&E | 42571.8021 | 42571.8021 | 37.7712 | -121.8104 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100898986 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42571.8021 | 42571.8021 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0865 | 2016 | 7 | 20 | 19 | 15 | 16-0051308 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3013 | 7.5825 | 229_68 | <25mph | <15mph | HFTD - Distribution
PG&E | 42572.9062 | 42572.9062 | 40.8566 | -122.3387 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101455670 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0870 | 2016 | 7 | 21 | 21 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.2798 | 215_106 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42575.6833 | 42575.6833 | 38.0105 | -122.1941 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | CCD | 103049639 |  | 115000 | Conductor | Overhead | Yes | 42575.6833 | 42575.6833 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0876 | 2016 | 7 | 24 | 16 | 24 | PS-2016-013 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 0 | 8.2416 | 256_170 | <25mph | <15mph | HFTD - Transmission
PG&E | 42576.6472 | 42576.6472 | 38.3522 | -120.7107 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42576.6472 | 42576.6472 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0878 | 2016 | 7 | 25 | 15 | 32 | 16-0052398 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 19951 | 9.9198 | 218_210 | <25mph | <15mph | HFTD - Distribution
PG&E | 42578.4951 | 42578.4951 | 37.8649 | -120.5134 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101041792 |  | 17000 | Conductor | Overhead | Yes | 42578.4951 | 42578.4951 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0880 | 2016 | 7 | 27 | 11 | 53 | 16-0052942 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 14734 | 12.2359 | 221_232 | <25mph | <15mph | HFTD - Distribution
PG&E | 42578.7118 | 42578.7118 | 38.5392 | -122.7656 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102029945 |  | 60000 | Conductor | Overhead | Yes | 42578.7118 | 42578.7118 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0882 | 2016 | 7 | 27 | 17 | 5 | FU-2016-047 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 13.0336 | 148_285 | <25mph | <15mph | HFTD - Transmission
PG&E | 42579.1118 | 42579.1118 | 35.3674 | -120.3977 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101849904 |  | 21000 | Conductor | Overhead | Yes | 42579.1118 | 42579.1118 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0883 | 2016 | 7 | 28 | 2 | 41 | 16-0053127 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 22592 | 6.9031 | 123_269 | <25mph | <15mph | HFTD - Distribution
PG&E | 42579.3417 | 42579.3417 | 37.8207 | -120.1388 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101037043 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0884 | 2016 | 7 | 28 | 8 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 8.3704 | 227_94 | <25mph | <15mph | HFTD - Distribution
PG&E | 42579.5403 | 42579.5403 | 37.2371 | -119.8157 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103323932 |  | 21000 | Conductor | Overhead | Yes | 42579.5403 | 42579.5403 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0885 | 2016 | 7 | 28 | 12 | 58 | 16-0053313 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 15215 | 3.6308 | 237_229 | <25mph | <15mph | HFTD - Distribution
PG&E | 42579.5549 | 42579.5549 | 39.7127 | -123.4973 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102195566 |  | 12000 | Conductor | Overhead | Yes | 42579.5549 | 42579.5549 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0886 | 2016 | 7 | 28 | 13 | 19 | 16-0053369 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 4447 | 3.1103 | 252_197 | <25mph | <15mph | HFTD - Distribution
PG&E | 42579.6 | 42579.6 | 37.8232 | -120.1356 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101037045 |  | 17000 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Guy/Span Wire | N.A. | N.A. | Unknown |  | no-match | 0888 | 2016 | 7 | 28 | 14 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Guy/Span Wire | N.A. | 7.2837 | 169_332 | <25mph | <15mph | HFTD - Distribution
PG&E | 42580 | 0.76111 | 38.5769 | -122.6187 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Selma Fire Department |  |  | 12000 | Conductor | Overhead | Yes | 42580 | 0.76111 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0890 | 2016 | 7 | 29 | 18 | 16 | 16-0053726 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 177834 | 3.9949 | 256_170 | <25mph | <15mph | HFTD - Distribution
PG&E | 42580.0632 | 42580.0632 | 41.0396 | -123.674 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Hoopa FD | 100962351 |  | 12000 | Conductor | Overhead | Yes | 42580.0632 | 42580.0632 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0891 | 2016 | 7 | 29 | 1 | 31 | 16-0053478 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1418 | 11.5031 | 88_408 | <25mph | <15mph | HFTD - Distribution
PG&E | 42582.5076 | 42582.5076 | 38.7827 | -120.9168 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101417359 |  | 21000 | Conductor | Overhead | Yes | 42582.5076 | 42582.5076 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0895 | 2016 | 7 | 31 | 12 | 11 | 16-0053949 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 10.4973 | 294_85 | <25mph | <15mph | HFTD - Distribution
PG&E | 42583 | 42583.5347 | 38.9044 | -121.1274 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100078299 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42583 | 42583.5347 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0896 | 2016 | 8 | 1 | 12 | 50 | 16-0054142 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 855 | 5.0633 | 203_282 | <25mph | <15mph | HFTD - Distribution
PG&E | 42583 | 42583.7701 | 38.6956 | -120.9283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412720 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0898 | 2016 | 8 | 1 | 18 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.7413 | 179_290 | <25mph | <15mph | HFTD - Distribution
PG&E | 42584 | 42584.6771 | 37.0312 | -119.4395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Fresno County FD | 100675986 |  | 12000 | Conductor | Overhead | Yes | 42584 | 42584.6771 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0900 | 2016 | 8 | 2 | 16 | 15 | 16-0054552 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 265566 | 12.2263 | 144_250 | <25mph | <15mph | HFTD - Distribution
PG&E | 42585 | 42585.1931 | 38.8474 | -120.812 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire garden valley fire | 103809676 |  | 21000 | Conductor | Overhead | Yes | 42585 | 42585.1931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0901 | 2016 | 8 | 3 | 4 | 38 | 16-0054597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2751 | 5.3291 | 268_186 | <25mph | <15mph | HFTD - Distribution
PG&E | 42585 | 42585.5285 | 39.3269 | -120.6033 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100001032 |  | 12000 | Conductor | Overhead | Yes | 42585 | 42585.5285 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0902 | 2016 | 8 | 3 | 12 | 41 | 16-0054769 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 20554 | 4.6057 | 208_286 | <25mph | <15mph | HFTD - Distribution
PG&E | 42587 | 42587.5292 | 38.4048 | -120.5292 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101244628 |  | 12000 | Conductor | Overhead | Yes | 42587 | 42587.5292 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0906 | 2016 | 8 | 5 | 12 | 42 | 16-0055368 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 363 | 6.6619 | 145_258 | <25mph | <15mph | HFTD - Distribution
PG&E | 42587 | 42587.6153 | 40.4797 | -123.7803 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103572261 |  | 12000 | Conductor | Overhead | Yes | 42587 | 42587.6153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0907 | 2016 | 8 | 5 | 14 | 46 | 16-0055425 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 7019 | 6.213 | 220_261 | <25mph | <15mph | HFTD - Distribution
PG&E | 42589 | 42589.5972 | 37.2316 | -122.1552 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire/woodside fire | 103413747 |  | 12000 | Conductor | Overhead | Yes | 42589 | 42589.5972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0910 | 2016 | 8 | 7 | 14 | 20 | 16-0055597 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29869 | 9.5487 | 143_255 | <25mph | <15mph | HFTD - Distribution
PG&E | 42590 | 42590.6556 | 37.1382 | -121.9672 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100519919 |  | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0912 | 2016 | 8 | 8 | 15 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 7.2774 | 105_337 | <25mph | <15mph | HFTD - Distribution
PG&E | 42591 | 42591.8063 | 38.9187 | -120.9525 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | El Dorado County FD | 100038028 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0915 | 2016 | 8 | 9 | 19 | 21 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.2662 | 155_203 | <25mph | <15mph | HFTD - Distribution
PG&E | 42592 | 42592.3583 | 37.0575 | -121.9556 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 101680487 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0917 | 2016 | 8 | 10 | 8 | 36 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 4.0654 | 157_187 | <25mph | <15mph | HFTD - Distribution
PG&E | 42594 | 42594.4222 | 38.8751 | -122.4223 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 102168360 |  | 12000 | Conductor | Overhead | Yes | 42594 | 42594.4222 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0922 | 2016 | 8 | 12 | 10 | 8 | 16-0056982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 1368 | 14.6908 | 100_335 | <25mph | <15mph | HFTD - Distribution
PG&E | 42595 | 0.60486 | 37.4642 | -119.8589 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire |  |  | 21000 | Conductor | Overhead | Yes | 42595 | 0.60486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0923 | 2016 | 8 | 13 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.0828 | 138_288 | <25mph | <15mph | HFTD - Distribution
PG&E | 42595 | 42595.5833 | 39.2009 | -121.213 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100011376 | PACIFIC BELL | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0924 | 2016 | 8 | 13 | 14 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 6.0967 | 190_305 | <25mph | <15mph | HFTD - Distribution
PG&E | 42597 | 42597.6549 | 37.8784 | -120.4488 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101020079 |  | 17000 | Conductor | Overhead | Yes | 42597 | 42597.6549 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0928 | 2016 | 8 | 15 | 15 | 43 | 16-0057465 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 122905 | 2.194 | 164_199 | <25mph | <15mph | HFTD - Distribution
PG&E | 42598 | 42598.5542 | 40.3417 | -123.8803 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | miranda/fruitland vol, calfire | 100990019 | None | 12000 | Conductor | Overhead | Yes | 42598 | 42598.5542 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0929 | 2016 | 8 | 16 | 13 | 18 | 16-0057668 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 137 | 3.2949 | 223_232 | <25mph | <15mph | HFTD - Distribution
PG&E | 42599 | 42599.516 | 41.2495 | -123.7671 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103315791 |  | 12000 | Conductor | Overhead | Yes | 42599 | 42599.516 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0932 | 2016 | 8 | 17 | 12 | 23 | 16-0058002 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 16544 | 4.1561 | 291_95 | <25mph | <15mph | HFTD - Distribution
PG&E | 42599 | 42599.7757 | 37.3078 | -119.6511 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101020932 |  | 21000 | Conductor | Overhead | Yes | 42599 | 42599.7757 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0934 | 2016 | 8 | 17 | 18 | 37 | 16-0058019 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 59379 | 7.634 | 168_329 | <25mph | <15mph | HFTD - Distribution
PG&E | 42601 | 42601.6826 | 39.2235 | -123.755 | Vegetation | RURAL | < 3 meters | Fire Agency | Albion-Little River FD | 102206661 |  | 12000 | Conductor | Overhead | Yes | 42601 | 42601.6826 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0938 | 2016 | 8 | 19 | 16 | 23 | 16-0058677 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 95106 | 14.9952 | 175_182 | <25mph | <15mph | HFTD - Distribution
PG&E | 42603 | 42603.5431 | 38.4445 | -122.2496 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102291451 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42603 | 42603.5431 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0940 | 2016 | 8 | 21 | 13 | 2 | 16-0058847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 12780 | 7.6482 | 273_155 | <25mph | <15mph | HFTD - Distribution
PG&E | 42604 | 42604.6736 | 37.9666 | -120.2395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Toulumne City FD | 101043683 |  | 17000 | Conductor | Overhead | Yes | 42604 | 42604.6736 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0941 | 2016 | 8 | 22 | 16 | 10 | 16-0059149 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 78534 | 8.4511 | 145_264 | <25mph | <15mph | HFTD - Distribution
PG&E | 42606 | 42606.5076 | 36.4633 | -121.712 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101750810 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42606 | 42606.5076 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0943 | 2016 | 8 | 24 | 12 | 11 | 16-0059702 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 232770 | 3.6968 | 257_177 | <25mph | <15mph | HFTD - Distribution
PG&E | 42607 | 42607.5028 | 36.9726 | -119.3816 | Vegetation | RURAL | < 3 meters | Utility: PG&E | N.A. | 100651318 | PONDEROSA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0945 | 2016 | 8 | 25 | 12 | 4 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.0098 | 249_176 | <25mph | <15mph | HFTD - Distribution
PG&E | 42612 | 42612.6674 | 36.5941 | -121.9212 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Unknown | 101734977 |  | 21000 | Conductor | Overhead | Yes | 42612 | 42612.6674 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0951 | 2016 | 8 | 30 | 16 | 1 | 16-0061130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 199327 | 17.3768 | 173_254 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42613 | 42613.6194 | 35.1918 | -120.4697 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101942860 |  | 12000 | Conductor | Overhead | Yes | 42613 | 42613.6194 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0955 | 2016 | 8 | 31 | 14 | 52 | 16-0061423 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 156294 | 10.6323 | 224_204 | <25mph | <15mph | HFTD - Distribution
PG&E | 42625 | 0.18333 | 36.3999 | -121.902 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire Hwy 1 Carmel Hill | 101669614 |  | 12000 | Conductor | Overhead | Yes | 42625 | 0.18333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0973 | 2016 | 9 | 12 | 4 | 24 | 16-0063826 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 130604 | 14.7849 | 256_182 | <25mph | <15mph | HFTD - Distribution
PG&E | 42625 | 0.52639 | 38.7832 | -120.6006 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101421708 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42625 | 0.52639 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0974 | 2016 | 9 | 12 | 12 | 38 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 4.7203 | 159_151 | <25mph | <15mph | HFTD - Distribution
PG&E | 42625.6306 | 42625.6306 | 39.5256 | -123.7655 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102185070 |  | 12000 | Conductor | Overhead | Yes | 42625.6306 | 42625.6306 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0977 | 2016 | 9 | 12 | 15 | 8 | 16-0064050 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 428 | 5.2324 | 275_159 | <25mph | <15mph | HFTD - Distribution
PG&E | 42626.4479 | 42626.4479 | 40.2958 | -122.1318 | Vegetation | RURAL | 300 - 999 Acres | Fire Agency | Cal Fire | 103702175 |  | 60000 | Conductor | Overhead | Yes | 42626.4479 | 42626.4479 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0979 | 2016 | 9 | 13 | 10 | 45 | INT-08528 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Animal | Animal | 0 | 9.6854 | 152_366 | <25mph | <15mph | HFTD - Transmission
PG&E | 42628 | 0.66389 | 37.1102 | -121.9509 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100520198 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42628 | 0.66389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0982 | 2016 | 9 | 15 | 15 | 56 | 16-0065001 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 28900 | 4.7461 | 163_321 | <25mph | <15mph | HFTD - Distribution
PG&E | 42629.8722 | 42629.8722 | 39.8387 | -121.7023 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 100441760 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42629.8722 | 42629.8722 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0983 | 2016 | 9 | 16 | 20 | 56 | 16-0065273 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 314427 | 7.2098 | 158_190 | <25mph | <15mph | HFTD - Distribution
PG&E | 42631 | 0.60625 | 37.1619 | -122.1347 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire & Boulder Creek Fire Dept. | 103410909 | Yes | 12000 | Conductor | Overhead | Yes | 42631 | 0.60625 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0986 | 2016 | 9 | 18 | 14 | 33 | 16-0065437 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 54983 | 2.5115 | 238_190 | <25mph | <15mph | HFTD - Distribution
PG&E | 42633 | 0.35069 | 40.0044 | -123.7871 | Vegetation | RURAL | < 3 meters | Self Extinguished | N.A. | 100992643 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42633 | 0.35069 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0990 | 2016 | 9 | 20 | 8 | 25 | 16-0065910 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 798 | 5.007 | 188_237 | <25mph | <15mph | HFTD - Distribution
PG&E | 42634 | 0.41736 | 39.1173 | -121.071 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100014315 | PACIFIC BELL | 115000 | Conductor | Overhead | Yes | 42634 | 0.41736 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0991 | 2016 | 9 | 21 | 10 | 1 | INT-08560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 7.6506 | 82_351 | <25mph | <15mph | HFTD - Transmission
PG&E | 42635 | 0.57847 | 40.224 | -122.3417 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101539450 | None | 12000 | Conductor | Overhead | Yes | 42635 | 0.57847 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0996 | 2016 | 9 | 22 | 13 | 53 | 16-0066692 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 14706 | 13.7018 | 196_291 | <25mph | <15mph | HFTD - Distribution
PG&E | 42636.2243 | 0.64097 | 39.3784 | -121.0922 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100091491 | None | 12000 | Conductor | Overhead | Yes | 42636.2243 | 0.64097 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0999 | 2016 | 9 | 23 | 15 | 23 | 16-0067089 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 80185 | 4.2958 | 195_315 | <25mph | <15mph | HFTD - Distribution
PG&E | 42638 | 0.80486 | 37.0993 | -122.1155 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire ben lomond fire | 101670837 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42638 | 0.80486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1003 | 2016 | 9 | 25 | 19 | 19 | 16-0067346 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1497 | 19.163 | 160_313 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42638.441 | 42638.441 | 38.8019 | -122.8176 | Vegetation | RURAL | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103613996 |  | 115000 | Other | Overhead | Yes | 42638.441 | 42638.441 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1004 | 2016 | 9 | 25 | 10 | 35 | INT-08572 | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Equip Failure - Other | 0 | 6.4295 | 256_169 | <25mph | <15mph | HFTD - Transmission
PG&E | 42639 | 0.44444 | 38.0157 | -122.6889 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | marin county fire | 102252082 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42639 | 0.44444 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1005 | 2016 | 9 | 26 | 10 | 40 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 8.4538 | 150_190 | <25mph | <15mph | HFTD - Distribution
PG&E | 42641 | 0.58333 | 35.2145 | -118.5625 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire |  |  | 0 – 750 | Conductor | Overhead | Yes | 42641 | 0.58333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1008 | 2016 | 9 | 28 | 14 | 0 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 14.543 | 186_244 | <25mph | <15mph | HFTD - Distribution
PG&E | 42644.6455 | 0.63819 | 39.4384 | -120.816 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | State goverment forestry | 100112411 |  | 12000 | Conductor | Overhead | Yes | 42644.6455 | 0.63819 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1011 | 2016 | 10 | 1 | 15 | 19 | 16-0068934 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6157 | 10.5833 | 171_240 | <25mph | <15mph | HFTD - Distribution
PG&E | 42645.6954 | 0.69514 | 39.8888 | -121.6648 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103358082 |  | 12000 | Other | Overhead | Yes | 42645.6954 | 0.69514 | Other | N.A. | N.A. | N.A. | Weather | lightning strike | Other/Unknown | 1013 | 2016 | 10 | 2 | 16 | 41 | 16-0069050 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 339550 | 21.9592 | 150_251 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42651.6284 | 0.62778 | 38.6686 | -120.9091 | Vegetation | RURAL | < 0.25 Acres | Customer | N.A. | 101380856 |  | 0 – 750 | Capacitor Bank | Overhead | Yes | 42651.6284 | 0.62778 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1021 | 2016 | 10 | 8 | 15 | 4 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 4.4845 | 168_326 | <25mph | <15mph | HFTD - Distribution
PG&E | 42651.6884 | 0.68819 | 39.0099 | -122.6145 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102152342 |  | 0 – 750 | Transformer | Overhead | Yes | 42651.6884 | 0.68819 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1022 | 2016 | 10 | 8 | 16 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 9.8555 | 203_276 | <25mph | <15mph | HFTD - Distribution
PG&E | 42652.7862 | 0.78611 | 38.656 | -120.9725 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101376768 |  | 12000 | Conductor | Overhead | Yes | 42652.7862 | 0.78611 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1024 | 2016 | 10 | 9 | 18 | 52 | 16-0070676 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 98361 | 10.5578 | 223_213 | <25mph | <15mph | HFTD - Distribution
PG&E | 42654.9701 | 0.96944 | 39.0201 | -120.8294 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire.foresthill fire | 100025501 |  | 60000 | Conductor | Overhead | Yes | 42654.9701 | 0.96944 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error |  | no-match | 1028 | 2016 | 10 | 11 | 23 | 16 | INT-08640 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 0 | 8.4037 | 252_173 | <25mph | <15mph | HFTD - Transmission
PG&E | 42656.9745 | 0.96806 | 40.4901 | -122.3729 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | SHASTA COUNTY FIRE | 101502366 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42656.9745 | 0.96806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1029 | 2016 | 10 | 13 | 23 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.7485 | 207_295 | <25mph | <15mph | HFTD - Distribution
PG&E | 42657.0644 | 0.063889 | 40.5007 | -121.9162 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101489328 |  | 12000 | Conductor | Overhead | Yes | 42657.0644 | 0.063889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1031 | 2016 | 10 | 14 | 1 | 32 | 16-0071832 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 213622 | 25.3168 | 148_336 | 25-40mph | >=15mph | HFTD - Distribution
PG&E | 42657.1893 | 0.18889 | 40.5228 | -121.6813 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101513661 |  | 12000 | Conductor | Overhead | Yes | 42657.1893 | 0.18889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1032 | 2016 | 10 | 14 | 4 | 32 | 16-0071897 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 38950 | 32.5033 | 161_377 | 25-40mph | >=15mph | HFTD - Distribution
PG&E | 42657.8228 | 0.82222 | 39.6245 | -121.5382 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100435570 |  | 0 – 750 | Conductor | Overhead | Yes | 42657.8228 | 0.82222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1036 | 2016 | 10 | 14 | 19 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 19.7872 | 174_288 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42662.4459 | 0.44583 | 38.5098 | -122.45 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | st helena | 102242552 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42662.4459 | 0.44583 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1040 | 2016 | 10 | 19 | 10 | 42 | 16-0073955 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 693 | 0.79097 | 128_266 | <25mph | <15mph | HFTD - Distribution
PG&E | 42666.7804 | 0.75694 | 38.021 | -120.5991 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101272943 |  | 115000 | Conductor | Overhead | Yes | 42666.7804 | 0.75694 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1043 | 2016 | 10 | 23 | 18 | 10 | INT-08709 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 0 | 4.06 | 197_252 | <25mph | <15mph | HFTD - Transmission
PG&E | 42683 | 0.37917 | 37.4532 | -119.6413 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | US FOREST SERVICE | 101017062 |  | 12000 | Conductor | Overhead | Yes | 42683 | 0.37917 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1046 | 2016 | 11 | 9 | 9 | 6 | 16-0078863 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1586 | 10.2493 | 255_166 | <25mph | <15mph | HFTD - Distribution
PG&E | 42688 | 0.55208 | 35.4577 | -120.4619 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101895511 |  | 21000 | Conductor | Overhead | Yes | 42688 | 0.55208 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1048 | 2016 | 11 | 14 | 13 | 15 | 16-0079725 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 19590 | 3.8625 | 205_98 | <25mph | <15mph | HFTD - Distribution
PG&E | 42689 | 0.72708 | 39.7275 | -121.6557 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100327525 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42689 | 0.72708 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 1049 | 2016 | 11 | 15 | 17 | 27 | 16-0080083 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 69231 | 19.4119 | 224_99 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42694 | 0.46111 | 39.6326 | -123.7823 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102200173 |  | 12000 | Conductor | Overhead | Yes | 42694 | 0.46111 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1050 | 2016 | 11 | 20 | 11 | 4 | 16-0081252 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 87261 | 14.3443 | 172_334 | <25mph | <15mph | HFTD - Distribution
PG&E | 42829.567 | 0.56181 | 35.6885 | -120.7653 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101945026 | None | 12000 | Conductor | Overhead | Yes | 42829.567 | 0.56181 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1064 | 2017 | 4 | 4 | 13 | 29 | 17-0036460 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 167151 | 2.8226 | 201_194 | <25mph | <15mph | HFTD - Distribution
PG&E | 42850.5271 | 0.52639 | 38.6583 | -120.9762 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101376746 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 42850.5271 | 0.52639 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1072 | 2017 | 4 | 25 | 12 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 15.4643 | 193_139 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42853.6815 | 0.65903 | 38.7679 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chris paper fire investigator, 530/677-1868. incident #caaeuo11821 | 101409833 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42853.6815 | 0.65903 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1077 | 2017 | 4 | 28 | 15 | 49 | 17-0043771 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 82614 | 13.1464 | 172_191 | <25mph | <15mph | HFTD - Distribution
PG&E | 42854.6453 | 0.62986 | 37.0349 | -119.5242 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100678661 | Unknown | 12000 | Conductor | Overhead | Yes | 42854.6453 | 0.62986 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1078 | 2017 | 4 | 29 | 15 | 7 | 17-0043911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 4.7079 | 201_281 | <25mph | <15mph | HFTD - Distribution
PG&E | 42855.3995 | 0.39722 | 35.6349 | -118.9563 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 661-324-6551 | 100216308 | Unknown | 21000 | Conductor | Overhead | Yes | 42855.3995 | 0.39722 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1079 | 2017 | 4 | 30 | 9 | 32 | 17-0043980 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 3065 | 11.9815 | 265_186 | <25mph | <15mph | HFTD - Distribution
PG&E | 42860.6614 | 15:52 | 40.3776 | -123.0019 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101501566 | None | 12000 | Conductor | Overhead | Yes | 42860.6614 | 15:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1084 | 2017 | 5 | 5 | 15 | 52 | 17-0045707 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 56893 | 8.6675 | 211_104 | <25mph | <15mph | HFTD - Distribution
PG&E | 42861.4744 | 0.47083 | 40.7951 | -124.029 | Vegetation | Rural | < 3 Meters | Fire Agency | chief rick harden 7074423352 | 103661154 | Unknown | 12000 | Conductor | Overhead | Yes | 42861.4744 | 0.47083 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1086 | 2017 | 5 | 6 | 11 | 18 | 17-0045785 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 113630 | 18.8851 | 207_202 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42864.7782 | 0.76806 | 40.8689 | -123.5156 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | todd wright fire chief. 5307392493 | 103796045 | Unknown | 12000 | Conductor | Overhead | Yes | 42864.7782 | 0.76806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1092 | 2017 | 5 | 9 | 18 | 26 | 17-0046642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 108117 | 13.9105 | 163_324 | <25mph | <15mph | HFTD - Distribution
PG&E | 42869 | 0.49931 | 38.0798 | -122.8665 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102247059 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42869 | 0.49931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1095 | 2017 | 5 | 14 | 11 | 59 | 17-0047802 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 377483 | 10.9708 | 166_332 | <25mph | <15mph | HFTD - Distribution
PG&E | 42870 | 0.12847 | 35.6261 | -120.8962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101873299 | Unknown | 21000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1097 | 2017 | 5 | 15 | 3 | 5 | 17-0047837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 337188 | 3.2091 | 260_107 | <25mph | <15mph | HFTD - Distribution
PG&E | 42870.6767 | 0.66667 | 37.1766 | -119.8189 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SHAUN FAIRBANKS 559-683-4823 | 101108423 | SIERRA | 21000 | Conductor | Overhead | Yes | 42870.6767 | 0.66667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1099 | 2017 | 5 | 15 | 16 | 0 | 17-0048096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20007 | 7.5963 | 182_250 | <25mph | <15mph | HFTD - Distribution
PG&E | 42879.6837 | 16:24 | 38.834 | -121.1197 | Vegetation | Rural | < 3 Meters | Fire Agency | Fire Capt | 103838109 | None | 12000 | Conductor | Overhead | Yes | 42879.6837 | 16:24 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | no-match | 1111 | 2017 | 5 | 24 | 16 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 12.3303 | 181_225 | <25mph | <15mph | HFTD - Distribution
PG&E | 42880.6288 | 0.62847 | 36.5217 | -121.8473 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Buddy Bloxham 831-236-5659 | 101778611 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42880.6288 | 0.62847 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1113 | 2017 | 5 | 25 | 15 | 5 | 17-0050761 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 13965 | 8.0348 | 161_209 | <25mph | <15mph | HFTD - Distribution
PG&E | 42880.7334 | 0.70486 | 38.3986 | -122.9876 | Vegetation | Rural | < 3 Meters | Utility: PG&E | N.A. | 101974034 | Unknown | 12000 | Conductor | Overhead | Yes | 42880.7334 | 0.70486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1114 | 2017 | 5 | 25 | 16 | 55 | 17-0050815 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 2644 | 5.2896 | 162_158 | <25mph | <15mph | HFTD - Distribution
PG&E | 42884.7708 | 18:29 | 39.2245 | -121.3753 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101304842 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1115 | 2017 | 5 | 29 | 18 | 29 | 17-0051324 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 616 | 9.0109 | 114_262 | <25mph | <15mph | HFTD - Distribution
PG&E | 42889.5662 | 0.55972 | 38.9017 | -121.2056 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100043664 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42889.5662 | 0.55972 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1122 | 2017 | 6 | 3 | 13 | 26 | 17-0052543 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29512 | 18.651 | 172_165 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42894.6382 | 0.63056 | 34.6058 | -120.0214 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SHAWN STEINER | 101947678 | Unknown | 12000 | Conductor | Overhead | Yes | 42894.6382 | 0.63056 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1136 | 2017 | 6 | 8 | 15 | 8 | 17-0053783 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 41311 | 13.9971 | 231_142 | <25mph | <15mph | HFTD - Distribution
PG&E | 42896.3177 | 07:37 | 35.4359 | -120.4957 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101890429 | Unknown | 21000 | Conductor | Overhead | Yes | 42896.3177 | 07:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1140 | 2017 | 6 | 10 | 7 | 37 | 17-0054182 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 34397 | 6.9076 | 220_118 | <25mph | <15mph | HFTD - Distribution
PG&E | 42899 | 0.60417 | 37.8526 | -122.1853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Tower 005/035c | Unknown | 115000 | Conductor | Overhead | Yes | 42899 | 0.60417 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1143 | 2017 | 6 | 13 | 14 | 30 | INT-09744 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | Balloons | 0 | 10.8472 | 298_95 | <25mph | <15mph | HFTD - Transmission
PG&E | 42901.1885 | 0.12361 | 40.299 | -122.4318 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101511631 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42901.1885 | 0.12361 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | Other/Unknown | 1145 | 2017 | 6 | 15 | 2 | 58 | 17-0055359 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1762 | 8.3679 | 174_336 | <25mph | <15mph | HFTD - Distribution
PG&E | 42901.3391 | 0.31875 | 39.2276 | -121.2348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE CHIEF | 103676075 | Unknown | 21000 | Conductor | Overhead | Yes | 42901.3391 | 0.31875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1147 | 2017 | 6 | 15 | 7 | 39 | 17-0055387 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 740 | 14.5193 | 170_174 | <25mph | <15mph | HFTD - Distribution
PG&E | 42901.6279 | 0.62569 | 39.3913 | -123.3054 | Vegetation | Rural | < 0.25 Acres | Fire Agency | STEPHEN | 103838176 | YES | 12000 | Conductor | Overhead | Yes | 42901.6279 | 0.62569 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1148 | 2017 | 6 | 15 | 15 | 1 | 17-0055557 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 180469 | 8.5012 | 189_307 | <25mph | <15mph | HFTD - Distribution
PG&E | 42902.8019 | 19:14 | 38.3443 | -122.7812 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101970801 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42902.8019 | 19:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1155 | 2017 | 6 | 16 | 19 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.1691 | 154_201 | <25mph | <15mph | HFTD - Distribution
PG&E | 42902.9378 | 22:30 | 38.0373 | -122.1847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101424286 | Unknown | 21000 | Conductor | Overhead | Yes | 42902.9378 | 22:30 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1156 | 2017 | 6 | 16 | 22 | 30 | 17-0055882 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 12000 | 12.3152 | 122_259 | <25mph | <15mph | HFTD - Distribution
PG&E | 42906.638 | 0.49375 | 40.3156 | -124.0611 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101006039 | Unknown | 12000 | Conductor | Overhead | Yes | 42906.638 | 0.49375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1180 | 2017 | 6 | 20 | 11 | 51 | 17-0057001 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 9256 | 19.7543 | 152_235 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42908.4214 | 0.4 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 0.4 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 2.7323 | 184_294 | <25mph | <15mph | HFTD - Distribution
PG&E | 42908.7461 | 0.75486 | 38.7583 | -120.7176 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101401088 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.7461 | 0.75486 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1188 | 2017 | 6 | 22 | 18 | 7 | 17-0057857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 8517 | 17.5701 | 170_328 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42909.5421 | 13:00 | 39.3051 | -122.4862 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 100329817 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42909.5421 | 13:00 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | no-match | 1190 | 2017 | 6 | 23 | 13 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 21.3005 | 214_106 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42910.439 | 0.43819 | 38.9438 | -121.0447 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100090318 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42910.439 | 0.43819 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1193 | 2017 | 6 | 24 | 10 | 31 | 17-0058318 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 582 | 2.1474 | 145_371 | <25mph | <15mph | HFTD - Distribution
PG&E | 42910.6292 | 0.61875 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 42910.6292 | 0.61875 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1194 | 2017 | 6 | 24 | 14 | 51 | 17-0058332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 21296 | 6.659 | 198_291 | <25mph | <15mph | HFTD - Distribution
PG&E | 42910.9354 | 0.93542 | 38.2908 | -120.849 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CONTACT BOBBY BOWMAN | 101238865 | None | 12000 | Conductor | Overhead | Yes | 42910.9354 | 0.93542 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1195 | 2017 | 6 | 24 | 22 | 27 | 17-0058399 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 4529 | 6.6062 | 210_259 | <25mph | <15mph | HFTD - Distribution
PG&E | 42911.1159 | 0.015972 | 39.4043 | -123.3869 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102193088 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42911.1159 | 0.015972 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1197 | 2017 | 6 | 25 | 0 | 23 | 17-0058406 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 23100 | 17.871 | 98_318 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42913.3944 | 0.39097 | 37.9559 | -122.6176 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | marin county fire | 102260068 | UNFILED | 12000 | Conductor | Overhead | Yes | 42913.3944 | 0.39097 | Other | N.A. | N.A. | N.A. | Unknown |  | Fell into (slight defect) | 1203 | 2017 | 6 | 27 | 9 | 23 | 17-0058882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 3920 | 3.9699 | 239_128 | <25mph | <15mph | HFTD - Distribution
PG&E | 42916.0559 | 01:20 | 39.821 | -121.5883 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103840463 | YES | 12000 | Conductor | Overhead | Yes | 42916.0559 | 01:20 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1210 | 2017 | 6 | 30 | 1 | 20 | 17-0059647 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 2888 | 5.9412 | 174_339 | <25mph | <15mph | HFTD - Distribution
PG&E | 42916.9965 | 23:54 | 38.5794 | -122.8835 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 101958804 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42916.9965 | 23:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1211 | 2017 | 6 | 30 | 23 | 54 | 17-0059922 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2025 | 8.1196 | 176_296 | <25mph | <15mph | HFTD - Distribution
PG&E | 42917 | 0.50139 | 39.8209 | -121.6418 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 003/039 | Unknown | 60000 | Conductor | Overhead | Yes | 42917 | 0.50139 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1212 | 2017 | 7 | 1 | 12 | 2 | INT-09792 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 22.7396 | 118_272 | <25mph | >=15mph | HFTD - Transmission
PG&E | 42917.1963 | 0.13333 | 38.1952 | -122.9197 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103855493 | Unknown | 12000 | Conductor | Overhead | Yes | 42917.1963 | 0.13333 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1214 | 2017 | 7 | 1 | 3 | 12 | 17-0059935 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 41370 | 18.3492 | 245_184 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42918 | 0.56111 | 39.8605 | -121.6274 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 000/017c | Unknown | 60000 | Conductor | Overhead | Yes | 42918 | 0.56111 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1216 | 2017 | 7 | 2 | 13 | 28 | INT-09794 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 4.7144 | 172_339 | <25mph | <15mph | HFTD - Transmission
PG&E | 42919.853 | 0.85139 | 38.7923 | -120.9438 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101388730 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42919.853 | 0.85139 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1218 | 2017 | 7 | 3 | 20 | 26 | 17-0060336 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 8134 | 7.9271 | 173_342 | <25mph | <15mph | HFTD - Distribution
PG&E | 42920.8451 | 20:16 | 40.4228 | -122.3975 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SCOTT CORN 530-448-2414 | 101481860 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42920.8451 | 20:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1221 | 2017 | 7 | 4 | 20 | 16 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 8.1896 | 194_287 | <25mph | <15mph | HFTD - Distribution
PG&E | 42921.5077 | 0.49861 | 39.2105 | -121.2266 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVE ROBERTSON 530 906 4892 | 100010286 | Unknown | 21000 | Conductor | Overhead | Yes | 42921.5077 | 0.49861 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1223 | 2017 | 7 | 5 | 11 | 58 | 17-0060605 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 10231 | 9.9712 | 199_277 | <25mph | <15mph | HFTD - Distribution
PG&E | 42923 | 0.63125 | 40.9054 | -122.3806 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101455950 | Unknown | 12000 | Conductor | Overhead | Yes | 42923 | 0.63125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1229 | 2017 | 7 | 7 | 15 | 9 | 17-0061903 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 20.461 | 211_104 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42923.8675 | 0.60486 | 37.499 | -119.799 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVEN WARD OFFICE 209-966-3542 CELL559-706-8811 | 103855637 | Unknown | 21000 | Conductor | Overhead | Yes | 42923.8675 | 0.60486 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1230 | 2017 | 7 | 7 | 14 | 31 | 17-0061288 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 554306 | 15.7731 | 252_212 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42924.8076 | 0.78403 | 40.2935 | -122.4089 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | TOM STROING, RED BLUFF | 101526269 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42924.8076 | 0.78403 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1234 | 2017 | 7 | 8 | 18 | 49 | 17-0061469 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 157484 | 7.5087 | 140_366 | <25mph | <15mph | HFTD - Distribution
PG&E | 42926.5237 | 0.52222 | 40.2603 | -123.8253 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103139646 | Unknown | 12000 | Conductor | Overhead | Yes | 42926.5237 | 0.52222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1238 | 2017 | 7 | 10 | 12 | 32 | 17-0061771 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 5910 | 8.9892 | 189_250 | <25mph | <15mph | HFTD - Distribution
PG&E | 42926.75 | 0.70833 | 37.3768 | -122.3597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | David Hibdon 831-254-1763 | 100270370 | Unknown | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1240 | 2017 | 7 | 10 | 17 | 0 | 17-0061857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3322 | 6.5916 | 206_182 | <25mph | <15mph | HFTD - Distribution
PG&E | 42927.9254 | 22:12 | 37.0122 | -121.9497 | Vegetation | Rural | < 3 Meters | Fire Agency | CAPT PHIL CRAMBLET 831-479-6842 | 101676689 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42927.9254 | 22:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1244 | 2017 | 7 | 11 | 22 | 12 | 17-0062198 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 714 | 3.9543 | 169_319 | <25mph | <15mph | HFTD - Distribution
PG&E | 42928 | 0.66944 | 40.6531 | -122.3343 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 000/001 | Unknown | 60000 | Conductor | Overhead | Yes | 42928 | 0.66944 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1245 | 2017 | 7 | 12 | 16 | 4 | INT-09837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 9.5513 | 158_185 | <25mph | <15mph | HFTD - Transmission
PG&E | 42928.6313 | 15:09 | 37.1491 | -122.0037 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 103565794 | Unknown | 21000 | Conductor | Overhead | Yes | 42928.6313 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1248 | 2017 | 7 | 12 | 15 | 9 | 17-0062439 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24690 | 5.2663 | 155_192 | <25mph | <15mph | HFTD - Distribution
PG&E | 42928.8485 | 20:21 | 40.0808 | -123.8339 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103841917 | Unknown | 12000 | Conductor | Overhead | Yes | 42928.8485 | 20:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1249 | 2017 | 7 | 12 | 20 | 21 | 17-0062445 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 4616 | 2.2363 | 143_386 | <25mph | <15mph | HFTD - Distribution
PG&E | 42931.6076 | 14:34 | 39.6231 | -121.5328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | russ fowler | 100404385 | Unknown | 12000 | Conductor | Overhead | Yes | 42931.6076 | 14:34 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1254 | 2017 | 7 | 15 | 14 | 34 | 17-0063126 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 54372 | 7.7421 | 187_223 | <25mph | <15mph | HFTD - Distribution
PG&E | 42932.4443 | 10:39 | 40.3414 | -123.8786 | Vegetation | Rural | < 3 Meters | Fire Agency | 707-726-1280 | 100990019 | Unknown | 12000 | Conductor | Overhead | Yes | 42932.4443 | 10:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1258 | 2017 | 7 | 16 | 10 | 39 | 17-0063223 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 198 | 11.3029 | 163_251 | <25mph | <15mph | HFTD - Distribution
PG&E | 42932.4994 | 11:59 | 36.6669 | -121.7515 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101761892 | None | 21000 | Fuse | Overhead | Yes | 42932.4994 | 11:59 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1259 | 2017 | 7 | 16 | 11 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 11.8584 | 78_370 | <25mph | <15mph | HFTD - Distribution
PG&E | 42932.5072 | 12:10 | 35.6613 | -120.922 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101942626 | Unknown | 21000 | Conductor | Overhead | Yes | 42932.5072 | 12:10 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1260 | 2017 | 7 | 16 | 12 | 10 | 17-0063242 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 1304 | 15.4796 | 166_166 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42934 | 0.47917 | 38.0484 | -120.5565 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 012/071 | Unknown | 115000 | Conductor | Overhead | Yes | 42934 | 0.47917 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1265 | 2017 | 7 | 18 | 11 | 30 | INT-09873 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 55499 | 0.58112 | 157_288 | <25mph | <15mph | HFTD - Transmission
PG&E | 42934 | 0.90278 | 38.0031 | -122.2093 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | Pole 000/002 to 000/003 | Unknown | 60000 | Conductor | Overhead | Yes | 42934 | 0.90278 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1266 | 2017 | 7 | 18 | 21 | 40 | INT-09875 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 0 | 7.8402 | 219_243 | <25mph | <15mph | HFTD - Transmission
PG&E | 42935 | 0.24444 | 37.0905 | -119.6047 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Tower 003/001 | Unknown | 115000 | Conductor | Overhead | Yes | 42935 | 0.24444 | Contact From Object | N.A. | Other | Electric Facility | Unknown |  | no-match | 1269 | 2017 | 7 | 19 | 5 | 52 | INT-09877 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 0 | 19.5055 | 147_239 | <25mph | >=15mph | HFTD - Transmission
PG&E | 42936.5736 | 13:45 | 35.0804 | -120.5538 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | PAUL LEE 805 903-3416 INC # 8291 | 101941116 | Unknown | 12000 | Conductor | Overhead | Yes | 42936.5736 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1275 | 2017 | 7 | 20 | 13 | 45 | 17-0064321 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 45999 | 7.409 | 220_78 | <25mph | <15mph | HFTD - Distribution
PG&E | 42938.518 | 12:25 | 40.8795 | -123.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Josh , comander chief of forest service. | 100980577 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.518 | 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1279 | 2017 | 7 | 22 | 12 | 25 | 17-0064721 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 23227 | 4.3128 | 183_408 | <25mph | <15mph | HFTD - Distribution
PG&E | 42938.6101 | 14:38 | 37.2994 | -122.1631 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100265488 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.6101 | 14:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1280 | 2017 | 7 | 22 | 14 | 38 | 17-0064738 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49181 | 8.7219 | 84_399 | <25mph | <15mph | HFTD - Distribution
PG&E | 42939.3906 | 09:22 | 40.642 | -122.2302 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT? | 101459708 | FRONTIER COMMUNICATI | 12000 | Conductor | Overhead | Yes | 42939.3906 | 09:22 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1282 | 2017 | 7 | 23 | 9 | 22 | 17-0064801 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 184712 | 2.8969 | 72_397 | <25mph | <15mph | HFTD - Distribution
PG&E | 42939.7676 | 18:25 | 39.6723 | -123.5336 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103823226 | Unknown | 12000 | Conductor | Overhead | Yes | 42939.7676 | 18:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1284 | 2017 | 7 | 23 | 18 | 25 | 17-0064854 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 12864 | 8.0612 | 252_142 | <25mph | <15mph | HFTD - Distribution
PG&E | 42940.5845 | 14:01 | 37.2635 | -122.3364 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike klink 650-879-0121 | 100322130 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42940.5845 | 14:01 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1286 | 2017 | 7 | 24 | 14 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 3.8678 | 248_141 | <25mph | <15mph | HFTD - Distribution
PG&E | 42940.8134 | 19:31 | 38.3519 | -120.7103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.8134 | 19:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1288 | 2017 | 7 | 24 | 19 | 31 | 17-0065145 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14281 | 17.496 | 157_198 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42940.9063 | 21:45 | 35.6024 | -120.9211 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101860186 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.9063 | 21:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1289 | 2017 | 7 | 24 | 21 | 45 | 17-0065191 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 21231 | 11.402 | 212_258 | <25mph | <15mph | HFTD - Distribution
PG&E | 42941.6609 | 15:51 | 38.3779 | -122.5388 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102031447 | Unknown | 12000 | Conductor | Overhead | Yes | 42941.6609 | 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1290 | 2017 | 7 | 25 | 15 | 51 | 17-0065437 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 18584 | 28.0096 | 203_107 | 25-40mph | >=15mph | HFTD - Distribution
PG&E | 42941.8004 | 19:12 | 39.5997 | -121.4449 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100403612 | Unknown | 12000 | Conductor | Overhead | Yes | 42941.8004 | 19:12 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1291 | 2017 | 7 | 25 | 19 | 12 | 17-0065453 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 68452 | 6.0359 | 133_260 | <25mph | <15mph | HFTD - Distribution
PG&E | 42944 | 0.58472 | 40.9997 | -121.9579 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101512624 | Unknown | 12000 | Conductor | Overhead | Yes | 42944 | 0.58472 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1293 | 2017 | 7 | 28 | 14 | 2 | 17-0066367 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 46581 | 16.7844 | 255_172 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42944.8062 | 19:20 | 35.7276 | -120.9903 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Luis Obispo CDF | 101945496 | None | 21000 | Conductor | Overhead | Yes | 42944.8062 | 19:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1295 | 2017 | 7 | 28 | 19 | 20 | 17-0066392 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 8300 | 9.3286 | 200_100 | <25mph | <15mph | HFTD - Distribution
PG&E | 42945.5612 | 13:28 | 35.4523 | -120.3834 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101889516 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42945.5612 | 13:28 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1297 | 2017 | 7 | 29 | 13 | 28 | 17-0066472 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 1962 | 2.836 | 180_320 | <25mph | <15mph | HFTD - Distribution
PG&E | 42946.4075 | 09:46 | 38.9132 | -122.6179 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike wink | 102151066 | None | 0 – 750 | Conductor | Overhead | Yes | 42946.4075 | 09:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1302 | 2017 | 7 | 30 | 9 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 14.1728 | 217_98 | <25mph | <15mph | HFTD - Distribution
PG&E | 42947.6123 | 14:41 | 38.7967 | -121.1329 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103782414 | Unknown | 12000 | Conductor | Overhead | Yes | 42947.6123 | 14:41 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1305 | 2017 | 7 | 31 | 14 | 41 | 17-0066797 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 210 | 7.6453 | 194_283 | <25mph | <15mph | HFTD - Distribution
PG&E | 42949 | 0.40417 | 39.2274 | -123.1081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 5/0 | None | 60000 | Conductor | Overhead | Yes | 42949 | 0.40417 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1307 | 2017 | 8 | 2 | 9 | 42 | INT-09925 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 8.5295 | 266_132 | <25mph | <15mph | HFTD - Transmission
PG&E | 42949.251 | 0.24583 | 40.7986 | -123.3961 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 100974913 | Unknown | 12000 | Conductor | Overhead | Yes | 42949.251 | 0.24583 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1308 | 2017 | 8 | 2 | 5 | 54 | 17-0067270 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 5832 | 5.8454 | 99_395 | <25mph | <15mph | HFTD - Distribution
PG&E | 42950.4588 | 0.45347 | 39.0732 | -121.0868 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100072742 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42950.4588 | 0.45347 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1312 | 2017 | 8 | 3 | 10 | 53 | 17-0067679 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 127440 | 10.4975 | 216_206 | <25mph | <15mph | HFTD - Distribution
PG&E | 42952.3565 | 08:33 | 38.4583 | -120.8695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JEFF MICHEL- 530 409 2223 | 101236223 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42952.3565 | 08:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1317 | 2017 | 8 | 5 | 8 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 15.2043 | 215_108 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42952.7592 | 0.75556 | 39.0968 | -123.2147 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102196629 | Unknown | 12000 | Conductor | Overhead | Yes | 42952.7592 | 0.75556 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1318 | 2017 | 8 | 5 | 18 | 8 | 17-0068200 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 134239 | 10.1422 | 205_264 | <25mph | <15mph | HFTD - Distribution
PG&E | 42953.4849 | 11:38 | 36.5857 | -121.7121 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101747125 | Unknown | 12000 | Conductor | Overhead | Yes | 42953.4849 | 11:38 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1321 | 2017 | 8 | 6 | 11 | 38 | 17-0068279 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 87172 | 9.4859 | 261_172 | <25mph | <15mph | HFTD - Distribution
PG&E | 42955.1829 | 0.17361 | 38.4949 | -122.6685 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 102025742 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42955.1829 | 0.17361 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1325 | 2017 | 8 | 8 | 4 | 10 | 17-0068642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 2750 | 9.3483 | 127_267 | <25mph | <15mph | HFTD - Distribution
PG&E | 42955.4775 | 11:27 | 37.0445 | -121.6343 | Vegetation | Urban | < 3 Meters | Utility: PG&E | N.A. | 100613200 | VERIZON CALIFORNIA | 21000 | Capacitor Bank | Overhead | Yes | 42955.4775 | 11:27 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | Other/Unknown | 1326 | 2017 | 8 | 8 | 11 | 27 | 17-0068774 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | 34192 | 1.2124 | 172_186 | <25mph | <15mph | HFTD - Distribution
PG&E | 42955.8578 | 20:35 | 37.2637 | -119.7103 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TROY CHEEK1-209-966-3621 | 103793352 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42955.8578 | 20:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1327 | 2017 | 8 | 8 | 20 | 35 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.6137 | 125_264 | <25mph | <15mph | HFTD - Distribution
PG&E | 42956.4786 | 11:29 | 38.6532 | -120.6273 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101402496 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42956.4786 | 11:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1328 | 2017 | 8 | 9 | 11 | 29 | 17-0069107 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 54216 | 10.9179 | 256_199 | <25mph | <15mph | HFTD - Distribution
PG&E | 42959.3812 | 09:08 | 34.6689 | -120.0286 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103391912 | Unknown | 12000 | Conductor | Overhead | Yes | 42959.3812 | 09:08 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | wire cut | Other/Unknown | 1330 | 2017 | 8 | 12 | 9 | 8 | 17-0069829 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 26070 | 6.4092 | 201_254 | <25mph | <15mph | HFTD - Distribution
PG&E | 42961 | 0.25972 | 40.1164 | -123.8064 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100986364 | Unknown | 12000 | Conductor | Overhead | Yes | 42961 | 0.25972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1332 | 2017 | 8 | 14 | 6 | 14 | 17-0070003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 959989 | 3.7729 | 123_268 | <25mph | <15mph | HFTD - Distribution
PG&E | 42961 | 0.99444 | 37.1272 | -122.1689 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 015/127 | None | 60000 | Conductor | Overhead | Yes | 42961 | 0.99444 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1333 | 2017 | 8 | 14 | 23 | 52 | INT-09976 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 1790869 | 11.9038 | 81_357 | <25mph | <15mph | HFTD - Transmission
PG&E | 42961.3308 | 07:56 | 39.1794 | -120.9761 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100083743 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42961.3308 | 07:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1334 | 2017 | 8 | 14 | 7 | 56 | 17-0070063 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3012 | 8.0138 | 200_304 | <25mph | <15mph | HFTD - Distribution
PG&E | 42962.8116 | 19:28 | 39.5037 | -121.2783 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 100396172 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42962.8116 | 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1335 | 2017 | 8 | 15 | 19 | 28 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.7124 | 148_191 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42964 | 0.63542 | 39.3703 | -121.0484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | PHIL MICHAEL 265-2894 INCIENT # CA NEV 21642 | 100083029 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42964 | 0.63542 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1338 | 2017 | 8 | 17 | 15 | 15 | 17-0071121 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 32850 | 11.7905 | 181_305 | <25mph | <15mph | HFTD - Distribution
PG&E | 42966 | 0.88611 | 40.5752 | -122.2985 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464623 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42966 | 0.88611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1341 | 2017 | 8 | 19 | 21 | 16 | 17-0071522 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 19044 | 6.2027 | 189_222 | <25mph | <15mph | HFTD - Distribution
PG&E | 42973 | 0.87014 | 38.7066 | -121.0193 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101382231 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42973 | 0.87014 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1350 | 2017 | 8 | 26 | 20 | 53 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.6104 | 128_265 | <25mph | <15mph | HFTD - Distribution
PG&E | 42974 | 0.83611 | 38.9165 | -121.151 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-477-0641 x7, log 22629 | 100077184 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42974 | 0.83611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1352 | 2017 | 8 | 27 | 20 | 4 | 17-0073228 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 905 | 8.9477 | 184_239 | <25mph | <15mph | HFTD - Distribution
PG&E | 42975 | 0.38472 | 38.7443 | -122.6491 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 103781085 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42975 | 0.38472 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1356 | 2017 | 8 | 28 | 9 | 14 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 17.9564 | 265_114 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42975 | 0.42153 | 39.0472 | -120.7859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | FORESTHILL | 100019525 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 0.42153 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1357 | 2017 | 8 | 28 | 10 | 7 | 17-0073379 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 10077 | 10.2849 | 128_281 | <25mph | <15mph | HFTD - Distribution
PG&E | 42975 | 0.5875 | 38.634 | -122.4194 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102253236 | Unknown | 21000 | Conductor | Overhead | Yes | 42975 | 0.5875 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1359 | 2017 | 8 | 28 | 14 | 6 | 17-0073526 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 1896 | 16.7686 | 208_222 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42975 | 0.62431 | 40.2853 | -123.8728 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 100990599 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 0.62431 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1361 | 2017 | 8 | 28 | 14 | 59 | 17-0073546 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2688 | 0.95829 | 138_274 | <25mph | <15mph | HFTD - Distribution
PG&E | 42976 | 0.53403 | 37.4507 | -119.6454 | Vegetation | Rural | > 5000 Acres | Fire Agency | USFS | 101017368 | Unknown | 12000 | Conductor | Overhead | Yes | 42976 | 0.53403 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1366 | 2017 | 8 | 29 | 12 | 49 | 17-0073823 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | 3rd Party | 3rd Party - Unknown | 5894785 | 1.7701 | 193_250 | <25mph | <15mph | HFTD - Distribution
PG&E | 42976 | 0.6625 | 38.302 | -122.5431 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 911 | 102026119 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 42976 | 0.6625 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1367 | 2017 | 8 | 29 | 15 | 54 | 17-0073928 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 485 | 8.2913 | 259_209 | <25mph | <15mph | HFTD - Distribution
PG&E | 42977 | 0.76458 | 40.6243 | -122.3039 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CASHU008896 | 103151338 | YES | 12000 | Conductor | Overhead | Yes | 42977 | 0.76458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1369 | 2017 | 8 | 30 | 18 | 21 | 17-0074287 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 76344 | 7.6808 | 287_94 | <25mph | <15mph | HFTD - Distribution
PG&E | 42977 | 0.94236 | 38.9993 | -120.9887 | Vegetation | Rural | < 3 Meters | Fire Agency | Andy 530-889-0111 | 100026238 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42977 | 0.94236 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1370 | 2017 | 8 | 30 | 22 | 37 | 17-0074333 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 3750 | 2.8977 | 145_384 | <25mph | <15mph | HFTD - Distribution
PG&E | 42978 | 0.27917 | 35.616 | -120.8577 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Derrick | 101860075 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 0.27917 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1372 | 2017 | 8 | 31 | 6 | 42 | 17-0074386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1620 | 12.4202 | 200_294 | <25mph | <15mph | HFTD - Distribution
PG&E | 42978 | 0.48125 | 37.1379 | -121.9966 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100519201 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 0.48125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1373 | 2017 | 8 | 31 | 11 | 33 | 17-0074457 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 99153 | 10.3974 | 206_107 | <25mph | <15mph | HFTD - Distribution
PG&E | 42979 | 0.33333 | 37.3757 | -119.8886 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101067028 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42979 | 0.33333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1378 | 2017 | 9 | 1 | 8 | 0 | 17-0074724 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 680 | 12.1778 | 213_139 | <25mph | <15mph | HFTD - Distribution
PG&E | 42979 | 0.74167 | 36.6518 | -121.7249 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MCFD | 103155761 | Unknown | 12000 | Conductor | Overhead | Yes | 42979 | 0.74167 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1382 | 2017 | 9 | 1 | 17 | 48 | 17-0074898 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 8152 | 3.6668 | 168_193 | <25mph | <15mph | HFTD - Distribution
PG&E | 42980 | 0.50069 | 37.6645 | -121.9223 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 100956020 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42980 | 0.50069 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1384 | 2017 | 9 | 2 | 12 | 1 | 17-0075132 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 7152 | 6.348 | 134_256 | <25mph | <15mph | HFTD - Distribution
PG&E | 42981 | 0.53611 | 37.2162 | -119.4807 | Vegetation | Rural | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103345573 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42981 | 0.53611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1388 | 2017 | 9 | 3 | 12 | 52 | 17-0075546 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 2362 | 10.8576 | 146_205 | <25mph | <15mph | HFTD - Distribution
PG&E | 42981 | 0.74444 | 37.4956 | -119.8367 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101086621 | Unknown | 21000 | Transformer | Overhead | Yes | 42981 | 0.74444 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 1389 | 2017 | 9 | 3 | 17 | 52 | 17-0075617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 4512 | 10.5097 | 266_196 | <25mph | <15mph | HFTD - Distribution
PG&E | 42982 | 0.14514 | 39.8317 | -121.8444 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102300100 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1392 | 2017 | 9 | 4 | 3 | 29 | 17-0075723 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 214974 | 4.6451 | 251_173 | <25mph | <15mph | HFTD - Distribution
PG&E | 42983 | 0.29028 | 39.6727 | -123.5128 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 102194697 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 42983 | 0.29028 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1395 | 2017 | 9 | 5 | 6 | 58 | 17-0075976 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10528 | 18.5256 | 176_318 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42984 | 0.80972 | 40.8392 | -122.3635 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103643183 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 0.80972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1399 | 2017 | 9 | 6 | 19 | 26 | 17-0076501 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 23830 | 10.8359 | 145_258 | <25mph | <15mph | HFTD - Distribution
PG&E | 42984 | 0.83889 | 37.2925 | -122.294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100256917 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 0.83889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1400 | 2017 | 9 | 6 | 20 | 8 | 17-0076502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4914 | 10.4084 | 142_396 | <25mph | <15mph | HFTD - Distribution
PG&E | 42986 | 0.19931 | 38.7478 | -120.859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101391575 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42986 | 0.19931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1401 | 2017 | 9 | 8 | 4 | 47 | 17-0076889 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 39736 | 11.6569 | 143_200 | <25mph | <15mph | HFTD - Distribution
PG&E | 42986 | 0.72292 | 38.6039 | -120.9275 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101379094 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42986 | 0.72292 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1402 | 2017 | 9 | 8 | 17 | 21 | 17-0077122 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 8504 | 6.2752 | 205_280 | <25mph | <15mph | HFTD - Distribution
PG&E | 42986 | 0.88472 | 37.9604 | -120.3764 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | John Lite 209-984-5623 | 101042521 | Unknown | 17000 | Conductor | Overhead | Yes | 42986 | 0.88472 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1403 | 2017 | 9 | 8 | 21 | 14 | 17-0077137 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49858 | 6.6561 | 203_272 | <25mph | <15mph | HFTD - Distribution
PG&E | 42989 | 0.30417 | 37.0008 | -121.6667 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100621936 | VERIZON CALIFORNIA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1407 | 2017 | 9 | 11 | 7 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.4109 | 220_201 | <25mph | <15mph | HFTD - Distribution
PG&E | 42989 | 0.36806 | 36.9515 | -121.842 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101790954 | PACIFIC BELL | 21000 | Fuse | Overhead | Yes | 42989 | 0.36806 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | no-match | 1408 | 2017 | 9 | 11 | 8 | 50 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | N.A. | 12.7091 | 170_184 | <25mph | <15mph | HFTD - Distribution
PG&E | 42990 | 0.39167 | 39.741 | -121.6079 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 911 | 100330302 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42990 | 0.39167 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1410 | 2017 | 9 | 12 | 9 | 24 | 17-0078149 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 402890 | 5.2759 | 70_399 | <25mph | <15mph | HFTD - Distribution
PG&E | 42992 | 0.5875 | 40.2942 | -123.8174 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100989497 | Unknown | 12000 | Conductor | Overhead | Yes | 42992 | 0.5875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1414 | 2017 | 9 | 14 | 14 | 6 | 17-0079010 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 19722 | 7.4403 | 176_322 | <25mph | <15mph | HFTD - Distribution
PG&E | 42993 | 0.62153 | 39.7461 | -121.4885 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100335239 | Unknown | 12000 | Conductor | Overhead | Yes | 42993 | 0.62153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1415 | 2017 | 9 | 15 | 14 | 55 | 17-0079388 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 8834 | 3.6247 | 81_367 | <25mph | <15mph | HFTD - Distribution
PG&E | 42995 | 0.73472 | 38.9946 | -121.0261 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100029537 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42995 | 0.73472 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Branch (OverHanging) | 1417 | 2017 | 9 | 17 | 17 | 38 | 17-0079585 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 28509 | 6.6998 | 271_165 | <25mph | <15mph | HFTD - Distribution
PG&E | 42996 | 0.54236 | 39.3889 | -121.4054 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 103795057 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42996 | 0.54236 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1418 | 2017 | 9 | 18 | 13 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 10.9535 | 198_294 | <25mph | <15mph | HFTD - Distribution
PG&E | 42996 | 0.99306 | 37.9088 | -120.4865 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | incident comander geoff marshall 209-419-4407 | 101040882 | Unknown | 17000 | Conductor | Overhead | Yes | 42996 | 0.99306 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1422 | 2017 | 9 | 18 | 23 | 50 | 17-0079858 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 382303 | 20.6164 | 120_244 | <25mph | >=15mph | HFTD - Distribution
PG&E | 42998 | 0.0875 | 37.2597 | -122.3222 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100322388 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42998 | 0.0875 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1424 | 2017 | 9 | 20 | 2 | 6 | 17-0080179 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 36593 | 13.2847 | 276_101 | <25mph | <15mph | HFTD - Distribution
PG&E | 43001 | 0.59514 | 40.6509 | -122.2974 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DARREN STEWART 448-2421 | 101467221 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43001 | 0.59514 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1429 | 2017 | 9 | 23 | 14 | 17 | 17-0081216 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 98820 | 11.0676 | 216_185 | <25mph | <15mph | HFTD - Distribution
PG&E | 43002 | 0.69583 | 38.3869 | -122.9667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DOUG JONES | 101973946 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43002 | 0.69583 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1432 | 2017 | 9 | 24 | 16 | 42 | 17-0081329 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 22574 | 6.0143 | 154_206 | <25mph | <15mph | HFTD - Distribution
PG&E | 43005 | 0.50833 | 39.4845 | -121.3545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | bill lopez cell 530 521-8052 | 100429924 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 43005 | 0.50833 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1436 | 2017 | 9 | 27 | 12 | 12 | 17-0082180 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 6370 | 13.6129 | 119_296 | <25mph | <15mph | HFTD - Distribution
PG&E | 43005 | 0.79583 | 40.7592 | -123.995 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103660812 | Unknown | 12000 | Conductor | Overhead | Yes | 43005 | 0.79583 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1437 | 2017 | 9 | 27 | 19 | 6 | 17-0082303 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 35394 | 13.6987 | 184_321 | <25mph | <15mph | HFTD - Distribution
PG&E | 43010 | 0.62222 | 38.9102 | -120.9185 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100110800 | None | 21000 | Other | Overhead | Yes | 43010 | 0.62222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1447 | 2017 | 10 | 2 | 14 | 56 | 17-0083516 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 160 | 18.6609 | 157_329 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43010 | 0.67014 | 38.7182 | -120.9756 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101375963 | Unknown | 21000 | Conductor | Overhead | Yes | 43010 | 0.67014 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1448 | 2017 | 10 | 2 | 16 | 5 | 17-0083539 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4797 | 21.1222 | 203_289 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43012 | 0.9875 | 38.6554 | -120.9934 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101375442 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 43012 | 0.9875 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1452 | 2017 | 10 | 4 | 23 | 42 | 17-0084323 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7553 | 9.7855 | 188_229 | <25mph | <15mph | HFTD - Distribution
PG&E | 43016 | 0.82222 | 39.7446 | -121.597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100330456 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 0.82222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1464 | 2017 | 10 | 8 | 19 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.9256 | 162_195 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43016 | 0.85764 | 39.6315 | -121.4225 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100347747 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 0.85764 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1465 | 2017 | 10 | 8 | 20 | 35 | 17-0085196 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 181992 | 7.1814 | 174_335 | <25mph | <15mph | HFTD - Distribution
PG&E | 43016 | 0.88194 | 39.4554 | -121.0498 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100099226 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 0.88194 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (Not overhanging, > 12ft) | 1466 | 2017 | 10 | 8 | 21 | 10 | 17-0085261 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 255784 | 12.1371 | 181_329 | <25mph | <15mph | HFTD - Distribution
PG&E | 43016 | 0.90694 | 39.2595 | -120.9965 | Vegetation | Urban | < 0.25 Acres | Fire Agency | PHILLIP NUNNICK 530 273-3158 INCENDENT # 26264 | 100072730 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 43016 | 0.90694 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1467 | 2017 | 10 | 8 | 21 | 46 | 17-0085308 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 12650 | 29.8567 | 146_261 | 25-40mph | >=15mph | HFTD - Distribution
PG&E | 43016 | 0.92986 | 39.7371 | -121.6464 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 103319605 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43016 | 0.92986 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1468 | 2017 | 10 | 8 | 22 | 19 | 17-0085504 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 42839 | 18.3728 | 197_319 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43016 | 0.95417 | 35.5528 | -118.9681 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | span 7/87-7/88, Vedder Tap | Unknown | 115000 | Conductor | Overhead | Yes | 43016 | 0.95417 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1470 | 2017 | 10 | 8 | 22 | 54 | INT-10231 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 66311 | 19.9938 | 134_262 | <25mph | >=15mph | HFTD - Transmission
PG&E | 43016 | 0.95694 | 39.3642 | -121.1131 | Vegetation | Rural | < 3 Meters | Fire Agency | INCIDENT NUMBER 26268 | 100068104 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43016 | 0.95694 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Fell into (No defect) | 1471 | 2017 | 10 | 8 | 22 | 58 | 17-0085355 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 198802 | 32.0506 | 159_257 | 25-40mph | >=15mph | HFTD - Distribution
PG&E | 43017 | 0.043056 | 38.7037 | -120.6725 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101408485 | Unknown | 21000 | Other | Overhead | Yes | 43017 | 0.043056 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1473 | 2017 | 10 | 9 | 1 | 2 | 17-0085324 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 419843 | 19.6005 | 195_314 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43017 | 0.072917 | 38.8576 | -122.7221 | Vegetation | Rural | < 0.25 Acres | Fire Agency | wink | 103570679 | Unknown | 12000 | Conductor | Overhead | Yes | 43017 | 0.072917 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Other/Unknown | 1477 | 2017 | 10 | 9 | 1 | 45 | 17-0085344 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 219653 | 30.6108 | 158_254 | 25-40mph | >=15mph | HFTD - Distribution
PG&E | 43018 | 0.56667 | 38.931 | -123.3023 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 102214553 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43018 | 0.56667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1481 | 2017 | 10 | 10 | 13 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 19.0585 | 158_230 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43019 | 0.49792 | 38.5015 | -123.0237 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101974930 | Unknown | 12000 | Conductor | Overhead | Yes | 43019 | 0.49792 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1484 | 2017 | 10 | 11 | 11 | 57 | 17-0086350 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 226925 | 7.6117 | 150_224 | <25mph | <15mph | HFTD - Distribution
PG&E | 43021 | 0.43542 | 37.0561 | -122.0206 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Scotts Valley Fire Dept. | 101677721 | Unknown | 21000 | Conductor | Overhead | Yes | 43021 | 0.43542 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Grow Into | 1487 | 2017 | 10 | 13 | 10 | 27 | 17-0087093 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Grow Into | 201996 | 9.9452 | 101_291 | <25mph | <15mph | HFTD - Distribution
PG&E | 43021 | 0.92986 | 39.7648 | -121.6307 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100325368 | PACIFIC BELL | 0 – 750 | Transformer | Overhead | Yes | 43021 | 0.92986 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1489 | 2017 | 10 | 13 | 22 | 19 | 17-0087321 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 7056 | 2.1281 | 157_198 | <25mph | <15mph | HFTD - Distribution
PG&E | 43024 | 0.50694 | 36.5831 | -121.9368 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101781248 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43024 | 0.50694 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | Other/Unknown | 1493 | 2017 | 10 | 16 | 12 | 10 | 17-0087767 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 6313 | 8.6929 | 155_187 | <25mph | <15mph | HFTD - Distribution
PG&E | 43024 | 0.51389 | 37.72 | -122.0687 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100900970 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43024 | 0.51389 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | no-match | 1494 | 2017 | 10 | 16 | 12 | 20 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 5.0831 | 242_181 | <25mph | <15mph | HFTD - Distribution
PG&E | 43024 | 0.51806 | 36.6641 | -121.0995 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Nick Shawkey E4462 209-402-1645 Cover Engine from Tuolumne Calaveras Unit | 101689865 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43024 | 0.51806 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1495 | 2017 | 10 | 16 | 12 | 26 | 17-0087754 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 519 | 14.8814 | 173_336 | <25mph | <15mph | HFTD - Distribution
PG&E | 43028 | 0.2625 | 39.2922 | -121.0157 | Vegetation | Rural | < 3 Meters | Fire Agency | PHILLIP NUNNINK INCIDENT # 27272 | 100087647 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43028 | 0.2625 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1499 | 2017 | 10 | 20 | 6 | 18 | 17-0088957 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 102410 | 10.8604 | 153_224 | <25mph | <15mph | HFTD - Distribution
PG&E | 43028 | 0.57292 | 34.5532 | -120.5303 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 101921492 | Unknown | 12000 | Conductor | Overhead | Yes | 43028 | 0.57292 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1502 | 2017 | 10 | 20 | 13 | 45 | 17-0089249 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 173 | 6.022 | 288_98 | <25mph | <15mph | HFTD - Distribution
PG&E | 43029 | 0.63056 | 39.064 | -122.7765 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102155186 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43029 | 0.63056 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1504 | 2017 | 10 | 21 | 15 | 8 | 17-0089392 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 13374 | 17.4574 | 254_170 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43031 | 0.89167 | 37.3713 | -122.348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100270421 | Unknown | 12000 | Conductor | Overhead | Yes | 43031 | 0.89167 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1507 | 2017 | 10 | 23 | 21 | 24 | 17-0089820 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1768 | 24.5535 | 221_49 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43036 | 0.64306 | 39.4516 | -123.3838 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102209084 | Unknown | 12000 | Conductor | Overhead | Yes | 43036 | 0.64306 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | no-match | 1510 | 2017 | 10 | 28 | 15 | 26 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 6.6585 | 123_298 | <25mph | <15mph | HFTD - Distribution
PG&E | 43039 | 0.87639 | 39.1119 | -122.9163 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Structure 020/003 | Unknown | 60000 | Conductor | Overhead | Yes | 43039 | 0.87639 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | no-match | 1513 | 2017 | 10 | 31 | 21 | 2 | INT-10325 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | 50730 | 2.5647 | 140_205 | <25mph | <15mph | HFTD - Transmission
PG&E | 43047.2998 | 07:11 | 37.7367 | -120.3459 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101191714 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43047.2998 | 07:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1516 | 2017 | 11 | 8 | 7 | 11 | 17-0093414 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 1573 | 5.3951 | 98_320 | <25mph | <15mph | HFTD - Distribution
PG&E | 43050.5115 | 0.49792 | 35.1191 | -120.3936 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Jordan Dayley ph#929-3911,engine#3467 | 101931190 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43050.5115 | 0.49792 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1518 | 2017 | 11 | 11 | 11 | 57 | 17-0094408 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29093 | 5.8124 | 170_294 | <25mph | <15mph | HFTD - Distribution
PG&E | 43059.3562 | 08:32 | 38.7584 | -120.8439 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101389405 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43059.3562 | 08:32 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1522 | 2017 | 11 | 20 | 8 | 32 | 17-0096436 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 12376 | 9.4273 | 228_225 | <25mph | <15mph | HFTD - Distribution
PG&E | 43068.7326 | 17:34 | 38.6841 | -120.6546 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 101419450 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 43068.7326 | 17:34 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1533 | 2017 | 11 | 29 | 17 | 34 | 17-0098456 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 582825 | 9.3832 | 241_163 | <25mph | <15mph | HFTD - Distribution
PG&E | 43076.5178 | 12:25 | 34.7115 | -120.1772 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 015/220 | Unknown | 115000 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1534 | 2017 | 12 | 7 | 12 | 25 | 17-0097211 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 10.6388 | 246_130 | <25mph | <15mph | HFTD - Transmission
PG&E | 43083 | 0.71944 | 34.5878 | -120.3566 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101911004 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 43083 | 0.71944 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1538 | 2017 | 12 | 14 | 17 | 16 | 17-0101672 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2896 | 7.0168 | 253_156 | <25mph | <15mph | HFTD - Distribution
PG&E | 43085 | 0.49375 | 38.8171 | -122.7041 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Shawn Ohare | 102167231 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43085 | 0.49375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1540 | 2017 | 12 | 16 | 11 | 51 | 17-0102101 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26120 | 6.1156 | 237_58 | <25mph | <15mph | HFTD - Distribution
PG&E | 43088 | 0.82292 | 40.7271 | -122.3263 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101457738 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43088 | 0.82292 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1545 | 2017 | 12 | 19 | 19 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 14.1308 | 149_336 | <25mph | <15mph | HFTD - Distribution
PG&E | 43089.3298 | 07:54 | 37.4012 | -122.3606 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100318864 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43089.3298 | 07:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1546 | 2017 | 12 | 20 | 7 | 54 | 17-0102756 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6602 | 25.9102 | 126_285 | 25-40mph | >=15mph | HFTD - Distribution
PG&E | 43089.586 | 14:03 | 35.6646 | -121.244 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103857828 | Unknown | 12000 | Fuse | Overhead | No |  |  | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1547 | 2017 | 12 | 20 | 14 | 3 | 17-0102828 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 31041 | 21.133 | 172_237 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43098 | 0.68819 | 37.8517 | -122.1586 | Vegetation | Rural | < 3 Meters | Fire Agency | 925-933-1313 | 100488954 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1552 | 2017 | 12 | 29 | 16 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 9.0247 | 140_206 | <25mph | <15mph | HFTD - Distribution
PG&E | 43116 | 0.60069 | 34.5703 | -119.9645 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101921689 | Verizon | 12000 | Conductor | Overhead | Yes | 43116 | 0.60069 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1556 | 2018 | 1 | 16 | 14 | 25 | 18-0006506 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 23519 | 7.2277 | 144_375 | <25mph | <15mph | HFTD - Distribution
PG&E | 43138 | 0.23889 | 40.6543 | -122.5198 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 103922730 | Unknown | 12000 | Conductor | Overhead | Yes | 43138 | 0.23889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1558 | 2018 | 2 | 7 | 5 | 44 | 18-0012073 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 9610 | 7.631 | 149_231 | <25mph | <15mph | HFTD - Distribution
PG&E | 43138 | 0.38611 | 38.0369 | -120.2096 | Vegetation | Rural | < 3 meters | Fire Agency | Jason Podesta 209-586-3362 | 101038120 | AT&T | 17000 | Conductor | Overhead | Yes | 43138 | 0.38611 | Contact From Object | N.A. | Other | Electric Facility | Human Error | third-party caused | Other/Unknown | 1559 | 2018 | 2 | 7 | 9 | 16 | 18-0012146 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 78738 | 7.4 | 230_191 | <25mph | <15mph | HFTD - Distribution
PG&E | 43143 | 0.84722 | 39.9395 | -121.6494 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430947 | Unknown | 12000 | Conductor | Overhead | Yes | 43143 | 0.84722 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1561 | 2018 | 2 | 12 | 20 | 20 | 18-0013604 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 149212 | 9.9721 | 208_94 | <25mph | <15mph | HFTD - Distribution
PG&E | 43157 | 0.68958 | 35.5302 | -118.9695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100208194 | Unknown | 21000 | Conductor | Overhead | Yes | 43157 | 0.68958 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1563 | 2018 | 2 | 26 | 16 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 1.8145 | 185_237 | <25mph | <15mph | HFTD - Distribution
PG&E | 43162 | 0.51042 | 39.1213 | -121.055 | Building | Urban | Structure Only | Unknown | N.A. | 100095928 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43162 | 0.51042 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1564 | 2018 | 3 | 3 | 12 | 15 | 18-0019280 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 15750 | 24.1762 | 136_386 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43165 | 0.74792 | 38.2811 | -120.8965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-647-5220 | 101238429 | AT&T | 12000 | Conductor | Overhead | Yes | 43165 | 0.74792 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1566 | 2018 | 3 | 6 | 17 | 57 | 18-0020396 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 142000 | 3.7671 | 147_303 | <25mph | <15mph | HFTD - Distribution
PG&E | 43185 | 0.7125 | 38.7304 | -122.6215 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102166450 | AT&T | 12000 | Conductor | Overhead | Yes | 43185 | 0.7125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1569 | 2018 | 3 | 26 | 17 | 6 | 18-0026824 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3255 | 4.8801 | 291_104 | <25mph | <15mph | HFTD - Distribution
PG&E | 43217 | 0.53333 | 39.1717 | -120.8652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | incident # 9960 ph # 530-8850111 | 100075314 | Unknown | 12000 | Conductor | Overhead | Yes | 43217 | 0.53333 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Dead | 1577 | 2018 | 4 | 27 | 12 | 48 | 18-0036310 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 28650 | 0.69339 | 172_185 | <25mph | <15mph | HFTD - Distribution
PG&E | 43229 | 0.58333 | 38.5908 | -123.3423 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CASE# 18CALNU 005865 | 101998286 | Unknown | 12000 | Conductor | Overhead | Yes | 43229 | 0.58333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1584 | 2018 | 5 | 9 | 14 | 0 | 18-0039683 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 29522 | 18.7683 | 264_137 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43231 | 0.42569 | 38.387 | -122.9856 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101973909 | Unknown | 12000 | Conductor | Overhead | Yes | 43231 | 0.42569 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1585 | 2018 | 5 | 11 | 10 | 13 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 12.8787 | 222_76 | <25mph | <15mph | HFTD - Distribution
PG&E | 43231 | 0.66042 | 40.3385 | -123.9137 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100989912 | Unknown | 12000 | Conductor | Overhead | Yes | 43231 | 0.66042 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1587 | 2018 | 5 | 11 | 15 | 51 | 18-0040389 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 5926 | 13.3837 | 153_302 | <25mph | <15mph | HFTD - Distribution
PG&E | 43231 | 0.73819 | 38.8218 | -120.9295 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Douglas Ferro. cell-530-708-2715. office-530-677-6192 | 101388939 | AT&T | 21000 | Conductor | Overhead | Yes | 43231 | 0.73819 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1588 | 2018 | 5 | 11 | 17 | 43 | 18-0040415 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 53784 | 7.4837 | 137_253 | <25mph | <15mph | HFTD - Distribution
PG&E | 43239 | 0.82222 | 40.2665 | -122.2727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103899310 | Unknown | 12000 | Conductor | Overhead | Yes | 43239 | 0.82222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1599 | 2018 | 5 | 19 | 19 | 44 | 18-0042559 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 31980 | 12.5399 | 286_88 | <25mph | <15mph | HFTD - Distribution
PG&E | 43248 | 0.27083 | 40.4382 | -122.3001 | Building | Rural | Structure Only | Unknown | N.A. | 101495757 | Unknown | 0 – 750 | conductor | Overhead | Yes | 43248 | 0.27083 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1610 | 2018 | 5 | 28 | 6 | 30 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 14.1792 | 221_204 | <25mph | <15mph | HFTD - Distribution
PG&E | 43255 | 0.39236 | 35.4593 | -120.4921 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101895513 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43255 | 0.39236 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1624 | 2018 | 6 | 4 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 10.7972 | 144_375 | <25mph | <15mph | HFTD - Distribution
PG&E | 43256 | 0.42569 | 40.6183 | -122.3173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JASON COLLINS 530-225-4628 | 101467801 | None | 12000 | Conductor | Overhead | Yes | 43256 | 0.42569 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1631 | 2018 | 6 | 5 | 10 | 13 | 18-0047539 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 277 | 16.4025 | 244_185 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43256 | 0.57292 | 38.5432 | -122.7202 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 102031673 | Unknown | 12000 | Conductor | Overhead | Yes | 43256 | 0.57292 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1633 | 2018 | 6 | 5 | 13 | 45 | 18-0047625 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 40599 | 0.57098 | 268_81 | <25mph | <15mph | HFTD - Distribution
PG&E | 43256 | 0.69861 | 38.7245 | -120.802 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 103667302 | AT&T | 12000 | Conductor | Overhead | Yes | 43256 | 0.69861 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1634 | 2018 | 6 | 5 | 16 | 46 | 18-0047702 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 40590 | 22.3947 | 200_151 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43259 | 0.79375 | 35.154 | -120.594 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101852092 | AT&T | 12000 | Conductor | Overhead | Yes | 43259 | 0.79375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1644 | 2018 | 6 | 8 | 19 | 3 | 18-0049130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2473 | 16.6738 | 179_283 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43260 | 0.031944 | 35.0745 | -120.5167 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101927520 | Unknown | 12000 | Conductor | Overhead | Yes | 43260 | 0.031944 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1645 | 2018 | 6 | 9 | 0 | 46 | 18-0049171 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 16825 | 8.735 | 190_243 | <25mph | <15mph | HFTD - Distribution
PG&E | 43261 | 0.72153 | 38.4157 | -122.9184 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101978419 | AT&T | 12000 | Conductor | Overhead | Yes | 43261 | 0.72153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1647 | 2018 | 6 | 10 | 17 | 19 | 18-0049445 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2386 | 16.9824 | 195_239 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43262 | 0.74236 | 34.7329 | -120.0861 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103015183 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43262 | 0.74236 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1649 | 2018 | 6 | 11 | 17 | 49 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 13.4941 | 215_100 | <25mph | <15mph | HFTD - Distribution
PG&E | 43264 | 0.47083 | 35.2927 | -120.429 | Vegetation | Rural | < 3 meters | Customer | N.A. | 101884565 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 0.47083 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1654 | 2018 | 6 | 13 | 11 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 4.3035 | 186_288 | <25mph | <15mph | HFTD - Distribution
PG&E | 43264 | 0.94444 | 38.4901 | -122.6661 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SRS181640125 | 101966547 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 0.94444 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1656 | 2018 | 6 | 13 | 22 | 40 | 18-0050782 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 295146 | 15.1291 | 208_252 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43265 | 0.675 | 40.4419 | -124.0197 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 101005522 | AT&T | 12000 | Conductor | Overhead | Yes | 43265 | 0.675 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1658 | 2018 | 6 | 14 | 16 | 12 | 18-0051223 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 19601 | 5.2934 | 177_272 | <25mph | <15mph | HFTD - Distribution
PG&E | 43266 | 0.12222 | 37.4869 | -122.4223 | Vegetation | Rural | < 0.25 Acres | Utility: PG&E | N.A. | Pole 10/5 | None | 60000 | Conductor | Overhead | Yes | 43266 | 0.12222 | Contamination | N.A. | N.A. | N.A. | Unknown |  | no-match | 1659 | 2018 | 6 | 15 | 2 | 56 | INT-11115 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 0 | 11.9619 | 163_178 | <25mph | <15mph | HFTD - Transmission
PG&E | 43266 | 0.41042 | 37.1986 | -119.4709 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RANCHARIA ENGINE 4255 USFS ENG 52 | 101058060 | Unknown | 12000 | Conductor | Overhead | Yes | 43266 | 0.41042 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1660 | 2018 | 6 | 15 | 9 | 51 | 18-0051354 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 35146 | 5.1841 | 225_90 | <25mph | <15mph | HFTD - Distribution
PG&E | 43266 | 0.42014 | 38.6238 | -121.0221 | Vegetation | Rural | < 3 meters | Customer | N.A. | 101376538 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43266 | 0.42014 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1661 | 2018 | 6 | 15 | 10 | 5 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 11.5397 | 244_164 | <25mph | <15mph | HFTD - Distribution
PG&E | 43267 | 0.83194 | 37.907 | -121.8063 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100483910 | Unknown | 21000 | Conductor | Overhead | Yes | 43267 | 0.83194 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1670 | 2018 | 6 | 16 | 19 | 58 | 18-0051687 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 3322 | 12.5495 | 235_188 | <25mph | <15mph | HFTD - Distribution
PG&E | 43267 | 0.85625 | 38.0494 | -122.206 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Contra Costa FD | 101423963 | Unknown | 21000 | Conductor | Overhead | Yes | 43267 | 0.85625 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 1671 | 2018 | 6 | 16 | 20 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 15.0089 | 147_245 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43270 | 0.01875 | 38.7604 | -120.8224 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101388356 | Unknown | 12000 | Conductor | Overhead | Yes | 43270 | 0.01875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1675 | 2018 | 6 | 19 | 0 | 27 | 18-0052111 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 141652 | 1.004 | 164_234 | <25mph | <15mph | HFTD - Distribution
PG&E | 43270 | 0.42847 | 38.5918 | -120.7097 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101395943 | AT&T | 21000 | Conductor | Overhead | Yes | 43270 | 0.42847 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1677 | 2018 | 6 | 19 | 10 | 17 | 18-0052222 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 4094 | 23.6519 | 147_242 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43270 | 0.61181 | 37.2158 | -119.6811 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JOE QUINSTORFF 559-683-8008 | 103372829 | Unknown | 21000 | Conductor | Overhead | Yes | 43270 | 0.61181 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1679 | 2018 | 6 | 19 | 14 | 41 | 18-0052327 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 123838 | 7.0997 | 215_103 | <25mph | <15mph | HFTD - Distribution
PG&E | 43271 | 0.35417 | 34.7561 | -120.2281 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101858890 | None | 0 – 750 | Conductor | Overhead | Yes | 43271 | 0.35417 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1680 | 2018 | 6 | 20 | 8 | 30 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 12.0354 | 183_228 | <25mph | <15mph | HFTD - Distribution
PG&E | 43272 | 0.79028 | 35.1224 | -120.3938 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101878933 | AT&T | 12000 | Conductor | Overhead | Yes | 43272 | 0.79028 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1683 | 2018 | 6 | 21 | 18 | 58 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 10.7167 | 212_272 | <25mph | <15mph | HFTD - Distribution
PG&E | 43273 | 0.73889 | 37.2485 | -119.5625 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Madera County | 101117749 | None | 0 – 750 | Conductor | Overhead | Yes | 43273 | 0.73889 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1686 | 2018 | 6 | 22 | 17 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 4.1836 | 235_60 | <25mph | <15mph | HFTD - Distribution
PG&E | 43274 | 0.39653 | 40.8632 | -122.3962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | RYAN MEANS 530-238-2416 | 101472252 | AT&T | 12000 | Conductor | Overhead | Yes | 43274 | 0.39653 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1688 | 2018 | 6 | 23 | 9 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 5.2159 | 191_283 | <25mph | <15mph | HFTD - Distribution
PG&E | 43278 | 0.78194 | 40.218 | -123.7989 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TJ alderpoint fire | 100990381 | Unknown | 12000 | Conductor | Overhead | Yes | 43278 | 0.78194 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1700 | 2018 | 6 | 27 | 18 | 46 | 18-0055205 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 21357 | 11.02 | 175_322 | <25mph | <15mph | HFTD - Distribution
PG&E | 43278 | 0.88819 | 39.8714 | -123.7119 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 103775148 | Verizon | 12000 | Conductor | Overhead | Yes | 43278 | 0.88819 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1701 | 2018 | 6 | 27 | 21 | 19 | 18-0055211 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 75544 | 8.4543 | 226_238 | <25mph | <15mph | HFTD - Distribution
PG&E | 43279 | 0.51875 | 38.5982 | -121.0081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | John Reis, 530-622-3858 | 101376954 | Unknown | 21000 | Conductor | Overhead | Yes | 43279 | 0.51875 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1702 | 2018 | 6 | 28 | 12 | 27 | 18-0055479 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 24671 | 4.0055 | 121_265 | <25mph | <15mph | HFTD - Distribution
PG&E | 43279 | 0.82014 | 38.5575 | -122.5043 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Brian Coffee | 102267918 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43279 | 0.82014 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1704 | 2018 | 6 | 28 | 19 | 41 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 6.6653 | 169_327 | <25mph | <15mph | HFTD - Distribution
PG&E | 43281 | 0.46806 | 39.3621 | -121.0809 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ENGINEER YUREK | 100091354 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 0.46806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1713 | 2018 | 6 | 30 | 11 | 14 | 18-0055945 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5724 | 7.068 | 177_318 | <25mph | <15mph | HFTD - Distribution
PG&E | 43281 | 0.92917 | 40.6043 | -122.24 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101469808 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43281 | 0.92917 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1716 | 2018 | 6 | 30 | 22 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 5.9401 | 123_268 | <25mph | <15mph | HFTD - Distribution
PG&E | 43281 | 0.94167 | 39.1141 | -121.077 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Matt Wallen (530) 277-3312 Incident # NEU015486 | 100105380 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 0.94167 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1717 | 2018 | 6 | 30 | 22 | 36 | 18-0056039 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 8004 | 13.4658 | 240_131 | <25mph | <15mph | HFTD - Distribution
PG&E | 43282 | 0.015972 | 40.2697 | -124.2386 | Vegetation | Rural | < 3 meters | Fire Agency | fire chief | 100986962 | Unknown | 12000 | Conductor | Overhead | Yes | 43282 | 0.015972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1718 | 2018 | 7 | 1 | 0 | 23 | 18-0056043 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 22872 | 8.1598 | 289_99 | <25mph | <15mph | HFTD - Distribution
PG&E | 43282 | 0.03125 | 38.8842 | -120.847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Brian Mackwood (530)708-2711 | 100109003 | None | 21000 | Conductor | Overhead | Yes | 43282 | 0.03125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1719 | 2018 | 7 | 1 | 0 | 45 | 18-0056045 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5760 | 11.7533 | 196_314 | <25mph | <15mph | HFTD - Distribution
PG&E | 43282 | 0.34236 | 39.4154 | -121.5122 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430344 | AT&T | 12000 | Conductor | Overhead | Yes | 43282 | 0.34236 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1720 | 2018 | 7 | 1 | 8 | 13 | 18-0056061 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 7848 | 1.9617 | 207_277 | <25mph | <15mph | HFTD - Distribution
PG&E | 43283 | 0.21667 | 38.6092 | -122.4595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 707-967-1467 | 102252558 | AT&T | 21000 | Conductor | Overhead | Yes | 43283 | 0.21667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1722 | 2018 | 7 | 2 | 5 | 12 | 18-0056178 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 403 | 22.7012 | 147_383 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43285 | 0.64306 | 39.5538 | -123.4255 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102196183 | Verizon | 12000 | Conductor | Overhead | Yes | 43285 | 0.64306 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1726 | 2018 | 7 | 4 | 15 | 26 | 18-0056986 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 32269 | 8.4554 | 178_317 | <25mph | <15mph | HFTD - Distribution
PG&E | 43290 | 0.31042 | 35.0785 | -120.3948 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101861366 | Unknown | 12000 | Conductor | Overhead | Yes | 43290 | 0.31042 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1735 | 2018 | 7 | 9 | 7 | 27 | 18-0057904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 21045 | 17.9744 | 216_205 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43291 | 0.28125 | 37.085 | -122.0744 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 101675262 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43291 | 0.28125 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1737 | 2018 | 7 | 10 | 6 | 45 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 11.2401 | 171_309 | <25mph | <15mph | HFTD - Distribution
PG&E | 43294 | 0.45764 | 39.4836 | -123.7924 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102184869 | AT&T | 12000 | Conductor | Overhead | Yes | 43294 | 0.45764 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1742 | 2018 | 7 | 13 | 10 | 59 | 18-0059522 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 328 | 9.5867 | 192_286 | <25mph | <15mph | HFTD - Distribution
PG&E | 43295 | 0.48194 | 38.4026 | -122.5489 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103141862 | Verizon | 12000 | Conductor | Overhead | Yes | 43295 | 0.48194 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1745 | 2018 | 7 | 14 | 11 | 34 | 18-0059821 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 6426 | 39.2776 | 179_223 | 25-40mph | >=15mph | HFTD - Distribution
PG&E | 43295 | 0.52778 | 38.5793 | -122.878 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103122744 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 0.52778 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1746 | 2018 | 7 | 14 | 12 | 40 | 18-0059799 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20804 | 30.5596 | 202_188 | 25-40mph | >=15mph | HFTD - Distribution
PG&E | 43295 | 0.53889 | 39.2093 | -121.197 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE DEPT LEFT BEFORE UPTAINING THAT INFO | 100086833 | None | 21000 | Conductor | Overhead | Yes | 43295 | 0.53889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1747 | 2018 | 7 | 14 | 12 | 56 | 18-0059841 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 3720 | 12.5941 | 207_189 | <25mph | <15mph | HFTD - Distribution
PG&E | 43295 | 0.61389 | 38.9524 | -121.2467 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100035452 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 0.61389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1748 | 2018 | 7 | 14 | 14 | 44 | 18-0059847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2430 | 1.1884 | 81_323 | <25mph | <15mph | HFTD - Distribution
PG&E | 43295 | 0.90139 | 36.3314 | -121.8829 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | ASSISTED JAIMIE | 101672234 | Unknown | 12000 | Conductor | Overhead | Yes | 43295 | 0.90139 | Contact From Object | N.A. | Animal | Pole | Other | bull rubbing pole | Other/Unknown | 1751 | 2018 | 7 | 14 | 21 | 38 | 18-0059900 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 493416 | 9.1931 | 133_262 | <25mph | <15mph | HFTD - Distribution
PG&E | 43298 | 0.46597 | 35.6986 | -120.9777 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | dennis byrnes 8055434244 inc # = 18ca-slu-007640 | 103886652 | Unknown | 21000 | Conductor | Overhead | Yes | 43298 | 0.46597 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1755 | 2018 | 7 | 17 | 11 | 11 | 18-0060637 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 9121 | 12.6745 | 199_230 | <25mph | <15mph | HFTD - Distribution
PG&E | 43298 | 0.49861 | 37.2217 | -121.6778 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Luis Morado state arson fire fighter | 100601345 | Unknown | 12000 | Conductor | Overhead | Yes | 43298 | 0.49861 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1756 | 2018 | 7 | 17 | 11 | 58 | 18-0060617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 5865 | 10.4828 | 287_98 | <25mph | <15mph | HFTD - Distribution
PG&E | 43298 | 0.70347 | 38.3955 | -122.9212 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101978449 | AT&T | 12000 | Conductor | Overhead | Yes | 43298 | 0.70347 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1759 | 2018 | 7 | 17 | 16 | 53 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.2118 | 216_106 | <25mph | <15mph | HFTD - Distribution
PG&E | 43298 | 0.81944 | 40.5927 | -122.4886 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101477082 | AT&T | 12000 | Conductor | Overhead | Yes | 43298 | 0.81944 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1760 | 2018 | 7 | 17 | 19 | 40 | 18-0060840 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 30162 | 6.2637 | 134_236 | <25mph | <15mph | HFTD - Distribution
PG&E | 43299 | 0.051389 | 38.3671 | -120.5578 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101247987 | Unknown | 12000 | Conductor | Overhead | Yes | 43299 | 0.051389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1761 | 2018 | 7 | 18 | 1 | 14 | 18-0060882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6420 | 5.3917 | 170_196 | <25mph | <15mph | HFTD - Distribution
PG&E | 43300 | 0.0055556 | 36.9372 | -119.4557 | Vegetation | Rural | < 0.25 Acres | Fire Agency | incident # 10559 | 100677019 | AT&T | 12000 | Conductor | Overhead | Yes | 43300 | 0.0055556 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1766 | 2018 | 7 | 19 | 0 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 5.6181 | 137_382 | <25mph | <15mph | HFTD - Distribution
PG&E | 43300 | 0.22847 | 40.1918 | -123.5373 | Vegetation | Rural | < 0.25 Acres | Fire Agency | fire captain | 103909820 | Unknown | 12000 | Conductor | Overhead | Yes | 43300 | 0.22847 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1767 | 2018 | 7 | 19 | 5 | 29 | 18-0061308 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 73380 | 10.1867 | 219_259 | <25mph | <15mph | HFTD - Distribution
PG&E | 43301 | 0.27153 | 37.4318 | -119.9441 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ZACH RUTHERFORD 209-966-3621 | 103909942 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43301 | 0.27153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1771 | 2018 | 7 | 20 | 6 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 3.6688 | 186_294 | <25mph | <15mph | HFTD - Distribution
PG&E | 43302 | 0.015972 | 38.6927 | -120.7921 | Vegetation | Rural | < 3 meters | Fire Agency | CAMINO | 101415904 | AT&T | 12000 | Conductor | Overhead | Yes | 43302 | 0.015972 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1774 | 2018 | 7 | 21 | 0 | 23 | 18-0062206 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 107552 | 6.3124 | 254_141 | <25mph | <15mph | HFTD - Distribution
PG&E | 43302 | 0.61875 | 35.6846 | -120.9427 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101943190 | Unknown | 21000 | Conductor | Overhead | Yes | 43302 | 0.61875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1775 | 2018 | 7 | 21 | 14 | 51 | 18-0062364 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 110814 | 23.7634 | 150_252 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43302 | 0.67778 | 40.3439 | -123.7092 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 101009789 | Unknown | 12000 | Conductor | Overhead | Yes | 43302 | 0.67778 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1776 | 2018 | 7 | 21 | 16 | 16 | 18-0062375 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 5184 | 3.1025 | 260_163 | <25mph | <15mph | HFTD - Distribution
PG&E | 43304 | 0.63264 | 39.4911 | -123.7844 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102184598 | Yes | 12000 | Conductor | Overhead | Yes | 43304 | 0.63264 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1781 | 2018 | 7 | 23 | 15 | 11 | 18-0062842 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 44840 | 2.821 | 202_111 | <25mph | <15mph | HFTD - Distribution
PG&E | 43304 | 0.72708 | 39.734 | -121.4965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103843963 | AT&T | 12000 | Conductor | Overhead | Yes | 43304 | 0.72708 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1782 | 2018 | 7 | 23 | 17 | 27 | 18-0062874 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 183629 | 3.7692 | 85_370 | <25mph | <15mph | HFTD - Distribution
PG&E | 43305 | 0.57431 | 39.0606 | -123.4456 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102212216 | Unknown | 12000 | Conductor | Overhead | Yes | 43305 | 0.57431 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1786 | 2018 | 7 | 24 | 13 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 15.1063 | 147_333 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43306 | 0.029167 | 39.7791 | -121.6173 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100327443 | Unknown | 12000 | Conductor | Overhead | Yes | 43306 | 0.029167 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1788 | 2018 | 7 | 25 | 0 | 42 | 18-0063320 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6742 | 10.3521 | 178_335 | <25mph | <15mph | HFTD - Distribution
PG&E | 43308 | 0.96667 | 37.18 | -122.029 | Vegetation | Rural | < 3 meters | Fire Agency | Jeremy Wise 408-378-4010 Incident # C182080066 | 100518365 | Unknown | 12000 | Conductor | Overhead | Yes | 43308 | 0.96667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1793 | 2018 | 7 | 27 | 23 | 12 | 18-0064525 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 30475 | 20.4003 | 138_204 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43309 | 0.28542 | 38.7473 | -120.7866 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101418155 | AT&T | 21000 | Conductor | Overhead | Yes | 43309 | 0.28542 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1794 | 2018 | 7 | 28 | 6 | 51 | 18-0064545 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 15429 | 8.664 | 173_337 | <25mph | <15mph | HFTD - Distribution
PG&E | 43310 | 0.48542 | 39.0968 | -123.5018 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102177329 | Unknown | 12000 | Conductor | Overhead | Yes | 43310 | 0.48542 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1796 | 2018 | 7 | 29 | 11 | 39 | 18-0064779 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4329 | 15.5342 | 159_261 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43310 | 0.72847 | 38.5777 | -120.8556 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101383255 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43310 | 0.72847 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1797 | 2018 | 7 | 29 | 17 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 7.4096 | 136_309 | <25mph | <15mph | HFTD - Distribution
PG&E | 43311 | 0.60833 | 38.1987 | -120.3638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NICK WEBB ( 209) 532-7424 | 103336176 | Unknown | 17000 | Conductor | Overhead | Yes | 43311 | 0.60833 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1800 | 2018 | 7 | 30 | 14 | 36 | 18-0065131 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18530 | 10.6529 | 209_280 | <25mph | <15mph | HFTD - Distribution
PG&E | 43312 | 0.33125 | 38.9559 | -122.7274 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102162351 | AT&T | 12000 | Conductor | Overhead | Yes | 43312 | 0.33125 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1803 | 2018 | 7 | 31 | 7 | 57 | 18-0065276 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 89832 | 5.1967 | 206_271 | <25mph | <15mph | HFTD - Distribution
PG&E | 43313 | 0.74861 | 38.9155 | -122.799 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102156435 | Unknown | 12000 | Conductor | Overhead | Yes | 43313 | 0.74861 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1805 | 2018 | 8 | 1 | 17 | 58 | 18-0065921 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2744 | 11.3872 | 85_357 | <25mph | <15mph | HFTD - Distribution
PG&E | 43315 | 0.40625 | 40.4988 | -121.8381 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | ZEIGGLER | 101492431 | Frontier | 12000 | Conductor | Overhead | Yes | 43315 | 0.40625 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1812 | 2018 | 8 | 3 | 9 | 45 | 18-0066484 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 4625 | 15.6081 | 66_397 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43316 | 0.30694 | 37.9756 | -122.5537 | Building | Urban | Structure Only | Fire Agency | ROSS VALLEY | 102241252 | AT&T | 12000 | Conductor | Overhead | Yes | 43316 | 0.30694 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1817 | 2018 | 8 | 4 | 7 | 22 | 18-0066666 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 6260 | 15.2351 | 241_183 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43317 | 0.58056 | 37.4005 | -119.7532 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | JIM FORGA 209-966-3621 | 101017235 | Unknown | 12000 | Conductor | Overhead | Yes | 43317 | 0.58056 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1821 | 2018 | 8 | 5 | 13 | 56 | 18-0066905 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 7325 | 8.1058 | 299_99 | <25mph | <15mph | HFTD - Distribution
PG&E | 43319 | 0.40764 | 38.6556 | -121.0226 | Vegetation | Urban | < 3 meters | Fire Agency | CAL FIRE | 103902317 | AT&T | 21000 | Conductor | Overhead | Yes | 43319 | 0.40764 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1823 | 2018 | 8 | 7 | 9 | 47 | 18-0067412 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 243 | 7.5936 | 132_238 | <25mph | <15mph | HFTD - Distribution
PG&E | 43319 | 0.42986 | 38.1052 | -120.4978 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101282323 | Unknown | 17000 | Lightning Arrestor | Overhead | Yes | 43319 | 0.42986 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1824 | 2018 | 8 | 7 | 10 | 19 | 18-0067659 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 388 | 10.5296 | 181_290 | <25mph | <15mph | HFTD - Distribution
PG&E | 43319 | 0.65694 | 40.4465 | -122.446 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464611 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43319 | 0.65694 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1826 | 2018 | 8 | 7 | 15 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 2.2502 | 162_201 | <25mph | <15mph | HFTD - Distribution
PG&E | 43319 | 0.71875 | 37.1181 | -122.1093 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101670606 | AT&T | 12000 | Conductor | Overhead | Yes | 43319 | 0.71875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1827 | 2018 | 8 | 7 | 17 | 15 | 18-0067641 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1988 | 12.1363 | 254_206 | <25mph | <15mph | HFTD - Distribution
PG&E | 43319 | 0.87708 | 38.2129 | -120.9184 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102042811 | Unknown | 12000 | Conductor | Overhead | Yes | 43319 | 0.87708 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1828 | 2018 | 8 | 7 | 21 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 4.3727 | 174_313 | <25mph | <15mph | HFTD - Distribution
PG&E | 43320 | 0.41875 | 40.7933 | -124.0242 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CHIEF | 100983089 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 0.41875 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1829 | 2018 | 8 | 8 | 10 | 3 | 18-0067921 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 27379 | 13.5277 | 198_275 | <25mph | <15mph | HFTD - Distribution
PG&E | 43320 | 0.66806 | 36.4703 | -121.7143 | Vegetation | Rural | < 3 meters | Customer | N.A. | 103910535 | None | 12000 | Conductor | Overhead | Yes | 43320 | 0.66806 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1830 | 2018 | 8 | 8 | 16 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 10.515 | 221_245 | <25mph | <15mph | HFTD - Distribution
PG&E | 43320 | 0.66875 | 37.2974 | -122.2651 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 100307515 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 0.66875 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1831 | 2018 | 8 | 8 | 16 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.7553 | 139_374 | <25mph | <15mph | HFTD - Distribution
PG&E | 43322 | 0.5375 | 38.799 | -120.73 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101386272 | AT&T | 12000 | Conductor | Overhead | Yes | 43322 | 0.5375 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1832 | 2018 | 8 | 10 | 12 | 54 | 18-0068798 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 26532 | 7.5402 | 254_173 | <25mph | <15mph | HFTD - Distribution
PG&E | 43322 | 0.84583 | 39.2093 | -121.0615 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100075517 | AT&T | 12000 | Conductor | Overhead | Yes | 43322 | 0.84583 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1835 | 2018 | 8 | 10 | 20 | 18 | 18-0068886 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 581901 | 3.7784 | 73_395 | <25mph | <15mph | HFTD - Distribution
PG&E | 43324 | 0.61528 | 38.6443 | -120.9211 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101410516 | Unknown | 21000 | Conductor | Overhead | Yes | 43324 | 0.61528 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1838 | 2018 | 8 | 12 | 14 | 46 | 18-0069084 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4032 | 17.1478 | 211_283 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43325 | 0.64792 | 38.708 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101377799 | Unknown | 21000 | Conductor | Overhead | Yes | 43325 | 0.64792 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1840 | 2018 | 8 | 13 | 15 | 33 | 18-0069470 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1004 | 10.2378 | 230_116 | <25mph | <15mph | HFTD - Distribution
PG&E | 43326 | 0.27986 | 40.686 | -122.141 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | j.t. zulliger 530-225-2420 | 103379843 | Unknown | 12000 | Conductor | Overhead | Yes | 43326 | 0.27986 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1842 | 2018 | 8 | 14 | 6 | 43 | 18-0069529 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 37986 | 4.4465 | 214_250 | <25mph | <15mph | HFTD - Distribution
PG&E | 43326 | 0.6375 | 36.9656 | -121.8681 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 103128221 | AT&T | 21000 | Conductor | Overhead | Yes | 43326 | 0.6375 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1843 | 2018 | 8 | 14 | 15 | 18 | 18-0069846 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 15580 | 2.5294 | 278_109 | <25mph | <15mph | HFTD - Distribution
PG&E | 43326 | 0.65694 | 38.0878 | -122.6002 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103916882 | Verizon | 0 – 750 | Conductor | Overhead | Yes | 43326 | 0.65694 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1844 | 2018 | 8 | 14 | 15 | 46 | 18-0069929 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 546 | 5.3513 | 203_274 | <25mph | <15mph | HFTD - Distribution
PG&E | 43329 | 0.40139 | 40.2997 | -122.3322 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chief | 101509747 | AT&T | 12000 | Conductor | Overhead | Yes | 43329 | 0.40139 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1845 | 2018 | 8 | 17 | 9 | 38 | 18-0071042 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 15510 | 13.0373 | 189_233 | <25mph | <15mph | HFTD - Distribution
PG&E | 43332 | 0.39861 | 39.8014 | -121.5813 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100400441 | Unknown | 12000 | Conductor | Overhead | Yes | 43332 | 0.39861 | Contact From Object | N.A. | Other | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1849 | 2018 | 8 | 20 | 9 | 34 | 18-0071596 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 394259 | 17.1084 | 130_244 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43333 | 0.42569 | 38.6972 | -120.889 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101385436 | Unknown | 12000 | Conductor | Overhead | Yes | 43333 | 0.42569 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1852 | 2018 | 8 | 21 | 10 | 13 | 18-0072055 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4572 | 7.0964 | 157_213 | <25mph | <15mph | HFTD - Distribution
PG&E | 43334 | 0.725 | 37.9519 | -120.3103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101030620 | Unknown | 17000 | Conductor | Overhead | Yes | 43334 | 0.725 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | dampeners | no-match | 1853 | 2018 | 8 | 22 | 17 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.9424 | 158_261 | <25mph | <15mph | HFTD - Distribution
PG&E | 43334 | 0.91389 | 39.0425 | -120.9695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100024728 | Verizon | 12000 | Conductor | Overhead | Yes | 43334 | 0.91389 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1854 | 2018 | 8 | 22 | 21 | 56 | 18-0072654 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29727 | 8.8854 | 172_191 | <25mph | <15mph | HFTD - Distribution
PG&E | 43336 | 0.068056 | 39.2029 | -121.2766 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100087099 | AT&T | 21000 | Conductor | Overhead | Yes | 43336 | 0.068056 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1857 | 2018 | 8 | 24 | 1 | 38 | 18-0073021 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 24360 | 8.9607 | 241_188 | <25mph | <15mph | HFTD - Distribution
PG&E | 43336 | 0.21042 | 39.1184 | -121.0154 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JIM SMITH BATT CHIEF 3 | 100097647 | Unknown | 12000 | Conductor | Overhead | Yes | 43336 | 0.21042 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1858 | 2018 | 8 | 24 | 5 | 3 | 18-0073024 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 4048 | 10.258 | 204_277 | <25mph | <15mph | HFTD - Distribution
PG&E | 43338 | 0.64514 | 39.3599 | -121.1209 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100107472 | Unknown | 12000 | Conductor | Overhead | Yes | 43338 | 0.64514 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1860 | 2018 | 8 | 26 | 15 | 29 | 18-0073601 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 36162 | 10.5291 | 201_296 | <25mph | <15mph | HFTD - Distribution
PG&E | 43340 | 0.53472 | 40.2139 | -123.5966 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100994840 | Unknown | 12000 | Conductor | Overhead | Yes | 43340 | 0.53472 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1866 | 2018 | 8 | 28 | 12 | 50 | 18-0074371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 82754 | 5.0493 | 194_314 | <25mph | <15mph | HFTD - Distribution
PG&E | 43343 | 0.54306 | 40.4775 | -122.4847 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103918932 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 0.54306 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1872 | 2018 | 8 | 31 | 13 | 2 | 18-0075616 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18300 | 2.6194 | 90_363 | <25mph | <15mph | HFTD - Distribution
PG&E | 43343 | 0.75278 | 39.5785 | -123.3842 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102196393 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 0.75278 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1873 | 2018 | 8 | 31 | 18 | 4 | 18-0075741 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18540 | 2.6744 | 105_308 | <25mph | <15mph | HFTD - Distribution
PG&E | 43343 | 0.75625 | 37.0548 | -122.0472 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 101803212 | Unknown | 21000 | Conductor | Overhead | Yes | 43343 | 0.75625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1874 | 2018 | 8 | 31 | 18 | 9 | 18-0075730 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 197397 | 10.8852 | 181_282 | <25mph | <15mph | HFTD - Distribution
PG&E | 43344 | 0.60069 | 36.8088 | -121.5916 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Twr 35/222 | None | 115000 | Conductor | Overhead | Yes | 43344 | 0.60069 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1875 | 2018 | 9 | 1 | 14 | 25 | INT-11331 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 702145 | 8.4404 | 131_254 | <25mph | <15mph | HFTD - Transmission
PG&E | 43345 | 0.65 | 37.4714 | -122.4248 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Arie Delay 659-740-4636 | 103808872 | Unknown | 12000 | Capacitor Bank | Overhead | Yes | 43345 | 0.65 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1876 | 2018 | 9 | 2 | 15 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 14.2035 | 259_173 | <25mph | <15mph | HFTD - Distribution
PG&E | 43346 | 0.77014 | 39.4547 | -121.4955 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100395672 | Unknown | 12000 | Conductor | Overhead | Yes | 43346 | 0.77014 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1880 | 2018 | 9 | 3 | 18 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 10.1463 | 153_187 | <25mph | <15mph | HFTD - Distribution
PG&E | 43348 | 0.70486 | 37.4655 | -119.9005 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JON BERRY 209-966-4700 | 101087053 | Unknown | 21000 | Conductor | Overhead | Yes | 43348 | 0.70486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1882 | 2018 | 9 | 5 | 16 | 55 | 18-0076909 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 4017 | 2.5862 | 137_210 | <25mph | <15mph | HFTD - Distribution
PG&E | 43349 | 0.67986 | 39.0904 | -120.9464 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 100020676 | Unknown | 12000 | Conductor | Overhead | Yes | 43349 | 0.67986 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1886 | 2018 | 9 | 6 | 16 | 19 | 18-0077280 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 30780 | 6.7204 | 178_319 | <25mph | <15mph | HFTD - Distribution
PG&E | 43352 | 0.18403 | 38.6534 | -122.8538 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 13/1 | None | 60000 | Conductor | Overhead | Yes | 43352 | 0.18403 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1887 | 2018 | 9 | 9 | 4 | 25 | INT-11353 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 13.6761 | 176_294 | <25mph | <15mph | HFTD - Transmission
PG&E | 43353 | 0.85903 | 38.0188 | -122.7225 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 102252760 | Unknown | 12000 | Conductor | Overhead | Yes | 43353 | 0.85903 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1889 | 2018 | 9 | 10 | 20 | 37 | 18-0078359 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 219903 | 4.9153 | 105_309 | <25mph | <15mph | HFTD - Distribution
PG&E | 43354 | 0.22431 | 37.376 | -119.6304 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | TROY CHEEK 209-966-3621 | 101023184 | Unknown | 12000 | Conductor | Overhead | Yes | 43354 | 0.22431 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1891 | 2018 | 9 | 11 | 5 | 23 | 18-0078387 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 288 | 37.7814 | 199_187 | 25-40mph | >=15mph | HFTD - Distribution
PG&E | 43357 | 0.63056 | 35.328 | -120.6982 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Sean Hernandez Cell # 805 903 3423 | 103400199 | Unknown | 12000 | Conductor | Overhead | Yes | 43357 | 0.63056 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1898 | 2018 | 9 | 14 | 15 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 1.3314 | 206_97 | <25mph | <15mph | HFTD - Distribution
PG&E | 43359 | 0.35139 | 35.3046 | -120.6389 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | Pole 4/23A | None | 70000 | Conductor | Overhead | Yes | 43359 | 0.35139 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1903 | 2018 | 9 | 16 | 8 | 26 | INT-11371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 29925 | 0.57476 | 149_357 | <25mph | <15mph | HFTD - Transmission
PG&E | 43359 | 0.43194 | 39.4627 | -123.7837 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 102184303 | AT&T | 12000 | Conductor | Overhead | Yes | 43359 | 0.43194 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1904 | 2018 | 9 | 16 | 10 | 22 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 11.3941 | 213_92 | <25mph | <15mph | HFTD - Distribution
PG&E | 43364 | 0.88194 | 39.0273 | -122.6627 | Vegetation | Rural | < 3 meters | Customer | N.A. | 102147414 | Unknown | 12000 | Conductor | Overhead | Yes | 43364 | 0.88194 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1908 | 2018 | 9 | 21 | 21 | 10 | 18-0082278 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 281055 | 7.5535 | 144_239 | <25mph | <15mph | HFTD - Distribution
PG&E | 43364 | 0.95972 | 38.6428 | -122.7453 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102218862 | Unknown | 12000 | Conductor | Overhead | Yes | 43364 | 0.95972 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1909 | 2018 | 9 | 21 | 23 | 2 | 18-0082304 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 9470 | 25.633 | 216_90 | 25-40mph | >=15mph | HFTD - Distribution
PG&E | 43366 | 0.66458 | 37.335 | -121.7679 | Vegetation | Urban | 10 - 99 Acres | Fire Agency | San Jose FD | 100576722 | AT&T | 21000 | Conductor | Overhead | Yes | 43366 | 0.66458 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1912 | 2018 | 9 | 23 | 15 | 57 | 18-0082586 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 231441 | 9.1969 | 229_213 | <25mph | <15mph | HFTD - Distribution
PG&E | 43367 | 0.024306 | 39.8152 | -121.6438 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Pole 3/42B | None | 60000 | Conductor | Overhead | Yes | 43367 | 0.024306 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1913 | 2018 | 9 | 24 | 0 | 35 | INT-11388 | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 2407691 | 10.7907 | 177_225 | <25mph | <15mph | HFTD - Transmission
PG&E | 43370 | 0.15278 | 37.5473 | -120.3255 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Twr 12/2 | None | 70000 | Conductor | Overhead | Yes | 43370 | 0.15278 | Contact From Object | N.A. | Other | Electric Facility | Unknown | guano | no-match | 1916 | 2018 | 9 | 27 | 3 | 40 | INT-11393 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 0 | 5.6633 | 206_185 | <25mph | <15mph | HFTD - Transmission
PG&E | 43370 | 0.52986 | 38.5148 | -122.4463 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Twr 000/010 | None | 60000 | Conductor | Overhead | Yes | 43370 | 0.52986 | Contact From Object | N.A. | Other | Electric Facility | Human Error | helicopter | no-match | 1917 | 2018 | 9 | 27 | 12 | 43 | INT-11394 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1488992 | 15.276 | 168_262 | <25mph | >=15mph | HFTD - Transmission
PG&E | 43372 | 0.67778 | 41.0219 | -123.655 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Hoopa Fire Dept | 100962165 | Unknown | 12000 | Conductor | Overhead | Yes | 43372 | 0.67778 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1923 | 2018 | 9 | 29 | 16 | 16 | 18-0084877 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 16028 | 1.1171 | 137_268 | <25mph | <15mph | HFTD - Distribution
PG&E | 43380 | 0.072222 | 37.178 | -122.0267 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Mike Mathiesen 408-472-1613 Incident # SCU7096 | 100518363 | Unknown | 12000 | Conductor | Overhead | Yes | 43380 | 0.072222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1929 | 2018 | 10 | 7 | 1 | 44 | 18-0087807 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 224444 | 2.1469 | 89_407 | <25mph | <15mph | HFTD - Distribution
PG&E | 43381 | 0.46042 | 38.2621 | -122.7881 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101987186 | AT&T | 12000 | Conductor | Overhead | No | N.A. | N.A. | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1933 | 2018 | 10 | 8 | 11 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 12.638 | 148_346 | <25mph | <15mph | HFTD - Distribution
PG&E | 43387 | 0.48611 | 40.3598 | -122.4388 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TOM STROING 530-200-5113 | 101506416 | AT&T | 12000 | Conductor | Overhead | Yes | 43387 | 0.48611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1938 | 2018 | 10 | 14 | 11 | 40 | 18-0090193 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 945 | 27.4784 | 151_222 | 25-40mph | >=15mph | HFTD - Distribution
PG&E | 43387 | 0.81875 | 38.446 | -120.5147 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | IC- Dillon Gissell- 209-295-7735 | 103384485 | Unknown | 12000 | Conductor | Overhead | Yes | 43387 | 0.81875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1939 | 2018 | 10 | 14 | 19 | 39 | 18-0090288 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3497327 | 3.8374 | 122_254 | <25mph | <15mph | HFTD - Distribution
PG&E | 43387 | 0.83889 | 38.8935 | -120.8497 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103674516 | Unknown | 21000 | Conductor | Overhead | Yes | 43387 | 0.83889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1940 | 2018 | 10 | 14 | 20 | 8 | 18-0090299 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 48095 | 7.96 | 176_269 | <25mph | <15mph | HFTD - Distribution
PG&E | 43388 | 0.14097 | 38.2897 | -120.5803 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103378003 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43388 | 0.14097 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1941 | 2018 | 10 | 15 | 3 | 23 | 18-0090342 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1464 | 9.1874 | 163_314 | <25mph | <15mph | HFTD - Distribution
PG&E | 43389 | 0.44722 | 40.5097 | -124.1624 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101004106 | Unknown | 12000 | Conductor | Overhead | Yes | 43389 | 0.44722 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1942 | 2018 | 10 | 16 | 10 | 44 | 18-0090952 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 2081 | 5.6665 | 166_277 | <25mph | <15mph | HFTD - Distribution
PG&E | 43389 | 0.6875 | 38.7754 | -122.8976 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MARK GRADEK (707) 889-4303 | 101962692 | AT&T | 12000 | Conductor | Overhead | Yes | 43389 | 0.6875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1943 | 2018 | 10 | 16 | 16 | 30 | 18-0091127 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 744 | 14.3383 | 156_183 | <25mph | <15mph | HFTD - Distribution
PG&E | 43393 | 0.60486 | 40.5218 | -124.1137 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Str. 003/000 | None | 60000 | Conductor | Overhead | Yes | 43393 | 0.60486 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1947 | 2018 | 10 | 20 | 14 | 31 | INT-11477 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 410982 | 15.6973 | 218_255 | <25mph | >=15mph | HFTD - Transmission
PG&E | 43394 | 0.022222 | 35.5035 | -120.6025 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101886776 | Unknown | 21000 | Conductor | Overhead | Yes | 43394 | 0.022222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1948 | 2018 | 10 | 21 | 0 | 32 | 18-0092526 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 302559 | 0.30731 | 67_380 | <25mph | <15mph | HFTD - Distribution
PG&E | 43397 | 0.29722 | 37.9475 | -120.2671 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SCOTT PITTMAN 209-768-8182 TCU INCIDENT# 012528 | 101047865 | Unknown | 17000 | Conductor | Overhead | Yes | 43397 | 0.29722 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1949 | 2018 | 10 | 24 | 7 | 8 | 18-0093599 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 13433 | 10.0852 | 118_282 | <25mph | <15mph | HFTD - Distribution
PG&E | 43397 | 0.59583 | 36.7265 | -119.1086 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CHRIS CHRISTOPHERSON (559)493-4320 I.C #18CAFKUO15649 | 100691946 | None | 12000 | Conductor | Overhead | Yes | 43397 | 0.59583 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1950 | 2018 | 10 | 24 | 14 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 5.8362 | 159_241 | <25mph | <15mph | HFTD - Distribution
PG&E | 43398 | 0.78264 | 35.5566 | -118.8168 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | GREG BLACK (661)391-7000 | 100203660 | None | 0 – 750 | Conductor | Overhead | Yes | 43398 | 0.78264 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1951 | 2018 | 10 | 25 | 18 | 47 | 18-0094369 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 1309 | 15.6464 | 223_76 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43399 | 0.87153 | 40.1528 | -122.3634 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT. ROB WAELTY 530-527-6113 | 101553579 | Unknown | 12000 | Conductor | Overhead | Yes | 43399 | 0.87153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1953 | 2018 | 10 | 26 | 20 | 55 | 18-0094702 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4812 | 1.3833 | 69_380 | <25mph | <15mph | HFTD - Distribution
PG&E | 43401 | 0.36806 | 36.3792 | -121.8454 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TONY (831) 625-6415 | 101672342 | Unknown | 12000 | Conductor | Overhead | Yes | 43401 | 0.36806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1954 | 2018 | 10 | 28 | 8 | 50 | 18-0094889 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 3046 | 16.096 | 217_101 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43405 | 0.86458 | 38.372 | -123.0507 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103852431 | AT&T | 12000 | Conductor | Overhead | Yes | 43405 | 0.86458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1958 | 2018 | 11 | 1 | 20 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 21.5695 | 137_226 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43411 | 0.65903 | 37.0003 | -121.9802 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 101684527 | Unknown | 21000 | Capacitor Bank | Overhead | Yes | 43411 | 0.65903 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1959 | 2018 | 11 | 7 | 15 | 49 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 2.5393 | 142_358 | <25mph | <15mph | HFTD - Distribution
PG&E | 43413 | 0.20069 | 39.8234 | -121.8382 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100402367 | AT&T | 12000 | Conductor | Overhead | Yes | 43413 | 0.20069 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1963 | 2018 | 11 | 9 | 4 | 49 | 18-0098482 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 11900 | 1.6773 | 158_202 | <25mph | <15mph | HFTD - Distribution
PG&E | 43413 | 0.37431 | 37.2809 | -122.1214 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100546562 | AT&T | 12000 | Conductor | Overhead | Yes | 43413 | 0.37431 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1964 | 2018 | 11 | 9 | 8 | 59 | 18-0098521 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 77077 | 7.1129 | 111_260 | <25mph | <15mph | HFTD - Distribution
PG&E | 43414 | 0.56319 | 37.0467 | -121.9853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101671641 | Unknown | 21000 | Conductor | Overhead | Yes | 43414 | 0.56319 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1966 | 2018 | 11 | 10 | 13 | 31 | 18-0098856 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 1482 | 20.6863 | 181_339 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43415 | 0.17917 | 38.4341 | -122.5522 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102032588 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43415 | 0.17917 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1967 | 2018 | 11 | 11 | 4 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.4656 | 230_66 | <25mph | <15mph | HFTD - Distribution
PG&E | 43417 | 0.65347 | 37.0644 | -121.9578 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101680441 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43417 | 0.65347 | Other | N.A. | N.A. | N.A. | Human Error | Grow house | Other/Unknown | 1973 | 2018 | 11 | 13 | 15 | 41 | 18-0099492 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 21484 | 9.4329 | 156_187 | <25mph | <15mph | HFTD - Distribution
PG&E | 43419 | 0.25625 | 38.3599 | -122.3682 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102241814 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43419 | 0.25625 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1974 | 2018 | 11 | 15 | 6 | 9 | 18-0099862 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 441 | 0.37625 | 132_263 | <25mph | <15mph | HFTD - Distribution
PG&E | 43419 | 0.27361 | 38.6082 | -120.9532 | Vegetation | Rural | < 0.25 Acres | Self Extinguished | N.A. | 101414740 | Unknown | 12000 | Conductor | Overhead | Yes | 43419 | 0.27361 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1975 | 2018 | 11 | 15 | 6 | 34 | 18-0099901 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 5325 | 7.2449 | 211_189 | <25mph | <15mph | HFTD - Distribution
PG&E | 43420 | 0.70972 | 38.7574 | -120.9012 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101409894 | AT&T | 21000 | Conductor | Overhead | Yes | 43420 | 0.70972 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1976 | 2018 | 11 | 16 | 17 | 2 | 18-0100490 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 119860 | 9.3935 | 156_202 | <25mph | <15mph | HFTD - Distribution
PG&E | 43421 | 0.72222 | 38.7082 | -120.6927 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101421319 | Unknown | 12000 | Conductor | Overhead | Yes | 43421 | 0.72222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1977 | 2018 | 11 | 17 | 17 | 20 | 18-0100697 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 35749 | 5.1336 | 122_266 | <25mph | <15mph | HFTD - Distribution
PG&E | 43425 | 0.094444 | 40.4383 | -124.3847 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101005309 | Frontier | 12000 | Conductor | Overhead | Yes | 43425 | 0.094444 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | Other/Unknown | 1982 | 2018 | 11 | 21 | 2 | 16 | 18-0101683 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 4834 | 14.51 | 201_273 | <25mph | <15mph | HFTD - Distribution
PG&E | 43446 | 0.50625 | 38.727 | -120.7947 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 101404403 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43446 | 0.50625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1984 | 2018 | 12 | 12 | 12 | 9 | No ILIS or TOTL available | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.7011 | 213_278 | <25mph | <15mph | HFTD - Distribution
PG&E | 43448 | 0.43889 | 40.4379 | -123.7834 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101009136 | Unknown | 12000 | Conductor | Overhead | Yes | 43448 | 0.43889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1985 | 2018 | 12 | 14 | 10 | 32 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.4933 | 225_71 | <25mph | <15mph | HFTD - Distribution
1. Butte | 42256 | 0.60139 | 38.3297 | -120.7042 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1987 | 2015 | 9 | 9 | 14 | 26 |  | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 1353755 | 6.6041 | 169_267 | <25mph | <15mph | HFTD - Distribution
2. Cascade (Neu Wind Complex) | 43016 | 0.98958 | 39.322 | -121.4021 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1988 | 2017 | 10 | 8 | 23 | 45 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Equip Failure | Conductor | 0 | 7.1971 | 208_90 | <25mph | <15mph | HFTD - Distribution
3. Redwood Valley (Mendocino Lake Complex) | 43016 | 0.98333 | 39.2487 | -123.1663 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1989 | 2017 | 10 | 8 | 23 | 36 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 19.9148 | 57_376 | <25mph | >=15mph | HFTD - Distribution
4. Nuns (Central LNU Complex) | 43016 | 0.91667 | 38.4041 | -122.5209 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1990 | 2017 | 10 | 8 | 22 | 0 |  | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 9.3371 | 155_254 | <25mph | <15mph | HFTD - Distribution
5. Atlas (Southern LNU Complex) | 43016 | 0.91111 | 38.3921 | -122.2437 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1991 | 2017 | 10 | 8 | 21 | 52 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 13.5134 | 208_279 | <25mph | <15mph | HFTD - Distribution
7. Camp Fire | 43412 | 0.27292 | 39.8134 | -121.4347 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 60000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1993 | 2018 | 11 | 8 | 6 | 33 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Conductor | 826291590 | 18.2809 | 156_335 | <25mph | >=15mph | HFTD - Transmission
PG&E | 43481 | 0.011806 | 38.0621 | -120.1964 | Vegetation | Conifer Forest | Structure Only | Cal Fire |  | 163661701 |  | 17000 | Conductor | Overhead | Yes | 43481 | 0.011806 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-01 | 2019 | 1 | 16 | 0 | 17 | 19-0010443 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1041827 | 24.1103 | 234_243 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43537 | 0.67222 | 39.8831 | -122.5498 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 6Fn0313191607 |  | 12000 | Conductor | Overhead | Yes | 43537 | 0.67222 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-194 | 2019 | 3 | 13 | 16 | 8 | 19-0033617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 21012 | 19.1124 | 134_343 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43543 | 0.53611 | 37.9956 | -120.3244 | Tree - cutting, 3rd party | Hardwood Forest | 1 meter - < 3 meters | Self Extinguished |  | 101045032 |  | 17000 | Conductor | Overhead | Yes | 43543 | 0.53611 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-187 | 2019 | 3 | 19 | 12 | 52 | 19-0035101 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 70602 | 13.0291 | 229_239 | <25mph | <15mph | HFTD - Distribution
PG&E | 43564 | 0.58819 | 34.6311 | -119.9813 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Fire Dept | Santa Barbra County FD | 101863014 |  | 12000 | Conductor | Overhead | Yes | 43564 | 0.58819 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-263 | 2019 | 4 | 9 | 14 | 7 | 19-0040969 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 70756 | 15.9085 | 246_53 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43564 | 0.64375 | 37.7341 | -120.0776 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 101076921 |  | 21000 | Pole | Overhead | Yes | 43564 | 0.64375 | Vegetation |  | Veg. contact | Pole |  |  | Branch (Not overhanging, > 12ft) | 2019-313 | 2019 | 4 | 9 | 15 | 27 | 19-0041008 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 179862 | 22.6475 | 241_182 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43575 | 0.28958 | 37.8686 | -121.6843 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | East County FD | Unknown |  | 17000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-321 | 2019 | 4 | 20 | 6 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 22.6108 | 170_232 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43583 | 0.525 | 39.6756 | -121.5677 |  | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 100404366 |  | 12000 | Conductor | Overhead | Yes | 43583 | 0.525 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-166 | 2019 | 4 | 28 | 12 | 36 | 19-0046853 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 79810 | 8.9649 | 175_331 | <25mph | <15mph | HFTD - Distribution
PG&E | 43593 | 0.43264 | 39.3851 | -122.557 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | Colusa FD | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-312 | 2019 | 5 | 8 | 10 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.7314 | 133_316 | <25mph | <15mph | HFTD - Distribution
PG&E | 43595 | 0.61944 | 40.704 | -122.8314 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Fire Dept | Lewiston FD | Keswick-Trinity 60Kv Line |  | 60000 | Conductor | Overhead | Yes | 43595 | 0.61944 | Vegetation |  | Contact from Object - Other | Electric Facility |  |  | no-match | 2019-301 | 2019 | 5 | 10 | 14 | 52 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.6998 | 123_389 | <25mph | <15mph | HFTD - Transmission
PG&E | 43600 | 0.89653 | 38.5731 | -122.9603 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Unknown |  | 103931177 |  | 12000 | Conductor | Overhead | Yes | 43600 | 0.89653 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-316 | 2019 | 5 | 15 | 21 | 31 | 19-0052480 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 27780 | 17.9493 | 115_271 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43602 | 0.63333 | 38.4797 | -123.1486 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 42811111 |  | 12000 | Conductor | Overhead | Yes | 43602 | 0.63333 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-200 | 2019 | 5 | 17 | 15 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.8024 | 107_266 | <25mph | <15mph | HFTD - Distribution
PG&E | 43602 | 0.7875 | 38.0476 | -122.2064 | Bird Found | Urban | 3 meters - 0.25 Acres | Fire Dept | Crockett FD | 2Jt0517191854 |  | 21000 | Pole | Overhead | Yes | 43602 | 0.7875 | Contact - Animal - Bird |  | Animal contact | Pole | Animal Contact |  | Other/Unknown | 2019-02 | 2019 | 5 | 17 | 18 | 54 | 19-0053464 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 17.125 | 147_242 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43609 | 0.62708 | 35.1696 | -120.5103 |  | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 40589503 |  | 500000 | Pole | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-100 | 2019 | 5 | 24 | 15 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 8.7091 | 205_188 | <25mph | <15mph | HFTD - Transmission
PG&E | 43614 | 0.70417 | 37.0371 | -119.5209 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 100680674 |  | 12000 | Pole | Overhead | Yes | 43614 | 0.70417 | Vegetation |  | Veg. contact | Pole |  |  | Dead | 2019-202 | 2019 | 5 | 29 | 16 | 54 | 19-0059237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 6780 | 6.2481 | 265_186 | <25mph | <15mph | HFTD - Distribution
PG&E | 43614 | 0.85069 | 39.0194 | -121.0608 |  | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match |  | 2019 | 5 | 29 | 20 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 10.0293 | 197_295 | <25mph | <15mph | HFTD - Distribution
PG&E | 43615 | 0.34583 | 35.7005 | -120.8104 | Vehicle | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 101871463 |  | 12000 | Pole | Overhead | Yes | 43615 | 0.34583 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-274 | 2019 | 5 | 30 | 8 | 18 | 19-0059906 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 171603 | 3.7561 | 208_112 | <25mph | <15mph | HFTD - Distribution
PG&E | 43616 | 0.64236 | 40.4431 | -121.8211 |  | Hardwood Woodland | 1 meter - < 3 meters | Self Extinguished |  | 101556319 |  | 12000 | Conductor | Overhead | Yes | 43616 | 0.64236 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-88 | 2019 | 5 | 31 | 15 | 25 | 19-0060901 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 55546 | 3.729 | 165_374 | <25mph | <15mph | HFTD - Distribution
PG&E | 43619 | 0.60486 | 40.6822 | -122.2806 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 101466598 |  | 12000 | Transformer | Overhead | Yes | 43619 | 0.60486 | Equipment - Overloaded | Transformer |  |  |  |  | no-match | 2019-161 | 2019 | 6 | 3 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 9.6637 | 145_374 | <25mph | <15mph | HFTD - Distribution
PG&E | 43619 | 0.61597 | 40.4419 | -122.3036 |  | Herbaceous | 1 meter - < 3 meters | Fire Dept | Anderson FD | 101495889 |  | 12000 | Insulator | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-456 | 2019 | 6 | 3 | 14 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.2059 | 146_387 | <25mph | <15mph | HFTD - Distribution
PG&E | 43622 | 0.37569 | 35.6384 | -118.9687 | Bird Found | Herbaceous | 0.25 - 10 Acres | Fire Dept | Kern County FD | 100216096 |  | 21000 | Conductor | Overhead | No |  |  | Contact - Animal - Other |  | Animal contact |  | Animal Contact |  | no-match | 2019-228 | 2019 | 6 | 6 | 9 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 8.7714 | 291_110 | <25mph | <15mph | HFTD - Distribution
PG&E | 43622 | 0.85417 | 38.4969 | -122.6435 |  | Barren/Other | < 1 meter | Self Extinguished |  | Unknown |  | 230000 | Circuit Breaker | Overhead | Yes | 43622 | 0.85417 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | no-match | 2019-102 | 2019 | 6 | 6 | 20 | 30 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 20.0966 | 129_267 | <25mph | >=15mph | HFTD - Transmission
PG&E | 43623 | 0.41528 | 38.7285 | -123.3528 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 042861101 |  | 21000 | Conductor | Overhead | Yes | 43623 | 0.41528 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-358 | 2019 | 6 | 7 | 9 | 58 | 19-0064216 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 5301 | 9.4575 | 98_280 | <25mph | <15mph | HFTD - Distribution
PG&E | 43624 | 0.78542 | 38.6105 | -122.9732 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 42751113 |  | 12000 | Conductor | Overhead | Yes | 43624 | 0.78542 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-355 | 2019 | 6 | 8 | 18 | 51 | 19-0064689 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 44664 | 19.8533 | 114_273 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43626 | 0.56181 | 38.8137 | -120.9433 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Other | Customer | 153652109 |  | 21000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-243 | 2019 | 6 | 10 | 13 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.416 | 202_284 | <25mph | <15mph | HFTD - Distribution
PG&E | 43626 | 0.67917 | 38.1107 | -122.9025 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 42291101 |  | 12000 | Conductor | Overhead | Yes | 43626 | 0.67917 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-401 | 2019 | 6 | 10 | 16 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 2.4799 | 159_198 | <25mph | <15mph | HFTD - Distribution
PG&E | 43626 | 0.69028 | 38.821 | -120.846 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Garden Valley FD | 153082106 |  | 21000 | Conductor | Overhead | Yes | 43626 | 0.69028 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-372 | 2019 | 6 | 10 | 16 | 34 | 19-0065481 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14169 | 3.2821 | 206_284 | <25mph | <15mph | HFTD - Distribution
PG&E | 43629 | 0.020833 | 36.5759 | -121.7284 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire |  | 182222104 |  | 21000 | Conductor | Overhead | Yes | 43629 | 0.020833 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-341 | 2019 | 6 | 13 | 0 | 30 | 19-0067072 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 148986 | 13.4853 | 167_161 | <25mph | <15mph | HFTD - Distribution
PG&E | 43630 | 0.19306 | 37.5525 | -120.3254 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 011/008 |  | 70000 | Insulator | Overhead | No |  |  | Equipment - PG&E | Insulator |  |  |  |  | no-match | 2019-79 | 2019 | 6 | 14 | 4 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | N.A. | 16.3246 | 229_214 | <25mph | >=15mph | HFTD - Transmission
PG&E | 43631 | 0.58889 | 38.8802 | -122.6125 | Tree - cutting, 3rd party | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 43361103 |  | 12000 | Pole | Overhead | Yes | 43631 | 0.58889 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | Other/Unknown | 2019-19 | 2019 | 6 | 15 | 14 | 8 | 19-0068074 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 259562 | 3.4453 | 130_288 | <25mph | <15mph | HFTD - Distribution
PG&E | 43633 | 0.43403 | 38.511 | -122.2134 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 43051101 |  | 12000 | Conductor | Overhead | Yes | 43633 | 0.43403 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-84 | 2019 | 6 | 17 | 10 | 25 | 19-0068579 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 306900 | 7.2677 | 147_267 | <25mph | <15mph | HFTD - Distribution
PG&E | 43634 | 0.82569 | 35.8876 | -120.9217 | Bird Found | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Pole | Overhead | Yes | 43634 | 0.82569 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | no-match | 2019-55 | 2019 | 6 | 18 | 19 | 49 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 18.1842 | 145_332 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43635 | 0.48889 | 39.8612 | -121.6907 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100400933 |  | 12000 | Conductor | Overhead | Yes | 43635 | 0.48889 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-224 | 2019 | 6 | 19 | 11 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.3558 | 187_228 | <25mph | <15mph | HFTD - Distribution
PG&E | 43642 | 0.55139 | 40.0185 | -122.4107 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | Circuit Id 103331101 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43642 | 0.55139 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-331 | 2019 | 6 | 26 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.2962 | 140_351 | <25mph | <15mph | HFTD - Distribution
PG&E | 43643 | 0.099306 | 36.8198 | -119.3334 | Bird Found | Hardwood Woodland | 0.25 - 10 Acres | Self Extinguished |  | Kings River-Sanger-Reedley 115Kv At 16/089 |  | 115000 | Insulator | Overhead | Yes | 43643 | 0.099306 | Equipment - PG&E | Insulator |  |  |  |  | no-match | 2019-104 | 2019 | 6 | 27 | 2 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | N.A. | 12.3568 | 273_175 | <25mph | <15mph | HFTD - Transmission
PG&E | 43647 | 0.09375 | 38.2955 | -120.8335 |  | Shrub | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-252 | 2019 | 7 | 1 | 2 | 15 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 14.0071 | 207_255 | <25mph | <15mph | HFTD - Distribution
PG&E | 43652 | 0.59861 | 34.6388 | -119.9695 |  | Herbaceous | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | 182721104 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43652 | 0.59861 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-153 | 2019 | 7 | 6 | 14 | 22 | 19-0074960 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 14213 | 3.9067 | 181_224 | <25mph | <15mph | HFTD - Distribution
PG&E | 43657 | 0.64375 | 39.5657 | -120.6614 | Vegetation | Conifer Forest | 0.25 - 10 Acres | Unknown |  | 100102596 |  | 12000 | Pole | Overhead | Yes | 43657 | 0.64375 | Vegetation |  | Veg. contact | Pole |  |  | no-match | 2019-03 | 2019 | 7 | 11 | 15 | 27 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.2742 | 214_325 | <25mph | <15mph | HFTD - Distribution
PG&E | 43659 | 0.55069 | 34.7273 | -120.4357 |  | Shrub | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | Y44 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43659 | 0.55069 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-154 | 2019 | 7 | 13 | 13 | 13 | 19-0077070 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 18256 | 8.9126 | 216_205 | <25mph | <15mph | HFTD - Distribution
PG&E | 43661 | 0.32708 | 38.3266 | -122.568 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 42721104 |  | 12000 | Conductor | Overhead | Yes | 43661 | 0.32708 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-343 | 2019 | 7 | 15 | 7 | 51 | 19-0077351 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2348 | 34.6382 | 132_257 | 25-40mph | >=15mph | HFTD - Distribution
PG&E | 43662 | 0.72986 | 40.1691 | -122.3053 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103541103 |  | 12000 | Conductor | Overhead | Yes | 43662 | 0.72986 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-375 | 2019 | 7 | 16 | 17 | 31 | 19-0078094 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 45533 | 11.6886 | 144_359 | <25mph | <15mph | HFTD - Distribution
PG&E | 43663 | 0.32569 | 34.5066 | -120.2247 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Santa Barbara County FD | 4Bx0717190747 |  | 12000 | Other | Overhead | Yes | 43663 | 0.32569 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-425 | 2019 | 7 | 17 | 7 | 49 | 19-0078239 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 19608 | 28.1419 | 235_46 | 25-40mph | >=15mph | HFTD - Distribution
PG&E | 43664 | 0.83125 | 37.081 | -119.4865 |  | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | No |  |  | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-09 | 2019 | 7 | 18 | 19 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 2.894 | 217_203 | <25mph | <15mph | HFTD - Distribution
PG&E | 43664 | 0.43542 | 38.3033 | -120.6718 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | B561 |  | 12000 | Other | Overhead | Yes | 43664 | 0.43542 | Equipment - PG&E | Other |  |  |  |  | Other/Unknown | 2019-68 | 2019 | 7 | 18 | 10 | 27 | 19-0078904 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45558 | 8.4459 | 253_164 | <25mph | <15mph | HFTD - Distribution
PG&E | 43665 | 0.49931 | 37.9162 | -120.349 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 163351703 |  | 17000 | Conductor | Overhead | Yes | 43665 | 0.49931 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-376 | 2019 | 7 | 19 | 11 | 59 | 19-0079030 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24042 | 8.2161 | 228_234 | <25mph | <15mph | HFTD - Distribution
PG&E | 43667 | 0.53194 | 37.0517 | -122.1522 | Vegetation | Urban | 1 meter - < 3 meters | Cal Fire |  | 82931101 |  | 12000 | Conductor | Overhead | Yes | 43667 | 0.53194 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-377 | 2019 | 7 | 21 | 12 | 46 | 19-0079583 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 89102 | 6.0013 | 254_171 | <25mph | <15mph | HFTD - Distribution
PG&E | 43667 | 0.42639 | 38.9716 | -120.9991 |  | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire | Placer Hill FD | 152241102 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43667 | 0.42639 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-127 | 2019 | 7 | 21 | 10 | 14 | 19-0079578 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 32850 | 2.0112 | 151_219 | <25mph | <15mph | HFTD - Distribution
PG&E | 43668 | 0.34097 | 38.7687 | -120.9633 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | El Dorado County FD | 6Ht0722190809 |  | 21000 | Other | Overhead | Yes | 43668 | 0.34097 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-49 | 2019 | 7 | 22 | 8 | 11 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 6.9601 | 201_281 | <25mph | <15mph | HFTD - Distribution
PG&E | 43668 | 0.90208 | 38.8618 | -121.1044 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 152561103 |  | 12000 | Conductor | Overhead | Yes | 43668 | 0.90208 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-336 | 2019 | 7 | 22 | 21 | 39 | 19-0080025 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 9842 | 11.9728 | 195_286 | <25mph | <15mph | HFTD - Distribution
PG&E | 43669 | 0.68819 | 37.2447 | -121.9999 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Santa Clara County FD | 83371104 |  | 12000 | Conductor | Overhead | Yes | 43669 | 0.68819 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-378 | 2019 | 7 | 23 | 16 | 31 | 19-0080428 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 19250 | 3.302 | 156_198 | <25mph | <15mph | HFTD - Distribution
PG&E | 43669 | 0.70486 | 37.2128 | -119.505 | Gun Shot | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | 252521103 |  | 12000 | Conductor | Overhead | Yes | 43669 | 0.70486 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-434 | 2019 | 7 | 23 | 16 | 55 | 19-0080383 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 513358 | 5.8456 | 265_196 | <25mph | <15mph | HFTD - Distribution
PG&E | 43671 | 0.010417 | 39.0662 | -120.9754 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Placer Hills FD | 152491101 |  | 12000 | Conductor | Overhead | Yes | 43671 | 0.010417 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-379 | 2019 | 7 | 25 | 0 | 15 | 19-0080924 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7845 | 10.1883 | 200_298 | <25mph | <15mph | HFTD - Distribution
PG&E | 43671 | 0.31875 | 39.1735 | -123.5763 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Oj 2 P/Ss Of Cgc# 215532055340 |  | 12000 | Other | Overhead | Yes | 43671 | 0.31875 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-380 | 2019 | 7 | 25 | 7 | 39 | 19-0080947 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 790 | 6.0339 | 89_305 | <25mph | <15mph | HFTD - Distribution
PG&E | 43672 | 0.50208 | 38.8003 | -120.8258 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire |  | 153082106 |  | 21000 | Conductor | Overhead | Yes | 43672 | 0.50208 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-381 | 2019 | 7 | 26 | 12 | 3 | 19-0081559 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 16465 | 4.5929 | 207_283 | <25mph | <15mph | HFTD - Distribution
PG&E | 43673 | 0.34861 | 40.3789 | -122.1873 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Self Extinguished |  | 103461102 |  | 12000 | Conductor | Overhead | Yes | 43673 | 0.34861 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-382 | 2019 | 7 | 27 | 8 | 22 | 19-0081756 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 456 | 11.9501 | 223_236 | <25mph | <15mph | HFTD - Distribution
PG&E | 43673 | 0.67847 | 37.7266 | -120.3246 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire |  | 252811102 |  | 12000 | Conductor | Overhead | Yes | 43673 | 0.67847 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-383 | 2019 | 7 | 27 | 16 | 17 | 19-0081851 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 2694 | 9.6205 | 149_370 | <25mph | <15mph | HFTD - Distribution
PG&E | 43673 | 0.20208 | 37.9486 | -120.4656 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 163781705 |  | 17000 | Conductor | Overhead | Yes | 43673 | 0.20208 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-385 | 2019 | 7 | 27 | 4 | 51 | 19-0081744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 1364 | 7.5204 | 229_224 | <25mph | <15mph | HFTD - Distribution
PG&E | 43676 | 0.63542 | 39.1207 | -121.072 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 152691104 |  | 12000 | Conductor | Overhead | Yes | 43676 | 0.63542 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-386 | 2019 | 7 | 30 | 15 | 15 | 19-0082713 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 31302 | 1.5622 | 72_405 | <25mph | <15mph | HFTD - Distribution
PG&E | 43678 | 0.56111 | 38.5721 | -120.6803 | Equipment Failure/Involved, Overhead | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 153662102 |  | 21000 | Conductor | Overhead | Yes | 43678 | 0.56111 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-170 | 2019 | 8 | 1 | 13 | 28 | 19-0083500 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1374 | 11.2785 | 213_271 | <25mph | <15mph | HFTD - Distribution
PG&E | 43682 | 0.94306 | 37.1869 | -119.7902 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Unknown |  | 322066125092 |  | 21000 | Transformer | Overhead | Yes | 43682 | 0.94306 | Equipment - Overloaded | Transformer |  |  |  |  | Other/Unknown | 2019-134 | 2019 | 8 | 5 | 22 | 38 | 19-0084586 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 996 | 11.4699 | 253_195 | <25mph | <15mph | HFTD - Distribution
PG&E | 43683 | 0.50833 | 39.0506 | -121.0614 | Vegetation | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 100107532 |  | 12000 | Insulator | Overhead | Yes | 43683 | 0.50833 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-391 | 2019 | 8 | 6 | 12 | 12 | 19-0084799 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 60943 | 6.1843 | 167_160 | <25mph | <15mph | HFTD - Distribution
PG&E | 43688 | 0.054861 | 39.1152 | -121.001 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100097796 |  | 12000 | Other | Overhead | Yes | 43688 | 0.054861 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-387 | 2019 | 8 | 11 | 1 | 19 | 19-0086613 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6200 | 14.6091 | 199_300 | <25mph | <15mph | HFTD - Distribution
PG&E | 43689 | 0.8375 | 39.0952 | -123.4937 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 102177212 |  | 12000 | Conductor | Overhead | Yes | 43689 | 0.8375 | Vegetation |  | Veg. contact |  |  |  | Fell into (No defect) | 2019-400 | 2019 | 8 | 12 | 20 | 6 | 19-0087090 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2508 | 6.9872 | 210_275 | <25mph | <15mph | HFTD - Distribution
PG&E | 43689 | 0.7375 | 38.6618 | -120.7451 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 101415488, 101404439 |  | 12000 | Pole | Overhead | Yes | 43689 | 0.7375 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (slight defect) | 2019-241 | 2019 | 8 | 12 | 17 | 42 | 19-0087080 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 54604 | 15.2648 | 93_301 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43690 | 0.4375 | 36.6102 | -121.4452 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 40761041 |  | 115000 | Other | Overhead | Yes | 43690 | 0.4375 | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-164 | 2019 | 8 | 13 | 10 | 30 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 5.4434 | 180_162 | <25mph | <15mph | HFTD - Transmission
PG&E | 43691 | 0.42778 | 35.379 | -120.4232 | Vegetation | Hardwood Woodland | < 1 meter | Cal Fire |  | 512769069280 |  | 21000 | Conductor | Overhead | Yes | 43691 | 0.42778 | Vegetation | [5 empty] | no-match |  | 2019 | 8 | 14 | 10 | 16 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.5585 | 242_183 | <25mph | <15mph | HFTD - Distribution
PG&E | 43693 | 0.34653 | 40.1235 | -123.8758 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Self Extinguished |  | 192221102-2101118022{5563} |  | 12000 | Conductor | Overhead | Yes | 43693 | 0.34653 | Vegetation | [5 empty] | Other/Unknown |  | 2019 | 8 | 16 | 8 | 19 | 19-0088744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 2979 | 4.0105 | 78_358 | <25mph | <15mph | HFTD - Distribution
PG&E | 43693 | 0.43819 | 39.3714 | -121.3221 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103191101 |  | 12000 | Conductor | Overhead | Yes | 43693 | 0.43819 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-397 | 2019 | 8 | 16 | 10 | 31 | 19-0088805 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4580 | 6.0086 | 254_161 | <25mph | <15mph | HFTD - Distribution
PG&E | 43696 | 0.72708 | 40.9399 | -123.6322 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | California Department of Forestry | 192171101 |  | 12000 | Conductor | Overhead | Yes | 43696 | 0.72708 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-340 | 2019 | 8 | 19 | 17 | 27 | 19-0089645 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 410686 | 4.2049 | 90_403 | <25mph | <15mph | HFTD - Distribution
PG&E | 43697 | 0.37708 | 41.1088 | -121.5034 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-297 | 2019 | 8 | 20 | 9 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.1717 | 178_411 | <25mph | <15mph | HFTD - Distribution
PG&E | 43699 | 0.93264 | 39.139 | -121.0194 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 152481106 |  | 12000 | Conductor | Overhead | Yes | 43699 | 0.93264 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-346 | 2019 | 8 | 22 | 22 | 23 | 19-0091224 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38628 | 10.5918 | 199_302 | <25mph | <15mph | HFTD - Distribution
PG&E | 43701 | 0.79306 | 39.0497 | -121.0614 | Vehicle | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 103956556 |  | 12000 | Pole | Overhead | Yes | 43701 | 0.79306 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-114 | 2019 | 8 | 24 | 19 | 2 | 19-0091826 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 144608 | 12.5435 | 138_217 | <25mph | <15mph | HFTD - Distribution
PG&E | 43702 | 0.55069 | 41.0935 | -123.6942 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Unknown | 115334464574 |  | 12000 | Transformer | Overhead | Yes | 43702 | 0.55069 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-351 | 2019 | 8 | 25 | 13 | 13 | 19-0091921 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 20311 | 14.3939 | 131_272 | <25mph | <15mph | HFTD - Distribution
PG&E | 43708 | 0.43056 | 40.661 | -122.356 | Vehicle | Barren/Other | 3 meters - 0.25 Acres | Fire Dept | Shasta Lake FD | 103571671 | Yes | 12000 | Fuse | Overbuild | Yes | 43708 | 0.43056 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-421 | 2019 | 8 | 31 | 10 | 20 | 19-0094332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3050 | 11.4855 | 143_386 | <25mph | <15mph | HFTD - Distribution
PG&E | 43709 | 0.70139 | 35.908 | -121.011 |  | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 103477437 |  | 12000 | Pole | Overhead | Yes | 43709 | 0.70139 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-17 | 2019 | 9 | 1 | 16 | 50 | 19-0094475 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45432 | 7.3653 | 133_243 | <25mph | <15mph | HFTD - Distribution
PG&E | 43713 | 0.95972 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire | California Department of Forestry | 101670112 |  | 12000 | Fuse | Overhead | Yes | 43713 | 0.95972 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-388 | 2019 | 9 | 5 | 23 | 2 | 19-0095858 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 17920 | 6.5368 | 147_193 | <25mph | <15mph | HFTD - Distribution
PG&E | 43718 | 0.30069 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 82841102 |  | 12000 | Conductor | Overhead | Yes | 43718 | 0.30069 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-369 | 2019 | 9 | 10 | 7 | 13 | 19-0097264 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 23500 | 11.5457 | 147_193 | <25mph | <15mph | HFTD - Distribution
PG&E | 43719 | 0.87708 | 38.3132 | -120.9809 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 163341103 |  | 12000 | Conductor | Overhead | Yes | 43719 | 0.87708 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-370 | 2019 | 9 | 11 | 21 | 3 | 19-0098003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25994 | 13.1511 | 241_121 | <25mph | <15mph | HFTD - Distribution
PG&E | 43719 | 0.78889 | 37.9937 | -122.137 | Bird Found | Hardwood Woodland | Other | Unknown |  | Unknown |  | 115000 | Other | Overhead | Yes | 43719 | 0.78889 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-42 | 2019 | 9 | 11 | 18 | 56 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | N.A. | 11.7227 | 200_256 | <25mph | <15mph | HFTD - Transmission
PG&E | 43720 | 0.60069 | 37.3144 | -122.1865 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 024131103 |  | 12000 | Conductor | Overhead | Yes | 43720 | 0.60069 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-217 | 2019 | 9 | 12 | 14 | 25 | 19-0098386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 89097 | 11.8169 | 147_201 | <25mph | <15mph | HFTD - Distribution
PG&E | 43721 | 0.27083 | 37.3348 | -121.7716 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 83392110 |  | 21000 | Splice/Clamp/Connector | Overhead | Yes | 43721 | 0.27083 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-444 | 2019 | 9 | 13 | 6 | 30 | 19-0098560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 35534 | 0.81774 | 166_202 | <25mph | <15mph | HFTD - Distribution
PG&E | 43721 | 0.37014 | 39.0754 | -121.1717 | Bird Found | Herbaceous | 0.25 - 10 Acres | Fire Dept | Consolidated FD | Etr0913190810 |  | 12000 | Other | Overhead | Yes | 43721 | 0.37014 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-46 | 2019 | 9 | 13 | 8 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 0.13542 | 159_207 | <25mph | <15mph | HFTD - Distribution
PG&E | 43723 | 0.52639 | 38.1194 | -120.8013 | Vehicle | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103959405 |  | 12000 | Pole | Overhead | Yes | 43723 | 0.52639 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-118 | 2019 | 9 | 15 | 12 | 38 | 19-0099234 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 5378 | 19.8556 | 128_245 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43724 | 0.61042 | 37.3762 | -119.8729 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 254452102 |  | 21000 | Conductor | Overhead | Yes | 43724 | 0.61042 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-417 | 2019 | 9 | 16 | 14 | 39 | 19-0099772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 121254 | 8.2417 | 249_205 | <25mph | <15mph | HFTD - Distribution
PG&E | 43730 | 0.49722 | 37.5168 | -119.9159 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103967994 |  | 21000 | Pole | Overhead | Yes | 43730 | 0.49722 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-452 | 2019 | 9 | 22 | 11 | 56 | 19-0102232 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 133232 | 12.2404 | 247_213 | <25mph | <15mph | HFTD - Distribution
PG&E | 43734 | 0.59167 | 36.9517 | -121.8278 | Vegetation | Shrub | 1 meter - < 3 meters | Cal Fire |  | 2287 |  | 21000 | Conductor | Overhead | Yes | 43734 | 0.59167 | Vegetation |  | Veg. contact |  |  |  | Branch (OverHanging) | 2019-352 | 2019 | 9 | 26 | 14 | 12 | 19-0104163 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 2856 | 16.0268 | 163_181 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43735 | 0.4375 | 36.5336 | -121.1464 | Vegetation | Barren/Other | 0.25 - 10 Acres | Cal Fire |  | 182492105 |  | 21000 | Conductor | Overhead | Yes | 43735 | 0.4375 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-359 | 2019 | 9 | 27 | 10 | 30 | 19-0104536 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20631 | 7.4063 | 193_158 | <25mph | <15mph | HFTD - Distribution
PG&E | 43736 | 0.55278 | 37.2553 | -119.5057 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 252531103 |  | 12000 | Conductor | Overhead | Yes | 43736 | 0.55278 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-36 | 2019 | 9 | 28 | 13 | 16 | 19-0104972 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 1296 | 9.3578 | 265_198 | <25mph | <15mph | HFTD - Distribution
PG&E | 43738 | 0.60347 | 34.6139 | -120.1799 | Contact with High Voltage, 3rd party | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 183041102 |  | 12000 | Conductor | Overhead | Yes | 43738 | 0.60347 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-13 | 2019 | 9 | 30 | 14 | 29 | 19-0105582 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 4080 | 1.595 | 237_52 | <25mph | <15mph | HFTD - Distribution
PG&E | 43742 | 0.79653 | 40.4964 | -122.0448 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | Yes | 43742 | 0.79653 | Equipment - Overloaded | Other |  |  |  |  | no-match | 2019-257 | 2019 | 10 | 4 | 19 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 9.9058 | 155_377 | <25mph | <15mph | HFTD - Distribution
PG&E | 43746 | 0.74931 | 35.2979 | -120.4868 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 182541103 |  | 12000 | Conductor | Overhead | Yes | 43746 | 0.74931 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-207 | 2019 | 10 | 8 | 17 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 3.2839 | 223_90 | <25mph | <15mph | HFTD - Distribution
PG&E | 43753 | 0.028472 | 37.3237 | -119.6173 |  | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | Circuit 254432102 |  | 21000 | Insulator | Overhead | Yes | 43753 | 0.028472 | Equipment - PG&E | Insulator |  |  |  |  | Other/Unknown | 2019-168 | 2019 | 10 | 15 | 0 | 41 | 19-0111571 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 741 | 6.821 | 260_202 | <25mph | <15mph | HFTD - Distribution
PG&E | 43755 | 0.82222 | 37.6494 | -120.357 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 5Tr1017191903 |  | 12000 | Conductor | Overhead | Yes | 43755 | 0.82222 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-423 | 2019 | 10 | 17 | 19 | 44 | 19-0113175 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 10105 | 13.285 | 228_220 | <25mph | <15mph | HFTD - Distribution
PG&E | 43758 | 0.71458 | 37.1585 | -122.1339 |  | Conifer Forest | 1 meter - < 3 meters | Employee |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match |  | 2019 | 10 | 20 | 17 | 9 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 12.5691 | 150_193 | <25mph | <15mph | HFTD - Distribution
PG&E | 43761 | 0.89375 | 38.7959 | -122.7673 |  | Herbaceous | 100+ Acres | Cal Fire |  | 001/006 |  | 230000 | Jumper | Overhead | Yes | 43761 | 0.88819 | Under Investigation | Jumper |  |  |  | This ignition relates to the Kincade Fire, which is reported in compliance with D.19-05-037. The origin and cause of the Kincade Fire is under investigation by CAL FIRE and PG&E. At this time, PG&E has not formed a conclusion about the origin or cause of the Kincade Fire. | no-match |  | 2019 | 10 | 23 | 21 | 27 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 23.9173 | 159_306 | <25mph | >=15mph | HFTD - Transmission
PG&E | 43766 | 0.74167 | 37.0309 | -121.7788 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 101682849 |  | 21000 | Conductor | Overhead | Yes | 43766 | 0.74167 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-389 | 2019 | 10 | 28 | 17 | 48 | 19-0118112 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 16698 | 22.4395 | 172_227 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43766 | 0.78194 | 38.5646 | -122.4642 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 43432104 |  | 21000 | Conductor | Overhead | Yes | 43766 | 0.78194 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-357 | 2019 | 10 | 28 | 18 | 46 | 19-0118147 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 496944 | 12.705 | 184_251 | <25mph | <15mph | HFTD - Distribution
PG&E | 43766 | 0.54167 | 39.3208 | -121.1273 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 100099164 |  | 12000 | Transformer | Overbuild | Yes | 43766 | 0.54167 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-398 | 2019 | 10 | 28 | 13 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.6326 | 165_186 | <25mph | <15mph | HFTD - Distribution
PG&E | 43767 | 0.14514 | 37.0374 | -121.5207 | Animal Found | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 1471 |  | 21000 | Fuse | Overhead | Yes | 43767 | 0.14514 | Contact - Animal - Other |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-283 | 2019 | 10 | 29 | 3 | 29 | 19-0118370 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 3294 | 9.0524 | 155_199 | <25mph | <15mph | HFTD - Distribution
PG&E | 43768 | 0.56389 | 38.4792 | -122.0302 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 063681102 |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact |  |  |  | no-match | 2019-338 | 2019 | 10 | 30 | 13 | 32 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 13.7479 | 155_266 | <25mph | <15mph | HFTD - Distribution
PG&E | 43769 | 0.88958 | 39.661 | -120.6264 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Fire Dept | Sierra County FD | 152101101 |  | 12000 | Conductor | Overhead | Yes | 43769 | 0.88958 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-390 | 2019 | 10 | 31 | 21 | 21 | 19-0115942 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 7121279 | 1.9823 | 150_204 | <25mph | <15mph | HFTD - Distribution
PG&E | 43769 | 0.72431 | 38.0458 | -122.1905 |  | Herbaceous | 1 meter - < 3 meters | Fire Dept | Crockett FD | 13432207 |  | 21000 | Conductor | Overhead | Yes | 43769 | 0.72431 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-05 | 2019 | 10 | 31 | 17 | 23 | 19-0119756 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 138161 | 16.5541 | 148_260 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43769 | 0.67292 | 38.3845 | -122.1893 | Vegetation | Agriculture | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact |  |  |  | no-match | 2019-396 | 2019 | 10 | 31 | 16 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.4513 | 148_242 | <25mph | <15mph | HFTD - Distribution
PG&E | 43772 | 0.76806 | 36.2323 | -121.7622 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 182941102 |  | 12000 | Conductor | Overhead | Yes | 43772 | 0.76806 | Vegetation |  | Veg. contact |  |  |  | Fell into (Moderate-Severe defect) | 2019-371 | 2019 | 11 | 3 | 18 | 26 | 19-0120570 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 59211 | 6.5731 | 154_220 | <25mph | <15mph | HFTD - Distribution
PG&E | 43773 | 0.98056 | 34.6619 | -120.0852 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 8145 |  | 12000 | Conductor | Overhead | Yes | 43773 | 0.98056 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-125 | 2019 | 11 | 4 | 23 | 32 | 19-0121150 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 20066 | 12.9782 | 241_55 | <25mph | <15mph | HFTD - Distribution
PG&E | 43779 | 0.40764 | 35.0787 | -120.4974 |  | Herbaceous | 1 meter - < 3 meters | Cal Fire |  | 4Bx1110190931 |  | 12000 | Conductor | Overhead | Yes | 43779 | 0.40764 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-431 | 2019 | 11 | 10 | 9 | 47 | 19-0123396 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 19943 | 14.5274 | 222_78 | <25mph | <15mph | HFTD - Distribution
PG&E | 43780 | 0.28611 | 36.6822 | -119.1806 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 4Tj1111191656 |  | 12000 | Other | Overhead | Yes | 43780 | 0.28611 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-453 | 2019 | 11 | 11 | 6 | 52 | 19-0123468 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 109129 | 8.0472 | 280_167 | <25mph | <15mph | HFTD - Distribution
PG&E | 43780 | 0.40694 | 37.8782 | -120.4596 | Vehicle | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 101020184 |  | 17000 | Other | Overhead | Yes | 43780 | 0.40694 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-82 | 2019 | 11 | 11 | 9 | 46 | 19-0123520 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 38170 | 9.7973 | 223_232 | <25mph | <15mph | HFTD - Distribution
PG&E | 43790 | 0.68472 | 40.3231 | -123.9202 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 192311141 |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-416 | 2019 | 11 | 21 | 16 | 26 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 1.5362 | 77_369 | <25mph | <15mph | HFTD - Distribution
PG&E | 43791 | 0.19653 | 39.6736 | -121.3855 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 103751102 |  | 12000 | Conductor | Overhead | Yes | 43791 | 0.19653 | Vegetation |  | Veg. contact |  |  |  | Fell into (slight defect) | 2019-428 | 2019 | 11 | 22 | 4 | 43 | 19-0127475 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3712 | 7.2856 | 255_176 | <25mph | <15mph | HFTD - Distribution
PG&E | 43795 | 0.59583 | 35.4427 | -120.7567 |  | Urban | 0.25 - 10 Acres | Cal Fire |  | 511791771829 |  | 12000 | Other | Overhead | Yes | 43795 | 0.59583 | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-211 | 2019 | 11 | 26 | 14 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 15.168 | 211_98 | <25mph | >=15mph | HFTD - Distribution
PG&E | 43796 | 0.65208 | 40.6579 | -122.4211 |  | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 103521102-2101107406{2413} |  | 12000 | Fuse | Overhead | Yes | 43796 | 0.65208 | Other Fire: Non-PG&E related | [5 empty] | Other/Unknown |  | 2019 | 11 | 27 | 15 | 39 | 19-0130770 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip failure | Fuse | 8302 | 3.7534 | 142_199 | <25mph | <15mph | HFTD - Distribution
PG&E | 43796 | 0.27569 | 37.2717 | -122.3078 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 24101103 |  | 12000 | Conductor | Overhead | Yes | 43796 | 0.27569 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-362 | 2019 | 11 | 27 | 6 | 37 | 19-0130047 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 16680 | 7.6635 | 140_386 | <25mph | <15mph | HFTD - Distribution
PG&E | 43798 | 0.84583 | 39.8503 | -121.6312 |  | Shrub | 1 meter - < 3 meters | Unknown |  | 40700248, 42578814, 42578813 |  | 60000 | Pole | Overhead | Yes | 43798 | 0.84583 | Equipment - PG&E | Pole |  |  |  |  | no-match | 2019-10 | 2019 | 11 | 29 | 20 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Pole | N.A. | 10.4217 | 173_341 | <25mph | <15mph | HFTD - Transmission
PG&E | 43817 | 0.22569 | 38.2817 | -120.517 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 101273893 |  | 12000 | Pole | Overhead | Yes | 43817 | 0.22569 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (No defect) | 2019-361 | 2019 | 12 | 18 | 5 | 25 | 19-0137065 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3185 | 11.984 | 220_255 | <25mph | <15mph | HFTD - Distribution
A. Kincade Fire | 2019-10-23 21:27 | 21:27 | 38.7925 | -122.7801 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 230000 | Conductor | Overhead |  |  |  | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1993 | 2019 | 10 | 23 | 21 | 27 |  | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Conductor | 826291590 | 18.2809 | 156_335 | <25mph | >=15mph | HFTD - Transmission |  |  |  | 0 | 0 | JBGC1 | 6.08 | 2018-11-08T07:13:00Z | 44 | 1 |  |  |  | 0 | 0 | JBGC1 | 6.08 | 2018-11-08T08:13:00Z | 44.98 | 2
B. Zogg Fire | 2020-09-27 16:03 | 16:03 | 40.5393 | -122.5666 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | Conductor | Overhead |  |  |  | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1993 | 2020 | 9 | 27 | 16 | 3 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Conductor | 826291590 | 18.2809 | 156_335 | <25mph | >=15mph | HFTD - Transmission |  |  |  | 0 | 0 | JBGC1 | 6.08 | 2018-11-08T07:13:00Z | 44 | 1 |  |  |  | 0 | 0 | JBGC1 | 6.08 | 2018-11-08T08:13:00Z | 44.98 | 2
Note on AM673: Chong, Yanping: was under investigation, Kincade

## Ign+Wind-HFTD
Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observations | [7 empty] | Used in the pivot | [7 empty] | Used in Pivot | Used for Tranche | Used in the Risk Input Sheet | Used in Pivot | Used in the Risk Input Sheet | Used in the Risk Input | Used in EO-WF-14
Utility Name | Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Suppressing Agency | Facility Identification | Other Companies | Voltage (Volts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | Notes (Optional): | Veg Subdriver | 0_Ignition ID | 0_Year | 0_Month | 0_Day | 0_Hour | 0_Minute | 0_Outage ID | 0_HFTD Zone | 0_HFTD | 0_RFW Applicable | 0_Transmission/Distribution | 0_Tranche | 0_Fire Greater than 300 Acres | 0_Driver | 0_Subdriver | 0_Customer Minutes Interrupted | 1_wg_mph | 1_we_sn | 1_Wind Categorization | 1_Wind Category | 1_Tranche | 4m/1h stid | 4m/1h time | 4m/1h dist | 4m/1h gust mph | 4m/1h count | 8m/1h stid | 8m/1h time | 8m/1h dist | 8m/1h gust mph | 8m/1h count | 4m/2h stid | 4m/2h time | 4m/2h dist | 4m/2h gust mph | 4m/2h count | 8m/2h stid | 8m/2h time | 8m/2h dist | 8m/2h gust mph | 8m/2h count
PG&E | 42020.2965 | 42020.2965 | 38.7753 | -122.7004 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 102167494 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0257 | 2015 | 1 | 16 | 7 | 7 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 15.1992 | 126_282 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | HWKC1 | 7.87 | 2015-01-16T14:56:00Z | 11.01 | 1 |  |  |  | 0 | 0 | HWKC1 | 7.87 | 2015-01-16T14:56:00Z | 11.01 | 2
PG&E | 42030.1604 | 42030.1604 | 37.0539 | -122.1587 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42030.1604 | 42030.1604 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0258 | 2015 | 1 | 26 | 3 | 51 | 15-0007000 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7602 | 4.1659 | 149_187 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | BNDC1 | 5.38 | 2015-01-26T11:50:00Z | 10 | 52 |  |  |  | 0 | 0 | BNDC1 | 5.38 | 2015-01-26T11:50:00Z | 10 | 97
PG&E | 42041.2507 | 42041.2507 | 38.6059 | -121.0221 | Vegetation | Rural | < 3 meters | Fire Agency |  | 6661 Ryan Ranch Road, El Dorado Hills |  | 21000 | Conductor | Overhead | Yes | 42041.2507 | 42041.2507 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0259 | 2015 | 2 | 6 | 6 | 1 | 15-0009876 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 51996 | 1.788 | 199_272 | <25mph | <15mph | HFTD - Distribution | D4314 | 3.45 | 2015-02-06T13:58:00Z | 46.95 | 12 | BENC1 | 4.89 | 2015-02-06T13:59:00Z | 59.01 | 40 | D4314 | 3.45 | 2015-02-06T13:58:00Z | 46.95 | 24 | BENC1 | 4.89 | 2015-02-06T13:59:00Z | 59.01 | 79
PG&E | 42042.7764 | 42042.7764 | 40.4674 | -123.6545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | mile marker 36.61, hwy 36, bridgeville |  | 12000 | Conductor | Overhead | Yes | 42042.7764 | 42042.7764 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0262 | 2015 | 2 | 7 | 18 | 38 | 15-0011390 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 7691 | 13.8601 | 88_377 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | MDDC1 | 6.88 | 2015-02-08T01:53:00Z | 24 | 1 |  |  |  | 0 | 0 | MDDC1 | 6.88 | 2015-02-08T01:53:00Z | 24 | 2
PG&E | 42058.0868 | 42058.0868 | 39.3027 | -121.0175 | Vegetation | Rural | < 3 meters | Fire Agency | NEVADA CITY FIRE | 100086316 |  | 12000 | Conductor | Overhead | Yes | 42058.0868 | 42058.0868 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0267 | 2015 | 2 | 23 | 2 | 5 | 15-0014910 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 93279 | 10.0636 | 199_311 | <25mph | <15mph | HFTD - Distribution | E3651 | 2.92 | 2015-02-23T09:05:00Z | 14.99 | 13 | KGOO | 5.49 | 2015-02-23T09:40:00Z | 31.07 | 67 | E3651 | 2.92 | 2015-02-23T10:50:00Z | 16.98 | 25 | KGOO | 5.49 | 2015-02-23T09:40:00Z | 31.07 | 131
PG&E | 42058.559 | 42058.559 | 38.5046 | -122.7408 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RINCON VALLEY | BEHIND 4870 CARRIAGE LN SANTA ROSA |  | 12000 | Conductor | Overhead | Yes | 42058.559 | 42058.559 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0268 | 2015 | 2 | 23 | 13 | 25 | 15-0015168 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 85762 | 12.3213 | 124_267 | <25mph | <15mph | HFTD - Distribution | RSAC1 | 2.39 | 2015-02-23T20:29:00Z | 34 | 11 | RSAC1 | 2.39 | 2015-02-23T20:29:00Z | 34 | 73 | RSAC1 | 2.39 | 2015-02-23T20:29:00Z | 34 | 22 | RSAC1 | 2.39 | 2015-02-23T20:29:00Z | 34 | 145
PG&E | 42067.7806 | 42067.7806 | 38.9995 | -122.7545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Kelseyville FD | 102156367 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42067.7806 | 42067.7806 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0271 | 2015 | 3 | 4 | 18 | 44 | 15-0017374 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29532 | 8.0458 | 124_295 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | KELC1 | 6.58 | 2015-03-05T01:57:00Z | 11.01 | 1 |  |  |  | 0 | 0 | KELC1 | 6.58 | 2015-03-05T01:57:00Z | 11.01 | 2
PG&E | 42070.566 | 42070.566 | 38.7091 | -122.6484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 14417 western mine rd, Middletown |  | 12000 | Conductor | Overhead | Yes | 42070.566 | 42070.566 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0272 | 2015 | 3 | 7 | 13 | 35 | 15-0018003 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2263 | 12.3057 | 128_279 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E2050 | 7.98 | 2015-03-07T21:33:00Z | 7 | 4 |  |  |  | 0 | 0 | E2050 | 7.98 | 2015-03-07T21:48:00Z | 8.99 | 8
PG&E | 42072.4 | 42072.4 | 38.7328 | -120.7524 | Building | Urban | Structure Only | Unknown |  | 101399208 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42072.4 | 42072.4 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0273 | 2015 | 3 | 9 | 9 | 36 | 15-0018212 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 35991 | 13.2535 | 210_279 | <25mph | <15mph | HFTD - Distribution | E5691 | 2.49 | 2015-03-09T15:46:00Z | 2.01 | 19 | E6490 | 5.16 | 2015-03-09T16:31:00Z | 3 | 37 | E5691 | 2.49 | 2015-03-09T17:31:00Z | 3 | 37 | C6129 | 5.81 | 2015-03-09T17:29:00Z | 4.99 | 73
PG&E | 42077.1042 | 42077.1042 | 38.9038 | -122.7579 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 9210 Wildcat Road, Kelseyville |  | 12000 | Conductor | Overhead | Yes | 42077.1042 | 42077.1042 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0274 | 2015 | 3 | 14 | 2 | 30 | 15-0019556 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2280 | 6.6558 | 124_289 | <25mph | <15mph | HFTD - Distribution | KELC1 | 2.83 | 2015-03-14T08:57:00Z | 0 | 1 | E4393 | 6.32 | 2015-03-14T08:57:00Z | 4.99 | 5 | KELC1 | 2.83 | 2015-03-14T09:57:00Z | 0 | 2 | E4393 | 6.32 | 2015-03-14T08:57:00Z | 4.99 | 10
PG&E | 42078.9493 | 42078.9493 | 38.3346 | -120.5325 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 103106530 |  | 12000 | Conductor | Overhead | Yes | 42078.9493 | 42078.9493 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0279 | 2015 | 3 | 15 | 22 | 47 | 15-0019709 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 14520 | 18.0364 | 220_257 | <25mph | >=15mph | HFTD - Distribution | D9396 | 3.65 | 2015-03-16T05:46:00Z | 2.01 | 11 | MTZC1 | 7.54 | 2015-03-16T04:56:00Z | 7 | 25 | D9396 | 3.65 | 2015-03-16T06:44:00Z | 2.01 | 20 | MTZC1 | 7.54 | 2015-03-16T04:56:00Z | 7 | 47
PG&E | 42084.4486 | 42084.4486 | 40.1645 | -122.2894 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101546309 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42084.4486 | 42084.4486 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0281 | 2015 | 3 | 21 | 10 | 46 | 15-0021120 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 10355 | 6.9716 | 145_359 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42096.4056 | 42096.4056 | 39.6772 | -121.492 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100338726 |  | 12000 | Conductor | Overhead | Yes | 42096.4056 | 42096.4056 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0284 | 2015 | 4 | 2 | 9 | 44 | 15-0023747 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 100204 | 13.8343 | 178_332 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | JBGC1 | 4.06 | 2015-04-02T16:13:00Z | 37 | 12 |  |  |  | 0 | 0 | JBGC1 | 4.06 | 2015-04-02T16:13:00Z | 37 | 21
PG&E | 42098.7007 | 42098.7007 | 38.8824 | -122.5914 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 20748 Jerusalem Grade Road, Middletown |  | 12000 | Other | Overhead | Yes | 42098.7007 | 42098.7007 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0285 | 2015 | 4 | 4 | 16 | 49 | 15-0024208 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 20448 | 15.6149 | 131_288 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | KELC1 | 6.51 | 2015-04-04T22:57:00Z | 22.01 | 13 |  |  |  | 0 | 0 | KELC1 | 6.51 | 2015-04-04T23:57:00Z | 25.99 | 26
PG&E | 42105.7194 | 42105.7194 | 40.5462 | -122.2343 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101491414 |  | 12000 | Conductor | Overhead | Yes | 42105.7194 | 42105.7194 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0286 | 2015 | 4 | 11 | 17 | 16 | 15-0026023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 11914 | 1.6378 | 148_380 | <25mph | <15mph | HFTD - Distribution | RRAC1 | 3.7 | 2015-04-11T23:24:00Z | 12.01 | 1 | C5599 | 6.52 | 2015-04-12T00:04:00Z | 14 | 9 | RRAC1 | 3.7 | 2015-04-11T23:24:00Z | 12.01 | 2 | C5599 | 6.52 | 2015-04-12T01:04:00Z | 20.98 | 18
PG&E | 42112.1299 | 42112.1299 | 38.6858 | -121.0084 | Vegetation | Urban | < 3 meters | Fire Agency | carmeron park F.D. | around t-7464 |  | 21000 | Conductor | Overhead | Yes | 42112.1299 | 42112.1299 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0293 | 2015 | 4 | 18 | 3 | 7 | 15-0027556 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 49438 | 4.8579 | 199_277 | <25mph | <15mph | HFTD - Distribution | D7401 | 0.28 | 2015-04-18T10:04:00Z | 8.99 | 33 | D7401 | 0.28 | 2015-04-18T10:04:00Z | 8.99 | 58 | D7401 | 0.28 | 2015-04-18T10:04:00Z | 8.99 | 65 | D7401 | 0.28 | 2015-04-18T10:04:00Z | 8.99 | 115
PG&E | 42121.5375 | 42121.5375 | 35.4871 | -120.6756 | Vegetation | Rural | < 3 meters | Unknown |  | 103310601 |  | 21000 | Conductor | Overhead | Yes | 42121.5375 | 42121.5375 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0301 | 2015 | 4 | 27 | 12 | 54 | 15-0029875 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 5836 | 3.3323 | 214_100 | <25mph | <15mph | HFTD - Distribution | E1179 | 1.84 | 2015-04-27T19:26:00Z | 8.99 | 8 | E2260 | 4.42 | 2015-04-27T19:11:00Z | 10.98 | 14 | E1179 | 1.84 | 2015-04-27T19:26:00Z | 8.99 | 16 | E2260 | 4.42 | 2015-04-27T20:32:00Z | 14 | 29
PG&E | 42124.0181 | 42124.0181 | 37.2401 | -122.2472 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 1145 VERDE R |  | 12000 | Conductor | Overhead | Yes | 42124.0181 | 42124.0181 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0304 | 2015 | 4 | 30 | 0 | 26 | 15-0030607 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1256 | 10.5301 | 145_197 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | LAHC1 | 4.52 | 2015-04-30T07:07:00Z | 4.99 | 9 |  |  |  | 0 | 0 | LAHC1 | 4.52 | 2015-04-30T08:07:00Z | 5.99 | 17
PG&E | 42126.7021 | 42126.7021 | 37.3284 | -119.643 | Vegetation | Rural | < 0.25 Acres | Fire Agency | MADERA COUNTY | 103768995 |  | 12000 | Conductor | Overhead | Yes | 42126.7021 | 42126.7021 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0305 | 2015 | 5 | 2 | 16 | 51 | 15-0031285 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 79805 | 7.1357 | 259_202 | <25mph | <15mph | HFTD - Distribution | AT301 | 1.62 | 2015-05-02T23:51:00Z | 18.99 | 34 | AT301 | 1.62 | 2015-05-02T23:51:00Z | 18.99 | 60 | AT301 | 1.62 | 2015-05-02T23:56:00Z | 18.99 | 65 | AT301 | 1.62 | 2015-05-02T23:56:00Z | 18.99 | 119
PG&E | 42130.7201 | 42130.7201 | 37.4273 | -119.8803 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | BOOSTER 8179 INDIAN PEEK N/O MIWUK | None | 21000 | Other | Overhead | Yes | 42130.7201 | 42130.7201 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0307 | 2015 | 5 | 6 | 17 | 17 | 15-0032311 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 81600 | 10.2211 | 249_208 | <25mph | <15mph | HFTD - Distribution | C1522 | 2.85 | 2015-05-06T23:47:00Z | 13 | 6 | MIAC1 | 7.42 | 2015-05-06T23:59:00Z | 20 | 9 | C1522 | 2.85 | 2015-05-06T23:47:00Z | 13 | 11 | MIAC1 | 7.42 | 2015-05-06T23:59:00Z | 20 | 17
PG&E | 42133.5486 | 42133.5486 | 39.2343 | -121.2468 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100000103 | None | 21000 | Conductor | Overhead | Yes | 42133.5486 | 42133.5486 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0311 | 2015 | 5 | 9 | 13 | 10 | 15-0033085 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 382926 | 8.0659 | 189_307 | <25mph | <15mph | HFTD - Distribution | E2572 | 3.27 | 2015-05-09T19:28:00Z | 7 | 12 | E2572 | 3.27 | 2015-05-09T19:28:00Z | 7 | 12 | E2572 | 3.27 | 2015-05-09T19:28:00Z | 7 | 12 | E2572 | 3.27 | 2015-05-09T19:28:00Z | 7 | 12
PG&E | 42133.9007 | 42133.9007 | 39.2848 | -121.0219 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100004095 | Pacific Bell | 12000 | Fuse | Overhead | Yes | 42133.9007 | 42133.9007 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0312 | 2015 | 5 | 9 | 21 | 37 | 15-0033109 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 11 | 15.0569 | 198_310 | <25mph | >=15mph | HFTD - Distribution | E5439 | 3.42 | 2015-05-10T04:00:00Z | 4 | 28 | RRRC1 | 5.26 | 2015-05-10T04:13:00Z | 5.99 | 66 | E5439 | 3.42 | 2015-05-10T04:00:00Z | 4 | 56 | RRRC1 | 5.26 | 2015-05-10T05:13:00Z | 5.99 | 130
PG&E | 42145.391 | 42145.391 | 38.5996 | -122.9935 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 4 SPANS LOAD SIDE 2993 |  | 12000 | Conductor | Overhead | Yes | 42145.391 | 42145.391 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0324 | 2015 | 5 | 21 | 9 | 23 | 15-0035686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2850 | 6.2166 | 114_273 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | D3481 | 5.82 | 2015-05-21T16:22:00Z | 4 | 31 |  |  |  | 0 | 0 | D3481 | 5.82 | 2015-05-21T17:17:00Z | 7 | 63
PG&E | 42151.9056 | 42151.9056 | 39.169 | -120.9612 | Vegetation | Rural | < 0.25 Acres | Fire Agency | PEARDALE F.D. | 100077687 |  | 12000 | Conductor | Overhead | Yes | 42151.9056 | 42151.9056 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0329 | 2015 | 5 | 27 | 21 | 44 | 15-0036850 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10828 | 11.7191 | 201_303 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E5439 | 7.11 | 2015-05-28T04:20:00Z | 2.01 | 62 |  |  |  | 0 | 0 | SETC1 | 4.24 | 2015-05-28T05:28:00Z | 5.99 | 119
PG&E | 42154.5361 | 42154.5361 | 38.7371 | -120.8122 | Vegetation | Urban | < 3 meters | Fire Agency | el dorado co fire district | across from 2669 hwy 49 |  | 12000 | Fuse | Overhead | Yes | 42154.5361 | 42154.5361 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0334 | 2015 | 5 | 30 | 12 | 52 | 15-0037405 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 115 | 10.597 | 208_280 | <25mph | <15mph | HFTD - Distribution | E5691 | 1.7 | 2015-05-30T19:47:00Z | 10 | 29 | E5691 | 1.7 | 2015-05-30T19:47:00Z | 10 | 47 | C6129 | 3.5 | 2015-05-30T20:49:00Z | 11.99 | 57 | C6129 | 3.5 | 2015-05-30T20:49:00Z | 11.99 | 93
PG&E | 42158.3979 | 42158.3979 | 39.6896 | -121.6216 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42158.3979 | 42158.3979 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0341 | 2015 | 6 | 3 | 9 | 33 | 15-0038091 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 28146 | 10.298 | 173_332 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | JBGC1 | 7.74 | 2015-06-03T16:13:00Z | 8.99 | 12 |  |  |  | 0 | 0 | CICC1 | 6.93 | 2015-06-03T16:54:00Z | 10 | 25
PG&E | 42159.5535 | 42159.5535 | 39.2694 | -123.7841 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42159.5535 | 42159.5535 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0344 | 2015 | 6 | 4 | 13 | 17 | 15-0038501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20525 | 19.0954 | 81_311 | <25mph | >=15mph | HFTD - Distribution | KLLR | 1.7 | 2015-06-04T19:55:00Z | 16.11 | 7 | KLLR | 1.7 | 2015-06-04T19:55:00Z | 16.11 | 9 | KLLR | 1.7 | 2015-06-04T20:55:00Z | 17.25 | 14 | KLLR | 1.7 | 2015-06-04T20:55:00Z | 17.25 | 18
PG&E | 42159.8333 | 42159.8333 | 38.6916 | -120.8606 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101412760 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42159.8333 | 42159.8333 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0347 | 2015 | 6 | 4 | 20 | 0 | 15-0038597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 9640 | 10.3503 | 205_277 | <25mph | <15mph | HFTD - Distribution | E6490 | 1.72 | 2015-06-05T02:01:00Z | 7 | 25 | D4464 | 6.46 | 2015-06-05T02:16:00Z | 8.01 | 60 | E6490 | 1.72 | 2015-06-05T02:01:00Z | 7 | 49 | D4464 | 6.46 | 2015-06-05T02:16:00Z | 8.01 | 119
PG&E | 42160.059 | 42160.059 | 38.3461 | -122.3998 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | 4870 REDWOOD |  | 21000 | Conductor | Overhead | Yes | 42160.059 | 42160.059 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0348 | 2015 | 6 | 5 | 1 | 25 | 15-0038607 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 53842 | 15.9469 | 139_258 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | E6860 | 6.98 | 2015-06-05T08:07:00Z | 1.01 | 23 |  |  |  | 0 | 0 | E6860 | 6.98 | 2015-06-05T09:22:00Z | 1.01 | 45
PG&E | 42160.6111 | 42160.6111 | 37.9578 | -120.4519 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101012484 |  | 17000 | Conductor | Overhead | Yes | 42160.6111 | 42160.6111 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0350 | 2015 | 6 | 5 | 14 | 40 | 15-0038686 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 14319 | 7.0168 | 223_237 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42161.6514 | 42161.6514 | 39.0409 | -123.4019 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 11480 ANDERSON VALLEY WAY @ BRIDGE |  | 12000 | Conductor | Overhead | Yes | 42161.6514 | 42161.6514 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0355 | 2015 | 6 | 6 | 15 | 38 | 15-0039056 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 1748 | 3.7796 | 97_298 | <25mph | <15mph | HFTD - Distribution | E4777 | 3.27 | 2015-06-06T22:26:00Z | 14 | 2 | BNVC1 | 4.68 | 2015-06-06T21:50:00Z | 17 | 7 | E4777 | 3.27 | 2015-06-06T22:40:00Z | 14 | 3 | BNVC1 | 4.68 | 2015-06-06T22:50:00Z | 21 | 13
PG&E | 42163.5958 | 42163.5958 | 38.1796 | -120.959 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 102048579 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42163.5958 | 42163.5958 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0360 | 2015 | 6 | 8 | 14 | 18 | 15-0039368 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 65168 | 4.5038 | 201_249 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | CMAC1 | 5.88 | 2015-06-08T20:59:00Z | 12.01 | 1 |  |  |  | 0 | 0 | CMAC1 | 5.88 | 2015-06-08T21:59:00Z | 12.01 | 2
PG&E | 42163.6771 | 42163.6771 | 39.8236 | -123.6093 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 2 spans loadside 1741 |  | 12000 | Conductor | Overhead | Yes | 42163.6771 | 42163.6771 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0362 | 2015 | 6 | 8 | 16 | 15 | 15-0039481 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1740 | 1.0148 | 132_246 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42164.6417 | 42164.6417 | 38.3651 | -122.2541 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | load side 2987 | Yes | 21000 | Conductor | Overhead | Yes | 42164.6417 | 42164.6417 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0368 | 2015 | 6 | 9 | 15 | 24 | 15-0039825 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 651298 | 7.1362 | 145_259 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | ATLC1 | 7.61 | 2015-06-09T21:29:00Z | 48 | 21 |  |  |  | 0 | 0 | ATLC1 | 7.61 | 2015-06-09T22:29:00Z | 53.02 | 41
PG&E | 42164.6806 | 42164.6806 | 38.3822 | -122.4316 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102269716 | Pacific Bell | 21000 | Unknown | Overhead | Yes | 42164.6806 | 42164.6806 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0369 | 2015 | 6 | 9 | 16 | 20 | 15-0039860 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 4184 | 4.5208 | 138_260 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E7241 | 7.11 | 2015-06-09T22:38:00Z | 17.98 | 18 |  |  |  | 0 | 0 | E7241 | 7.11 | 2015-06-09T22:38:00Z | 17.98 | 38
PG&E | 42167.5465 | 42167.5465 | 40.4077 | -122.4104 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS STREET FROM 4139 OLD HAPPY VALLEY RD |  | 12000 | Lightning Arrestor | Overhead | No |  |  | Equipment/ Facility Failure | Lightning Arrestor | N.A. | N.A. | Unknown |  | no-match | 0378 | 2015 | 6 | 12 | 13 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Lightning Arrestor | N.A. | 9.5962 | 140_372 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E7114 | 7.46 | 2015-06-12T19:27:00Z | 14.99 | 8 |  |  |  | 0 | 0 | E7114 | 7.46 | 2015-06-12T20:15:00Z | 20 | 16
PG&E | 42167.9806 | 42167.9806 | 39.2308 | -121.1559 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 10903 PROSPECTOR RD ROUGH AND READY | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42167.9806 | 42167.9806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0380 | 2015 | 6 | 12 | 23 | 32 | 15-0040789 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 20 | 13.2853 | 193_307 | <25mph | <15mph | HFTD - Distribution | E2572 | 1.63 | 2015-06-13T06:29:00Z | 5.99 | 18 | E5439 | 5.49 | 2015-06-13T06:25:00Z | 8.99 | 65 | E2572 | 1.63 | 2015-06-13T06:34:00Z | 5.99 | 35 | RRRC1 | 5.44 | 2015-06-13T07:13:00Z | 12.01 | 129
PG&E | 42170.6493 | 42170.6493 | 37.1852 | -121.7595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Jose city | 100618215 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42170.6493 | 42170.6493 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0384 | 2015 | 6 | 15 | 15 | 35 | 15-0041178 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 345 | 7.5345 | 166_194 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | C9520 | 5.63 | 2015-06-15T21:46:00Z | 11.99 | 42 |  |  |  | 0 | 0 | C2789 | 6.18 | 2015-06-15T23:35:00Z | 14 | 84
PG&E | 42176.5632 | 42176.5632 | 37.375 | -119.6116 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103204866 |  | 0 – 750 | Conductor | Overhead | No |  |  | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0399 | 2015 | 6 | 21 | 13 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 9.3936 | 260_205 | <25mph | <15mph | HFTD - Distribution | D7171 | 3.95 | 2015-06-21T19:55:00Z | 16.98 | 25 | MIAC1 | 7.96 | 2015-06-21T19:59:00Z | 22.01 | 69 | AT301 | 3.85 | 2015-06-21T21:27:00Z | 18.99 | 49 | MIAC1 | 7.96 | 2015-06-21T19:59:00Z | 22.01 | 133
PG&E | 42177.4986 | 42177.4986 | 39.1737 | -121.0667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | SENTINAL WY |  | 12000 | Conductor | Overhead | Yes | 42177.4986 | 42177.4986 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0400 | 2015 | 6 | 22 | 11 | 58 | 15-0042502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 148438 | 8.3404 | 197_304 | <25mph | <15mph | HFTD - Distribution | AS856 | 3.16 | 2015-06-22T18:58:00Z | 10 | 25 | E5439 | 4.77 | 2015-06-22T18:56:00Z | 10.98 | 85 | AS856 | 3.16 | 2015-06-22T19:58:00Z | 11.99 | 49 | AS856 | 3.16 | 2015-06-22T19:58:00Z | 11.99 | 170
PG&E | 42179.7951 | 42179.7951 | 39.9921 | -123.9258 | Vegetation | Rural | < 3 meters | Customer |  | 4 spans load side 8207 |  | 12000 | Conductor | Overhead | Yes | 42179.7951 | 42179.7951 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0406 | 2015 | 6 | 24 | 19 | 5 | 15-0043176 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1080 | 15.1757 | 76_351 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42182.5333 | 42182.5333 | 37.9474 | -120.4274 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101034512 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.5333 | 42182.5333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0414 | 2015 | 6 | 27 | 12 | 48 | 15-0043755 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 150075 | 6.5103 | 224_236 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 | KO22 | 5.72 | 2015-06-27T19:55:00Z | 16.11 | 1
PG&E | 42182.7854 | 42182.7854 | 37.9911 | -120.438 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | MORMON CREEK 100' FROM S/OF HWY 49 |  | 17000 | Conductor | Overhead | Yes | 42182.7854 | 42182.7854 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0415 | 2015 | 6 | 27 | 18 | 51 | 15-0043784 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 5249 | 10.5236 | 224_239 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42182.8854 | 42182.8854 | 39.2699 | -121.0403 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 16151 INDAIN FLAT RD |  | 12000 | Conductor | Overhead | Yes | 42182.8854 | 42182.8854 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0416 | 2015 | 6 | 27 | 21 | 15 | 15-0043789 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4210 | 10.7773 | 198_309 | <25mph | <15mph | HFTD - Distribution | E5439 | 2.06 | 2015-06-28T04:15:00Z | 2.01 | 40 | RRRC1 | 4.73 | 2015-06-28T04:13:00Z | 7 | 49 | E5439 | 2.06 | 2015-06-28T05:15:00Z | 4 | 72 | RRRC1 | 4.73 | 2015-06-28T04:13:00Z | 7 | 88
PG&E | 42182.9361 | 42182.9361 | 38.1194 | -120.6218 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 101281699 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42182.9361 | 42182.9361 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0417 | 2015 | 6 | 27 | 22 | 28 | 15-0043798 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 517 | 11.6492 | 216_246 | <25mph | <15mph | HFTD - Distribution | C9085 | 3.92 | 2015-06-28T05:15:00Z | 1.01 | 2 | C9085 | 3.92 | 2015-06-28T05:15:00Z | 1.01 | 2 | C9085 | 3.92 | 2015-06-28T06:05:00Z | 1.01 | 5 | C9085 | 3.92 | 2015-06-28T06:05:00Z | 1.01 | 5
PG&E | 42183.1181 | 42183.1181 | 35.491 | -120.731 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 13505 Santa Lucia Rd. Atascadero |  | 12000 | Conductor | Overhead | Yes | 42183.1181 | 42183.1181 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0418 | 2015 | 6 | 28 | 2 | 50 | 15-0043807 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 12323 | 9.8825 | 108_293 | <25mph | <15mph | HFTD - Distribution | E6394 | 1.17 | 2015-06-28T09:37:00Z | 0 | 4 | E2260 | 6.83 | 2015-06-28T09:01:00Z | 3 | 6 | E6394 | 1.17 | 2015-06-28T10:22:00Z | 3 | 8 | E6394 | 1.17 | 2015-06-28T10:22:00Z | 3 | 15
PG&E | 42183.8799 | 42183.8799 | 39.7405 | -121.4974 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | DEADWOOD RD, JARBO GAP |  | 12000 | Conductor | Overhead | Yes | 42183.8799 | 42183.8799 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0424 | 2015 | 6 | 28 | 21 | 7 | 15-0043869 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 45683 | 8.9868 | 178_335 | <25mph | <15mph | HFTD - Distribution | JBGC1 | 0.55 | 2015-06-29T03:13:00Z | 4.99 | 1 | JBGC1 | 0.55 | 2015-06-29T03:13:00Z | 4.99 | 2 | JBGC1 | 0.55 | 2015-06-29T04:13:00Z | 5.99 | 2 | JBGC1 | 0.55 | 2015-06-29T04:13:00Z | 5.99 | 7
PG&E | 42185.7625 | 42185.7625 | 36.2199 | -121.7534 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | loadside of 88973 | unknown | 12000 | Conductor | Overhead | Yes | 42185.7625 | 42185.7625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0432 | 2015 | 6 | 30 | 18 | 18 | 15-0044405 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 158 | 4.041 | 166_141 | <25mph | <15mph | HFTD - Distribution | PPSC1 | 2.3 | 2015-07-01T01:04:00Z | 8.99 | 1 | PPSC1 | 2.3 | 2015-07-01T01:04:00Z | 8.99 | 3 | PPSC1 | 2.3 | 2015-07-01T01:04:00Z | 8.99 | 2 | PPSC1 | 2.3 | 2015-07-01T01:04:00Z | 8.99 | 8
PG&E | 42186.3868 | 42186.3868 | 38.5715 | -122.5443 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42186.3868 | 42186.3868 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0433 | 2015 | 7 | 1 | 9 | 17 | 15-0044529 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 85168 | 1.0096 | 133_271 | <25mph | <15mph | HFTD - Distribution | E2050 | 3.6 | 2015-07-01T16:14:00Z | 3 | 4 | E2050 | 3.6 | 2015-07-01T16:14:00Z | 3 | 21 | E2050 | 3.6 | 2015-07-01T17:15:00Z | 4.99 | 8 | E2050 | 3.6 | 2015-07-01T17:15:00Z | 4.99 | 33
PG&E | 42186.5396 | 42186.5396 | 39.4146 | -121.379 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42186.5396 | 42186.5396 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0434 | 2015 | 7 | 1 | 12 | 57 | 15-0044609 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 11.1661 | 183_317 | <25mph | <15mph | HFTD - Distribution | BNGC1 | 2.37 | 2015-07-01T19:51:00Z | 15.99 | 1 | BNGC1 | 2.37 | 2015-07-01T19:51:00Z | 15.99 | 1 | BNGC1 | 2.37 | 2015-07-01T20:51:00Z | 17 | 2 | BNGC1 | 2.37 | 2015-07-01T20:51:00Z | 17 | 2
PG&E | 42188.141 | 42188.141 | 35.6785 | -120.9567 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 1 soan 1 conducter 1 span loade side transformer formtr 1008493290 |  | 21000 | Conductor | Overhead | Yes | 42188.141 | 42188.141 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0438 | 2015 | 7 | 3 | 3 | 23 | 15-0045239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 978 | 8.0641 | 202_111 | <25mph | <15mph | HFTD - Distribution | TABC1 | 2.38 | 2015-07-03T10:07:00Z | 1.01 | 1 | D4060 | 6.58 | 2015-07-03T10:19:00Z | 2.01 | 5 | TABC1 | 2.38 | 2015-07-03T11:07:00Z | 3 | 2 | TABC1 | 2.38 | 2015-07-03T11:07:00Z | 3 | 10
PG&E | 42189.0514 | 42189.0514 | 38.9566 | -121.0434 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100037226 |  | 12000 | Other | Overhead | Yes | 42189.0514 | 42189.0514 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | Booster | Other/Unknown | 0441 | 2015 | 7 | 4 | 1 | 14 | 15-0045440 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 53865 | 8.7379 | 198_292 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | D8862 | 5.23 | 2015-07-04T07:21:00Z | 5.99 | 25 |  |  |  | 0 | 0 | D8862 | 5.23 | 2015-07-04T07:21:00Z | 5.99 | 49
PG&E | 42190.4042 | 42190.4042 | 35.5323 | -120.7371 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 0 – 750 | Conductor | Overhead | No |  |  | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0444 | 2015 | 7 | 5 | 9 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 11.411 | 211_103 | <25mph | <15mph | HFTD - Distribution | E6394 | 1.7 | 2015-07-05T16:08:00Z | 12.01 | 4 | E6394 | 1.7 | 2015-07-05T16:08:00Z | 12.01 | 4 | E6394 | 1.7 | 2015-07-05T16:54:00Z | 13 | 8 | E6394 | 1.7 | 2015-07-05T16:54:00Z | 13 | 8
PG&E | 42190.8896 | 42190.8896 | 38.6524 | -120.6278 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | one span east of c/o 1055 |  | 21000 | Conductor | Overhead | Yes | 42190.8896 | 42190.8896 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0445 | 2015 | 7 | 5 | 21 | 21 | 15-0045605 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 22374 | 12.1034 | 215_275 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | GZFC1 | 5.69 | 2015-07-06T04:17:00Z | 3 | 1 |  |  |  | 0 | 0 | GZFC1 | 5.69 | 2015-07-06T04:17:00Z | 3 | 2
PG&E | 42192.4458 | 42192.4458 | 39.1138 | -121.0655 | Vegetation | Rural | < 0.25 Acres | Unknown |  |  |  | 12000 | Conductor | Overhead | Yes | 42192.4458 | 42192.4458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0448 | 2015 | 7 | 7 | 10 | 42 | 15-0045985 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 46738 | 7.2813 | 197_300 | <25mph | <15mph | HFTD - Distribution | C5488 | 3.42 | 2015-07-07T17:40:00Z | 4.99 | 4 | E1789 | 4.22 | 2015-07-07T17:18:00Z | 7 | 55 | C5488 | 3.42 | 2015-07-07T18:20:00Z | 7 | 9 | E1789 | 4.22 | 2015-07-07T18:42:00Z | 8.01 | 115
PG&E | 42192.6438 | 42192.6438 | 35.155 | -120.5442 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 303corraltos cyn rd | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42192.6438 | 42192.6438 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0449 | 2015 | 7 | 7 | 15 | 27 | 15-0046127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 98566 | 7.6944 | 220_82 | <25mph | <15mph | HFTD - Distribution | C9814 | 3.58 | 2015-07-07T22:23:00Z | 10 | 6 | KSBP | 7.64 | 2015-07-07T21:56:00Z | 34.52 | 7 | C9814 | 3.58 | 2015-07-07T23:03:00Z | 10 | 12 | KSBP | 7.64 | 2015-07-07T21:56:00Z | 34.52 | 14
PG&E | 42193.4743 | 42193.4743 | 39.224 | -121.0635 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 100094468 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42193.4743 | 42193.4743 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0451 | 2015 | 7 | 8 | 11 | 23 | 15-0046274 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 22064 | 1.9773 | 197_306 | <25mph | <15mph | HFTD - Distribution | E6355 | 2.74 | 2015-07-08T18:19:00Z | 8.99 | 46 | RRRC1 | 6.2 | 2015-07-08T18:13:00Z | 12.01 | 89 | E6355 | 2.74 | 2015-07-08T19:20:00Z | 8.99 | 91 | RRRC1 | 6.2 | 2015-07-08T19:13:00Z | 12.01 | 174
PG&E | 42197.7111 | 42197.7111 | 37.4713 | -122.4256 | Vegetation | Rural | < 0.25 Acres | Fire Agency | COUNTY FIRE | 1 s w c509 |  | 12000 | Conductor | Overhead | Yes | 42197.7111 | 42197.7111 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown | Jumper | Other/Unknown | 0456 | 2015 | 7 | 12 | 17 | 4 | 15-0047023 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 117853 | 8.7739 | 137_210 | <25mph | <15mph | HFTD - Distribution | D9259 | 3.49 | 2015-07-12T23:43:00Z | 5.99 | 4 | PUGC1 | 7 | 2015-07-12T23:18:00Z | 25.99 | 48 | D9259 | 3.49 | 2015-07-13T00:28:00Z | 5.99 | 8 | PUGC1 | 7 | 2015-07-12T23:18:00Z | 25.99 | 99
PG&E | 42200.375 | 42200.375 | 36.997 | -121.7381 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101795728 |  | 21000 | Conductor | Overhead | Yes | 42200.375 | 42200.375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0463 | 2015 | 7 | 15 | 9 | 0 | 15-0047650 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3800 | 7.3003 | 167_184 | <25mph | <15mph | HFTD - Distribution | CTOC1 | 3.71 | 2015-07-15T15:27:00Z | 3 | 1 | E4962 | 6.01 | 2015-07-15T15:52:00Z | 4.99 | 32 | CTOC1 | 3.71 | 2015-07-15T15:27:00Z | 3 | 2 | C4503 | 7.38 | 2015-07-15T16:55:00Z | 7 | 65
PG&E | 42201.7993 | 42201.7993 | 37.1989 | -119.7712 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 20334 ROAD 400 |  | 12000 | Conductor | Overhead | Yes | 42201.7993 | 42201.7993 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0465 | 2015 | 7 | 16 | 19 | 11 | 15-0048064 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 11.2562 | 207_226 | <25mph | <15mph | HFTD - Distribution | D7022 | 1.32 | 2015-07-17T01:21:00Z | 11.01 | 20 | D7022 | 1.32 | 2015-07-17T01:21:00Z | 11.01 | 20 | D7022 | 1.32 | 2015-07-17T01:21:00Z | 11.01 | 38 | D7022 | 1.32 | 2015-07-17T01:21:00Z | 11.01 | 38
PG&E | 42203.7083 | 42203.7083 | 38.8383 | -123.6297 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | off HWY 1 PA |  | 12000 | Conductor | Overhead | Yes | 42203.7083 | 42203.7083 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0470 | 2015 | 7 | 18 | 17 | 0 | 15-0048394 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 51806 | 20.752 | 86_287 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | ANVC1 | 6.68 | 2015-07-18T23:36:00Z | 14.99 | 10 |  |  |  | 0 | 0 | ANVC1 | 6.68 | 2015-07-18T23:36:00Z | 14.99 | 20
PG&E | 42207.5979 | 42207.5979 | 38.7935 | -120.714 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | s\ 3204 stope dr |  | 12000 | Conductor | Overhead | Yes | 42207.5979 | 42207.5979 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0478 | 2015 | 7 | 22 | 14 | 21 | 15-0049908 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 149206 | 3.7513 | 212_283 | <25mph | <15mph | HFTD - Distribution | E3165 | 1.79 | 2015-07-22T20:38:00Z | 10 | 5 | BDMC1 | 7.66 | 2015-07-22T20:36:00Z | 17 | 24 | E3165 | 1.79 | 2015-07-22T21:39:00Z | 14 | 11 | BDMC1 | 7.66 | 2015-07-22T20:36:00Z | 17 | 51
PG&E | 42209.6042 | 42209.6042 | 36.6913 | -119.0312 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46970 DUNLAP RD | YES | 0 – 750 | Transformer | Overhead | Yes | 42209.6042 | 42209.6042 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0482 | 2015 | 7 | 24 | 14 | 30 | 15-0050401 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 281 | 2.316 | 287_168 | <25mph | <15mph | HFTD - Distribution | PHRC1 | 0.81 | 2015-07-24T20:58:00Z | 14.99 | 1 | PHRC1 | 0.81 | 2015-07-24T20:58:00Z | 14.99 | 11 | PHRC1 | 0.81 | 2015-07-24T21:58:00Z | 15.99 | 2 | PHRC1 | 0.81 | 2015-07-24T21:58:00Z | 15.99 | 24
PG&E | 42211.5174 | 42211.5174 | 39.1586 | -121.0634 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 15499 ALLISON RANCH RD |  | 12000 | Conductor | Overhead | Yes | 42211.5174 | 42211.5174 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0485 | 2015 | 7 | 26 | 12 | 25 | 15-0050558 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2224 | 8.9153 | 197_303 | <25mph | <15mph | HFTD - Distribution | E1789 | 3.9 | 2015-07-26T19:24:00Z | 12.01 | 10 | E1789 | 3.9 | 2015-07-26T19:24:00Z | 12.01 | 68 | E1789 | 3.9 | 2015-07-26T19:54:00Z | 12.01 | 20 | E6355 | 6.63 | 2015-07-26T20:21:00Z | 12.01 | 133
PG&E | 42215.7472 | 42215.7472 | 37.9021 | -120.4739 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101019808 |  | 17000 | Conductor | Overhead | Yes | 42215.7472 | 42215.7472 | Contact From Object | N.A. | Other | Electric Facility | Unknown | osprey nest | Other/Unknown | 0499 | 2015 | 7 | 30 | 17 | 56 | 15-0051764 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 615 | 7.9687 | 222_234 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | GNSC1 | 4.96 | 2015-07-31T00:03:00Z | 18.99 | 1 |  |  |  | 0 | 0 | GNSC1 | 4.96 | 2015-07-31T00:03:00Z | 18.99 | 2
PG&E | 42215.7993 | 42215.7993 | 37.8102 | -120.1287 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE |  |  | 17000 | Conductor | Overhead | Yes | 42215.7993 | 42215.7993 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0500 | 2015 | 7 | 30 | 19 | 11 | 15-0051772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26776 | 8.9312 | 237_229 | <25mph | <15mph | HFTD - Distribution | SEWC1 | 1.66 | 2015-07-31T01:16:00Z | 14.99 | 5 | SEWC1 | 1.66 | 2015-07-31T01:16:00Z | 14.99 | 7 | SEWC1 | 1.66 | 2015-07-31T01:16:00Z | 14.99 | 10 | SEWC1 | 1.66 | 2015-07-31T01:16:00Z | 14.99 | 14
PG&E | 42216.9479 | 42216.9479 | 38.3805 | -120.5628 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | ACROSS FROM 1958 QUAIL LN WEST POINT | None | 12000 | Conductor | Overhead | Yes | 42216.9479 | 42216.9479 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0503 | 2015 | 7 | 31 | 22 | 45 | 15-0052033 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 33559 | 14.2556 | 218_260 | <25mph | <15mph | HFTD - Distribution | AT450 | 2.7 | 2015-08-01T05:19:00Z | 3 | 3 | C9148 | 7.8 | 2015-08-01T04:48:00Z | 7 | 20 | AT450 | 2.7 | 2015-08-01T06:45:00Z | 4 | 5 | C9148 | 7.8 | 2015-08-01T04:48:00Z | 7 | 38
PG&E | 42217.6042 | 42217.6042 | 34.9524 | -120.2952 | Vegetation | Rural | 10 - 99 Acres | Unknown |  | 101868639 |  | 12000 | Conductor | Overhead | Yes | 42217.6042 | 42217.6042 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0505 | 2015 | 8 | 1 | 14 | 30 | 15-0052506 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 1528 | 8.881 | 232_71 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42218.6833 | 42218.6833 | 37.6317 | -120.1547 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101076992 |  | 21000 | Conductor | Overhead | Yes | 42218.6833 | 42218.6833 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0508 | 2015 | 8 | 2 | 16 | 24 | 15-0064792 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 3.9691 | 236_219 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42219.0049 | 42219.0049 | 40.5056 | -122.347 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | COTTONWOOD FIRE DEPT | 101503428 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42219.0049 | 42219.0049 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0509 | 2015 | 8 | 3 | 0 | 7 | 15-0052184 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 10427 | 13.2206 | 143_378 | <25mph | <15mph | HFTD - Distribution | RRAC1 | 2.97 | 2015-08-03T06:24:00Z | 8.01 | 7 | RRAC1 | 2.97 | 2015-08-03T06:24:00Z | 8.01 | 15 | RRAC1 | 2.97 | 2015-08-03T06:24:00Z | 8.01 | 14 | RRAC1 | 2.97 | 2015-08-03T06:24:00Z | 8.01 | 30
PG&E | 42219.7451 | 42219.7451 | 39.3361 | -121.1894 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Pole 000/008 |  | 60000 | Conductor | Overhead | Yes | 42219.7451 | 42219.7451 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0510 | 2015 | 8 | 3 | 17 | 53 | TM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 7.5021 | 191_313 | <25mph | <15mph | HFTD - Transmission |  |  |  | 0 | 0 | RRRC1 | 4.47 | 2015-08-04T00:13:00Z | 14 | 30 |  |  |  | 0 | 0 | RRRC1 | 4.47 | 2015-08-04T01:13:00Z | 14.99 | 60
PG&E | 42220.6701 | 42220.6701 | 40.0822 | -121.1538 | Vegetation | Rural | < 0.25 Acres | Fire Agency | USFS | 100441220 | None | 0 – 750 | Fuse | Overhead | Yes | 42220.6701 | 42220.6701 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 0511 | 2015 | 8 | 4 | 16 | 5 | 15-0052743 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 4591 | 1.7808 | 193_354 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | TR180 | 5.53 | 2015-08-04T22:59:00Z | 14 | 1 |  |  |  | 0 | 0 | TR180 | 5.53 | 2015-08-04T22:59:00Z | 14 | 2
PG&E | 42220.7479 | 42220.7479 | 37.5879 | -120.229 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Str. 007/019 |  | 70000 | Conductor | Overhead | Yes | 42220.7479 | 42220.7479 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0512 | 2015 | 8 | 4 | 17 | 57 | LB-2015-028 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 8.863 | 233_216 | <25mph | <15mph | HFTD - Transmission |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42223.2722 | 42223.2722 | 37.84 | -122.1823 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100498058 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42223.2722 | 42223.2722 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0517 | 2015 | 8 | 7 | 6 | 32 | 15-0053493 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 13.1042 | 151_212 | <25mph | <15mph | HFTD - Distribution | ONOC1 | 2.72 | 2015-08-07T12:33:00Z | 14 | 60 | LTRC1 | 6.31 | 2015-08-07T13:28:00Z | 24.99 | 155 | ONOC1 | 2.72 | 2015-08-07T12:33:00Z | 14 | 120 | LTRC1 | 6.31 | 2015-08-07T13:28:00Z | 24.99 | 305
PG&E | 42224.3208 | 42224.3208 | 39.2007 | -121.2137 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100076217 | Pacific Bell | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0519 | 2015 | 8 | 8 | 7 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 7.7252 | 190_305 | <25mph | <15mph | HFTD - Distribution | E2572 | 2.41 | 2015-08-08T13:53:00Z | 1.01 | 13 | E1789 | 5.79 | 2015-08-08T14:12:00Z | 4.99 | 42 | E2572 | 2.41 | 2015-08-08T15:38:00Z | 1.01 | 20 | E1789 | 5.79 | 2015-08-08T15:42:00Z | 4.99 | 77
PG&E | 42228.7347 | 42228.7347 | 40.2153 | -123.8681 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 1 SP LD SD METER 1007960761 |  | 12000 | Conductor | Overhead | Yes | 42228.7347 | 42228.7347 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0525 | 2015 | 8 | 12 | 17 | 38 | 15-0054643 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 14640 | 0.6842 | 79_363 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | ERCC1 | 5.81 | 2015-08-13T00:28:00Z | 15.99 | 1 |  |  |  | 0 | 0 | ERCC1 | 5.81 | 2015-08-13T00:28:00Z | 15.99 | 2
PG&E | 42229.1569 | 42229.1569 | 37.2072 | -119.7343 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 44365 SAVAGE RD COARSEGOLD |  | 21000 | Conductor | Overhead | Yes | 42229.1569 | 42229.1569 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0526 | 2015 | 8 | 13 | 3 | 46 | 15-0054655 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 7600 | 15.6363 | 163_282 | <25mph | >=15mph | HFTD - Distribution | D7022 | 2.54 | 2015-08-13T10:41:00Z | 0 | 6 | E5766 | 4.34 | 2015-08-13T10:42:00Z | 0 | 18 | D7022 | 2.54 | 2015-08-13T11:41:00Z | 0 | 12 | E5766 | 4.34 | 2015-08-13T11:42:00Z | 0 | 36
PG&E | 42230.6312 | 42230.6312 | 40.9829 | -121.7802 | Vegetation | Rural | < 0.25 Acres | Unknown |  | 101514540 |  | 21000 | Conductor | Overhead | Yes | 42230.6312 | 42230.6312 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0530 | 2015 | 8 | 14 | 15 | 9 | 15-0055136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3072 | 10.0331 | 167_404 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | AS418 | 7.42 | 2015-08-14T21:31:00Z | 17 | 6 |  |  |  | 0 | 0 | AS418 | 7.42 | 2015-08-14T23:01:00Z | 17 | 12
PG&E | 42230.7389 | 42230.7389 | 37.8894 | -120.4933 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | ENTRANCE TO 14650 HWY 108, JAMESTOWN |  | 17000 | Conductor | Overhead | Yes | 42230.7389 | 42230.7389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0531 | 2015 | 8 | 14 | 17 | 44 | 15-0055160 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 1726 | 9.2286 | 222_233 | <25mph | <15mph | HFTD - Distribution | GNSC1 | 3.85 | 2015-08-15T00:03:00Z | 17 | 1 | GNSC1 | 3.85 | 2015-08-15T00:03:00Z | 17 | 8 | GNSC1 | 3.85 | 2015-08-15T00:03:00Z | 17 | 2 | GNSC1 | 3.85 | 2015-08-15T00:03:00Z | 17 | 15
PG&E | 42231.5701 | 42231.5701 | 37.9607 | -122.5709 | Vegetation | Urban | < 0.25 Acres | Fire Agency | COUNTY FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42231.5701 | 42231.5701 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0533 | 2015 | 8 | 15 | 13 | 41 | 15-0055217 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 5973 | 6.9969 | 131_237 | <25mph | <15mph | HFTD - Distribution | MDEC1 | 2.44 | 2015-08-15T20:36:00Z | 8.01 | 5 | NBRC1 | 5.44 | 2015-08-15T20:33:00Z | 13 | 10 | MDEC1 | 2.44 | 2015-08-15T21:36:00Z | 12.01 | 10 | NBRC1 | 5.44 | 2015-08-15T21:33:00Z | 14 | 20
PG&E | 42232.316 | 42232.316 | 35.4572 | -120.6567 | Vegetation | Rural | < 3 meters | Utility: PG&E |  | 8932 SAN GABRIEL RD. SW C/O OF LOT, Atascadero | None | 0 – 750 | Conductor | Overhead | Yes | 42232.316 | 42232.316 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0534 | 2015 | 8 | 16 | 7 | 35 | 15-0055284 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 7.6585 | 215_99 | <25mph | <15mph | HFTD - Distribution | E1179 | 1.71 | 2015-08-16T14:13:00Z | 2.01 | 4 | E1179 | 1.71 | 2015-08-16T14:13:00Z | 2.01 | 9 | E2260 | 2.13 | 2015-08-16T15:10:00Z | 2.01 | 11 | E2260 | 2.13 | 2015-08-16T15:10:00Z | 2.01 | 19
PG&E | 42233.359 | 42233.359 | 37.0757 | -122.023 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101800237 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0537 | 2015 | 8 | 17 | 8 | 37 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 5.0262 | 154_188 | <25mph | <15mph | HFTD - Distribution | E5965 | 3.61 | 2015-08-17T15:35:00Z | 4 | 32 | AR172 | 6.98 | 2015-08-17T15:30:00Z | 4.99 | 145 | E5965 | 3.61 | 2015-08-17T16:35:00Z | 7 | 63 | E5965 | 3.61 | 2015-08-17T16:35:00Z | 7 | 286
PG&E | 42233.7312 | 42233.7312 | 38.8337 | -123.5533 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 14 spans load side 2345 |  | 12000 | Conductor | Overhead | Yes | 42233.7312 | 42233.7312 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0539 | 2015 | 8 | 17 | 17 | 33 | 15-0055664 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 676 | 5.4473 | 90_286 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42233.8729 | 42233.8729 | 36.6867 | -119.0612 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 46371 ORCHARD DRIVE |  | 12000 | Conductor | Overhead | Yes | 42233.8729 | 42233.8729 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0540 | 2015 | 8 | 17 | 20 | 57 | 15-0055696 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 34398 | 10.2483 | 285_168 | <25mph | <15mph | HFTD - Distribution | PHRC1 | 2.47 | 2015-08-18T02:58:00Z | 5.99 | 1 | PHRC1 | 2.47 | 2015-08-18T02:58:00Z | 5.99 | 2 | PHRC1 | 2.47 | 2015-08-18T03:58:00Z | 8.99 | 2 | PHRC1 | 2.47 | 2015-08-18T03:58:00Z | 8.99 | 14
PG&E | 42235.2639 | 42235.2639 | 39.2831 | -123.2931 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | MTR#50001225 | None | 12000 | Conductor | Overhead | Yes | 42235.2639 | 42235.2639 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0545 | 2015 | 8 | 19 | 6 | 20 | 15-0055982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5403 | 6.0572 | 102_311 | <25mph | <15mph | HFTD - Distribution | AU552 | 3.69 | 2015-08-19T12:42:00Z | 5.99 | 12 | AU552 | 3.69 | 2015-08-19T12:42:00Z | 5.99 | 40 | AU552 | 3.69 | 2015-08-19T12:42:00Z | 5.99 | 24 | AU552 | 3.69 | 2015-08-19T12:42:00Z | 5.99 | 78
PG&E | 42238.8597 | 42238.8597 | 38.7748 | -120.8564 | Vegetation | Rural | < 3 meters | Self Extinguished |  | at base of co pole 21721 - 720 Woodridge Rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42238.8597 | 42238.8597 | Contact From Object | N.A. | Vegetation | Communication Facility | Unknown | tree hit phone lines | Fell into (Moderate-Severe defect) | 0549 | 2015 | 8 | 22 | 20 | 38 | 15-0056766 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26513 | 9.4458 | 206_282 | <25mph | <15mph | HFTD - Distribution | E5691 | 3.87 | 2015-08-23T03:21:00Z | 4 | 12 | E5691 | 3.87 | 2015-08-23T03:21:00Z | 4 | 45 | E5691 | 3.87 | 2015-08-23T03:21:00Z | 4 | 24 | E5691 | 3.87 | 2015-08-23T03:21:00Z | 4 | 89
PG&E | 42240.95 | 42240.95 | 37.896 | -122.6011 | Vegetation | Rural | < 3 meters | Fire Agency | marin county fire | 200' east of pan toll rd 50' north of panoramic hwy |  | 12000 | Unknown | Overhead | Yes | 42240.95 | 42240.95 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0552 | 2015 | 8 | 24 | 22 | 48 | 15-0057082 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 1128 | 13.1626 | 130_234 | <25mph | <15mph | HFTD - Distribution | MDEC1 | 2.32 | 2015-08-25T05:36:00Z | 13 | 5 | MDEC1 | 2.32 | 2015-08-25T05:36:00Z | 13 | 9 | MDEC1 | 2.32 | 2015-08-25T06:36:00Z | 14.99 | 10 | MDEC1 | 2.32 | 2015-08-25T06:36:00Z | 14.99 | 18
PG&E | 42242.5028 | 42242.5028 | 37.9638 | -122.5243 | Vegetation | Urban | < 0.25 Acres | Fire Agency | srfd | 102242504 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42242.5028 | 42242.5028 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0555 | 2015 | 8 | 26 | 12 | 4 | 15-0057475 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 28873 | 2.3344 | 133_237 | <25mph | <15mph | HFTD - Distribution | D7094 | 3.73 | 2015-08-26T18:29:00Z | 4.99 | 4 | MDEC1 | 4.24 | 2015-08-26T18:36:00Z | 14 | 20 | D7094 | 3.73 | 2015-08-26T19:30:00Z | 7 | 8 | MDEC1 | 4.24 | 2015-08-26T18:36:00Z | 14 | 41
PG&E | 42242.9924 | 42242.9924 | 36.3897 | -121.3653 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101756678 | None | 21000 | Conductor | Overhead | Yes | 42242.9924 | 42242.9924 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0557 | 2015 | 8 | 26 | 23 | 49 | 15-0057613 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 8445 | 26.8734 | 183_150 | 25-40mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42243.1458 | 42243.1458 | 37.8448 | -122.1992 | Vegetation | Urban | < 0.25 Acres | Unknown |  | 100487196 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42243.1458 | 42243.1458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0558 | 2015 | 8 | 27 | 3 | 30 | 15-0057619 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 176351 | 4.6001 | 147_231 | <25mph | <15mph | HFTD - Distribution | E4855 | 1.92 | 2015-08-27T10:15:00Z | 7 | 59 | LTRC1 | 7.26 | 2015-08-27T10:28:00Z | 14.99 | 137 | E4855 | 1.92 | 2015-08-27T10:15:00Z | 7 | 112 | LTRC1 | 7.26 | 2015-08-27T10:28:00Z | 14.99 | 271
PG&E | 42244.4917 | 42244.4917 | 38.8513 | -121.1469 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100055373 | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0562 | 2015 | 8 | 28 | 11 | 48 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 10.3663 | 193_286 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PLTC1 | 7.53 | 2015-08-28T17:56:00Z | 10 | 16 |  |  |  | 0 | 0 | PLTC1 | 7.53 | 2015-08-28T18:56:00Z | 13 | 30
PG&E | 42244.5014 | 42244.5014 | 37.9047 | -122.2058 | Vegetation | Rural | < 0.25 Acres | Fire Agency | EB MUD | 103623279 |  | 0 – 750 | Conductor | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0563 | 2015 | 8 | 28 | 12 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 8.9364 | 147_234 | <25mph | <15mph | HFTD - Distribution | E5555 | 3.43 | 2015-08-28T18:54:00Z | 10 | 32 | E5555 | 3.43 | 2015-08-28T18:54:00Z | 10 | 123 | LBNL1 | 3.01 | 2015-08-28T19:45:00Z | 11.61 | 66 | E6179 | 6.07 | 2015-08-28T19:49:00Z | 13 | 251
PG&E | 42245.1458 | 42245.1458 | 38.6302 | -122.8327 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Dirt road across from 3204 Rio Lindo Rd, Healdsburg |  | 12000 | Conductor | Overhead | Yes | 42245.1458 | 42245.1458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0566 | 2015 | 8 | 29 | 3 | 30 | 15-0058127 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4780 | 5.6914 | 120_274 | <25mph | <15mph | HFTD - Distribution | D2144 | 1.2 | 2015-08-29T10:00:00Z | 3 | 9 | HWKC1 | 7.25 | 2015-08-29T09:56:00Z | 4.99 | 27 | D2144 | 1.2 | 2015-08-29T10:00:00Z | 3 | 15 | HWKC1 | 7.25 | 2015-08-29T10:56:00Z | 12.01 | 52
PG&E | 42246.7118 | 42246.7118 | 38.4039 | -120.5559 | Vegetation | Rural | < 0.25 Acres | Fire Agency |  | centennial mine rd |  | 12000 | Conductor | Overhead | Yes | 42246.7118 | 42246.7118 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0567 | 2015 | 8 | 30 | 17 | 5 | 15-0058273 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 40298 | 9.3233 | 219_261 | <25mph | <15mph | HFTD - Distribution | AT450 | 1.93 | 2015-08-30T23:45:00Z | 12.01 | 13 | C9148 | 6.15 | 2015-08-30T23:49:00Z | 14.99 | 27 | AT450 | 1.93 | 2015-08-30T23:45:00Z | 12.01 | 25 | C9148 | 6.15 | 2015-08-30T23:49:00Z | 14.99 | 53
PG&E | 42247.6028 | 42247.6028 | 36.5325 | -121.1462 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 29401 Hwy 25 |  | 21000 | Conductor | Overhead | Yes | 42247.6028 | 42247.6028 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0568 | 2015 | 8 | 31 | 14 | 28 | 15-0058455 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25668 | 11.3997 | 193_158 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PCLC1 | 4.27 | 2015-08-31T20:37:00Z | 13 | 1 |  |  |  | 0 | 0 | PCLC1 | 4.27 | 2015-08-31T20:37:00Z | 13 | 2
PG&E | 42251.3257 | 42251.3257 | 40.2318 | -122.3643 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | E/O FRONTIER RD & N/O WAGON WAY |  | 12000 | Conductor | Overhead | Yes | 42251.3257 | 42251.3257 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0577 | 2015 | 9 | 4 | 7 | 49 | 15-0059323 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 9563 | 10.12 | 142_362 | <25mph | <15mph | HFTD - Distribution | D6527 | 1.77 | 2015-09-04T13:53:00Z | 4.99 | 1 | E7114 | 5.07 | 2015-09-04T14:49:00Z | 24 | 4 | D6527 | 1.77 | 2015-09-04T13:53:00Z | 4.99 | 1 | E7114 | 5.07 | 2015-09-04T15:21:00Z | 30 | 7
PG&E | 42253.8104 | 42253.8104 | 34.6195 | -120.2534 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Santa Barbara County Fire | meter# 1008400678 | Verizon | 12000 | Conductor | Overhead | Yes | 42253.8104 | 42253.8104 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0582 | 2015 | 9 | 6 | 19 | 27 | 15-0059612 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 863 | 7.384 | 158_212 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | C9206 | 6.79 | 2015-09-07T02:01:00Z | 4.99 | 8 |  |  |  | 0 | 0 | C9206 | 6.79 | 2015-09-07T02:01:00Z | 4.99 | 15
PG&E | 42256.4493 | 42256.4493 | 37.1041 | -121.8853 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100520291 |  | 12000 | Conductor | Overhead | Yes | 42256.4493 | 42256.4493 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0587 | 2015 | 9 | 9 | 10 | 47 | 15-0060074 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 142401 | 10.1251 | 161_190 | <25mph | <15mph | HFTD - Distribution | E6085 | 0.69 | 2015-09-09T17:16:00Z | 8.01 | 10 | E6085 | 0.69 | 2015-09-09T17:16:00Z | 8.01 | 101 | E6085 | 0.69 | 2015-09-09T18:31:00Z | 10 | 20 | C2789 | 6.89 | 2015-09-09T18:40:00Z | 11.01 | 197
PG&E | 42257.2375 | 42257.2375 | 37.4609 | -121.8434 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100619766 | None | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0588 | 2015 | 9 | 10 | 5 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 14.0503 | 212_257 | <25mph | <15mph | HFTD - Distribution | E3968 | 2.89 | 2015-09-10T12:37:00Z | 2.01 | 12 | RSPC1 | 6.56 | 2015-09-10T12:28:00Z | 7 | 16 | E3968 | 2.89 | 2015-09-10T12:37:00Z | 2.01 | 25 | RSPC1 | 6.56 | 2015-09-10T13:28:00Z | 7 | 33
PG&E | 42257.6833 | 42257.6833 | 38.5049 | -122.3535 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103159970 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42257.6833 | 42257.6833 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0589 | 2015 | 9 | 10 | 16 | 24 | 15-0060610 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 130124 | 3.6761 | 163_209 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | ATLC1 | 5.22 | 2015-09-10T22:29:00Z | 28.99 | 1 |  |  |  | 0 | 0 | ATLC1 | 5.22 | 2015-09-10T22:29:00Z | 28.99 | 2
PG&E | 42257.7771 | 42257.7771 | 40.7569 | -123.7958 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 096/004 |  | 115000 | Conductor | Overhead | Yes | 42257.7771 | 42257.7771 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0590 | 2015 | 9 | 10 | 18 | 39 | RM-2015-063 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 9.2278 | 141_267 | <25mph | <15mph | HFTD - Transmission |  |  |  | 0 | 0 | KNNC1 | 7.39 | 2015-09-11T00:55:00Z | 8.99 | 1 |  |  |  | 0 | 0 | KNNC1 | 7.39 | 2015-09-11T00:55:00Z | 8.99 | 2
PG&E | 42258.3438 | 42258.3438 | 38.1094 | -122.87 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102293992 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42258.3438 | 42258.3438 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0592 | 2015 | 9 | 11 | 8 | 15 | 15-0060698 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 32419 | 4.233 | 144_213 | <25mph | <15mph | HFTD - Distribution | PREC1 | 3.64 | 2015-09-11T15:05:00Z | 8.99 | 1 | PTRCA | 4.48 | 2015-09-11T15:10:00Z | 12.91 | 7 | PREC1 | 3.64 | 2015-09-11T16:05:00Z | 10 | 2 | PTRCA | 4.48 | 2015-09-11T16:10:00Z | 13.4 | 14
PG&E | 42259.4104 | 42259.4104 | 39.1164 | -121.0693 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | TOP OF AVALON PLACE, GRASS VALLEY TOWER NUMBER 19/152 40689729 |  | 115000 | Conductor | Overhead | Yes | 42259.4104 | 42259.4104 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0594 | 2015 | 9 | 12 | 9 | 51 | VD-2015-079 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 15.4664 | 188_228 | <25mph | >=15mph | HFTD - Transmission | E1789 | 3.95 | 2015-09-12T16:48:00Z | 7 | 8 | E1789 | 3.95 | 2015-09-12T16:48:00Z | 7 | 41 | E1789 | 3.95 | 2015-09-12T16:48:00Z | 7 | 16 | E1789 | 3.95 | 2015-09-12T16:48:00Z | 7 | 83
PG&E | 42259.4646 | 42259.4646 | 38.603 | -120.6741 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101394996 |  | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0595 | 2015 | 9 | 12 | 11 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 12.6722 | 196_301 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42265.7118 | 42265.7118 | 37.8992 | -120.4551 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101019893 |  | 17000 | Conductor | Overhead | Yes | 42265.7118 | 42265.7118 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0602 | 2015 | 9 | 18 | 17 | 5 | 15-0062207 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 35222 | 9.1735 | 191_232 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | GNSC1 | 5.2 | 2015-09-19T00:03:00Z | 14.99 | 1 |  |  |  | 0 | 0 | GNSC1 | 5.2 | 2015-09-19T00:03:00Z | 14.99 | 2
PG&E | 42266.4104 | 42266.4104 | 38.4755 | -122.9069 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FORESTVILLE | 103334444 |  | 12000 | Conductor | Overhead | Yes | 42266.4104 | 42266.4104 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0603 | 2015 | 9 | 19 | 9 | 51 | 15-0062267 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 488 | 1.2724 | 223_234 | <25mph | <15mph | HFTD - Distribution | D4623 | 2.94 | 2015-09-19T16:36:00Z | 1.01 | 7 | E5234 | 7.03 | 2015-09-19T16:28:00Z | 5.99 | 81 | D4623 | 2.94 | 2015-09-19T17:51:00Z | 3 | 13 | E5234 | 7.03 | 2015-09-19T16:28:00Z | 5.99 | 171
PG&E | 42267.7868 | 42267.7868 | 39.8638 | -121.6599 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42267.7868 | 42267.7868 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0604 | 2015 | 9 | 20 | 18 | 53 | 15-0062407 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 3479 | 3.8017 | 117_266 | <25mph | <15mph | HFTD - Distribution | C8878 | 0.76 | 2015-09-21T01:53:00Z | 4 | 16 | CSTC1 | 5.81 | 2015-09-21T01:51:00Z | 10 | 19 | C8878 | 0.76 | 2015-09-21T02:33:00Z | 4 | 33 | CSTC1 | 5.81 | 2015-09-21T01:51:00Z | 10 | 38
PG&E | 42268.1708 | 42268.1708 | 38.6587 | -121.0404 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 1of3@13833 |  | 21000 | Conductor | Overhead | Yes | 42268.1708 | 42268.1708 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 0605 | 2015 | 9 | 21 | 4 | 6 | 15-0062450 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | 162824 | 5.4184 | 171_342 | <25mph | <15mph | HFTD - Distribution | D4464 | 3.9 | 2015-09-21T10:25:00Z | 5.99 | 20 | BENC1 | 7.43 | 2015-09-21T10:59:00Z | 8.99 | 46 | D4464 | 3.9 | 2015-09-21T11:40:00Z | 7 | 37 | BENC1 | 7.43 | 2015-09-21T11:59:00Z | 8.99 | 79
PG&E | 42268.5993 | 42268.5993 | 40.4786 | -123.771 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | mile marker 29.1, e of hairpin turn |  | 12000 | Conductor | Overhead | Yes | 42268.5993 | 42268.5993 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0606 | 2015 | 9 | 21 | 14 | 23 | 15-0062556 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 13197 | 7.5594 | 198_275 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42271.1875 | 42271.1875 | 38.6769 | -123.314 | Vegetation | Rural | < 0.25 Acres | Unknown |  | Str. 041/007 |  | 60000 | Conductor | Overhead | Yes | 42271.1875 | 42271.1875 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0613 | 2015 | 9 | 24 | 4 | 30 | FU-2015-057 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 22680 | 6.9914 | 141_345 | <25mph | <15mph | HFTD - Transmission |  |  |  | 0 | 0 | D2695 | 7.76 | 2015-09-24T11:12:00Z | 8.99 | 4 |  |  |  | 0 | 0 | D2695 | 7.76 | 2015-09-24T11:12:00Z | 8.99 | 8
PG&E | 42271.5806 | 42271.5806 | 39.3508 | -121.2454 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 9692 Rices-Texas Hill rd. | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42271.5806 | 42271.5806 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0614 | 2015 | 9 | 24 | 13 | 56 | 15-0063159 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 51917 | 8.169 | 100_277 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | RRRC1 | 7.59 | 2015-09-24T20:13:00Z | 10 | 2 |  |  |  | 0 | 0 | BNGC1 | 7.8 | 2015-09-24T21:51:00Z | 12.01 | 4
PG&E | 42272.7278 | 42272.7278 | 38.7169 | -120.7693 | Vegetation | Rural | < 0.25 Acres | Fire Agency | el dorado F D | 101405928 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42272.7278 | 42272.7278 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0616 | 2015 | 9 | 25 | 17 | 28 | 15-0063666 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 111180 | 10.4745 | 211_198 | <25mph | <15mph | HFTD - Distribution | E5691 | 2.8 | 2015-09-25T23:45:00Z | 7 | 16 | C6129 | 4.54 | 2015-09-25T23:39:00Z | 12.01 | 40 | E5691 | 2.8 | 2015-09-25T23:45:00Z | 7 | 28 | C6129 | 4.54 | 2015-09-25T23:39:00Z | 12.01 | 76
PG&E | 42275.4042 | 42275.4042 | 37.9623 | -122.1765 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100458692 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42275.4042 | 42275.4042 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0619 | 2015 | 9 | 28 | 9 | 42 | 15-0066062 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 2125 | 6.386 | 190_282 | <25mph | <15mph | HFTD - Distribution | PLEC1 | 3.75 | 2015-09-28T16:28:00Z | 14.99 | 6 | UPBC1 | 6.07 | 2015-09-28T15:42:00Z | 20.98 | 147 | PLEC1 | 3.75 | 2015-09-28T16:28:00Z | 14.99 | 7 | MZXC1 | 5.72 | 2015-09-28T17:18:00Z | 20.98 | 286
PG&E | 42277.7257 | 42277.7257 | 38.5747 | -120.682 | Vegetation | Rural | < 0.25 Acres | Fire Agency | el dorado county | 7901 shenandoah ln |  | 21000 | Conductor | Overhead | Yes | 42277.7257 | 42277.7257 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0625 | 2015 | 9 | 30 | 17 | 25 | 15-0066934 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 28912 | 3.2693 | 149_204 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42280.3104 | 42280.3104 | 39.0633 | -122.6237 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 2323 new long valley rd | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0631 | 2015 | 10 | 3 | 7 | 27 | No ILIS or TOTL available | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 10.2588 | 251_181 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42280.8826 | 42280.8826 | 39.7358 | -121.6855 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | honey run rd at cutouts 16015 |  | 12000 | Conductor | Overhead | Yes | 42280.8826 | 42280.8826 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0632 | 2015 | 10 | 3 | 21 | 11 | 15-0067708 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 10499 | 6.7716 | 130_298 | <25mph | <15mph | HFTD - Distribution | PDEC1 | 3.46 | 2015-10-04T04:00:00Z | 14 | 1 | E4833 | 6.49 | 2015-10-04T03:45:00Z | 18.99 | 7 | PDEC1 | 3.46 | 2015-10-04T05:00:00Z | 15.99 | 2 | E4833 | 6.49 | 2015-10-04T03:45:00Z | 18.99 | 15
PG&E | 42281.0437 | 42281.0437 | 39.7923 | -121.5803 | Vegetation | Urban | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42281.0437 | 42281.0437 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0634 | 2015 | 10 | 4 | 1 | 3 | 15-0067711 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2697 | 17.8391 | 119_301 | <25mph | >=15mph | HFTD - Distribution | E4833 | 1.69 | 2015-10-04T07:12:00Z | 18.01 | 13 | JBGC1 | 6.22 | 2015-10-04T07:13:00Z | 53.02 | 27 | E4833 | 1.69 | 2015-10-04T07:12:00Z | 18.01 | 25 | JBGC1 | 6.22 | 2015-10-04T07:13:00Z | 53.02 | 52
PG&E | 42281.0639 | 42281.0639 | 39.2279 | -121.3774 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | in field at 6275 sandstonel ln |  | 12000 | Conductor | Overhead | Yes | 42281.0639 | 42281.0639 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0635 | 2015 | 10 | 4 | 1 | 32 | 15-0067743 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 4021 | 6.2139 | 175_338 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42284.6277 | 42284.6277 | 35.3079 | -120.8328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101924901 | Pacific Bell | 12000 | Conductor | Overhead | Yes | 42284.6277 | 42284.6277 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0640 | 2015 | 10 | 7 | 15 | 3 | 15-0068730 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 77896 | 2.8464 | 148_378 | <25mph | <15mph | HFTD - Distribution | E1668 | 0.48 | 2015-10-07T22:00:00Z | 15.99 | 5 | E1668 | 0.48 | 2015-10-07T22:00:00Z | 15.99 | 7 | E6113 | 0.7 | 2015-10-07T22:46:00Z | 18.01 | 11 | E6113 | 0.7 | 2015-10-07T22:46:00Z | 18.01 | 14
PG&E | 42286.2722 | 42286.2722 | 38.364 | -122.9173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 320 Freestone St, Frestone | Pacific Bell | 0 – 750 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0642 | 2015 | 10 | 9 | 6 | 32 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 7.488 | 210_104 | <25mph | <15mph | HFTD - Distribution | D2849 | 3.33 | 2015-10-09T13:22:00Z | 3 | 22 | D2849 | 3.33 | 2015-10-09T13:22:00Z | 3 | 49 | D2849 | 3.33 | 2015-10-09T13:22:00Z | 3 | 44 | D2849 | 3.33 | 2015-10-09T13:22:00Z | 3 | 99
PG&E | 42293.4049 | 42293.4049 | 39.187 | -123.2015 | Vegetation | Rural | < 3 meters | Unknown |  | 102196855 |  | 12000 | Conductor | Overhead | Yes | 42293.4049 | 42293.4049 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0653 | 2015 | 10 | 16 | 9 | 43 | 15-0070948 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 65228 | 2.6808 | 253_157 | <25mph | <15mph | HFTD - Distribution | E7513 | 1.34 | 2015-10-16T16:08:00Z | 3 | 13 | E7513 | 1.34 | 2015-10-16T16:08:00Z | 3 | 25 | E7513 | 1.34 | 2015-10-16T17:38:00Z | 4 | 25 | E7513 | 1.34 | 2015-10-16T17:38:00Z | 4 | 49
PG&E | 42302.2431 | 42302.2431 | 37.7843 | -121.7683 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | cutouts 9504 |  | 21000 | Conductor | Overhead | Yes | 42302.2431 | 42302.2431 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0657 | 2015 | 10 | 25 | 5 | 50 | 15-0073203 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 10710 | 7.7814 | 190_281 | <25mph | <15mph | HFTD - Distribution | VAQC1 | 1.86 | 2015-10-25T12:45:00Z | 15.99 | 2 | VAQC1 | 1.86 | 2015-10-25T12:45:00Z | 15.99 | 2 | VAQC1 | 1.86 | 2015-10-25T13:45:00Z | 18.99 | 4 | VAQC1 | 1.86 | 2015-10-25T13:45:00Z | 18.99 | 4
PG&E | 42307.1868 | 42307.1868 | 39.5059 | -123.7672 | Vegetation | Rural | < 3 meters | Fire Agency | local fire | in field next to hwy / 1 span SS of Fuse 4617 |  | 12000 | Conductor | Overhead | Yes | 42307.1868 | 42307.1868 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0661 | 2015 | 10 | 30 | 4 | 29 | 15-0074188 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 273183 | 6.0304 | 151_219 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42307.7174 | 42307.7174 | 38.3166 | -120.7226 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 7600 HWY 49, Jackson | None | 0 – 750 | Transformer | Overhead | No |  |  | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 0662 | 2015 | 10 | 30 | 17 | 13 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 8.2726 | 82_324 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | MTZC1 | 6.34 | 2015-10-30T23:56:00Z | 11.01 | 1 |  |  |  | 0 | 0 | MTZC1 | 6.34 | 2015-10-30T23:56:00Z | 11.01 | 2
PG&E | 42308.3229 | 42308.3229 | 38.1157 | -120.8931 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal FIRE | 103763040 |  | 12000 | Conductor | Overhead | Yes | 42308.3229 | 42308.3229 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0663 | 2015 | 10 | 31 | 7 | 45 | 15-0074424 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 314565 | 3.1706 | 211_256 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | CMAC1 | 7.6 | 2015-10-31T13:59:00Z | 12.01 | 1 |  |  |  | 0 | 0 | CMAC1 | 7.6 | 2015-10-31T14:59:00Z | 13 | 2
PG&E | 42317.2465 | 42317.2465 | 34.9984 | -120.3634 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE |  |  | 12000 | Conductor | Overhead | Yes | 42317.2465 | 42317.2465 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0673 | 2015 | 11 | 9 | 5 | 55 | 15-0076534 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 205393 | 9.4792 | 175_300 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | AU609 | 7.47 | 2015-11-09T13:07:00Z | 2.01 | 4 |  |  |  | 0 | 0 | AU609 | 7.47 | 2015-11-09T13:07:00Z | 2.01 | 7
PG&E | 42323.6875 | 42323.6875 | 37.0007 | -121.885 | Vegetation | Rural | < 3 meters | Customer |  | 101691004 | Pacific Bell | 21000 | Conductor | Overhead | Yes | 42323.6875 | 42323.6875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0676 | 2015 | 11 | 15 | 16 | 30 | 15-0077978 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 25920 | 16.4134 | 159_198 | <25mph | >=15mph | HFTD - Distribution | E7291 | 2.82 | 2015-11-16T00:21:00Z | 32.01 | 33 | E7291 | 2.82 | 2015-11-16T00:21:00Z | 32.01 | 123 | E7291 | 2.82 | 2015-11-16T00:21:00Z | 32.01 | 62 | E7291 | 2.82 | 2015-11-16T00:21:00Z | 32.01 | 232
PG&E | 42329.4417 | 42329.4417 | 38.0679 | -120.1872 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101045952 | Pacific Bell | 17000 | Conductor | Overhead | Yes | 42329.4417 | 42329.4417 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 0677 | 2015 | 11 | 21 | 10 | 36 | 15-0079868 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18350 | 4.5257 | 161_184 | <25mph | <15mph | HFTD - Distribution | MOUC1 | 3.29 | 2015-11-21T18:02:00Z | 17 | 1 | MOUC1 | 3.29 | 2015-11-21T18:02:00Z | 17 | 1 | MOUC1 | 3.29 | 2015-11-21T19:02:00Z | 18.01 | 2 | MOUC1 | 3.29 | 2015-11-21T19:02:00Z | 18.01 | 2
PG&E | 42339.5021 | 42339.5021 | 35.6744 | -120.9932 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal FIRE | 101860660 |  | 21000 | Conductor | Overhead | Yes | 42339.5021 | 42339.5021 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0680 | 2015 | 12 | 1 | 12 | 3 | 15-0081983 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 42427 | 9.2617 | 160_329 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | TABC1 | 4.07 | 2015-12-01T19:07:00Z | 8.99 | 1 |  |  |  | 0 | 0 | TABC1 | 4.07 | 2015-12-01T19:07:00Z | 8.99 | 2
PG&E | 42341.5069 | 42341.5069 | 40.0277 | -120.9652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | usfs | spanish creek campground |  | 12000 | Conductor | Overhead | Yes | 42341.5069 | 42341.5069 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0683 | 2015 | 12 | 3 | 12 | 10 | 15-0082505 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 196854 | 4.6483 | 155_201 | <25mph | <15mph | HFTD - Distribution | CHAC1 | 3.2 | 2015-12-03T19:47:00Z | 47 | 2 | CHAC1 | 3.2 | 2015-12-03T19:47:00Z | 47 | 3 | CHAC1 | 3.2 | 2015-12-03T20:47:00Z | 59.01 | 4 | CHAC1 | 3.2 | 2015-12-03T20:47:00Z | 59.01 | 6
PG&E | 42346.5285 | 42346.5285 | 38.2489 | -120.5228 | Other | Rural | Structure Only | Unknown |  | 7026 Railroad Flat Road, Mountain Ranch |  | 12000 | Conductor | Overhead | Yes | 42346.5285 | 42346.5285 | Contact From Object | N.A. | Other | Electric Facility | Human Error | AT&T work error | Other/Unknown | 0684 | 2015 | 12 | 8 | 12 | 41 | 15-0083435 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1120 | 11.1655 | 201_351 | <25mph | <15mph | HFTD - Distribution | ESPC1 | 3.04 | 2015-12-08T20:13:00Z | 5.99 | 6 | ESPC1 | 3.04 | 2015-12-08T20:13:00Z | 5.99 | 6 | ESPC1 | 3.04 | 2015-12-08T21:13:00Z | 10 | 13 | ESPC1 | 3.04 | 2015-12-08T21:13:00Z | 10 | 13
PG&E | 42369.8 | 42369.8 | 37.1568 | -121.9868 | Vegetation | Rural | < 0.25 Acres | Fire Agency | LOS GATOS MONTE SERENO SARATOGA | 100518215 | Verizon | 21000 | Conductor | Overhead | Yes | 42369.8 | 42369.8 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 0689 | 2015 | 12 | 31 | 19 | 12 | 15-0087962 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7979 | 8.4855 | 224_72 | <25mph | <15mph | HFTD - Distribution | D8979 | 2.76 | 2016-01-01T02:57:00Z | 10 | 23 | E6085 | 6.01 | 2016-01-01T02:32:00Z | 10 | 176 | D8979 | 2.76 | 2016-01-01T04:08:00Z | 12.01 | 45 | D8979 | 2.76 | 2016-01-01T04:08:00Z | 12.01 | 346
PG&E | 42390.8972 | 42390.8972 | 40.553 | -124.1116 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100994021 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42390.8972 | 42390.8972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0690 | 2016 | 1 | 21 | 21 | 32 | 16-0007239 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 6468 | 9.9649 | 156_193 | <25mph | <15mph | HFTD - Distribution | KFOT | 1.14 | 2016-01-22T05:15:00Z | 36.82 | 28 | KFOT | 1.14 | 2016-01-22T05:15:00Z | 36.82 | 28 | KFOT | 1.14 | 2016-01-22T05:35:00Z | 48.34 | 55 | KFOT | 1.14 | 2016-01-22T05:35:00Z | 48.34 | 55
PG&E | 42392.6535 | 42392.6535 | 39.9486 | -122.3728 | Vegetation | RURAL | < 0.25 Acres | Self Extinguished | N.A. | 101524077 |  | 12000 | Conductor | Overhead | Yes | 42392.6535 | 42392.6535 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0691 | 2016 | 1 | 23 | 15 | 41 | 16-0007778 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 133520 | 22.3041 | 69_382 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42405.8681 | 42405.8681 | 40.0156 | -122.4333 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | TEHAMA COUNTY & LOCAL VOLUNTEER | 101529688 | None | 12000 | Conductor | Overhead | Yes | 42405.8681 | 42405.8681 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0693 | 2016 | 2 | 5 | 20 | 50 | 16-0011034 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 11424 | 14.1578 | 137_227 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42408.1632 | 42408.1632 | 39.7852 | -121.5056 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100337507 |  | 12000 | Conductor | Overhead | Yes | 42408.1632 | 42408.1632 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0694 | 2016 | 2 | 8 | 3 | 55 | 16-0011201 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 87046 | 5.6741 | 139_351 | <25mph | <15mph | HFTD - Distribution | JBGC1 | 3.52 | 2016-02-08T11:13:00Z | 45.99 | 1 | JBGC1 | 3.52 | 2016-02-08T11:13:00Z | 45.99 | 23 | JBGC1 | 3.52 | 2016-02-08T12:13:00Z | 57 | 2 | JBGC1 | 3.52 | 2016-02-08T12:13:00Z | 57 | 46
PG&E | 42463.5007 | 42463.5007 | 38.6804 | -123.125 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101968191 |  | 12000 | Conductor | Overhead | Yes | 42463.5007 | 42463.5007 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0702 | 2016 | 4 | 3 | 12 | 1 | 16-0025794 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 3528 | 6.9875 | 148_373 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42468.5514 | 42468.5514 | 39.0429 | -121.1002 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100086751 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42468.5514 | 42468.5514 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0705 | 2016 | 4 | 8 | 13 | 14 | 16-0027237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 11817 | 2.5181 | 289_93 | <25mph | <15mph | HFTD - Distribution | C0713 | 3.59 | 2016-04-08T19:24:00Z | 8.01 | 17 | E1789 | 7.22 | 2016-04-08T20:00:00Z | 8.99 | 40 | C0713 | 3.59 | 2016-04-08T20:34:00Z | 10 | 33 | C0713 | 3.59 | 2016-04-08T20:34:00Z | 10 | 80
PG&E | 42473.8111 | 42473.8111 | 40.4954 | -124.1219 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103659313 |  | 12000 | Conductor | Overhead | Yes | 42473.8111 | 42473.8111 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0706 | 2016 | 4 | 13 | 19 | 28 | 16-0028421 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 688 | 8.5227 | 195_296 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | KFOT | 4.03 | 2016-04-14T01:55:00Z | 32.21 | 30 |  |  |  | 0 | 0 | KFOT | 4.03 | 2016-04-14T01:55:00Z | 32.21 | 58
PG&E | 42481.3924 | 42481.3924 | 39.293 | -123.769 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 103312287 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0711 | 2016 | 4 | 21 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 9.0201 | 145_250 | <25mph | <15mph | HFTD - Distribution | E6025 | 0.21 | 2016-04-21T16:15:00Z | 3 | 4 | E6025 | 0.21 | 2016-04-21T16:15:00Z | 3 | 4 | E6025 | 0.21 | 2016-04-21T17:15:00Z | 4.99 | 8 | E6025 | 0.21 | 2016-04-21T17:15:00Z | 4.99 | 8
PG&E | 42490 | 0.74931 | 38.3142 | -120.9015 | Vegetation | RURAL | < 3 meters | Fire Agency | Kern County FD |  |  | 12000 | Conductor | Overhead | Yes | 42490 | 0.74931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0719 | 2016 | 4 | 30 | 17 | 59 | 16-0032910 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 722 | 8.5677 | 277_158 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | CMAC1 | 6.54 | 2016-04-30T06:59:00Z | 23 | 3 |  |  |  | 0 | 0 | CFAC1 | 4.81 | 2016-04-30T07:05:00Z | 28.99 | 6
PG&E | 42502.8438 | 42502.8438 | 35.1922 | -120.4563 | Vegetation | RURAL | < 3 meters | Self Extinguished | N.A. | 101857280 |  | 12000 | Conductor | Overhead | Yes | 42502.8438 | 42502.8438 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0727 | 2016 | 5 | 12 | 20 | 15 | 16-0035728 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 54088 | 3.4097 | 71_376 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | AU609 | 7.02 | 2016-05-13T02:21:00Z | 10 | 11 |  |  |  | 0 | 0 | AU609 | 7.02 | 2016-05-13T02:21:00Z | 10 | 25
PG&E | 42505.6625 | 42505.6625 | 36.7948 | -119.3966 | Vegetation | RURAL | 100 - 299 Acres | Fire Agency | Cal Fire | 100729685 | None | 12000 | Conductor | Overhead | Yes | 42505.6625 | 42505.6625 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0730 | 2016 | 5 | 15 | 15 | 54 | 16-0036136 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 180310 | 10.2803 | 175_303 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | FCHC1 | 7.54 | 2016-05-15T22:00:00Z | 12.01 | 1 |  |  |  | 0 | 0 | FCHC1 | 7.54 | 2016-05-15T23:00:00Z | 15.99 | 2
PG&E | 42508 | 0.76667 | 39.7381 | -123.1587 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42508 | 0.76667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0735 | 2016 | 5 | 18 | 18 | 24 | 16-0036911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1482 | 1.95 | 289_96 | <25mph | <15mph | HFTD - Distribution | C3111 | 2.79 | 2016-05-18T06:56:00Z | 0 | 2 | EELC1 | 7.26 | 2016-05-18T06:45:00Z | 13 | 3 | C3111 | 2.79 | 2016-05-18T07:57:00Z | 0 | 6 | EELC1 | 7.26 | 2016-05-18T06:45:00Z | 13 | 8
PG&E | 42509.0708 | 42509.0708 | 34.6645 | -120.4 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Santa Barbara County FD | 101916587 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42509.0708 | 42509.0708 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | no-match | 0738 | 2016 | 5 | 19 | 1 | 42 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 5.916 | 140_376 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | D4531 | 5.16 | 2016-05-19T08:04:00Z | 4 | 3 |  |  |  | 0 | 0 | D4531 | 5.16 | 2016-05-19T09:19:00Z | 4 | 7
PG&E | 42509.7875 | 42509.7875 | 38.8168 | -123.5843 | Vegetation | RURAL | < 3 meters | Fire Agency | Gualala Firw | 102183917 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42509.7875 | 42509.7875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0740 | 2016 | 5 | 19 | 18 | 54 | 16-0037247 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 4510 | 40.5937 | 88_285 | 40-55mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42510.6257 | 0.62569 | 39.0559 | -123.4581 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102198323 |  | 12000 | Conductor | Overhead | Yes | 42510.6257 | 0.62569 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0741 | 2016 | 5 | 20 | 15 | 1 | 16-0037479 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2720 | 14.9654 | 208_225 | <25mph | <15mph | HFTD - Distribution | E1763 | 3.93 | 2016-05-20T21:19:00Z | 11.01 | 4 | BNVC1 | 7.56 | 2016-05-20T21:50:00Z | 25.99 | 6 | E1763 | 3.93 | 2016-05-20T22:18:00Z | 12.01 | 8 | BNVC1 | 7.56 | 2016-05-20T22:50:00Z | 27 | 15
PG&E | 42514.525 | 42514.525 | 38.0811 | -120.668 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101278239 |  | 12000 | Conductor | Overhead | Yes | 42514.525 | 42514.525 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0747 | 2016 | 5 | 24 | 12 | 36 | 16-0038096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 10678 | 11.9408 | 171_236 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42519.5965 | 42519.5965 | 40.5795 | -122.4694 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103156596 | Yes | 12000 | Conductor | Overhead | Yes | 42519.5965 | 42519.5965 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0751 | 2016 | 5 | 29 | 14 | 19 | 16-0039619 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3860 | 11.1608 | 256_169 | <25mph | <15mph | HFTD - Distribution | MMOC1 | 1.91 | 2016-05-29T21:00:00Z | 8.01 | 5 | E6886 | 6.63 | 2016-05-29T20:41:00Z | 8.01 | 13 | MMOC1 | 1.91 | 2016-05-29T22:00:00Z | 8.01 | 10 | C5599 | 7.38 | 2016-05-29T21:31:00Z | 8.99 | 26
PG&E | 42521.1681 | 42521.1681 | 35.7984 | -120.9743 | Vegetation | RURAL | < 0.25 Acres | Utility: PG&E | N.A. | 101863413 |  | 12000 | Conductor | Overhead | Yes | 42521.1681 | 42521.1681 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0754 | 2016 | 5 | 31 | 4 | 2 | 16-0039748 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 51888 | 14.9631 | 293_100 | <25mph | <15mph | HFTD - Distribution | E9175 | 3.45 | 2016-05-31T10:42:00Z | 1.01 | 13 | E9175 | 3.45 | 2016-05-31T10:42:00Z | 1.01 | 17 | E9175 | 3.45 | 2016-05-31T11:22:00Z | 1.01 | 25 | E9175 | 3.45 | 2016-05-31T11:22:00Z | 1.01 | 33
PG&E | 42524 | 42524.5111 | 38.6435 | -120.6959 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | cal-fire and usfs | 103119737 |  | 21000 | Conductor | Overhead | Yes | 42524 | 42524.5111 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0764 | 2016 | 6 | 3 | 12 | 16 | 16-0040808 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 101354 | 4.1999 | 173_161 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E6490 | 7.82 | 2016-06-03T06:56:00Z | 0 | 16 |  |  |  | 0 | 0 | E6490 | 7.82 | 2016-06-03T07:56:00Z | 2.01 | 32
PG&E | 42525 | 0.92708 | 38.5117 | -122.9373 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42525 | 0.92708 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0768 | 2016 | 6 | 4 | 22 | 15 | 16-0041119 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7220 | 9.2554 | 161_208 | <25mph | <15mph | HFTD - Distribution | D9841 | 2.58 | 2016-06-04T06:52:00Z | 0 | 11 | E9070 | 7.35 | 2016-06-04T06:25:00Z | 5.99 | 75 | D9841 | 2.58 | 2016-06-04T07:52:00Z | 0 | 21 | E9070 | 7.35 | 2016-06-04T07:25:00Z | 5.99 | 142
PG&E | 42526.6556 | 42526.6556 | 40.3441 | -123.71 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101009790 |  | 60000 | Conductor | Overhead | Yes | 42526.6556 | 42526.6556 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0774 | 2016 | 6 | 5 | 15 | 44 | HM-2016-016 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 4.5459 | 85_370 | <25mph | <15mph | HFTD - Transmission |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42527 | 42527.825 | 38.9129 | -121.1192 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire/placer fire | 100050264 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42527 | 42527.825 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0775 | 2016 | 6 | 6 | 19 | 48 | 16-0041497 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 2039 | 7.5231 | 261_162 | <25mph | <15mph | HFTD - Distribution | D8862 | 3.32 | 2016-06-06T06:49:00Z | 4 | 4 | D8862 | 3.32 | 2016-06-06T06:49:00Z | 4 | 4 | D8862 | 3.32 | 2016-06-06T07:04:00Z | 5.99 | 8 | D8862 | 3.32 | 2016-06-06T07:04:00Z | 5.99 | 8
PG&E | 42531.6604 | 42531.6604 | 39.9934 | -123.7883 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100992291 |  | 12000 | Conductor | Overhead | Yes | 42531.6604 | 42531.6604 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0788 | 2016 | 6 | 10 | 15 | 51 | 16-0042501 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | N.A. | 14.26 | 257_169 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | AV037 | 5.5 | 2016-06-10T22:23:00Z | 8.99 | 3 |  |  |  | 0 | 0 | AV037 | 5.5 | 2016-06-10T23:13:00Z | 11.01 | 7
PG&E | 42531.6646 | 42531.6646 | 38.1792 | -120.6657 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103809655 |  | 12000 | Conductor | Overhead | Yes | 42531.6646 | 42531.6646 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0789 | 2016 | 6 | 10 | 15 | 57 | 16-0042508 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 17.8656 | 82_351 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42532 | 42532.8229 | 39.3265 | -121.3921 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101292512 |  | 0 – 750 | Transformer | Overhead | Yes | 42532 | 42532.8229 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 0790 | 2016 | 6 | 11 | 19 | 45 | 16-0042611 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 642 | 6.2372 | 214_249 | <25mph | <15mph | HFTD - Distribution | BNGC1 | 3.76 | 2016-06-11T06:51:00Z | 1.01 | 1 | BNGC1 | 3.76 | 2016-06-11T06:51:00Z | 1.01 | 1 | BNGC1 | 3.76 | 2016-06-11T07:51:00Z | 4 | 2 | BNGC1 | 3.76 | 2016-06-11T07:51:00Z | 4 | 2
PG&E | 42533 | 42533.4319 | 38.0491 | -120.3976 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101042514 |  | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0792 | 2016 | 6 | 12 | 10 | 22 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 16.9807 | 141_210 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42533 | 42533.5514 | 37.5096 | -120.0462 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101083986 |  | 0 – 750 | Conductor | Overhead | Yes | 42533 | 42533.5514 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0795 | 2016 | 6 | 12 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 22.6022 | 143_332 | <25mph | >=15mph | HFTD - Distribution | MPOC1 | 3.28 | 2016-06-12T06:07:00Z | 11.01 | 1 | MPOC1 | 3.28 | 2016-06-12T06:07:00Z | 11.01 | 1 | MPOC1 | 3.28 | 2016-06-12T06:07:00Z | 11.01 | 2 | MPOC1 | 3.28 | 2016-06-12T06:07:00Z | 11.01 | 2
PG&E | 42533.0729 | 0.072917 | 37.4643 | -122.3459 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Unknown | 100265854 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42533.0729 | 0.072917 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0796 | 2016 | 6 | 12 | 1 | 45 | 16-0042637 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 19836 | 19.954 | 153_253 | <25mph | >=15mph | HFTD - Distribution | PUGC1 | 2.7 | 2016-06-12T08:18:00Z | 8.01 | 8 | AU981 | 5.46 | 2016-06-12T08:44:00Z | 20 | 85 | PUGC1 | 2.7 | 2016-06-12T08:18:00Z | 8.01 | 17 | E2649 | 7.02 | 2016-06-12T09:44:00Z | 24 | 171
PG&E | 42536 | 42536.5479 | 38.4433 | -120.7568 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103169620 |  | 12000 | Conductor | Overhead | Yes | 42536 | 42536.5479 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0801 | 2016 | 6 | 15 | 13 | 9 | 16-0043476 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 23963 | 7.7425 | 127_264 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | MTZC1 | 6.74 | 2016-06-15T06:56:00Z | 4.99 | 1 |  |  |  | 0 | 0 | MTZC1 | 6.74 | 2016-06-15T07:56:00Z | 5.99 | 2
PG&E | 42540 | 42540.5049 | 39.3811 | -123.7737 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102187888 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42540 | 42540.5049 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0807 | 2016 | 6 | 19 | 12 | 7 | 16-0044317 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6100 | 14.1625 | 226_169 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E6025 | 6.3 | 2016-06-19T06:30:00Z | 3 | 5 |  |  |  | 0 | 0 | E6025 | 6.3 | 2016-06-19T06:30:00Z | 3 | 9
PG&E | 42540 | 42540.7215 | 38.4508 | -122.3546 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire--napa fire | 102256859 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42540 | 42540.7215 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0808 | 2016 | 6 | 19 | 17 | 19 | 16-0044337 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 672 | 7.3683 | 81_317 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | ATLC1 | 5.13 | 2016-06-19T06:29:00Z | 11.01 | 1 |  |  |  | 0 | 0 | ATLC1 | 5.13 | 2016-06-19T06:29:00Z | 11.01 | 2
PG&E | 42541 | 42541.6979 | 41.0697 | -123.6789 | Vegetation | RURAL | < 3 meters | Fire Agency | Hoopa FD | 101011420 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42541 | 42541.6979 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0811 | 2016 | 6 | 20 | 16 | 45 | 16-0044577 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 7361 | 7.0385 | 271_159 | <25mph | <15mph | HFTD - Distribution | HOAC1 | 1.56 | 2016-06-20T06:40:00Z | 3 | 1 | HOAC1 | 1.56 | 2016-06-20T06:40:00Z | 3 | 1 | HOAC1 | 1.56 | 2016-06-20T06:40:00Z | 3 | 2 | HOAC1 | 1.56 | 2016-06-20T06:40:00Z | 3 | 2
PG&E | 42542 | 0.86736 | 35.5352 | -120.8457 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101900832 |  | 12000 | Conductor | Overhead | Yes | 42542 | 0.86736 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0812 | 2016 | 6 | 21 | 20 | 49 | 16-0044904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7806 | 2.4781 | 88_410 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E6394 | 6.56 | 2016-06-21T06:59:00Z | 1.01 | 4 |  |  |  | 0 | 0 | E6394 | 6.56 | 2016-06-21T07:59:00Z | 1.01 | 8
PG&E | 42542 | 42542.4229 | 39.0294 | -121.2927 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100024816 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | no-match | 0813 | 2016 | 6 | 21 | 10 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 10.9438 | 187_296 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E5440 | 6.7 | 2016-06-21T06:47:00Z | 7 | 28 |  |  |  | 0 | 0 | E5440 | 6.7 | 2016-06-21T06:47:00Z | 7 | 56
PG&E | 42542 | 42542.7035 | 38.4233 | -122.5448 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | KENWOOD FIRE XST | 102036904 | Yes | 0 – 750 | Conductor | Overhead | Yes | 42542 | 42542.7035 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0814 | 2016 | 6 | 21 | 16 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 2.3548 | 133_263 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E1582 | 5.25 | 2016-06-21T06:33:00Z | 4 | 14 |  |  |  | 0 | 0 | E1582 | 5.25 | 2016-06-21T06:33:00Z | 4 | 28
PG&E | 42545 | 42545.6097 | 40.22 | -122.283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101526647 | PACIFIC BELL | 0 – 750 | Unknown | Overhead | Yes | 42545 | 42545.6097 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0821 | 2016 | 6 | 24 | 14 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 15.3241 | 197_279 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | KRBL | 5.07 | 2016-06-24T06:54:00Z | 23.02 | 1 |  |  |  | 0 | 0 | KRBL | 5.07 | 2016-06-24T06:54:00Z | 23.02 | 1
PG&E | 42547 | 42547.6931 | 39.5042 | -121.4475 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100375810 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42547 | 42547.6931 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 0823 | 2016 | 6 | 26 | 16 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 8.0953 | 173_336 | <25mph | <15mph | HFTD - Distribution | TT309 | 3.14 | 2016-06-26T06:45:00Z | 8.01 | 1 | TT309 | 3.14 | 2016-06-26T06:45:00Z | 8.01 | 1 | TT309 | 3.14 | 2016-06-26T06:45:00Z | 8.01 | 2 | TT309 | 3.14 | 2016-06-26T06:45:00Z | 8.01 | 2
PG&E | 42547.4625 | 42547.4625 | 40.4832 | -122.0466 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101483777 | FRONTIER | 12000 | Conductor | Overhead | Yes | 42547.4625 | 42547.4625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0826 | 2016 | 6 | 26 | 11 | 6 | 16-0045846 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 15520 | 13.515 | 214_111 | <25mph | <15mph | HFTD - Distribution | AR225 | 3.09 | 2016-06-26T17:25:00Z | 8.01 | 10 | AR225 | 3.09 | 2016-06-26T17:25:00Z | 8.01 | 10 | AR225 | 3.09 | 2016-06-26T18:45:00Z | 8.01 | 22 | AR225 | 3.09 | 2016-06-26T18:45:00Z | 8.01 | 22
PG&E | 42551 | 0.0020833 | 39.8157 | -121.5994 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire |  |  | 12000 | Conductor | Overhead | Yes | 42551 | 0.0020833 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0832 | 2016 | 6 | 30 | 0 | 3 | 16-0046763 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 299100 | 7.6229 | 180_156 | <25mph | <15mph | HFTD - Distribution | C4565 | 1.82 | 2016-06-30T06:40:00Z | 3 | 2 | C4565 | 1.82 | 2016-06-30T06:40:00Z | 3 | 15 | C4565 | 1.82 | 2016-06-30T07:30:00Z | 3 | 5 | C4565 | 1.82 | 2016-06-30T07:30:00Z | 3 | 31
PG&E | 42551 | 42551.7181 | 40.0353 | -122.5694 | Vegetation | RURAL | 300 - 999 Acres | Fire Agency | Cal Fire | 101528146 |  | 12000 | Conductor | Overhead | Yes | 42551 | 42551.7181 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0833 | 2016 | 6 | 30 | 17 | 14 | 16-0047210 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Fell into (slight defect) | 4520 | 9.209 | 174_339 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42551.5972 | 42551.5972 | 37.9927 | -120.3996 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Cal Fire | 102327111 | PACIFIC BELL | 17000 | Conductor | Overhead | Yes | 42551.5972 | 42551.5972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0834 | 2016 | 6 | 30 | 14 | 20 | 16-0047073 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 278 | 9.6736 | 226_239 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42554.625 | 42554.625 | 38.0348 | -120.3809 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101050507 |  | 17000 | Conductor | Overhead | Yes | 42554.625 | 42554.625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0837 | 2016 | 7 | 3 | 15 | 0 | 16-0047689 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38812 | 10.2237 | 178_227 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | MOUC1 | 7.53 | 2016-07-03T21:02:00Z | 14.99 | 1 |  |  |  | 0 | 0 | MOUC1 | 7.53 | 2016-07-03T22:02:00Z | 17 | 2
PG&E | 42559.4507 | 42559.4507 | 38.3373 | -122.1211 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 102291118 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42559.4507 | 42559.4507 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0842 | 2016 | 7 | 8 | 10 | 49 | 16-0048647 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 19469 | 7.9878 | 164_311 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E6079 | 6.28 | 2016-07-08T17:23:00Z | 14.99 | 12 |  |  |  | 0 | 0 | E6079 | 6.28 | 2016-07-08T17:23:00Z | 14.99 | 23
PG&E | 42563.5958 | 42563.5958 | 35.3471 | -120.3813 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101879190 |  | 21000 | Conductor | Overhead | Yes | 42563.5958 | 42563.5958 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0848 | 2016 | 7 | 12 | 14 | 18 | 16-0049403 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 18883 | 14.2521 | 163_201 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42566.2215 | 42566.2215 | 35.1839 | -120.5018 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101846594 |  | 12000 | Conductor | Overhead | Yes | 42566.2215 | 42566.2215 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0851 | 2016 | 7 | 15 | 5 | 19 | 16-0050086 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 62404 | 4.7111 | 293_96 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | D6295 | 5.2 | 2016-07-15T12:11:00Z | 0 | 8 |  |  |  | 0 | 0 | D6295 | 5.2 | 2016-07-15T13:01:00Z | 0 | 15
PG&E | 42566.5896 | 42566.5896 | 38.6965 | -120.8598 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412774 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.5896 | 42566.5896 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0852 | 2016 | 7 | 15 | 14 | 9 | 16-0050274 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 11253 | 4.6799 | 222_84 | <25mph | <15mph | HFTD - Distribution | C6129 | 0.59 | 2016-07-15T20:39:00Z | 12.01 | 31 | C6129 | 0.59 | 2016-07-15T20:39:00Z | 12.01 | 65 | C6129 | 0.59 | 2016-07-15T20:39:00Z | 12.01 | 61 | C6129 | 0.59 | 2016-07-15T20:39:00Z | 12.01 | 130
PG&E | 42566.6014 | 42566.6014 | 38.1366 | -122.7092 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | NOVATO FIRE AND OTHERS | 102013570 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42566.6014 | 42566.6014 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0853 | 2016 | 7 | 15 | 14 | 26 | 16-0050269 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 758 | 4.6138 | 125_247 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | BBEC1 | 7.51 | 2016-07-15T21:11:00Z | 13 | 25 |  |  |  | 0 | 0 | BBEC1 | 7.51 | 2016-07-15T21:11:00Z | 13 | 50
PG&E | 42567.0403 | 42567.0403 | 36.4379 | -121.9198 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101669758 |  | 12000 | Other | Overhead | Yes | 42567.0403 | 42567.0403 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 0855 | 2016 | 7 | 16 | 0 | 58 | 16-0050335 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 8976 | 2.0878 | 288_94 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E6019 | 7.86 | 2016-07-16T07:42:00Z | 4.99 | 4 |  |  |  | 0 | 0 | E6019 | 7.86 | 2016-07-16T08:27:00Z | 4.99 | 8
PG&E | 42567.3465 | 42567.3465 | 37.4828 | -119.87 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101079104 | None | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0856 | 2016 | 7 | 16 | 8 | 19 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 17.2897 | 159_153 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | MPOC1 | 6.57 | 2016-07-16T15:07:00Z | 8.01 | 10 |  |  |  | 0 | 0 | MPOC1 | 6.57 | 2016-07-16T15:07:00Z | 8.01 | 19
PG&E | 42567.8514 | 42567.8514 | 38.4944 | -122.4944 | Vegetation | URBAN | < 0.25 Acres | Fire Agency | Cal Fire | 102265740 | None | 12000 | Conductor | Overhead | Yes | 42567.8514 | 42567.8514 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0857 | 2016 | 7 | 16 | 20 | 26 | 16-0050320 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 13240 | 10.3059 | 249_211 | <25mph | <15mph | HFTD - Distribution | TR110 | 3.79 | 2016-07-17T02:49:00Z | 5.99 | 1 | E1582 | 7.62 | 2016-07-17T03:03:00Z | 8.01 | 7 | TR110 | 3.79 | 2016-07-17T02:49:00Z | 5.99 | 2 | E1582 | 7.62 | 2016-07-17T03:03:00Z | 8.01 | 14
PG&E | 42571.8021 | 42571.8021 | 37.7712 | -121.8104 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100898986 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42571.8021 | 42571.8021 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0865 | 2016 | 7 | 20 | 19 | 15 | 16-0051308 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3013 | 7.5825 | 229_68 | <25mph | <15mph | HFTD - Distribution | LVMC1 | 3.62 | 2016-07-21T02:02:00Z | 18.01 | 1 | VAQC1 | 4.3 | 2016-07-21T01:45:00Z | 20 | 57 | LVMC1 | 3.62 | 2016-07-21T03:02:00Z | 18.99 | 2 | VAQC1 | 4.3 | 2016-07-21T02:45:00Z | 24 | 115
PG&E | 42572.9062 | 42572.9062 | 40.8566 | -122.3387 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101455670 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0870 | 2016 | 7 | 21 | 21 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.2798 | 215_106 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | SLFC1 | 6.48 | 2016-07-22T04:19:00Z | 15.99 | 5 |  |  |  | 0 | 0 | SLFC1 | 6.48 | 2016-07-22T04:19:00Z | 15.99 | 10
PG&E | 42575.6833 | 42575.6833 | 38.0105 | -122.1941 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | CCD | 103049639 |  | 115000 | Conductor | Overhead | Yes | 42575.6833 | 42575.6833 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0876 | 2016 | 7 | 24 | 16 | 24 | PS-2016-013 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 0 | 8.2416 | 256_170 | <25mph | <15mph | HFTD - Transmission | E6179 | 3.92 | 2016-07-24T23:20:00Z | 12.01 | 12 | DPXC1 | 4.78 | 2016-07-24T22:48:00Z | 22.12 | 80 | E6179 | 3.92 | 2016-07-25T00:20:00Z | 14.99 | 24 | DPXC1 | 4.78 | 2016-07-24T22:48:00Z | 22.12 | 156
PG&E | 42576.6472 | 42576.6472 | 38.3522 | -120.7107 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42576.6472 | 42576.6472 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0878 | 2016 | 7 | 25 | 15 | 32 | 16-0052398 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 19951 | 9.9198 | 218_210 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | MTZC1 | 4.1 | 2016-07-25T21:56:00Z | 8.99 | 2 |  |  |  | 0 | 0 | MTZC1 | 4.1 | 2016-07-25T22:56:00Z | 11.01 | 4
PG&E | 42578.4951 | 42578.4951 | 37.8649 | -120.5134 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101041792 |  | 17000 | Conductor | Overhead | Yes | 42578.4951 | 42578.4951 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0880 | 2016 | 7 | 27 | 11 | 53 | 16-0052942 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 14734 | 12.2359 | 221_232 | <25mph | <15mph | HFTD - Distribution | GNSC1 | 2.2 | 2016-07-27T18:03:00Z | 10 | 1 | GNSC1 | 2.2 | 2016-07-27T18:03:00Z | 10 | 8 | GNSC1 | 2.2 | 2016-07-27T19:03:00Z | 10 | 2 | GNSC1 | 2.2 | 2016-07-27T19:03:00Z | 10 | 16
PG&E | 42578.7118 | 42578.7118 | 38.5392 | -122.7656 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102029945 |  | 60000 | Conductor | Overhead | Yes | 42578.7118 | 42578.7118 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0882 | 2016 | 7 | 27 | 17 | 5 | FU-2016-047 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 13.0336 | 148_285 | <25mph | <15mph | HFTD - Transmission | E6724 | 1.55 | 2016-07-27T23:20:00Z | 14 | 19 | E6724 | 1.55 | 2016-07-27T23:20:00Z | 14 | 89 | E6724 | 1.55 | 2016-07-28T00:30:00Z | 14 | 37 | E6724 | 1.55 | 2016-07-28T00:30:00Z | 14 | 166
PG&E | 42579.1118 | 42579.1118 | 35.3674 | -120.3977 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101849904 |  | 21000 | Conductor | Overhead | Yes | 42579.1118 | 42579.1118 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0883 | 2016 | 7 | 28 | 2 | 41 | 16-0053127 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 22592 | 6.9031 | 123_269 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42579.3417 | 42579.3417 | 37.8207 | -120.1388 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101037043 |  | 0 – 750 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 0884 | 2016 | 7 | 28 | 8 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 8.3704 | 227_94 | <25mph | <15mph | HFTD - Distribution | SEWC1 | 2.5 | 2016-07-28T14:16:00Z | 10 | 5 | SEWC1 | 2.5 | 2016-07-28T14:16:00Z | 10 | 5 | SEWC1 | 2.5 | 2016-07-28T14:16:00Z | 10 | 10 | SEWC1 | 2.5 | 2016-07-28T14:16:00Z | 10 | 10
PG&E | 42579.5403 | 42579.5403 | 37.2371 | -119.8157 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103323932 |  | 21000 | Conductor | Overhead | Yes | 42579.5403 | 42579.5403 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 0885 | 2016 | 7 | 28 | 12 | 58 | 16-0053313 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 15215 | 3.6308 | 237_229 | <25mph | <15mph | HFTD - Distribution | E5766 | 0.77 | 2016-07-28T19:25:00Z | 8.01 | 12 | E5766 | 0.77 | 2016-07-28T19:25:00Z | 8.01 | 12 | E5766 | 0.77 | 2016-07-28T19:25:00Z | 8.01 | 12 | E5766 | 0.77 | 2016-07-28T19:25:00Z | 8.01 | 12
PG&E | 42579.5549 | 42579.5549 | 39.7127 | -123.4973 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102195566 |  | 12000 | Conductor | Overhead | Yes | 42579.5549 | 42579.5549 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 0886 | 2016 | 7 | 28 | 13 | 19 | 16-0053369 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 4447 | 3.1103 | 252_197 | <25mph | <15mph | HFTD - Distribution | LAYC1 | 0.97 | 2016-07-28T19:29:00Z | 7 | 1 | LAYC1 | 0.97 | 2016-07-28T19:29:00Z | 7 | 1 | LAYC1 | 0.97 | 2016-07-28T20:29:00Z | 10 | 2 | LAYC1 | 0.97 | 2016-07-28T20:29:00Z | 10 | 2
PG&E | 42579.6 | 42579.6 | 37.8232 | -120.1356 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101037045 |  | 17000 | Other | Overhead | No |  |  | Equipment/ Facility Failure | Guy/Span Wire | N.A. | N.A. | Unknown |  | no-match | 0888 | 2016 | 7 | 28 | 14 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Guy/Span Wire | N.A. | 7.2837 | 169_332 | <25mph | <15mph | HFTD - Distribution | SEWC1 | 2.46 | 2016-07-28T21:16:00Z | 14.99 | 5 | SEWC1 | 2.46 | 2016-07-28T21:16:00Z | 14.99 | 5 | SEWC1 | 2.46 | 2016-07-28T22:16:00Z | 15.99 | 9 | SEWC1 | 2.46 | 2016-07-28T22:16:00Z | 15.99 | 9
PG&E | 42580 | 0.76111 | 38.5769 | -122.6187 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Selma Fire Department |  |  | 12000 | Conductor | Overhead | Yes | 42580 | 0.76111 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0890 | 2016 | 7 | 29 | 18 | 16 | 16-0053726 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 177834 | 3.9949 | 256_170 | <25mph | <15mph | HFTD - Distribution | E2050 | 1.89 | 2016-07-29T06:56:00Z | 0 | 15 | E2362 | 7.38 | 2016-07-29T06:20:00Z | 4 | 26 | E2050 | 1.89 | 2016-07-29T07:56:00Z | 0 | 30 | E2362 | 7.38 | 2016-07-29T06:20:00Z | 4 | 50
PG&E | 42580.0632 | 42580.0632 | 41.0396 | -123.674 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Hoopa FD | 100962351 |  | 12000 | Conductor | Overhead | Yes | 42580.0632 | 42580.0632 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0891 | 2016 | 7 | 29 | 1 | 31 | 16-0053478 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1418 | 11.5031 | 88_408 | <25mph | <15mph | HFTD - Distribution | HOAC1 | 0.58 | 2016-07-29T07:40:00Z | 3 | 1 | HOAC1 | 0.58 | 2016-07-29T07:40:00Z | 3 | 1 | HOAC1 | 0.58 | 2016-07-29T08:40:00Z | 4 | 2 | HOAC1 | 0.58 | 2016-07-29T08:40:00Z | 4 | 2
PG&E | 42582.5076 | 42582.5076 | 38.7827 | -120.9168 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101417359 |  | 21000 | Conductor | Overhead | Yes | 42582.5076 | 42582.5076 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error |  | Other/Unknown | 0895 | 2016 | 7 | 31 | 12 | 11 | 16-0053949 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 10.4973 | 294_85 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PLTC1 | 6.02 | 2016-07-31T18:56:00Z | 12.01 | 43 |  |  |  | 0 | 0 | PLTC1 | 6.02 | 2016-07-31T18:56:00Z | 12.01 | 81
PG&E | 42583 | 42583.5347 | 38.9044 | -121.1274 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100078299 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42583 | 42583.5347 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0896 | 2016 | 8 | 1 | 12 | 50 | 16-0054142 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 855 | 5.0633 | 203_282 | <25mph | <15mph | HFTD - Distribution | D8862 | 3.4 | 2016-08-01T06:23:00Z | 4 | 4 | LICC1 | 7.66 | 2016-08-01T06:13:00Z | 8.99 | 5 | D8862 | 3.4 | 2016-08-01T06:23:00Z | 4 | 8 | LICC1 | 7.66 | 2016-08-01T07:13:00Z | 11.01 | 10
PG&E | 42583 | 42583.7701 | 38.6956 | -120.9283 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101412720 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0898 | 2016 | 8 | 1 | 18 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.7413 | 179_290 | <25mph | <15mph | HFTD - Distribution | D4464 | 2.83 | 2016-08-01T06:05:00Z | 4 | 17 | D4464 | 2.83 | 2016-08-01T06:05:00Z | 4 | 73 | D4464 | 2.83 | 2016-08-01T06:05:00Z | 4 | 31 | BENC1 | 7.25 | 2016-08-01T07:59:00Z | 4.99 | 136
PG&E | 42584 | 42584.6771 | 37.0312 | -119.4395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Fresno County FD | 100675986 |  | 12000 | Conductor | Overhead | Yes | 42584 | 42584.6771 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0900 | 2016 | 8 | 2 | 16 | 15 | 16-0054552 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 265566 | 12.2263 | 144_250 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | MTQC1 | 4.04 | 2016-08-02T06:52:00Z | 4 | 5 |  |  |  | 0 | 0 | MTQC1 | 4.04 | 2016-08-02T07:52:00Z | 4 | 11
PG&E | 42585 | 42585.1931 | 38.8474 | -120.812 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | cal fire garden valley fire | 103809676 |  | 21000 | Conductor | Overhead | Yes | 42585 | 42585.1931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0901 | 2016 | 8 | 3 | 4 | 38 | 16-0054597 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2751 | 5.3291 | 268_186 | <25mph | <15mph | HFTD - Distribution | D5266 | 2.62 | 2016-08-03T06:44:00Z | 3 | 13 | BDMC1 | 6.95 | 2016-08-03T06:36:00Z | 5.99 | 31 | D5266 | 2.62 | 2016-08-03T07:54:00Z | 3 | 22 | BDMC1 | 6.95 | 2016-08-03T07:36:00Z | 7 | 63
PG&E | 42585 | 42585.5285 | 39.3269 | -120.6033 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100001032 |  | 12000 | Conductor | Overhead | Yes | 42585 | 42585.5285 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0902 | 2016 | 8 | 3 | 12 | 41 | 16-0054769 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 20554 | 4.6057 | 208_286 | <25mph | <15mph | HFTD - Distribution | CISCO | 2.6 | 2016-08-03T06:00:00Z | 7.9 | 12 | CISCO | 2.6 | 2016-08-03T06:00:00Z | 7.9 | 16 | CISCO | 2.6 | 2016-08-03T07:30:00Z | 10.11 | 22 | CISCO | 2.6 | 2016-08-03T07:30:00Z | 10.11 | 30
PG&E | 42587 | 42587.5292 | 38.4048 | -120.5292 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101244628 |  | 12000 | Conductor | Overhead | Yes | 42587 | 42587.5292 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0906 | 2016 | 8 | 5 | 12 | 42 | 16-0055368 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 363 | 6.6619 | 145_258 | <25mph | <15mph | HFTD - Distribution | AT450 | 0.53 | 2016-08-05T07:00:00Z | 0 | 13 | MTZC1 | 6.75 | 2016-08-05T06:56:00Z | 8.99 | 24 | AT450 | 0.53 | 2016-08-05T08:00:00Z | 0 | 25 | MTZC1 | 6.75 | 2016-08-05T07:56:00Z | 8.99 | 47
PG&E | 42587 | 42587.6153 | 40.4797 | -123.7803 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103572261 |  | 12000 | Conductor | Overhead | Yes | 42587 | 42587.6153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 0907 | 2016 | 8 | 5 | 14 | 46 | 16-0055425 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 7019 | 6.213 | 220_261 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E8593 | 4.09 | 2016-08-05T07:00:00Z | 5.99 | 13 |  |  |  | 0 | 0 | E8593 | 4.09 | 2016-08-05T07:30:00Z | 7 | 25
PG&E | 42589 | 42589.5972 | 37.2316 | -122.1552 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire/woodside fire | 103413747 |  | 12000 | Conductor | Overhead | Yes | 42589 | 42589.5972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0910 | 2016 | 8 | 7 | 14 | 20 | 16-0055597 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29869 | 9.5487 | 143_255 | <25mph | <15mph | HFTD - Distribution | E6800 | 0.63 | 2016-08-07T06:51:00Z | 4 | 4 | BNDC1 | 7.02 | 2016-08-07T06:50:00Z | 14.99 | 59 | E6800 | 0.63 | 2016-08-07T07:36:00Z | 4 | 8 | BNDC1 | 7.02 | 2016-08-07T07:50:00Z | 14.99 | 116
PG&E | 42590 | 42590.6556 | 37.1382 | -121.9672 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100519919 |  | 0 – 750 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 0912 | 2016 | 8 | 8 | 15 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 7.2774 | 105_337 | <25mph | <15mph | HFTD - Distribution | D9791 | 1.67 | 2016-08-08T07:00:00Z | 0 | 27 | E6085 | 4.45 | 2016-08-08T06:06:00Z | 5.99 | 135 | D8979 | 1.09 | 2016-08-08T07:42:00Z | 1.01 | 55 | E6085 | 4.45 | 2016-08-08T06:06:00Z | 5.99 | 267
PG&E | 42591 | 42591.8063 | 38.9187 | -120.9525 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | El Dorado County FD | 100038028 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0915 | 2016 | 8 | 9 | 19 | 21 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.2662 | 155_203 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | D8862 | 6.76 | 2016-08-09T06:14:00Z | 4.99 | 17 |  |  |  | 0 | 0 | D8862 | 6.76 | 2016-08-09T06:14:00Z | 4.99 | 34
PG&E | 42592 | 42592.3583 | 37.0575 | -121.9556 | Vegetation | RURAL | < 3 meters | Customer | N.A. | 101680487 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0917 | 2016 | 8 | 10 | 8 | 36 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 4.0654 | 157_187 | <25mph | <15mph | HFTD - Distribution | AR172 | 3.97 | 2016-08-10T07:00:00Z | 4.99 | 43 | C8539 | 7.1 | 2016-08-10T06:56:00Z | 4.99 | 172 | AR172 | 3.97 | 2016-08-10T07:15:00Z | 4.99 | 84 | E5038 | 6.34 | 2016-08-10T07:31:00Z | 4.99 | 340
PG&E | 42594 | 42594.4222 | 38.8751 | -122.4223 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 102168360 |  | 12000 | Conductor | Overhead | Yes | 42594 | 42594.4222 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0922 | 2016 | 8 | 12 | 10 | 8 | 16-0056982 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 1368 | 14.6908 | 100_335 | <25mph | <15mph | HFTD - Distribution | KNXC1 | 0.95 | 2016-08-12T06:09:00Z | 3 | 1 | KNXC1 | 0.95 | 2016-08-12T06:09:00Z | 3 | 9 | KNXC1 | 0.95 | 2016-08-12T07:09:00Z | 4 | 2 | KNXC1 | 0.95 | 2016-08-12T07:09:00Z | 4 | 18
PG&E | 42595 | 0.60486 | 37.4642 | -119.8589 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire |  |  | 21000 | Conductor | Overhead | Yes | 42595 | 0.60486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0923 | 2016 | 8 | 13 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.0828 | 138_288 | <25mph | <15mph | HFTD - Distribution | E9110 | 3.11 | 2016-08-13T06:44:00Z | 5.99 | 3 | E9110 | 3.11 | 2016-08-13T06:44:00Z | 5.99 | 7 | E9110 | 3.11 | 2016-08-13T07:59:00Z | 5.99 | 7 | E9110 | 3.11 | 2016-08-13T07:59:00Z | 5.99 | 15
PG&E | 42595 | 42595.5833 | 39.2009 | -121.213 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100011376 | PACIFIC BELL | 0 – 750 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 0924 | 2016 | 8 | 13 | 14 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 6.0967 | 190_305 | <25mph | <15mph | HFTD - Distribution | E2572 | 2.38 | 2016-08-13T06:48:00Z | 1.01 | 11 | E1789 | 5.78 | 2016-08-13T07:00:00Z | 4.99 | 36 | E2572 | 2.38 | 2016-08-13T06:48:00Z | 1.01 | 21 | E1789 | 5.78 | 2016-08-13T07:18:00Z | 7 | 70
PG&E | 42597 | 42597.6549 | 37.8784 | -120.4488 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101020079 |  | 17000 | Conductor | Overhead | Yes | 42597 | 42597.6549 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0928 | 2016 | 8 | 15 | 15 | 43 | 16-0057465 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 122905 | 2.194 | 164_199 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | GNSC1 | 4.26 | 2016-08-15T06:03:00Z | 11.01 | 1 |  |  |  | 0 | 0 | GNSC1 | 4.26 | 2016-08-15T06:03:00Z | 11.01 | 2
PG&E | 42598 | 42598.5542 | 40.3417 | -123.8803 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | miranda/fruitland vol, calfire | 100990019 | None | 12000 | Conductor | Overhead | Yes | 42598 | 42598.5542 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0929 | 2016 | 8 | 16 | 13 | 18 | 16-0057668 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 137 | 3.2949 | 223_232 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42599 | 42599.516 | 41.2495 | -123.7671 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 103315791 |  | 12000 | Conductor | Overhead | Yes | 42599 | 42599.516 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0932 | 2016 | 8 | 17 | 12 | 23 | 16-0058002 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 16544 | 4.1561 | 291_95 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | TS777 | 6.47 | 2016-08-17T06:04:00Z | 3 | 2 |  |  |  | 0 | 0 | NTCC1 | 5.46 | 2016-08-17T07:45:00Z | 4 | 4
PG&E | 42599 | 42599.7757 | 37.3078 | -119.6511 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101020932 |  | 21000 | Conductor | Overhead | Yes | 42599 | 42599.7757 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0934 | 2016 | 8 | 17 | 18 | 37 | 16-0058019 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 59379 | 7.634 | 168_329 | <25mph | <15mph | HFTD - Distribution | D7171 | 3.9 | 2016-08-17T06:09:00Z | 5.99 | 26 | BSNC1 | 5.02 | 2016-08-17T06:48:00Z | 8.01 | 57 | D7171 | 3.9 | 2016-08-17T06:09:00Z | 5.99 | 54 | BSNC1 | 5.02 | 2016-08-17T07:48:00Z | 8.01 | 114
PG&E | 42601 | 42601.6826 | 39.2235 | -123.755 | Vegetation | RURAL | < 3 meters | Fire Agency | Albion-Little River FD | 102206661 |  | 12000 | Conductor | Overhead | Yes | 42601 | 42601.6826 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0938 | 2016 | 8 | 19 | 16 | 23 | 16-0058677 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 95106 | 14.9952 | 175_182 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E6025 | 4.66 | 2016-08-19T07:00:00Z | 0 | 4 |  |  |  | 0 | 0 | E6025 | 4.66 | 2016-08-19T08:00:00Z | 1.01 | 7
PG&E | 42603 | 42603.5431 | 38.4445 | -122.2496 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102291451 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42603 | 42603.5431 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0940 | 2016 | 8 | 21 | 13 | 2 | 16-0058847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 12780 | 7.6482 | 273_155 | <25mph | <15mph | HFTD - Distribution | ATLC1 | 2.26 | 2016-08-21T06:29:00Z | 2.01 | 1 | ATLC1 | 2.26 | 2016-08-21T06:29:00Z | 2.01 | 1 | ATLC1 | 2.26 | 2016-08-21T07:29:00Z | 4 | 2 | ATLC1 | 2.26 | 2016-08-21T07:29:00Z | 4 | 3
PG&E | 42604 | 42604.6736 | 37.9666 | -120.2395 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Toulumne City FD | 101043683 |  | 17000 | Conductor | Overhead | Yes | 42604 | 42604.6736 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0941 | 2016 | 8 | 22 | 16 | 10 | 16-0059149 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 78534 | 8.4511 | 145_264 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | MOUC1 | 6.67 | 2016-08-22T06:02:00Z | 13 | 5 |  |  |  | 0 | 0 | MOUC1 | 6.67 | 2016-08-22T07:02:00Z | 14 | 10
PG&E | 42606 | 42606.5076 | 36.4633 | -121.712 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101750810 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42606 | 42606.5076 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 0943 | 2016 | 8 | 24 | 12 | 11 | 16-0059702 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 232770 | 3.6968 | 257_177 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42607 | 42607.5028 | 36.9726 | -119.3816 | Vegetation | RURAL | < 3 meters | Utility: PG&E | N.A. | 100651318 | PONDEROSA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 0945 | 2016 | 8 | 25 | 12 | 4 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.0098 | 249_176 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | MTQC1 | 5.65 | 2016-08-25T06:52:00Z | 4.99 | 6 |  |  |  | 0 | 0 | TRMC1 | 5.94 | 2016-08-25T07:52:00Z | 4.99 | 13
PG&E | 42612 | 42612.6674 | 36.5941 | -121.9212 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Unknown | 101734977 |  | 21000 | Conductor | Overhead | Yes | 42612 | 42612.6674 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0951 | 2016 | 8 | 30 | 16 | 1 | 16-0061130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 199327 | 17.3768 | 173_254 | <25mph | >=15mph | HFTD - Distribution | E8505 | 2.6 | 2016-08-30T06:15:00Z | 20 | 48 | E8505 | 2.6 | 2016-08-30T06:15:00Z | 20 | 52 | E8505 | 2.6 | 2016-08-30T06:15:00Z | 20 | 91 | E8505 | 2.6 | 2016-08-30T06:15:00Z | 20 | 99
PG&E | 42613 | 42613.6194 | 35.1918 | -120.4697 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101942860 |  | 12000 | Conductor | Overhead | Yes | 42613 | 42613.6194 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 0955 | 2016 | 8 | 31 | 14 | 52 | 16-0061423 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 156294 | 10.6323 | 224_204 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | C9687 | 6.31 | 2016-08-31T06:30:00Z | 4.99 | 13 |  |  |  | 0 | 0 | C9687 | 6.31 | 2016-08-31T06:30:00Z | 4.99 | 23
PG&E | 42625 | 0.18333 | 36.3999 | -121.902 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire Hwy 1 Carmel Hill | 101669614 |  | 12000 | Conductor | Overhead | Yes | 42625 | 0.18333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 0973 | 2016 | 9 | 12 | 4 | 24 | 16-0063826 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 130604 | 14.7849 | 256_182 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | TR419 | 7.81 | 2016-09-12T06:15:00Z | 14 | 1 |  |  |  | 0 | 0 | TR419 | 7.81 | 2016-09-12T07:15:00Z | 15.99 | 2
PG&E | 42625 | 0.52639 | 38.7832 | -120.6006 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101421708 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42625 | 0.52639 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 0974 | 2016 | 9 | 12 | 12 | 38 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 4.7203 | 159_151 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E3165 | 7.91 | 2016-09-12T06:37:00Z | 4 | 6 |  |  |  | 0 | 0 | E3165 | 7.91 | 2016-09-12T06:37:00Z | 4 | 12
PG&E | 42625.6306 | 42625.6306 | 39.5256 | -123.7655 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102185070 |  | 12000 | Conductor | Overhead | Yes | 42625.6306 | 42625.6306 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 0977 | 2016 | 9 | 12 | 15 | 8 | 16-0064050 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 428 | 5.2324 | 275_159 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42626.4479 | 42626.4479 | 40.2958 | -122.1318 | Vegetation | RURAL | 300 - 999 Acres | Fire Agency | Cal Fire | 103702175 |  | 60000 | Conductor | Overhead | Yes | 42626.4479 | 42626.4479 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0979 | 2016 | 9 | 13 | 10 | 45 | INT-08528 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Animal | Animal | 0 | 9.6854 | 152_366 | <25mph | <15mph | HFTD - Transmission |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42628 | 0.66389 | 37.1102 | -121.9509 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100520198 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42628 | 0.66389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 0982 | 2016 | 9 | 15 | 15 | 56 | 16-0065001 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 28900 | 4.7461 | 163_321 | <25mph | <15mph | HFTD - Distribution | D8979 | 1.17 | 2016-09-15T06:16:00Z | 7 | 56 | D8979 | 1.17 | 2016-09-15T06:16:00Z | 7 | 108 | D8979 | 1.17 | 2016-09-15T07:18:00Z | 8.01 | 107 | E9039 | 4.03 | 2016-09-15T07:56:00Z | 8.99 | 204
PG&E | 42629.8722 | 42629.8722 | 39.8387 | -121.7023 | Vegetation | RURAL | 10 - 99 Acres | Fire Agency | Cal Fire | 100441760 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42629.8722 | 42629.8722 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 0983 | 2016 | 9 | 16 | 20 | 56 | 16-0065273 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 314427 | 7.2098 | 158_190 | <25mph | <15mph | HFTD - Distribution | C8878 | 3.59 | 2016-09-17T03:53:00Z | 0 | 12 | CSTC1 | 4.21 | 2016-09-17T03:51:00Z | 7 | 14 | C8878 | 3.59 | 2016-09-17T03:53:00Z | 0 | 12 | CSTC1 | 4.21 | 2016-09-17T04:51:00Z | 7 | 16
PG&E | 42631 | 0.60625 | 37.1619 | -122.1347 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire & Boulder Creek Fire Dept. | 103410909 | Yes | 12000 | Conductor | Overhead | Yes | 42631 | 0.60625 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 0986 | 2016 | 9 | 18 | 14 | 33 | 16-0065437 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 54983 | 2.5115 | 238_190 | <25mph | <15mph | HFTD - Distribution | BNDC1 | 2.99 | 2016-09-18T06:50:00Z | 7 | 23 | BNDC1 | 2.99 | 2016-09-18T06:50:00Z | 7 | 49 | BNDC1 | 2.99 | 2016-09-18T06:50:00Z | 7 | 43 | BNDC1 | 2.99 | 2016-09-18T06:50:00Z | 7 | 94
PG&E | 42633 | 0.35069 | 40.0044 | -123.7871 | Vegetation | RURAL | < 3 meters | Self Extinguished | N.A. | 100992643 | VERIZON CALIFORNIA I | 12000 | Conductor | Overhead | Yes | 42633 | 0.35069 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 0990 | 2016 | 9 | 20 | 8 | 25 | 16-0065910 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 798 | 5.007 | 188_237 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | AV037 | 4.73 | 2016-09-20T06:23:00Z | 4 | 3 |  |  |  | 0 | 0 | AV037 | 4.73 | 2016-09-20T07:03:00Z | 4 | 7
PG&E | 42634 | 0.41736 | 39.1173 | -121.071 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100014315 | PACIFIC BELL | 115000 | Conductor | Overhead | Yes | 42634 | 0.41736 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 0991 | 2016 | 9 | 21 | 10 | 1 | INT-08560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 7.6506 | 82_351 | <25mph | <15mph | HFTD - Transmission | E1789 | 3.84 | 2016-09-21T06:54:00Z | 13 | 29 | E1789 | 3.84 | 2016-09-21T06:54:00Z | 13 | 87 | E1789 | 3.84 | 2016-09-21T06:54:00Z | 13 | 57 | E1789 | 3.84 | 2016-09-21T06:54:00Z | 13 | 165
PG&E | 42635 | 0.57847 | 40.224 | -122.3417 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101539450 | None | 12000 | Conductor | Overhead | Yes | 42635 | 0.57847 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 0996 | 2016 | 9 | 22 | 13 | 53 | 16-0066692 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 14706 | 13.7018 | 196_291 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E7114 | 6.08 | 2016-09-22T06:24:00Z | 14 | 4 |  |  |  | 0 | 0 | E7114 | 6.08 | 2016-09-22T07:54:00Z | 18.01 | 8
PG&E | 42636.2243 | 0.64097 | 39.3784 | -121.0922 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 100091491 | None | 12000 | Conductor | Overhead | Yes | 42636.2243 | 0.64097 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 0999 | 2016 | 9 | 23 | 15 | 23 | 16-0067089 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 80185 | 4.2958 | 195_315 | <25mph | <15mph | HFTD - Distribution | E3651 | 3.67 | 2016-09-23T12:20:00Z | 0 | 12 | RRRC1 | 5.34 | 2016-09-23T12:13:00Z | 8.01 | 13 | E3651 | 3.67 | 2016-09-23T13:20:00Z | 0 | 24 | RRRC1 | 5.34 | 2016-09-23T12:13:00Z | 8.01 | 26
PG&E | 42638 | 0.80486 | 37.0993 | -122.1155 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire ben lomond fire | 101670837 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42638 | 0.80486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1003 | 2016 | 9 | 25 | 19 | 19 | 16-0067346 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1497 | 19.163 | 160_313 | <25mph | >=15mph | HFTD - Distribution | BNDC1 | 3.83 | 2016-09-25T06:50:00Z | 8.99 | 28 | BNDC1 | 3.83 | 2016-09-25T06:50:00Z | 8.99 | 47 | BNDC1 | 3.83 | 2016-09-25T07:50:00Z | 10 | 55 | BNDC1 | 3.83 | 2016-09-25T07:50:00Z | 10 | 96
PG&E | 42638.441 | 42638.441 | 38.8019 | -122.8176 | Vegetation | RURAL | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103613996 |  | 115000 | Other | Overhead | Yes | 42638.441 | 42638.441 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1004 | 2016 | 9 | 25 | 10 | 35 | INT-08572 | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Equip Failure - Other | 0 | 6.4295 | 256_169 | <25mph | <15mph | HFTD - Transmission |  |  |  | 0 | 0 | HWKC1 | 4.73 | 2016-09-25T16:56:00Z | 35.99 | 2 |  |  |  | 0 | 0 | HWKC1 | 4.73 | 2016-09-25T17:56:00Z | 35.99 | 4
PG&E | 42639 | 0.44444 | 38.0157 | -122.6889 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | marin county fire | 102252082 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42639 | 0.44444 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1005 | 2016 | 9 | 26 | 10 | 40 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 8.4538 | 150_190 | <25mph | <15mph | HFTD - Distribution | WDAC1 | 2.97 | 2016-09-26T06:51:00Z | 12.01 | 2 | WDAC1 | 2.97 | 2016-09-26T06:51:00Z | 12.01 | 27 | WDAC1 | 2.97 | 2016-09-26T06:51:00Z | 12.01 | 4 | WDAC1 | 2.97 | 2016-09-26T06:51:00Z | 12.01 | 56
PG&E | 42641 | 0.58333 | 35.2145 | -118.5625 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire |  |  | 0 – 750 | Conductor | Overhead | Yes | 42641 | 0.58333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1008 | 2016 | 9 | 28 | 14 | 0 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 14.543 | 186_244 | <25mph | <15mph | HFTD - Distribution | HFLC1 | 3.31 | 2016-09-28T06:13:00Z | 15.99 | 7 | HFLC1 | 3.31 | 2016-09-28T06:13:00Z | 15.99 | 28 | HFLC1 | 3.31 | 2016-09-28T06:13:00Z | 15.99 | 15 | HFLC1 | 3.31 | 2016-09-28T06:13:00Z | 15.99 | 58
PG&E | 42644.6455 | 0.63819 | 39.4384 | -120.816 | Vegetation | RURAL | .26 - 9.99 Acres | Fire Agency | State goverment forestry | 100112411 |  | 12000 | Conductor | Overhead | Yes | 42644.6455 | 0.63819 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1011 | 2016 | 10 | 1 | 15 | 19 | 16-0068934 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 6157 | 10.5833 | 171_240 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42645.6954 | 0.69514 | 39.8888 | -121.6648 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 103358082 |  | 12000 | Other | Overhead | Yes | 42645.6954 | 0.69514 | Other | N.A. | N.A. | N.A. | Weather | lightning strike | Other/Unknown | 1013 | 2016 | 10 | 2 | 16 | 41 | 16-0069050 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 339550 | 21.9592 | 150_251 | <25mph | >=15mph | HFTD - Distribution | C8878 | 1.4 | 2016-10-02T23:28:00Z | 1.01 | 12 | CSTC1 | 5.65 | 2016-10-02T22:51:00Z | 18.01 | 19 | C8878 | 1.4 | 2016-10-03T00:38:00Z | 14 | 24 | CSTC1 | 5.65 | 2016-10-02T23:51:00Z | 28.01 | 42
PG&E | 42651.6284 | 0.62778 | 38.6686 | -120.9091 | Vegetation | RURAL | < 0.25 Acres | Customer | N.A. | 101380856 |  | 0 – 750 | Capacitor Bank | Overhead | Yes | 42651.6284 | 0.62778 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1021 | 2016 | 10 | 8 | 15 | 4 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 4.4845 | 168_326 | <25mph | <15mph | HFTD - Distribution | C6129 | 3.74 | 2016-10-08T21:09:00Z | 12.01 | 18 | C6129 | 3.74 | 2016-10-08T21:09:00Z | 12.01 | 64 | C6129 | 3.74 | 2016-10-08T21:09:00Z | 12.01 | 36 | C6129 | 3.74 | 2016-10-08T21:09:00Z | 12.01 | 126
PG&E | 42651.6884 | 0.68819 | 39.0099 | -122.6145 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102152342 |  | 0 – 750 | Transformer | Overhead | Yes | 42651.6884 | 0.68819 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1022 | 2016 | 10 | 8 | 16 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 9.8555 | 203_276 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42652.7862 | 0.78611 | 38.656 | -120.9725 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101376768 |  | 12000 | Conductor | Overhead | Yes | 42652.7862 | 0.78611 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1024 | 2016 | 10 | 9 | 18 | 52 | 16-0070676 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 98361 | 10.5578 | 223_213 | <25mph | <15mph | HFTD - Distribution | D7401 | 2.79 | 2016-10-10T01:03:00Z | 1.01 | 8 | BENC1 | 4.97 | 2016-10-10T00:59:00Z | 8.01 | 63 | D7401 | 2.79 | 2016-10-10T02:03:00Z | 1.01 | 16 | BENC1 | 4.97 | 2016-10-10T00:59:00Z | 8.01 | 126
PG&E | 42654.9701 | 0.96944 | 39.0201 | -120.8294 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | cal fire.foresthill fire | 100025501 |  | 60000 | Conductor | Overhead | Yes | 42654.9701 | 0.96944 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error |  | no-match | 1028 | 2016 | 10 | 11 | 23 | 16 | INT-08640 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 0 | 8.4037 | 252_173 | <25mph | <15mph | HFTD - Transmission | AU268 | 0.89 | 2016-10-12T06:04:00Z | 2.01 | 6 | FSHC1 | 7.19 | 2016-10-12T05:33:00Z | 3 | 7 | AU268 | 0.89 | 2016-10-12T06:49:00Z | 2.01 | 9 | FSHC1 | 7.19 | 2016-10-12T06:33:00Z | 3 | 11
PG&E | 42656.9745 | 0.96806 | 40.4901 | -122.3729 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | SHASTA COUNTY FIRE | 101502366 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 42656.9745 | 0.96806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1029 | 2016 | 10 | 13 | 23 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.7485 | 207_295 | <25mph | <15mph | HFTD - Distribution | E6886 | 3.41 | 2016-10-14T05:33:00Z | 41 | 4 | KRDD | 4.3 | 2016-10-14T05:55:00Z | 50.64 | 17 | E6886 | 3.41 | 2016-10-14T06:48:00Z | 47 | 8 | KRDD | 4.3 | 2016-10-14T06:53:00Z | 56.39 | 39
PG&E | 42657.0644 | 0.063889 | 40.5007 | -121.9162 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101489328 |  | 12000 | Conductor | Overhead | Yes | 42657.0644 | 0.063889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1031 | 2016 | 10 | 14 | 1 | 32 | 16-0071832 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 213622 | 25.3168 | 148_336 | 25-40mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42657.1893 | 0.18889 | 40.5228 | -121.6813 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101513661 |  | 12000 | Conductor | Overhead | Yes | 42657.1893 | 0.18889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1032 | 2016 | 10 | 14 | 4 | 32 | 16-0071897 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 38950 | 32.5033 | 161_377 | 25-40mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | VIOC1 | 5.45 | 2016-10-14T10:52:00Z | 31 | 1 |  |  |  | 0 | 0 | VIOC1 | 5.45 | 2016-10-14T10:52:00Z | 31 | 2
PG&E | 42657.8228 | 0.82222 | 39.6245 | -121.5382 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 100435570 |  | 0 – 750 | Conductor | Overhead | Yes | 42657.8228 | 0.82222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1036 | 2016 | 10 | 14 | 19 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 19.7872 | 174_288 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | CICC1 | 5.69 | 2016-10-15T01:54:00Z | 18.99 | 1 |  |  |  | 0 | 0 | CICC1 | 5.69 | 2016-10-15T01:54:00Z | 18.99 | 2
PG&E | 42662.4459 | 0.44583 | 38.5098 | -122.45 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | st helena | 102242552 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42662.4459 | 0.44583 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1040 | 2016 | 10 | 19 | 10 | 42 | 16-0073955 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 693 | 0.79097 | 128_266 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | AT925 | 4.5 | 2016-10-19T17:15:00Z | 8.01 | 12 |  |  |  | 0 | 0 | AT925 | 4.5 | 2016-10-19T18:40:00Z | 10 | 24
PG&E | 42666.7804 | 0.75694 | 38.021 | -120.5991 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 101272943 |  | 115000 | Conductor | Overhead | Yes | 42666.7804 | 0.75694 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1043 | 2016 | 10 | 23 | 18 | 10 | INT-08709 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 0 | 4.06 | 197_252 | <25mph | <15mph | HFTD - Transmission |  |  |  | 0 | 0 | E2861 | 6.79 | 2016-10-24T01:26:00Z | 3 | 10 |  |  |  | 0 | 0 | E2861 | 6.79 | 2016-10-24T02:29:00Z | 3 | 20
PG&E | 42683 | 0.37917 | 37.4532 | -119.6413 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | US FOREST SERVICE | 101017062 |  | 12000 | Conductor | Overhead | Yes | 42683 | 0.37917 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1046 | 2016 | 11 | 9 | 9 | 6 | 16-0078863 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1586 | 10.2493 | 255_166 | <25mph | <15mph | HFTD - Distribution | TR172 | 1.09 | 2016-11-09T07:45:00Z | 8.99 | 5 | TR172 | 1.09 | 2016-11-09T07:45:00Z | 8.99 | 25 | TR172 | 1.09 | 2016-11-09T08:45:00Z | 12.01 | 8 | TR172 | 1.09 | 2016-11-09T08:45:00Z | 12.01 | 47
PG&E | 42688 | 0.55208 | 35.4577 | -120.4619 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | Cal Fire | 101895511 |  | 21000 | Conductor | Overhead | Yes | 42688 | 0.55208 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1048 | 2016 | 11 | 14 | 13 | 15 | 16-0079725 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 19590 | 3.8625 | 205_98 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42689 | 0.72708 | 39.7275 | -121.6557 | Vegetation | RURAL | < 0.25 Acres | Fire Agency | CAL FIRE/BUTTE COUNTY FIRE DEPT. | 100327525 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42689 | 0.72708 | Contact From Object | N.A. | Vehicle | Pole | Human Error |  | Other/Unknown | 1049 | 2016 | 11 | 15 | 17 | 27 | 16-0080083 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 69231 | 19.4119 | 224_99 | <25mph | >=15mph | HFTD - Distribution | PDEC1 | 2.44 | 2016-11-15T08:00:00Z | 2.01 | 2 | PDEC1 | 2.44 | 2016-11-15T08:00:00Z | 2.01 | 2 | PDEC1 | 2.44 | 2016-11-15T09:00:00Z | 2.01 | 3 | PDEC1 | 2.44 | 2016-11-15T09:00:00Z | 2.01 | 3
PG&E | 42694 | 0.46111 | 39.6326 | -123.7823 | Vegetation | RURAL | < 3 meters | Fire Agency | Cal Fire | 102200173 |  | 12000 | Conductor | Overhead | Yes | 42694 | 0.46111 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1050 | 2016 | 11 | 20 | 11 | 4 | 16-0081252 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 87261 | 14.3443 | 172_334 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42829.567 | 0.56181 | 35.6885 | -120.7653 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101945026 | None | 12000 | Conductor | Overhead | Yes | 42829.567 | 0.56181 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1064 | 2017 | 4 | 4 | 13 | 29 | 17-0036460 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 167151 | 2.8226 | 201_194 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | D4060 | 7.1 | 2017-04-04T20:22:00Z | 5.99 | 3 |  |  |  | 0 | 0 | D4060 | 7.1 | 2017-04-04T20:22:00Z | 5.99 | 3
PG&E | 42850.5271 | 0.52639 | 38.6583 | -120.9762 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101376746 | Unknown | 0 – 750 | Transformer | Overhead | Yes | 42850.5271 | 0.52639 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1072 | 2017 | 4 | 25 | 12 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 15.4643 | 193_139 | <25mph | >=15mph | HFTD - Distribution | D7401 | 2.53 | 2017-04-25T18:45:00Z | 10 | 3 | C6129 | 7.33 | 2017-04-25T19:24:00Z | 20 | 56 | D7401 | 2.53 | 2017-04-25T18:45:00Z | 10 | 5 | C6129 | 7.33 | 2017-04-25T19:24:00Z | 20 | 102
PG&E | 42853.6815 | 0.65903 | 38.7679 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chris paper fire investigator, 530/677-1868. incident #caaeuo11821 | 101409833 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42853.6815 | 0.65903 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1077 | 2017 | 4 | 28 | 15 | 49 | 17-0043771 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 82614 | 13.1464 | 172_191 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | D7401 | 6.46 | 2017-04-28T22:51:00Z | 25.99 | 53 |  |  |  | 0 | 0 | D7401 | 6.46 | 2017-04-28T22:51:00Z | 25.99 | 104
PG&E | 42854.6453 | 0.62986 | 37.0349 | -119.5242 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100678661 | Unknown | 12000 | Conductor | Overhead | Yes | 42854.6453 | 0.62986 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1078 | 2017 | 4 | 29 | 15 | 7 | 17-0043911 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 4.7079 | 201_281 | <25mph | <15mph | HFTD - Distribution | PRHC1 | 2.76 | 2017-04-29T22:27:00Z | 10 | 1 | PRHC1 | 2.76 | 2017-04-29T22:27:00Z | 10 | 1 | PRHC1 | 2.76 | 2017-04-29T23:27:00Z | 13 | 2 | PRHC1 | 2.76 | 2017-04-29T23:27:00Z | 13 | 2
PG&E | 42855.3995 | 0.39722 | 35.6349 | -118.9563 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 661-324-6551 | 100216308 | Unknown | 21000 | Conductor | Overhead | Yes | 42855.3995 | 0.39722 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1079 | 2017 | 4 | 30 | 9 | 32 | 17-0043980 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 3065 | 11.9815 | 265_186 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42860.6614 | 15:52 | 40.3776 | -123.0019 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101501566 | None | 12000 | Conductor | Overhead | Yes | 42860.6614 | 15:52 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1084 | 2017 | 5 | 5 | 15 | 52 | 17-0045707 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 56893 | 8.6675 | 211_104 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | YOBC1 | 4.35 | 2017-05-05T22:35:00Z | 5.99 | 1 |  |  |  | 0 | 0 | YOBC1 | 4.35 | 2017-05-05T23:35:00Z | 7 | 2
PG&E | 42861.4744 | 0.47083 | 40.7951 | -124.029 | Vegetation | Rural | < 3 Meters | Fire Agency | chief rick harden 7074423352 | 103661154 | Unknown | 12000 | Conductor | Overhead | Yes | 42861.4744 | 0.47083 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1086 | 2017 | 5 | 6 | 11 | 18 | 17-0045785 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 113630 | 18.8851 | 207_202 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | D8223 | 6.16 | 2017-05-06T17:35:00Z | 27 | 35 |  |  |  | 0 | 0 | D8223 | 6.16 | 2017-05-06T19:10:00Z | 30 | 76
PG&E | 42864.7782 | 0.76806 | 40.8689 | -123.5156 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | todd wright fire chief. 5307392493 | 103796045 | Unknown | 12000 | Conductor | Overhead | Yes | 42864.7782 | 0.76806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1092 | 2017 | 5 | 9 | 18 | 26 | 17-0046642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 108117 | 13.9105 | 163_324 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | LYEC1 | 5.31 | 2017-05-10T00:46:00Z | 10 | 1 |  |  |  | 0 | 0 | LYEC1 | 5.31 | 2017-05-10T00:46:00Z | 10 | 2
PG&E | 42869 | 0.49931 | 38.0798 | -122.8665 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102247059 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42869 | 0.49931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1095 | 2017 | 5 | 14 | 11 | 59 | 17-0047802 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 377483 | 10.9708 | 166_332 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PTRCA | 4.65 | 2017-05-14T06:30:00Z | 27.2 | 12 |  |  |  | 0 | 0 | PTRCA | 4.65 | 2017-05-14T06:30:00Z | 27.2 | 18
PG&E | 42870 | 0.12847 | 35.6261 | -120.8962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101873299 | Unknown | 21000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1097 | 2017 | 5 | 15 | 3 | 5 | 17-0047837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 337188 | 3.2091 | 260_107 | <25mph | <15mph | HFTD - Distribution | TABC1 | 2.62 | 2017-05-15T06:07:00Z | 3 | 1 | TABC1 | 2.62 | 2017-05-15T06:07:00Z | 3 | 1 | TABC1 | 2.62 | 2017-05-15T07:07:00Z | 3 | 2 | TABC1 | 2.62 | 2017-05-15T07:07:00Z | 3 | 2
PG&E | 42870.6767 | 0.66667 | 37.1766 | -119.8189 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SHAUN FAIRBANKS 559-683-4823 | 101108423 | SIERRA | 21000 | Conductor | Overhead | Yes | 42870.6767 | 0.66667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1099 | 2017 | 5 | 15 | 16 | 0 | 17-0048096 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20007 | 7.5963 | 182_250 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E5766 | 4.44 | 2017-05-15T22:22:00Z | 5.99 | 11 |  |  |  | 0 | 0 | E5766 | 4.44 | 2017-05-15T22:22:00Z | 5.99 | 23
PG&E | 42879.6837 | 16:24 | 38.834 | -121.1197 | Vegetation | Rural | < 3 Meters | Fire Agency | Fire Capt | 103838109 | None | 12000 | Conductor | Overhead | Yes | 42879.6837 | 16:24 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | no-match | 1111 | 2017 | 5 | 24 | 16 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 12.3303 | 181_225 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PLTC1 | 5.95 | 2017-05-24T22:56:00Z | 15.99 | 21 |  |  |  | 0 | 0 | PLTC1 | 5.95 | 2017-05-24T23:56:00Z | 15.99 | 40
PG&E | 42880.6288 | 0.62847 | 36.5217 | -121.8473 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Buddy Bloxham 831-236-5659 | 101778611 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42880.6288 | 0.62847 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1113 | 2017 | 5 | 25 | 15 | 5 | 17-0050761 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 13965 | 8.0348 | 161_209 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E8505 | 7.82 | 2017-05-25T21:07:00Z | 31 | 34 |  |  |  | 0 | 0 | KMRY | 4.75 | 2017-05-25T22:54:00Z | 32.21 | 77
PG&E | 42880.7334 | 0.70486 | 38.3986 | -122.9876 | Vegetation | Rural | < 3 Meters | Utility: PG&E | N.A. | 101974034 | Unknown | 12000 | Conductor | Overhead | Yes | 42880.7334 | 0.70486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, > 12ft) | 1114 | 2017 | 5 | 25 | 16 | 55 | 17-0050815 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 2644 | 5.2896 | 162_158 | <25mph | <15mph | HFTD - Distribution | D2849 | 1.17 | 2017-05-26T00:17:00Z | 10 | 12 | DUTWW | 7.06 | 2017-05-26T00:00:00Z | 17.81 | 55 | D2849 | 1.17 | 2017-05-26T00:17:00Z | 10 | 23 | DUTWW | 7.06 | 2017-05-26T01:00:00Z | 17.81 | 109
PG&E | 42884.7708 | 18:29 | 39.2245 | -121.3753 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101304842 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1115 | 2017 | 5 | 29 | 18 | 29 | 17-0051324 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 616 | 9.0109 | 114_262 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42889.5662 | 0.55972 | 38.9017 | -121.2056 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100043664 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42889.5662 | 0.55972 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1122 | 2017 | 6 | 3 | 13 | 26 | 17-0052543 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29512 | 18.651 | 172_165 | <25mph | >=15mph | HFTD - Distribution | LICC1 | 3.58 | 2017-06-03T20:13:00Z | 8.99 | 1 | LICC1 | 3.58 | 2017-06-03T20:13:00Z | 8.99 | 19 | LICC1 | 3.58 | 2017-06-03T20:13:00Z | 8.99 | 2 | AR944 | 7.74 | 2017-06-03T20:45:00Z | 8.99 | 36
PG&E | 42894.6382 | 0.63056 | 34.6058 | -120.0214 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SHAWN STEINER | 101947678 | Unknown | 12000 | Conductor | Overhead | Yes | 42894.6382 | 0.63056 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1136 | 2017 | 6 | 8 | 15 | 8 | 17-0053783 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 41311 | 13.9971 | 231_142 | <25mph | <15mph | HFTD - Distribution | KIZA | 3.08 | 2017-06-08T21:55:00Z | 19.57 | 2 | SXWC1 | 5.38 | 2017-06-08T22:09:00Z | 23 | 18 | KIZA | 3.08 | 2017-06-08T23:15:00Z | 20.71 | 5 | SXWC1 | 5.38 | 2017-06-08T23:09:00Z | 24 | 39
PG&E | 42896.3177 | 07:37 | 35.4359 | -120.4957 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101890429 | Unknown | 21000 | Conductor | Overhead | Yes | 42896.3177 | 07:37 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1140 | 2017 | 6 | 10 | 7 | 37 | 17-0054182 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 34397 | 6.9076 | 220_118 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E2260 | 7.67 | 2017-06-10T14:14:00Z | 4 | 5 |  |  |  | 0 | 0 | E2260 | 7.67 | 2017-06-10T15:26:00Z | 12.01 | 10
PG&E | 42899 | 0.60417 | 37.8526 | -122.1853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Tower 005/035c | Unknown | 115000 | Conductor | Overhead | Yes | 42899 | 0.60417 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1143 | 2017 | 6 | 13 | 14 | 30 | INT-09744 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | Balloons | 0 | 10.8472 | 298_95 | <25mph | <15mph | HFTD - Transmission | LBNL1 | 3.84 | 2017-06-13T07:00:00Z | 14.05 | 45 | LBNL1 | 3.84 | 2017-06-13T07:00:00Z | 14.05 | 123 | LBNL1 | 3.84 | 2017-06-13T07:00:00Z | 14.05 | 93 | LTRC1 | 6.59 | 2017-06-13T07:28:00Z | 17 | 258
PG&E | 42901.1885 | 0.12361 | 40.299 | -122.4318 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101511631 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42901.1885 | 0.12361 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | Other/Unknown | 1145 | 2017 | 6 | 15 | 2 | 58 | 17-0055359 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 1762 | 8.3679 | 174_336 | <25mph | <15mph | HFTD - Distribution | E7114 | 1.68 | 2017-06-15T10:47:00Z | 3 | 4 | E7114 | 1.68 | 2017-06-15T10:47:00Z | 3 | 4 | E7114 | 1.68 | 2017-06-15T10:47:00Z | 3 | 7 | E7114 | 1.68 | 2017-06-15T10:47:00Z | 3 | 7
PG&E | 42901.3391 | 0.31875 | 39.2276 | -121.2348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE CHIEF | 103676075 | Unknown | 21000 | Conductor | Overhead | Yes | 42901.3391 | 0.31875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1147 | 2017 | 6 | 15 | 7 | 39 | 17-0055387 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 740 | 14.5193 | 170_174 | <25mph | <15mph | HFTD - Distribution | E2572 | 2.6 | 2017-06-15T15:03:00Z | 1.01 | 11 | E1789 | 7.9 | 2017-06-15T15:06:00Z | 4 | 25 | E2572 | 2.6 | 2017-06-15T16:03:00Z | 2.01 | 21 | E1789 | 7.9 | 2017-06-15T16:00:00Z | 5.99 | 48
PG&E | 42901.6279 | 0.62569 | 39.3913 | -123.3054 | Vegetation | Rural | < 0.25 Acres | Fire Agency | STEPHEN | 103838176 | YES | 12000 | Conductor | Overhead | Yes | 42901.6279 | 0.62569 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1148 | 2017 | 6 | 15 | 15 | 1 | 17-0055557 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 180469 | 8.5012 | 189_307 | <25mph | <15mph | HFTD - Distribution | E4027 | 2.73 | 2017-06-15T21:48:00Z | 17 | 22 | AU552 | 4.26 | 2017-06-15T22:04:00Z | 20 | 36 | E4027 | 2.73 | 2017-06-15T23:03:00Z | 17 | 39 | AU552 | 4.26 | 2017-06-15T23:01:00Z | 20 | 65
PG&E | 42902.8019 | 19:14 | 38.3443 | -122.7812 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101970801 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42902.8019 | 19:14 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1155 | 2017 | 6 | 16 | 19 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 8.1691 | 154_201 | <25mph | <15mph | HFTD - Distribution | AR323 | 3.41 | 2017-06-17T01:49:00Z | 15.99 | 12 | BTOWW | 5.5 | 2017-06-17T01:45:00Z | 22.1 | 44 | AR323 | 3.41 | 2017-06-17T01:49:00Z | 15.99 | 24 | BTOWW | 5.5 | 2017-06-17T01:45:00Z | 22.1 | 92
PG&E | 42902.9378 | 22:30 | 38.0373 | -122.1847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101424286 | Unknown | 21000 | Conductor | Overhead | Yes | 42902.9378 | 22:30 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1156 | 2017 | 6 | 16 | 22 | 30 | 17-0055882 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 12000 | 12.3152 | 122_259 | <25mph | <15mph | HFTD - Distribution | UPBC1 | 3.49 | 2017-06-17T05:00:00Z | 32.97 | 21 | UPBC1 | 3.49 | 2017-06-17T05:00:00Z | 32.97 | 63 | UPBC1 | 3.49 | 2017-06-17T05:00:00Z | 32.97 | 41 | UPBC1 | 3.49 | 2017-06-17T05:00:00Z | 32.97 | 122
PG&E | 42906.638 | 0.49375 | 40.3156 | -124.0611 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101006039 | Unknown | 12000 | Conductor | Overhead | Yes | 42906.638 | 0.49375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1180 | 2017 | 6 | 20 | 11 | 51 | 17-0057001 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 9256 | 19.7543 | 152_235 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42908.4214 | 0.4 | 38.3965 | -120.4727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101251777 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.4214 | 0.4 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1186 | 2017 | 6 | 22 | 9 | 36 | 17-0057686 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 22732 | 2.7323 | 184_294 | <25mph | <15mph | HFTD - Distribution | AT450 | 2.61 | 2017-06-22T17:04:00Z | 4 | 16 | ULBC1 | 6.95 | 2017-06-22T16:33:00Z | 8.99 | 34 | AT450 | 2.61 | 2017-06-22T18:04:00Z | 5.99 | 27 | ULBC1 | 6.95 | 2017-06-22T16:33:00Z | 8.99 | 59
PG&E | 42908.7461 | 0.75486 | 38.7583 | -120.7176 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101401088 | Unknown | 12000 | Conductor | Overhead | Yes | 42908.7461 | 0.75486 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1188 | 2017 | 6 | 22 | 18 | 7 | 17-0057857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 8517 | 17.5701 | 170_328 | <25mph | >=15mph | HFTD - Distribution | E5691 | 3.88 | 2017-06-23T00:37:00Z | 7 | 22 | E6490 | 7.72 | 2017-06-23T00:14:00Z | 7 | 35 | E5691 | 3.88 | 2017-06-23T00:37:00Z | 7 | 42 | E6490 | 7.72 | 2017-06-23T00:14:00Z | 7 | 67
PG&E | 42909.5421 | 13:00 | 39.3051 | -122.4862 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 100329817 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42909.5421 | 13:00 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | power theft | no-match | 1190 | 2017 | 6 | 23 | 13 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 21.3005 | 214_106 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | SYWC1 | 6.32 | 2017-06-23T19:26:00Z | 11.01 | 1 |  |  |  | 0 | 0 | SYWC1 | 6.32 | 2017-06-23T20:26:00Z | 11.01 | 2
PG&E | 42910.439 | 0.43819 | 38.9438 | -121.0447 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100090318 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42910.439 | 0.43819 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1193 | 2017 | 6 | 24 | 10 | 31 | 17-0058318 | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 582 | 2.1474 | 145_371 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PLTC1 | 7.98 | 2017-06-24T16:56:00Z | 10 | 22 |  |  |  | 0 | 0 | PLTC1 | 7.98 | 2017-06-24T17:56:00Z | 10 | 43
PG&E | 42910.6292 | 0.61875 | 38.3622 | -120.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101255656 | Unknown | 12000 | Fuse | Overhead | Yes | 42910.6292 | 0.61875 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1194 | 2017 | 6 | 24 | 14 | 51 | 17-0058332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 21296 | 6.659 | 198_291 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | MTZC1 | 6.33 | 2017-06-24T21:56:00Z | 8.99 | 1 |  |  |  | 0 | 0 | MTZC1 | 6.33 | 2017-06-24T21:56:00Z | 8.99 | 2
PG&E | 42910.9354 | 0.93542 | 38.2908 | -120.849 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CONTACT BOBBY BOWMAN | 101238865 | None | 12000 | Conductor | Overhead | Yes | 42910.9354 | 0.93542 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1195 | 2017 | 6 | 24 | 22 | 27 | 17-0058399 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 4529 | 6.6062 | 210_259 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | CFAC1 | 7.57 | 2017-06-25T05:05:00Z | 10 | 10 |  |  |  | 0 | 0 | CFAC1 | 7.57 | 2017-06-25T05:05:00Z | 10 | 24
PG&E | 42911.1159 | 0.015972 | 39.4043 | -123.3869 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102193088 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42911.1159 | 0.015972 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1197 | 2017 | 6 | 25 | 0 | 23 | 17-0058406 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 23100 | 17.871 | 98_318 | <25mph | >=15mph | HFTD - Distribution | AT319 | 3.31 | 2017-06-25T09:44:00Z | 4 | 24 | AU552 | 7.7 | 2017-06-25T09:46:00Z | 4.99 | 54 | AT319 | 3.31 | 2017-06-25T09:44:00Z | 4 | 48 | AU552 | 7.7 | 2017-06-25T10:45:00Z | 4.99 | 104
PG&E | 42913.3944 | 0.39097 | 37.9559 | -122.6176 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | marin county fire | 102260068 | UNFILED | 12000 | Conductor | Overhead | Yes | 42913.3944 | 0.39097 | Other | N.A. | N.A. | N.A. | Unknown |  | Fell into (slight defect) | 1203 | 2017 | 6 | 27 | 9 | 23 | 17-0058882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 3920 | 3.9699 | 239_128 | <25mph | <15mph | HFTD - Distribution | MDEC1 | 2.55 | 2017-06-27T15:36:00Z | 24 | 18 | MDEC1 | 2.55 | 2017-06-27T15:36:00Z | 24 | 24 | MDEC1 | 2.55 | 2017-06-27T15:36:00Z | 24 | 35 | MDEC1 | 2.55 | 2017-06-27T15:36:00Z | 24 | 47
PG&E | 42916.0559 | 01:20 | 39.821 | -121.5883 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103840463 | YES | 12000 | Conductor | Overhead | Yes | 42916.0559 | 01:20 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1210 | 2017 | 6 | 30 | 1 | 20 | 17-0059647 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 2888 | 5.9412 | 174_339 | <25mph | <15mph | HFTD - Distribution | C4565 | 1.69 | 2017-06-30T07:43:00Z | 3 | 6 | JBGC1 | 7.9 | 2017-06-30T08:13:00Z | 10 | 20 | C4565 | 1.69 | 2017-06-30T07:43:00Z | 3 | 12 | JBGC1 | 7.9 | 2017-06-30T09:13:00Z | 11.01 | 40
PG&E | 42916.9965 | 23:54 | 38.5794 | -122.8835 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 101958804 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42916.9965 | 23:54 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1211 | 2017 | 6 | 30 | 23 | 54 | 17-0059922 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2025 | 8.1196 | 176_296 | <25mph | <15mph | HFTD - Distribution | R08WW | 2.5 | 2017-07-01T06:00:00Z | 7.29 | 9 | DRYWW | 4.93 | 2017-07-01T06:00:00Z | 7.61 | 41 | R08WW | 2.5 | 2017-07-01T06:00:00Z | 7.29 | 18 | DRYWW | 4.93 | 2017-07-01T07:00:00Z | 9.19 | 82
PG&E | 42917 | 0.50139 | 39.8209 | -121.6418 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 003/039 | Unknown | 60000 | Conductor | Overhead | Yes | 42917 | 0.50139 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1212 | 2017 | 7 | 1 | 12 | 2 | INT-09792 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 22.7396 | 118_272 | <25mph | >=15mph | HFTD - Transmission | C4565 | 2.41 | 2017-07-01T06:53:00Z | 2.01 | 18 | CSTC1 | 7.61 | 2017-07-01T06:51:00Z | 11.01 | 21 | C4565 | 2.41 | 2017-07-01T07:53:00Z | 3 | 36 | CSTC1 | 7.61 | 2017-07-01T06:51:00Z | 11.01 | 41
PG&E | 42917.1963 | 0.13333 | 38.1952 | -122.9197 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103855493 | Unknown | 12000 | Conductor | Overhead | Yes | 42917.1963 | 0.13333 | Equipment/ Facility Failure | Pole | N.A. | N.A. | Unknown |  | Other/Unknown | 1214 | 2017 | 7 | 1 | 3 | 12 | 17-0059935 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 41370 | 18.3492 | 245_184 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | PRWC1 | 7.17 | 2017-07-01T10:50:00Z | 27.98 | 13 |  |  |  | 0 | 0 | PRWC1 | 7.17 | 2017-07-01T10:50:00Z | 27.98 | 26
PG&E | 42918 | 0.56111 | 39.8605 | -121.6274 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | Pole 000/017c | Unknown | 60000 | Conductor | Overhead | Yes | 42918 | 0.56111 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1216 | 2017 | 7 | 2 | 13 | 28 | INT-09794 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 4.7144 | 172_339 | <25mph | <15mph | HFTD - Transmission | C4565 | 1.76 | 2017-07-02T06:43:00Z | 2.01 | 18 | CSTC1 | 7.55 | 2017-07-02T06:51:00Z | 8.99 | 21 | C4565 | 1.76 | 2017-07-02T07:33:00Z | 2.01 | 36 | CSTC1 | 7.55 | 2017-07-02T06:51:00Z | 8.99 | 41
PG&E | 42919.853 | 0.85139 | 38.7923 | -120.9438 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101388730 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42919.853 | 0.85139 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1218 | 2017 | 7 | 3 | 20 | 26 | 17-0060336 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 8134 | 7.9271 | 173_342 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PLTC1 | 4.45 | 2017-07-04T02:56:00Z | 7 | 25 |  |  |  | 0 | 0 | PLTC1 | 4.45 | 2017-07-04T03:56:00Z | 7 | 50
PG&E | 42920.8451 | 20:16 | 40.4228 | -122.3975 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | SCOTT CORN 530-448-2414 | 101481860 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42920.8451 | 20:16 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1221 | 2017 | 7 | 4 | 20 | 16 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 8.1896 | 194_287 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E6886 | 4.89 | 2017-07-05T02:19:00Z | 11.01 | 4 |  |  |  | 0 | 0 | E6886 | 4.89 | 2017-07-05T02:19:00Z | 11.01 | 8
PG&E | 42921.5077 | 0.49861 | 39.2105 | -121.2266 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVE ROBERTSON 530 906 4892 | 100010286 | Unknown | 21000 | Conductor | Overhead | Yes | 42921.5077 | 0.49861 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1223 | 2017 | 7 | 5 | 11 | 58 | 17-0060605 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 10231 | 9.9712 | 199_277 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E1789 | 6.76 | 2017-07-05T18:54:00Z | 8.01 | 16 |  |  |  | 0 | 0 | E1789 | 6.76 | 2017-07-05T19:30:00Z | 11.01 | 32
PG&E | 42923 | 0.63125 | 40.9054 | -122.3806 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 101455950 | Unknown | 12000 | Conductor | Overhead | Yes | 42923 | 0.63125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1229 | 2017 | 7 | 7 | 15 | 9 | 17-0061903 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 20.461 | 211_104 | <25mph | >=15mph | HFTD - Distribution | CTANT | 2.76 | 2017-07-07T06:45:00Z | 13.04 | 11 | CTANT | 2.76 | 2017-07-07T06:45:00Z | 13.04 | 11 | CTANT | 2.76 | 2017-07-07T07:45:00Z | 15.52 | 20 | CTANT | 2.76 | 2017-07-07T07:45:00Z | 15.52 | 20
PG&E | 42923.8675 | 0.60486 | 37.499 | -119.799 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | STEVEN WARD OFFICE 209-966-3542 CELL559-706-8811 | 103855637 | Unknown | 21000 | Conductor | Overhead | Yes | 42923.8675 | 0.60486 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1230 | 2017 | 7 | 7 | 14 | 31 | 17-0061288 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 554306 | 15.7731 | 252_212 | <25mph | >=15mph | HFTD - Distribution | JSDC1 | 3.81 | 2017-07-08T03:47:00Z | 7 | 1 | C1522 | 5.09 | 2017-07-08T03:01:00Z | 7 | 8 | JSDC1 | 3.81 | 2017-07-08T04:47:00Z | 8.01 | 2 | C1522 | 5.09 | 2017-07-08T04:31:00Z | 8.99 | 17
PG&E | 42924.8076 | 0.78403 | 40.2935 | -122.4089 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | TOM STROING, RED BLUFF | 101526269 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42924.8076 | 0.78403 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1234 | 2017 | 7 | 8 | 18 | 49 | 17-0061469 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 157484 | 7.5087 | 140_366 | <25mph | <15mph | HFTD - Distribution | E7114 | 0.65 | 2017-07-09T01:29:00Z | 35.99 | 4 | E7114 | 0.65 | 2017-07-09T01:29:00Z | 35.99 | 4 | E7114 | 0.65 | 2017-07-09T01:29:00Z | 35.99 | 8 | E7114 | 0.65 | 2017-07-09T01:29:00Z | 35.99 | 8
PG&E | 42926.5237 | 0.52222 | 40.2603 | -123.8253 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103139646 | Unknown | 12000 | Conductor | Overhead | Yes | 42926.5237 | 0.52222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1238 | 2017 | 7 | 10 | 12 | 32 | 17-0061771 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 5910 | 8.9892 | 189_250 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42926.75 | 0.70833 | 37.3768 | -122.3597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | David Hibdon 831-254-1763 | 100270370 | Unknown | 12000 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1240 | 2017 | 7 | 10 | 17 | 0 | 17-0061857 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3322 | 6.5916 | 206_182 | <25mph | <15mph | HFTD - Distribution | E4551 | 0.89 | 2017-07-11T00:03:00Z | 5.99 | 1 | PUGC1 | 7.47 | 2017-07-11T00:18:00Z | 14.99 | 17 | E4551 | 0.89 | 2017-07-11T00:03:00Z | 5.99 | 1 | PUGC1 | 7.47 | 2017-07-11T01:18:00Z | 18.01 | 30
PG&E | 42927.9254 | 22:12 | 37.0122 | -121.9497 | Vegetation | Rural | < 3 Meters | Fire Agency | CAPT PHIL CRAMBLET 831-479-6842 | 101676689 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42927.9254 | 22:12 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1244 | 2017 | 7 | 11 | 22 | 12 | 17-0062198 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 714 | 3.9543 | 169_319 | <25mph | <15mph | HFTD - Distribution | E5038 | 3.28 | 2017-07-12T04:30:00Z | 11.01 | 44 | C8539 | 5.04 | 2017-07-12T04:21:00Z | 14 | 153 | E5038 | 3.28 | 2017-07-12T04:30:00Z | 11.01 | 84 | C8539 | 5.04 | 2017-07-12T04:21:00Z | 14 | 311
PG&E | 42928 | 0.66944 | 40.6531 | -122.3343 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 000/001 | Unknown | 60000 | Conductor | Overhead | Yes | 42928 | 0.66944 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1245 | 2017 | 7 | 12 | 16 | 4 | INT-09837 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 9.5513 | 158_185 | <25mph | <15mph | HFTD - Transmission | C5599 | 3.4 | 2017-07-12T06:46:00Z | 0 | 4 | C5599 | 3.4 | 2017-07-12T06:46:00Z | 0 | 4 | C5599 | 3.4 | 2017-07-12T07:46:00Z | 0 | 7 | C5599 | 3.4 | 2017-07-12T07:46:00Z | 0 | 7
PG&E | 42928.6313 | 15:09 | 37.1491 | -122.0037 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 103565794 | Unknown | 21000 | Conductor | Overhead | Yes | 42928.6313 | 15:09 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1248 | 2017 | 7 | 12 | 15 | 9 | 17-0062439 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24690 | 5.2663 | 155_192 | <25mph | <15mph | HFTD - Distribution | D8979 | 3.17 | 2017-07-12T21:47:00Z | 8.01 | 19 | LSGC1 | 4.79 | 2017-07-12T21:32:00Z | 14.99 | 117 | D8979 | 3.17 | 2017-07-12T22:17:00Z | 8.99 | 32 | LSGC1 | 4.79 | 2017-07-12T22:32:00Z | 15.99 | 200
PG&E | 42928.8485 | 20:21 | 40.0808 | -123.8339 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103841917 | Unknown | 12000 | Conductor | Overhead | Yes | 42928.8485 | 20:21 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1249 | 2017 | 7 | 12 | 20 | 21 | 17-0062445 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 4616 | 2.2363 | 143_386 | <25mph | <15mph | HFTD - Distribution | AV037 | 2.72 | 2017-07-13T02:33:00Z | 11.01 | 3 | AV037 | 2.72 | 2017-07-13T02:33:00Z | 11.01 | 4 | AV037 | 2.72 | 2017-07-13T02:33:00Z | 11.01 | 6 | ERCC1 | 4.01 | 2017-07-13T03:28:00Z | 12.01 | 8
PG&E | 42931.6076 | 14:34 | 39.6231 | -121.5328 | Vegetation | Rural | < 0.25 Acres | Fire Agency | russ fowler | 100404385 | Unknown | 12000 | Conductor | Overhead | Yes | 42931.6076 | 14:34 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1254 | 2017 | 7 | 15 | 14 | 34 | 17-0063126 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 54372 | 7.7421 | 187_223 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | CICC1 | 5.91 | 2017-07-15T20:54:00Z | 12.01 | 1 |  |  |  | 0 | 0 | CICC1 | 5.91 | 2017-07-15T21:54:00Z | 12.01 | 2
PG&E | 42932.4443 | 10:39 | 40.3414 | -123.8786 | Vegetation | Rural | < 3 Meters | Fire Agency | 707-726-1280 | 100990019 | Unknown | 12000 | Conductor | Overhead | Yes | 42932.4443 | 10:39 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1258 | 2017 | 7 | 16 | 10 | 39 | 17-0063223 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 198 | 11.3029 | 163_251 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42932.4994 | 11:59 | 36.6669 | -121.7515 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101761892 | None | 21000 | Fuse | Overhead | Yes | 42932.4994 | 11:59 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1259 | 2017 | 7 | 16 | 11 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 11.8584 | 78_370 | <25mph | <15mph | HFTD - Distribution | E6666 | 1.85 | 2017-07-16T18:50:00Z | 14.99 | 12 | E6666 | 1.85 | 2017-07-16T18:50:00Z | 14.99 | 16 | E6666 | 1.85 | 2017-07-16T19:50:00Z | 15.99 | 22 | E6666 | 1.85 | 2017-07-16T19:50:00Z | 15.99 | 30
PG&E | 42932.5072 | 12:10 | 35.6613 | -120.922 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101942626 | Unknown | 21000 | Conductor | Overhead | Yes | 42932.5072 | 12:10 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1260 | 2017 | 7 | 16 | 12 | 10 | 17-0063242 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 1304 | 15.4796 | 166_166 | <25mph | >=15mph | HFTD - Distribution | TABC1 | 0.35 | 2017-07-16T19:07:00Z | 7 | 1 | D4060 | 6.39 | 2017-07-16T18:30:00Z | 7 | 17 | TABC1 | 0.35 | 2017-07-16T20:07:00Z | 8.99 | 2 | D4060 | 6.39 | 2017-07-16T20:00:00Z | 10 | 33
PG&E | 42934 | 0.47917 | 38.0484 | -120.5565 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Structure 012/071 | Unknown | 115000 | Conductor | Overhead | Yes | 42934 | 0.47917 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1265 | 2017 | 7 | 18 | 11 | 30 | INT-09873 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 55499 | 0.58112 | 157_288 | <25mph | <15mph | HFTD - Transmission |  |  |  | 0 | 0 | C9085 | 5.13 | 2017-07-18T06:53:00Z | 2.01 | 65 |  |  |  | 0 | 0 | C9085 | 5.13 | 2017-07-18T06:53:00Z | 2.01 | 122
PG&E | 42934 | 0.90278 | 38.0031 | -122.2093 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | Pole 000/002 to 000/003 | Unknown | 60000 | Conductor | Overhead | Yes | 42934 | 0.90278 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1266 | 2017 | 7 | 18 | 21 | 40 | INT-09875 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 0 | 7.8402 | 219_243 | <25mph | <15mph | HFTD - Transmission | E4251 | 2.95 | 2017-07-18T06:15:00Z | 12.01 | 4 | E9944 | 7.08 | 2017-07-18T06:21:00Z | 15.99 | 75 | E4251 | 2.95 | 2017-07-18T06:15:00Z | 12.01 | 9 | MZXC1 | 5.07 | 2017-07-18T07:24:00Z | 18.99 | 146
PG&E | 42935 | 0.24444 | 37.0905 | -119.6047 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | Tower 003/001 | Unknown | 115000 | Conductor | Overhead | Yes | 42935 | 0.24444 | Contact From Object | N.A. | Other | Electric Facility | Unknown |  | no-match | 1269 | 2017 | 7 | 19 | 5 | 52 | INT-09877 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 0 | 19.5055 | 147_239 | <25mph | >=15mph | HFTD - Transmission |  |  |  | 0 | 0 | PRHC1 | 5.59 | 2017-07-19T06:27:00Z | 3 | 1 |  |  |  | 0 | 0 | PRHC1 | 5.59 | 2017-07-19T07:27:00Z | 3 | 2
PG&E | 42936.5736 | 13:45 | 35.0804 | -120.5538 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | PAUL LEE 805 903-3416 INC # 8291 | 101941116 | Unknown | 12000 | Conductor | Overhead | Yes | 42936.5736 | 13:45 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1275 | 2017 | 7 | 20 | 13 | 45 | 17-0064321 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 45999 | 7.409 | 220_78 | <25mph | <15mph | HFTD - Distribution | D6295 | 2.82 | 2017-07-20T20:33:00Z | 12.01 | 9 | D6295 | 2.82 | 2017-07-20T20:33:00Z | 12.01 | 28 | D6295 | 2.82 | 2017-07-20T20:33:00Z | 12.01 | 17 | D6295 | 2.82 | 2017-07-20T20:33:00Z | 12.01 | 54
PG&E | 42938.518 | 12:25 | 40.8795 | -123.7638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Josh , comander chief of forest service. | 100980577 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.518 | 12:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1279 | 2017 | 7 | 22 | 12 | 25 | 17-0064721 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 23227 | 4.3128 | 183_408 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | BHTC1 | 5.5 | 2017-07-22T18:46:00Z | 7 | 1 |  |  |  | 0 | 0 | BHTC1 | 5.5 | 2017-07-22T19:46:00Z | 8.01 | 2
PG&E | 42938.6101 | 14:38 | 37.2994 | -122.1631 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100265488 | Unknown | 12000 | Conductor | Overhead | Yes | 42938.6101 | 14:38 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1280 | 2017 | 7 | 22 | 14 | 38 | 17-0064738 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49181 | 8.7219 | 84_399 | <25mph | <15mph | HFTD - Distribution | E0516 | 3.56 | 2017-07-22T21:33:00Z | 8.99 | 14 | C6623 | 4.81 | 2017-07-22T21:23:00Z | 12.01 | 87 | E0516 | 3.56 | 2017-07-22T21:49:00Z | 10 | 29 | C6623 | 4.81 | 2017-07-22T21:23:00Z | 12.01 | 168
PG&E | 42939.3906 | 09:22 | 40.642 | -122.2302 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT? | 101459708 | FRONTIER COMMUNICATI | 12000 | Conductor | Overhead | Yes | 42939.3906 | 09:22 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1282 | 2017 | 7 | 23 | 9 | 22 | 17-0064801 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 184712 | 2.8969 | 72_397 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | C5599 | 5.97 | 2017-07-23T15:31:00Z | 2.01 | 8 |  |  |  | 0 | 0 | C5599 | 5.97 | 2017-07-23T17:02:00Z | 4 | 15
PG&E | 42939.7676 | 18:25 | 39.6723 | -123.5336 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103823226 | Unknown | 12000 | Conductor | Overhead | Yes | 42939.7676 | 18:25 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1284 | 2017 | 7 | 23 | 18 | 25 | 17-0064854 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 12864 | 8.0612 | 252_142 | <25mph | <15mph | HFTD - Distribution | LAYC1 | 3.32 | 2017-07-24T00:29:00Z | 11.01 | 1 | LAYC1 | 3.32 | 2017-07-24T00:29:00Z | 11.01 | 7 | LAYC1 | 3.32 | 2017-07-24T00:29:00Z | 11.01 | 2 | LAYC1 | 3.32 | 2017-07-24T00:29:00Z | 11.01 | 14
PG&E | 42940.5845 | 14:01 | 37.2635 | -122.3364 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike klink 650-879-0121 | 100322130 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42940.5845 | 14:01 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1286 | 2017 | 7 | 24 | 14 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 3.8678 | 248_141 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | LAHC1 | 5.31 | 2017-07-24T20:07:00Z | 13 | 1 |  |  |  | 0 | 0 | LAHC1 | 5.31 | 2017-07-24T20:07:00Z | 13 | 2
PG&E | 42940.8134 | 19:31 | 38.3519 | -120.7103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101263632 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.8134 | 19:31 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1288 | 2017 | 7 | 24 | 19 | 31 | 17-0065145 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14281 | 17.496 | 157_198 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | MTZC1 | 4.1 | 2017-07-25T01:56:00Z | 7 | 1 |  |  |  | 0 | 0 | MTZC1 | 4.1 | 2017-07-25T01:56:00Z | 7 | 2
PG&E | 42940.9063 | 21:45 | 35.6024 | -120.9211 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101860186 | Unknown | 12000 | Conductor | Overhead | Yes | 42940.9063 | 21:45 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1289 | 2017 | 7 | 24 | 21 | 45 | 17-0065191 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 21231 | 11.402 | 212_258 | <25mph | <15mph | HFTD - Distribution | TABC1 | 3.74 | 2017-07-25T04:07:00Z | 3 | 1 | TABC1 | 3.74 | 2017-07-25T04:07:00Z | 3 | 1 | TABC1 | 3.74 | 2017-07-25T05:07:00Z | 4 | 2 | TABC1 | 3.74 | 2017-07-25T05:07:00Z | 4 | 2
PG&E | 42941.6609 | 15:51 | 38.3779 | -122.5388 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102031447 | Unknown | 12000 | Conductor | Overhead | Yes | 42941.6609 | 15:51 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1290 | 2017 | 7 | 25 | 15 | 51 | 17-0065437 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 18584 | 28.0096 | 203_107 | 25-40mph | >=15mph | HFTD - Distribution | KENWW | 2.06 | 2017-07-25T22:00:00Z | 15.3 | 4 | KENWW | 2.06 | 2017-07-25T22:00:00Z | 15.3 | 11 | F11WW | 3.22 | 2017-07-25T23:00:00Z | 15.5 | 10 | F11WW | 3.22 | 2017-07-25T23:00:00Z | 15.5 | 24
PG&E | 42941.8004 | 19:12 | 39.5997 | -121.4449 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100403612 | Unknown | 12000 | Conductor | Overhead | Yes | 42941.8004 | 19:12 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1291 | 2017 | 7 | 25 | 19 | 12 | 17-0065453 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 68452 | 6.0359 | 133_260 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42944 | 0.58472 | 40.9997 | -121.9579 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101512624 | Unknown | 12000 | Conductor | Overhead | Yes | 42944 | 0.58472 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1293 | 2017 | 7 | 28 | 14 | 2 | 17-0066367 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 46581 | 16.7844 | 255_172 | <25mph | >=15mph | HFTD - Distribution | OMTC1 | 1.45 | 2017-07-28T06:26:00Z | 2.01 | 1 | OMTC1 | 1.45 | 2017-07-28T06:26:00Z | 2.01 | 1 | OMTC1 | 1.45 | 2017-07-28T06:26:00Z | 2.01 | 2 | OMTC1 | 1.45 | 2017-07-28T06:26:00Z | 2.01 | 2
PG&E | 42944.8062 | 19:20 | 35.7276 | -120.9903 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | San Luis Obispo CDF | 101945496 | None | 21000 | Conductor | Overhead | Yes | 42944.8062 | 19:20 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1295 | 2017 | 7 | 28 | 19 | 20 | 17-0066392 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 8300 | 9.3286 | 200_100 | <25mph | <15mph | HFTD - Distribution | E9175 | 1.53 | 2017-07-29T02:10:00Z | 7 | 12 | TABC1 | 6.16 | 2017-07-29T02:07:00Z | 10 | 13 | E9175 | 1.53 | 2017-07-29T02:10:00Z | 7 | 20 | TABC1 | 6.16 | 2017-07-29T02:07:00Z | 10 | 22
PG&E | 42945.5612 | 13:28 | 35.4523 | -120.3834 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101889516 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42945.5612 | 13:28 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1297 | 2017 | 7 | 29 | 13 | 28 | 17-0066472 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 1962 | 2.836 | 180_320 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42946.4075 | 09:46 | 38.9132 | -122.6179 | Vegetation | Rural | < 0.25 Acres | Fire Agency | mike wink | 102151066 | None | 0 – 750 | Conductor | Overhead | Yes | 42946.4075 | 09:46 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1302 | 2017 | 7 | 30 | 9 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 14.1728 | 217_98 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | KELC1 | 4.76 | 2017-07-30T15:57:00Z | 8.01 | 8 |  |  |  | 0 | 0 | KELC1 | 4.76 | 2017-07-30T16:57:00Z | 10 | 17
PG&E | 42947.6123 | 14:41 | 38.7967 | -121.1329 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103782414 | Unknown | 12000 | Conductor | Overhead | Yes | 42947.6123 | 14:41 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1305 | 2017 | 7 | 31 | 14 | 41 | 17-0066797 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 210 | 7.6453 | 194_283 | <25mph | <15mph | HFTD - Distribution | D2336 | 3.3 | 2017-07-31T20:45:00Z | 4 | 1 | PLTC1 | 7.08 | 2017-07-31T20:56:00Z | 11.01 | 15 | D2336 | 3.3 | 2017-07-31T21:57:00Z | 7 | 6 | D7393 | 6.59 | 2017-07-31T22:23:00Z | 11.01 | 34
PG&E | 42949 | 0.40417 | 39.2274 | -123.1081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 5/0 | None | 60000 | Conductor | Overhead | Yes | 42949 | 0.40417 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1307 | 2017 | 8 | 2 | 9 | 42 | INT-09925 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 8.5295 | 266_132 | <25mph | <15mph | HFTD - Transmission |  |  |  | 0 | 0 | COWC1 | 7.26 | 2017-08-02T06:01:00Z | 14 | 11 |  |  |  | 0 | 0 | COWC1 | 7.26 | 2017-08-02T06:01:00Z | 14 | 23
PG&E | 42949.251 | 0.24583 | 40.7986 | -123.3961 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Cal Fire | 100974913 | Unknown | 12000 | Conductor | Overhead | Yes | 42949.251 | 0.24583 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1308 | 2017 | 8 | 2 | 5 | 54 | 17-0067270 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 5832 | 5.8454 | 99_395 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | UDWC1 | 7.47 | 2017-08-02T12:24:00Z | 1.01 | 1 |  |  |  | 0 | 0 | UDWC1 | 7.47 | 2017-08-02T13:24:00Z | 1.01 | 2
PG&E | 42950.4588 | 0.45347 | 39.0732 | -121.0868 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100072742 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42950.4588 | 0.45347 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1312 | 2017 | 8 | 3 | 10 | 53 | 17-0067679 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 127440 | 10.4975 | 216_206 | <25mph | <15mph | HFTD - Distribution | C5488 | 3.14 | 2017-08-03T17:57:00Z | 5.99 | 5 | E1789 | 5.51 | 2017-08-03T18:00:00Z | 7 | 48 | C5488 | 3.14 | 2017-08-03T18:38:00Z | 7 | 8 | E1789 | 5.51 | 2017-08-03T19:00:00Z | 7 | 91
PG&E | 42952.3565 | 08:33 | 38.4583 | -120.8695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JEFF MICHEL- 530 409 2223 | 101236223 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42952.3565 | 08:33 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1317 | 2017 | 8 | 5 | 8 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 15.2043 | 215_108 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | CFAC1 | 6.33 | 2017-08-05T15:05:00Z | 7 | 10 |  |  |  | 0 | 0 | CFAC1 | 6.33 | 2017-08-05T15:05:00Z | 7 | 17
PG&E | 42952.7592 | 0.75556 | 39.0968 | -123.2147 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102196629 | Unknown | 12000 | Conductor | Overhead | Yes | 42952.7592 | 0.75556 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1318 | 2017 | 8 | 5 | 18 | 8 | 17-0068200 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 134239 | 10.1422 | 205_264 | <25mph | <15mph | HFTD - Distribution | KUKI | 2.28 | 2017-08-06T00:56:00Z | 17.27 | 12 | COWC1 | 7.84 | 2017-08-06T01:01:00Z | 23 | 26 | KUKI | 2.28 | 2017-08-06T01:25:00Z | 19.57 | 13 | COWC1 | 7.84 | 2017-08-06T02:01:00Z | 32.01 | 40
PG&E | 42953.4849 | 11:38 | 36.5857 | -121.7121 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101747125 | Unknown | 12000 | Conductor | Overhead | Yes | 42953.4849 | 11:38 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1321 | 2017 | 8 | 6 | 11 | 38 | 17-0068279 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 87172 | 9.4859 | 261_172 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E8875 | 7.87 | 2017-08-06T18:20:00Z | 12.01 | 16 |  |  |  | 0 | 0 | E6666 | 7.23 | 2017-08-06T19:30:00Z | 15.99 | 32
PG&E | 42955.1829 | 0.17361 | 38.4949 | -122.6685 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 102025742 | PACIFIC BELL | 12000 | Transformer | Overhead | Yes | 42955.1829 | 0.17361 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1325 | 2017 | 8 | 8 | 4 | 10 | 17-0068642 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 2750 | 9.3483 | 127_267 | <25mph | <15mph | HFTD - Distribution | RSAC1 | 2.6 | 2017-08-08T10:29:00Z | 5.99 | 16 | D9840 | 5.11 | 2017-08-08T10:31:00Z | 5.99 | 63 | C3628 | 3.62 | 2017-08-08T11:46:00Z | 5.99 | 31 | D9840 | 5.11 | 2017-08-08T10:31:00Z | 5.99 | 120
PG&E | 42955.4775 | 11:27 | 37.0445 | -121.6343 | Vegetation | Urban | < 3 Meters | Utility: PG&E | N.A. | 100613200 | VERIZON CALIFORNIA | 21000 | Capacitor Bank | Overhead | Yes | 42955.4775 | 11:27 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | Other/Unknown | 1326 | 2017 | 8 | 8 | 11 | 27 | 17-0068774 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | 34192 | 1.2124 | 172_186 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | C4787 | 5.95 | 2017-08-08T18:13:00Z | 7 | 43 |  |  |  | 0 | 0 | C4787 | 5.95 | 2017-08-08T18:48:00Z | 8.01 | 85
PG&E | 42955.8578 | 20:35 | 37.2637 | -119.7103 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TROY CHEEK1-209-966-3621 | 103793352 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42955.8578 | 20:35 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1327 | 2017 | 8 | 8 | 20 | 35 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.6137 | 125_264 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | D7171 | 6.79 | 2017-08-09T02:39:00Z | 5.99 | 32 |  |  |  | 0 | 0 | D7171 | 6.79 | 2017-08-09T03:39:00Z | 7 | 69
PG&E | 42956.4786 | 11:29 | 38.6532 | -120.6273 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101402496 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42956.4786 | 11:29 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1328 | 2017 | 8 | 9 | 11 | 29 | 17-0069107 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 54216 | 10.9179 | 256_199 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | GZFC1 | 5.69 | 2017-08-09T18:17:00Z | 8.01 | 3 |  |  |  | 0 | 0 | GZFC1 | 5.69 | 2017-08-09T19:17:00Z | 11.01 | 5
PG&E | 42959.3812 | 09:08 | 34.6689 | -120.0286 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103391912 | Unknown | 12000 | Conductor | Overhead | Yes | 42959.3812 | 09:08 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | wire cut | Other/Unknown | 1330 | 2017 | 8 | 12 | 9 | 8 | 17-0069829 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 26070 | 6.4092 | 201_254 | <25mph | <15mph | HFTD - Distribution | SXWC1 | 1.34 | 2017-08-12T15:09:00Z | 4 | 7 | SXWC1 | 1.34 | 2017-08-12T15:09:00Z | 4 | 14 | UCSE | 1.88 | 2017-08-12T17:00:00Z | 7.2 | 14 | AP901 | 5.95 | 2017-08-12T17:00:00Z | 8.99 | 32
PG&E | 42961 | 0.25972 | 40.1164 | -123.8064 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100986364 | Unknown | 12000 | Conductor | Overhead | Yes | 42961 | 0.25972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1332 | 2017 | 8 | 14 | 6 | 14 | 17-0070003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 959989 | 3.7729 | 123_268 | <25mph | <15mph | HFTD - Distribution | ERCC1 | 1.77 | 2017-08-14T06:28:00Z | 11.01 | 2 | ERCC1 | 1.77 | 2017-08-14T06:28:00Z | 11.01 | 2 | ERCC1 | 1.77 | 2017-08-14T06:28:00Z | 11.01 | 7 | ERCC1 | 1.77 | 2017-08-14T06:28:00Z | 11.01 | 7
PG&E | 42961 | 0.99444 | 37.1272 | -122.1689 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Pole 015/127 | None | 60000 | Conductor | Overhead | Yes | 42961 | 0.99444 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1333 | 2017 | 8 | 14 | 23 | 52 | INT-09976 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 1790869 | 11.9038 | 81_357 | <25mph | <15mph | HFTD - Transmission | BNDC1 | 0.33 | 2017-08-14T06:50:00Z | 18.01 | 21 | BNDC1 | 0.33 | 2017-08-14T06:50:00Z | 18.01 | 31 | BNDC1 | 0.33 | 2017-08-14T06:50:00Z | 18.01 | 48 | BNDC1 | 0.33 | 2017-08-14T06:50:00Z | 18.01 | 68
PG&E | 42961.3308 | 07:56 | 39.1794 | -120.9761 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100083743 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42961.3308 | 07:56 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1334 | 2017 | 8 | 14 | 7 | 56 | 17-0070063 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3012 | 8.0138 | 200_304 | <25mph | <15mph | HFTD - Distribution | D8321 | 3.61 | 2017-08-14T14:50:00Z | 2.01 | 14 | E5439 | 6.04 | 2017-08-14T14:50:00Z | 8.01 | 69 | D8321 | 3.61 | 2017-08-14T15:40:00Z | 4 | 30 | AT999 | 5.18 | 2017-08-14T15:32:00Z | 11.01 | 144
PG&E | 42962.8116 | 19:28 | 39.5037 | -121.2783 | Vegetation | Rural | < 3 Meters | Unknown | N.A. | 100396172 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42962.8116 | 19:28 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1335 | 2017 | 8 | 15 | 19 | 28 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.7124 | 148_191 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | PKCC1 | 4.51 | 2017-08-16T02:10:00Z | 13 | 2 |  |  |  | 0 | 0 | PKCC1 | 4.51 | 2017-08-16T02:10:00Z | 13 | 4
PG&E | 42964 | 0.63542 | 39.3703 | -121.0484 | Vegetation | Rural | < 0.25 Acres | Fire Agency | PHIL MICHAEL 265-2894 INCIENT # CA NEV 21642 | 100083029 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42964 | 0.63542 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1338 | 2017 | 8 | 17 | 15 | 15 | 17-0071121 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 32850 | 11.7905 | 181_305 | <25mph | <15mph | HFTD - Distribution | E3651 | 2.23 | 2017-08-17T07:00:00Z | 0 | 13 | RRRC1 | 5.9 | 2017-08-17T06:13:00Z | 5.99 | 14 | E3651 | 2.23 | 2017-08-17T08:00:00Z | 0 | 25 | RRRC1 | 5.9 | 2017-08-17T06:13:00Z | 5.99 | 27
PG&E | 42966 | 0.88611 | 40.5752 | -122.2985 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464623 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42966 | 0.88611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1341 | 2017 | 8 | 19 | 21 | 16 | 17-0071522 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 19044 | 6.2027 | 189_222 | <25mph | <15mph | HFTD - Distribution | C5599 | 2.67 | 2017-08-19T06:47:00Z | 0 | 4 | RRAC1 | 4.12 | 2017-08-19T06:24:00Z | 4.99 | 11 | C5599 | 2.67 | 2017-08-19T07:16:00Z | 3 | 8 | RRAC1 | 4.12 | 2017-08-19T07:24:00Z | 4.99 | 22
PG&E | 42973 | 0.87014 | 38.7066 | -121.0193 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101382231 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42973 | 0.87014 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1350 | 2017 | 8 | 26 | 20 | 53 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.6104 | 128_265 | <25mph | <15mph | HFTD - Distribution | E4740 | 2.39 | 2017-08-26T07:00:00Z | 2.01 | 33 | FSLC1 | 6.06 | 2017-08-26T06:05:00Z | 5.37 | 58 | D7401 | 1.71 | 2017-08-26T07:54:00Z | 4.99 | 65 | FSLC1 | 6.06 | 2017-08-26T07:20:00Z | 5.59 | 115
PG&E | 42974 | 0.83611 | 38.9165 | -121.151 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-477-0641 x7, log 22629 | 100077184 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42974 | 0.83611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1352 | 2017 | 8 | 27 | 20 | 4 | 17-0073228 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 905 | 8.9477 | 184_239 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | D8862 | 4.91 | 2017-08-27T06:02:00Z | 8.99 | 8 |  |  |  | 0 | 0 | D8862 | 4.91 | 2017-08-27T07:47:00Z | 8.99 | 14
PG&E | 42975 | 0.38472 | 38.7443 | -122.6491 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 103781085 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42975 | 0.38472 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1356 | 2017 | 8 | 28 | 9 | 14 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 17.9564 | 265_114 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | LKRC1 | 6.54 | 2017-08-28T06:05:00Z | 8.99 | 1 |  |  |  | 0 | 0 | LKRC1 | 6.54 | 2017-08-28T06:05:00Z | 8.99 | 2
PG&E | 42975 | 0.42153 | 39.0472 | -120.7859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | FORESTHILL | 100019525 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 0.42153 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1357 | 2017 | 8 | 28 | 10 | 7 | 17-0073379 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 10077 | 10.2849 | 128_281 | <25mph | <15mph | HFTD - Distribution | AU268 | 3.78 | 2017-08-28T06:44:00Z | 2.01 | 5 | AU268 | 3.78 | 2017-08-28T06:44:00Z | 2.01 | 6 | AU268 | 3.78 | 2017-08-28T07:47:00Z | 2.01 | 8 | AU268 | 3.78 | 2017-08-28T07:47:00Z | 2.01 | 10
PG&E | 42975 | 0.5875 | 38.634 | -122.4194 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 102253236 | Unknown | 21000 | Conductor | Overhead | Yes | 42975 | 0.5875 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1359 | 2017 | 8 | 28 | 14 | 6 | 17-0073526 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 1896 | 16.7686 | 208_222 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | AT925 | 4.29 | 2017-08-28T06:57:00Z | 1.01 | 12 |  |  |  | 0 | 0 | AT925 | 4.29 | 2017-08-28T07:58:00Z | 1.01 | 24
PG&E | 42975 | 0.62431 | 40.2853 | -123.8728 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 100990599 | Unknown | 12000 | Conductor | Overhead | Yes | 42975 | 0.62431 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1361 | 2017 | 8 | 28 | 14 | 59 | 17-0073546 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2688 | 0.95829 | 138_274 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42976 | 0.53403 | 37.4507 | -119.6454 | Vegetation | Rural | > 5000 Acres | Fire Agency | USFS | 101017368 | Unknown | 12000 | Conductor | Overhead | Yes | 42976 | 0.53403 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1366 | 2017 | 8 | 29 | 12 | 49 | 17-0073823 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | 3rd Party | 3rd Party - Unknown | 5894785 | 1.7701 | 193_250 | <25mph | <15mph | HFTD - Distribution | D0826 | 0.24 | 2017-08-29T06:01:00Z | 3 | 4 | MIAC1 | 5.9 | 2017-08-29T06:59:00Z | 8.99 | 28 | D0826 | 0.24 | 2017-08-29T06:01:00Z | 3 | 8 | MIAC1 | 5.9 | 2017-08-29T06:59:00Z | 8.99 | 59
PG&E | 42976 | 0.6625 | 38.302 | -122.5431 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 911 | 102026119 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 42976 | 0.6625 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1367 | 2017 | 8 | 29 | 15 | 54 | 17-0073928 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 485 | 8.2913 | 259_209 | <25mph | <15mph | HFTD - Distribution | F11WW | 3.32 | 2017-08-29T06:00:00Z | 2.1 | 2 | KENWW | 7.3 | 2017-08-29T06:00:00Z | 6.4 | 21 | F11WW | 3.32 | 2017-08-29T06:00:00Z | 2.1 | 3 | KENWW | 7.3 | 2017-08-29T06:00:00Z | 6.4 | 38
PG&E | 42977 | 0.76458 | 40.6243 | -122.3039 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CASHU008896 | 103151338 | YES | 12000 | Conductor | Overhead | Yes | 42977 | 0.76458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1369 | 2017 | 8 | 30 | 18 | 21 | 17-0074287 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 76344 | 7.6808 | 287_94 | <25mph | <15mph | HFTD - Distribution | C5599 | 2.06 | 2017-08-30T06:47:00Z | 1.01 | 8 | RRAC1 | 7.52 | 2017-08-30T06:24:00Z | 7 | 9 | C5599 | 2.06 | 2017-08-30T07:46:00Z | 3 | 17 | RRAC1 | 7.52 | 2017-08-30T06:24:00Z | 7 | 19
PG&E | 42977 | 0.94236 | 38.9993 | -120.9887 | Vegetation | Rural | < 3 Meters | Fire Agency | Andy 530-889-0111 | 100026238 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42977 | 0.94236 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1370 | 2017 | 8 | 30 | 22 | 37 | 17-0074333 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 3750 | 2.8977 | 145_384 | <25mph | <15mph | HFTD - Distribution | D9434 | 3.56 | 2017-08-30T06:53:00Z | 2.01 | 15 | AT999 | 7.28 | 2017-08-30T06:33:00Z | 3 | 37 | D9434 | 3.56 | 2017-08-30T07:53:00Z | 3 | 34 | C5488 | 5.56 | 2017-08-30T07:44:00Z | 4 | 82
PG&E | 42978 | 0.27917 | 35.616 | -120.8577 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Derrick | 101860075 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 0.27917 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1372 | 2017 | 8 | 31 | 6 | 42 | 17-0074386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1620 | 12.4202 | 200_294 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | TABC1 | 4.66 | 2017-08-31T06:07:00Z | 2.01 | 1 |  |  |  | 0 | 0 | TABC1 | 4.66 | 2017-08-31T06:07:00Z | 2.01 | 2
PG&E | 42978 | 0.48125 | 37.1379 | -121.9966 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100519201 | Unknown | 21000 | Conductor | Overhead | Yes | 42978 | 0.48125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1373 | 2017 | 8 | 31 | 11 | 33 | 17-0074457 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 99153 | 10.3974 | 206_107 | <25mph | <15mph | HFTD - Distribution | D8979 | 2.5 | 2017-08-31T06:03:00Z | 4.99 | 19 | D3546 | 7.44 | 2017-08-31T06:10:00Z | 7 | 105 | D8979 | 2.5 | 2017-08-31T06:03:00Z | 4.99 | 37 | D3546 | 7.44 | 2017-08-31T06:10:00Z | 7 | 206
PG&E | 42979 | 0.33333 | 37.3757 | -119.8886 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101067028 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42979 | 0.33333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1378 | 2017 | 9 | 1 | 8 | 0 | 17-0074724 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 680 | 12.1778 | 213_139 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E9110 | 4.96 | 2017-09-01T06:35:00Z | 8.01 | 6 |  |  |  | 0 | 0 | E9110 | 4.96 | 2017-09-01T07:50:00Z | 8.99 | 12
PG&E | 42979 | 0.74167 | 36.6518 | -121.7249 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MCFD | 103155761 | Unknown | 12000 | Conductor | Overhead | Yes | 42979 | 0.74167 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1382 | 2017 | 9 | 1 | 17 | 48 | 17-0074898 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 8152 | 3.6668 | 168_193 | <25mph | <15mph | HFTD - Distribution | E6666 | 3.59 | 2017-09-01T06:25:00Z | 5.99 | 4 | E6666 | 3.59 | 2017-09-01T06:25:00Z | 5.99 | 12 | E6666 | 3.59 | 2017-09-01T07:55:00Z | 8.01 | 9 | E6666 | 3.59 | 2017-09-01T07:55:00Z | 8.01 | 27
PG&E | 42980 | 0.50069 | 37.6645 | -121.9223 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 100956020 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42980 | 0.50069 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1384 | 2017 | 9 | 2 | 12 | 1 | 17-0075132 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 7152 | 6.348 | 134_256 | <25mph | <15mph | HFTD - Distribution | AU719 | 3.94 | 2017-09-02T06:56:00Z | 2.01 | 13 | D3560 | 6.84 | 2017-09-02T07:00:00Z | 8.01 | 31 | AU719 | 3.94 | 2017-09-02T07:56:00Z | 3 | 26 | D3560 | 6.84 | 2017-09-02T07:45:00Z | 8.99 | 65
PG&E | 42981 | 0.53611 | 37.2162 | -119.4807 | Vegetation | Rural | 1000 - 4999 Acres | Fire Agency | Cal Fire | 103345573 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42981 | 0.53611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1388 | 2017 | 9 | 3 | 12 | 52 | 17-0075546 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 2362 | 10.8576 | 146_205 | <25mph | <15mph | HFTD - Distribution | NFRC1 | 1.81 | 2017-09-03T06:55:00Z | 11.01 | 5 | NFRC1 | 1.81 | 2017-09-03T06:55:00Z | 11.01 | 5 | C6459 | 2.52 | 2017-09-03T08:00:00Z | 12.01 | 9 | C6459 | 2.52 | 2017-09-03T08:00:00Z | 12.01 | 9
PG&E | 42981 | 0.74444 | 37.4956 | -119.8367 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 209-966-3621 | 101086621 | Unknown | 21000 | Transformer | Overhead | Yes | 42981 | 0.74444 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | Other/Unknown | 1389 | 2017 | 9 | 3 | 17 | 52 | 17-0075617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 4512 | 10.5097 | 266_196 | <25mph | <15mph | HFTD - Distribution | JSDC1 | 3.33 | 2017-09-03T06:47:00Z | 5.99 | 1 | E9110 | 4.74 | 2017-09-03T06:40:00Z | 8.99 | 6 | JSDC1 | 3.33 | 2017-09-03T07:47:00Z | 5.99 | 2 | E9110 | 4.74 | 2017-09-03T07:55:00Z | 10 | 17
PG&E | 42982 | 0.14514 | 39.8317 | -121.8444 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 102300100 | PACIFIC BELL | 12000 | Conductor | Overhead | No |  |  | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1392 | 2017 | 9 | 4 | 3 | 29 | 17-0075723 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 214974 | 4.6451 | 251_173 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | D8204 | 5.42 | 2017-09-04T06:37:00Z | 8.99 | 14 |  |  |  | 0 | 0 | D8204 | 5.42 | 2017-09-04T07:13:00Z | 8.99 | 34
PG&E | 42983 | 0.29028 | 39.6727 | -123.5128 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 102194697 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 42983 | 0.29028 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1395 | 2017 | 9 | 5 | 6 | 58 | 17-0075976 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 10528 | 18.5256 | 176_318 | <25mph | >=15mph | HFTD - Distribution | LAYC1 | 2.53 | 2017-09-05T06:29:00Z | 7 | 1 | LAYC1 | 2.53 | 2017-09-05T06:29:00Z | 7 | 8 | LAYC1 | 2.53 | 2017-09-05T07:29:00Z | 7 | 2 | LAYC1 | 2.53 | 2017-09-05T07:29:00Z | 7 | 15
PG&E | 42984 | 0.80972 | 40.8392 | -122.3635 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103643183 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 0.80972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1399 | 2017 | 9 | 6 | 19 | 26 | 17-0076501 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 23830 | 10.8359 | 145_258 | <25mph | <15mph | HFTD - Distribution | CTANT | 1.93 | 2017-09-06T06:00:00Z | 8.08 | 5 | SLFC1 | 6.48 | 2017-09-06T06:19:00Z | 12.01 | 11 | CTANT | 1.93 | 2017-09-06T06:00:00Z | 8.08 | 9 | SLFC1 | 6.48 | 2017-09-06T07:19:00Z | 18.01 | 20
PG&E | 42984 | 0.83889 | 37.2925 | -122.294 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100256917 | Unknown | 12000 | Conductor | Overhead | Yes | 42984 | 0.83889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1400 | 2017 | 9 | 6 | 20 | 8 | 17-0076502 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4914 | 10.4084 | 142_396 | <25mph | <15mph | HFTD - Distribution | LAHC1 | 2.3 | 2017-09-06T06:07:00Z | 4 | 1 | LAHC1 | 2.3 | 2017-09-06T06:07:00Z | 4 | 7 | LAHC1 | 2.3 | 2017-09-06T07:07:00Z | 4 | 2 | LAHC1 | 2.3 | 2017-09-06T07:07:00Z | 4 | 13
PG&E | 42986 | 0.19931 | 38.7478 | -120.859 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101391575 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42986 | 0.19931 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1401 | 2017 | 9 | 8 | 4 | 47 | 17-0076889 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 39736 | 11.6569 | 143_200 | <25mph | <15mph | HFTD - Distribution | E5691 | 3.77 | 2017-09-08T06:56:00Z | 0 | 37 | E3165 | 7.16 | 2017-09-08T06:32:00Z | 3 | 78 | E5691 | 3.77 | 2017-09-08T07:56:00Z | 0 | 73 | E3165 | 7.16 | 2017-09-08T06:32:00Z | 3 | 154
PG&E | 42986 | 0.72292 | 38.6039 | -120.9275 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101379094 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 42986 | 0.72292 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1402 | 2017 | 9 | 8 | 17 | 21 | 17-0077122 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 8504 | 6.2752 | 205_280 | <25mph | <15mph | HFTD - Distribution | BENC1 | 0.96 | 2017-09-08T06:59:00Z | 7 | 14 | BENC1 | 0.96 | 2017-09-08T06:59:00Z | 7 | 59 | BENC1 | 0.96 | 2017-09-08T06:59:00Z | 7 | 27 | BENC1 | 0.96 | 2017-09-08T06:59:00Z | 7 | 116
PG&E | 42986 | 0.88472 | 37.9604 | -120.3764 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | John Lite 209-984-5623 | 101042521 | Unknown | 17000 | Conductor | Overhead | Yes | 42986 | 0.88472 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1403 | 2017 | 9 | 8 | 21 | 14 | 17-0077137 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 49858 | 6.6561 | 203_272 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | F0305 | 6.4 | 2017-09-08T07:00:00Z | 0 | 17 |  |  |  | 0 | 0 | F0305 | 6.4 | 2017-09-08T08:00:00Z | 0 | 33
PG&E | 42989 | 0.30417 | 37.0008 | -121.6667 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100621936 | VERIZON CALIFORNIA | 0 – 750 | Conductor | Overhead | No |  |  | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1407 | 2017 | 9 | 11 | 7 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.4109 | 220_201 | <25mph | <15mph | HFTD - Distribution | AU710 | 3.82 | 2017-09-11T06:15:00Z | 3 | 5 | C4787 | 7.93 | 2017-09-11T06:33:00Z | 11.01 | 40 | AU710 | 3.82 | 2017-09-11T08:00:00Z | 3 | 9 | C4787 | 7.93 | 2017-09-11T06:33:00Z | 11.01 | 79
PG&E | 42989 | 0.36806 | 36.9515 | -121.842 | Vegetation | Rural | < 3 Meters | Self Extinguished | N.A. | 101790954 | PACIFIC BELL | 21000 | Fuse | Overhead | Yes | 42989 | 0.36806 | Contact From Object | N.A. | Other | Electric Facility | Weather | lightning strike | no-match | 1408 | 2017 | 9 | 11 | 8 | 50 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | N.A. | 12.7091 | 170_184 | <25mph | <15mph | HFTD - Distribution | CTOC1 | 3.41 | 2017-09-11T06:27:00Z | 4.99 | 32 | CTOC1 | 3.41 | 2017-09-11T06:27:00Z | 4.99 | 63 | E7291 | 2.85 | 2017-09-11T07:39:00Z | 7 | 65 | E7291 | 2.85 | 2017-09-11T07:39:00Z | 7 | 124
PG&E | 42990 | 0.39167 | 39.741 | -121.6079 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 911 | 100330302 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42990 | 0.39167 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1410 | 2017 | 9 | 12 | 9 | 24 | 17-0078149 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 402890 | 5.2759 | 70_399 | <25mph | <15mph | HFTD - Distribution | PDEC1 | 1.25 | 2017-09-12T06:00:00Z | 8.99 | 2 | JBGC1 | 6.33 | 2017-09-12T06:13:00Z | 23 | 9 | PDEC1 | 1.25 | 2017-09-12T06:00:00Z | 8.99 | 3 | JBGC1 | 6.33 | 2017-09-12T06:13:00Z | 23 | 17
PG&E | 42992 | 0.5875 | 40.2942 | -123.8174 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100989497 | Unknown | 12000 | Conductor | Overhead | Yes | 42992 | 0.5875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1414 | 2017 | 9 | 14 | 14 | 6 | 17-0079010 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 19722 | 7.4403 | 176_322 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 42993 | 0.62153 | 39.7461 | -121.4885 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100335239 | Unknown | 12000 | Conductor | Overhead | Yes | 42993 | 0.62153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1415 | 2017 | 9 | 15 | 14 | 55 | 17-0079388 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 8834 | 3.6247 | 81_367 | <25mph | <15mph | HFTD - Distribution | JBGC1 | 0.7 | 2017-09-15T06:13:00Z | 3 | 1 | JBGC1 | 0.7 | 2017-09-15T06:13:00Z | 3 | 3 | JBGC1 | 0.7 | 2017-09-15T07:13:00Z | 7 | 2 | JBGC1 | 0.7 | 2017-09-15T07:13:00Z | 7 | 5
PG&E | 42995 | 0.73472 | 38.9946 | -121.0261 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100029537 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42995 | 0.73472 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Branch (OverHanging) | 1417 | 2017 | 9 | 17 | 17 | 38 | 17-0079585 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 28509 | 6.6998 | 271_165 | <25mph | <15mph | HFTD - Distribution | C0713 | 1.74 | 2017-09-17T06:54:00Z | 0 | 9 | AT999 | 7.97 | 2017-09-17T06:52:00Z | 3 | 18 | C0713 | 1.74 | 2017-09-17T07:54:00Z | 0 | 19 | AT999 | 7.97 | 2017-09-17T07:07:00Z | 3 | 37
PG&E | 42996 | 0.54236 | 39.3889 | -121.4054 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 103795057 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 42996 | 0.54236 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1418 | 2017 | 9 | 18 | 13 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 10.9535 | 198_294 | <25mph | <15mph | HFTD - Distribution | BNGC1 | 1.17 | 2017-09-18T06:51:00Z | 4.99 | 1 | TT309 | 5.6 | 2017-09-18T06:45:00Z | 7 | 2 | BNGC1 | 1.17 | 2017-09-18T07:51:00Z | 7 | 2 | TT309 | 5.6 | 2017-09-18T06:45:00Z | 7 | 4
PG&E | 42996 | 0.99306 | 37.9088 | -120.4865 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | incident comander geoff marshall 209-419-4407 | 101040882 | Unknown | 17000 | Conductor | Overhead | Yes | 42996 | 0.99306 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1422 | 2017 | 9 | 18 | 23 | 50 | 17-0079858 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 382303 | 20.6164 | 120_244 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | GNSC1 | 5.23 | 2017-09-18T06:03:00Z | 4.99 | 1 |  |  |  | 0 | 0 | GNSC1 | 5.23 | 2017-09-18T07:03:00Z | 4.99 | 2
PG&E | 42998 | 0.0875 | 37.2597 | -122.3222 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100322388 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 42998 | 0.0875 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1424 | 2017 | 9 | 20 | 2 | 6 | 17-0080179 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 36593 | 13.2847 | 276_101 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | LAHC1 | 4.84 | 2017-09-20T06:07:00Z | 4 | 1 |  |  |  | 0 | 0 | LAHC1 | 4.84 | 2017-09-20T07:07:00Z | 4 | 2
PG&E | 43001 | 0.59514 | 40.6509 | -122.2974 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DARREN STEWART 448-2421 | 101467221 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43001 | 0.59514 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | Third-party caused | Other/Unknown | 1429 | 2017 | 9 | 23 | 14 | 17 | 17-0081216 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 98820 | 11.0676 | 216_185 | <25mph | <15mph | HFTD - Distribution | C5599 | 3.73 | 2017-09-23T06:16:00Z | 4.99 | 4 | C5599 | 3.73 | 2017-09-23T06:16:00Z | 4.99 | 10 | C5599 | 3.73 | 2017-09-23T06:16:00Z | 4.99 | 8 | C5599 | 3.73 | 2017-09-23T06:16:00Z | 4.99 | 20
PG&E | 43002 | 0.69583 | 38.3869 | -122.9667 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | DOUG JONES | 101973946 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43002 | 0.69583 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1432 | 2017 | 9 | 24 | 16 | 42 | 17-0081329 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 22574 | 6.0143 | 154_206 | <25mph | <15mph | HFTD - Distribution | D2849 | 0.23 | 2017-09-24T07:00:00Z | 1.01 | 13 | BGAC1 | 6.8 | 2017-09-24T06:05:00Z | 7 | 71 | D2849 | 0.23 | 2017-09-24T07:55:00Z | 1.01 | 25 | BGAC1 | 6.8 | 2017-09-24T06:05:00Z | 7 | 147
PG&E | 43005 | 0.50833 | 39.4845 | -121.3545 | Vegetation | Rural | < 0.25 Acres | Fire Agency | bill lopez cell 530 521-8052 | 100429924 | PACIFIC BELL | 12000 | Fuse | Overhead | Yes | 43005 | 0.50833 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1436 | 2017 | 9 | 27 | 12 | 12 | 17-0082180 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 6370 | 13.6129 | 119_296 | <25mph | <15mph | HFTD - Distribution | TT309 | 3.08 | 2017-09-27T06:45:00Z | 4 | 1 | BNGC1 | 7.37 | 2017-09-27T06:51:00Z | 7 | 2 | TT309 | 3.08 | 2017-09-27T07:45:00Z | 4 | 2 | BNGC1 | 7.37 | 2017-09-27T06:51:00Z | 7 | 4
PG&E | 43005 | 0.79583 | 40.7592 | -123.995 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 103660812 | Unknown | 12000 | Conductor | Overhead | Yes | 43005 | 0.79583 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1437 | 2017 | 9 | 27 | 19 | 6 | 17-0082303 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 35394 | 13.6987 | 184_321 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | KNNC1 | 4.42 | 2017-09-27T06:55:00Z | 10 | 11 |  |  |  | 0 | 0 | KNNC1 | 4.42 | 2017-09-27T07:55:00Z | 10 | 21
PG&E | 43010 | 0.62222 | 38.9102 | -120.9185 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 100110800 | None | 21000 | Other | Overhead | Yes | 43010 | 0.62222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | Third-party caused | Other/Unknown | 1447 | 2017 | 10 | 2 | 14 | 56 | 17-0083516 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 160 | 18.6609 | 157_329 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | E6476 | 6.41 | 2017-10-02T06:55:00Z | 10 | 14 |  |  |  | 0 | 0 | E6476 | 6.41 | 2017-10-02T06:55:00Z | 10 | 31
PG&E | 43010 | 0.67014 | 38.7182 | -120.9756 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101375963 | Unknown | 21000 | Conductor | Overhead | Yes | 43010 | 0.67014 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1448 | 2017 | 10 | 2 | 16 | 5 | 17-0083539 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 4797 | 21.1222 | 203_289 | <25mph | >=15mph | HFTD - Distribution | D7401 | 3.14 | 2017-10-02T06:03:00Z | 4 | 70 | E4740 | 4.79 | 2017-10-02T06:50:00Z | 4 | 92 | D7401 | 3.14 | 2017-10-02T06:03:00Z | 4 | 147 | E4740 | 4.79 | 2017-10-02T07:50:00Z | 4.99 | 190
PG&E | 43012 | 0.9875 | 38.6554 | -120.9934 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101375442 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 43012 | 0.9875 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1452 | 2017 | 10 | 4 | 23 | 42 | 17-0084323 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 7553 | 9.7855 | 188_229 | <25mph | <15mph | HFTD - Distribution | D7401 | 2.11 | 2017-10-04T06:24:00Z | 8.01 | 20 | D7401 | 2.11 | 2017-10-04T06:24:00Z | 8.01 | 106 | D7401 | 2.11 | 2017-10-04T06:24:00Z | 8.01 | 39 | D7401 | 2.11 | 2017-10-04T06:24:00Z | 8.01 | 207
PG&E | 43016 | 0.82222 | 39.7446 | -121.597 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100330456 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 0.82222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1464 | 2017 | 10 | 8 | 19 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 16.9256 | 162_195 | <25mph | >=15mph | HFTD - Distribution | PDEC1 | 1.6 | 2017-10-08T07:00:00Z | 1.01 | 2 | JBGC1 | 5.77 | 2017-10-08T06:13:00Z | 11.01 | 9 | PDEC1 | 1.6 | 2017-10-08T08:00:00Z | 1.01 | 3 | JBGC1 | 5.77 | 2017-10-08T07:13:00Z | 13 | 17
PG&E | 43016 | 0.85764 | 39.6315 | -121.4225 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100347747 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 0.85764 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1465 | 2017 | 10 | 8 | 20 | 35 | 17-0085196 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 181992 | 7.1814 | 174_335 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43016 | 0.88194 | 39.4554 | -121.0498 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100099226 | Unknown | 12000 | Conductor | Overhead | Yes | 43016 | 0.88194 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (Not overhanging, > 12ft) | 1466 | 2017 | 10 | 8 | 21 | 10 | 17-0085261 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 255784 | 12.1371 | 181_329 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43016 | 0.90694 | 39.2595 | -120.9965 | Vegetation | Urban | < 0.25 Acres | Fire Agency | PHILLIP NUNNICK 530 273-3158 INCENDENT # 26264 | 100072730 | PACIFIC BELL | 12000 | Other | Overhead | Yes | 43016 | 0.90694 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1467 | 2017 | 10 | 8 | 21 | 46 | 17-0085308 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 12650 | 29.8567 | 146_261 | 25-40mph | >=15mph | HFTD - Distribution | E9947 | 1.53 | 2017-10-08T06:34:00Z | 3 | 26 | RRRC1 | 7.14 | 2017-10-08T06:13:00Z | 8.01 | 59 | E9947 | 1.53 | 2017-10-08T06:34:00Z | 3 | 52 | RRRC1 | 7.14 | 2017-10-08T07:13:00Z | 8.99 | 117
PG&E | 43016 | 0.92986 | 39.7371 | -121.6464 | Vegetation | Rural | < 3 Meters | Fire Agency | 911 | 103319605 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43016 | 0.92986 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1468 | 2017 | 10 | 8 | 22 | 19 | 17-0085504 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 42839 | 18.3728 | 197_319 | <25mph | >=15mph | HFTD - Distribution | PDEC1 | 1.62 | 2017-10-08T07:00:00Z | 1.01 | 2 | C4565 | 7.55 | 2017-10-08T06:43:00Z | 3 | 8 | PDEC1 | 1.62 | 2017-10-08T08:00:00Z | 1.01 | 3 | C4565 | 7.55 | 2017-10-08T07:53:00Z | 3 | 15
PG&E | 43016 | 0.95417 | 35.5528 | -118.9681 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | span 7/87-7/88, Vedder Tap | Unknown | 115000 | Conductor | Overhead | Yes | 43016 | 0.95417 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1470 | 2017 | 10 | 8 | 22 | 54 | INT-10231 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Conductor | 66311 | 19.9938 | 134_262 | <25mph | >=15mph | HFTD - Transmission |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43016 | 0.95694 | 39.3642 | -121.1131 | Vegetation | Rural | < 3 Meters | Fire Agency | INCIDENT NUMBER 26268 | 100068104 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43016 | 0.95694 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Fell into (No defect) | 1471 | 2017 | 10 | 8 | 22 | 58 | 17-0085355 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 198802 | 32.0506 | 159_257 | 25-40mph | >=15mph | HFTD - Distribution | E3651 | 3.94 | 2017-10-08T06:45:00Z | 3 | 13 | RRRC1 | 4.2 | 2017-10-08T06:13:00Z | 8.01 | 20 | E3651 | 3.94 | 2017-10-08T06:45:00Z | 3 | 25 | RRRC1 | 4.2 | 2017-10-08T07:13:00Z | 8.99 | 39
PG&E | 43017 | 0.043056 | 38.7037 | -120.6725 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 101408485 | Unknown | 21000 | Other | Overhead | Yes | 43017 | 0.043056 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Branch (OverHanging) | 1473 | 2017 | 10 | 9 | 1 | 2 | 17-0085324 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 419843 | 19.6005 | 195_314 | <25mph | >=15mph | HFTD - Distribution | AV185 | 3.98 | 2017-10-09T06:00:00Z | 15.99 | 3 | KPVF | 4.58 | 2017-10-09T06:55:00Z | 33.38 | 28 | AV185 | 3.98 | 2017-10-09T07:30:00Z | 18.99 | 5 | KPVF | 4.58 | 2017-10-09T06:55:00Z | 33.38 | 55
PG&E | 43017 | 0.072917 | 38.8576 | -122.7221 | Vegetation | Rural | < 0.25 Acres | Fire Agency | wink | 103570679 | Unknown | 12000 | Conductor | Overhead | Yes | 43017 | 0.072917 | Contact From Object | N.A. | Vegetation | Electric Facility | Weather | Oct 8/9 wind storm | Other/Unknown | 1477 | 2017 | 10 | 9 | 1 | 45 | 17-0085344 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 219653 | 30.6108 | 158_254 | 25-40mph | >=15mph | HFTD - Distribution | LKRC1 | 3.67 | 2017-10-09T06:05:00Z | 34.99 | 2 | LKRC1 | 3.67 | 2017-10-09T06:05:00Z | 34.99 | 2 | LKRC1 | 3.67 | 2017-10-09T07:05:00Z | 48 | 4 | LKRC1 | 3.67 | 2017-10-09T07:05:00Z | 48 | 4
PG&E | 43018 | 0.56667 | 38.931 | -123.3023 | Vegetation | Rural | < 3 Meters | Customer | N.A. | 102214553 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43018 | 0.56667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1481 | 2017 | 10 | 10 | 13 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 19.0585 | 158_230 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | E4371 | 5.14 | 2017-10-10T06:02:00Z | 10 | 8 |  |  |  | 0 | 0 | BNVC1 | 4.62 | 2017-10-10T07:50:00Z | 13 | 17
PG&E | 43019 | 0.49792 | 38.5015 | -123.0237 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 101974930 | Unknown | 12000 | Conductor | Overhead | Yes | 43019 | 0.49792 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1484 | 2017 | 10 | 11 | 11 | 57 | 17-0086350 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 226925 | 7.6117 | 150_224 | <25mph | <15mph | HFTD - Distribution | D9841 | 2.93 | 2017-10-11T06:47:00Z | 0 | 31 | R30WW | 7.7 | 2017-10-11T06:00:00Z | 2.51 | 39 | D9841 | 2.93 | 2017-10-11T07:47:00Z | 0 | 61 | R30WW | 7.7 | 2017-10-11T08:00:00Z | 3.2 | 75
PG&E | 43021 | 0.43542 | 37.0561 | -122.0206 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Scotts Valley Fire Dept. | 101677721 | Unknown | 21000 | Conductor | Overhead | Yes | 43021 | 0.43542 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Grow Into | 1487 | 2017 | 10 | 13 | 10 | 27 | 17-0087093 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Grow Into | 201996 | 9.9452 | 101_291 | <25mph | <15mph | HFTD - Distribution | C5272 | 2.36 | 2017-10-13T06:52:00Z | 4 | 38 | E6085 | 7.97 | 2017-10-13T06:50:00Z | 10 | 171 | C5272 | 2.36 | 2017-10-13T06:52:00Z | 4 | 75 | E6085 | 7.97 | 2017-10-13T07:35:00Z | 11.01 | 340
PG&E | 43021 | 0.92986 | 39.7648 | -121.6307 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100325368 | PACIFIC BELL | 0 – 750 | Transformer | Overhead | Yes | 43021 | 0.92986 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1489 | 2017 | 10 | 13 | 22 | 19 | 17-0087321 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 7056 | 2.1281 | 157_198 | <25mph | <15mph | HFTD - Distribution | PDEC1 | 0.84 | 2017-10-13T07:00:00Z | 2.01 | 2 | JBGC1 | 7.79 | 2017-10-13T06:13:00Z | 11.01 | 21 | PDEC1 | 0.84 | 2017-10-13T07:00:00Z | 2.01 | 3 | JBGC1 | 7.79 | 2017-10-13T07:13:00Z | 13 | 41
PG&E | 43024 | 0.50694 | 36.5831 | -121.9368 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101781248 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43024 | 0.50694 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | Other/Unknown | 1493 | 2017 | 10 | 16 | 12 | 10 | 17-0087767 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 6313 | 8.6929 | 155_187 | <25mph | <15mph | HFTD - Distribution | E6019 | 2.26 | 2017-10-16T06:15:00Z | 12.01 | 22 | E6019 | 2.26 | 2017-10-16T06:15:00Z | 12.01 | 26 | E6019 | 2.26 | 2017-10-16T07:30:00Z | 12.01 | 42 | E6019 | 2.26 | 2017-10-16T07:30:00Z | 12.01 | 50
PG&E | 43024 | 0.51389 | 37.72 | -122.0687 | Vegetation | Urban | < 3 Meters | Fire Agency | Unknown | 100900970 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43024 | 0.51389 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | no-match | 1494 | 2017 | 10 | 16 | 12 | 20 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 5.0831 | 242_181 | <25mph | <15mph | HFTD - Distribution | E9856 | 0.77 | 2017-10-16T06:58:00Z | 4.99 | 6 | OKSC1 | 6.18 | 2017-10-16T06:33:00Z | 12.01 | 54 | E9856 | 0.77 | 2017-10-16T07:43:00Z | 4.99 | 16 | LTRC1 | 7.87 | 2017-10-16T07:28:00Z | 15.99 | 112
PG&E | 43024 | 0.51806 | 36.6641 | -121.0995 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Nick Shawkey E4462 209-402-1645 Cover Engine from Tuolumne Calaveras Unit | 101689865 | PACIFIC BELL | 0 – 750 | Conductor | Overhead | Yes | 43024 | 0.51806 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1495 | 2017 | 10 | 16 | 12 | 26 | 17-0087754 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 519 | 14.8814 | 173_336 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E1697 | 6.85 | 2017-10-16T06:58:00Z | 4 | 4 |  |  |  | 0 | 0 | E1697 | 6.85 | 2017-10-16T07:43:00Z | 5.99 | 8
PG&E | 43028 | 0.2625 | 39.2922 | -121.0157 | Vegetation | Rural | < 3 Meters | Fire Agency | PHILLIP NUNNINK INCIDENT # 27272 | 100087647 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43028 | 0.2625 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1499 | 2017 | 10 | 20 | 6 | 18 | 17-0088957 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 102410 | 10.8604 | 153_224 | <25mph | <15mph | HFTD - Distribution | E9947 | 3.74 | 2017-10-20T06:59:00Z | 11.01 | 20 | RRRC1 | 5.48 | 2017-10-20T06:13:00Z | 22.01 | 73 | E3651 | 3.59 | 2017-10-20T08:00:00Z | 14.99 | 40 | KGOO | 4.76 | 2017-10-20T07:55:00Z | 35.68 | 145
PG&E | 43028 | 0.57292 | 34.5532 | -120.5303 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 101921492 | Unknown | 12000 | Conductor | Overhead | Yes | 43028 | 0.57292 | Equipment/ Facility Failure | Crossarm | N.A. | N.A. | Unknown |  | Other/Unknown | 1502 | 2017 | 10 | 20 | 13 | 45 | 17-0089249 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Crossarm | 173 | 6.022 | 288_98 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E2332 | 4.19 | 2017-10-20T06:04:00Z | 23 | 21 |  |  |  | 0 | 0 | E2332 | 4.19 | 2017-10-20T06:04:00Z | 23 | 37
PG&E | 43029 | 0.63056 | 39.064 | -122.7765 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102155186 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43029 | 0.63056 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1504 | 2017 | 10 | 21 | 15 | 8 | 17-0089392 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 13374 | 17.4574 | 254_170 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43031 | 0.89167 | 37.3713 | -122.348 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | 100270421 | Unknown | 12000 | Conductor | Overhead | Yes | 43031 | 0.89167 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1507 | 2017 | 10 | 23 | 21 | 24 | 17-0089820 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1768 | 24.5535 | 221_49 | <25mph | >=15mph | HFTD - Distribution | E4551 | 1.61 | 2017-10-23T06:48:00Z | 3 | 6 | LAHC1 | 6.84 | 2017-10-23T06:07:00Z | 7 | 18 | E4551 | 1.61 | 2017-10-23T07:58:00Z | 4 | 12 | E4863 | 4.38 | 2017-10-23T07:49:00Z | 8.99 | 36
PG&E | 43036 | 0.64306 | 39.4516 | -123.3838 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 102209084 | Unknown | 12000 | Conductor | Overhead | Yes | 43036 | 0.64306 | Contact From Object | N.A. | Vehicle | Communication Facility | Human Error |  | no-match | 1510 | 2017 | 10 | 28 | 15 | 26 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 6.6585 | 123_298 | <25mph | <15mph | HFTD - Distribution | E4027 | 3.28 | 2017-10-28T06:58:00Z | 0 | 12 | AT319 | 5.75 | 2017-10-28T06:58:00Z | 2.01 | 24 | E4027 | 3.28 | 2017-10-28T07:58:00Z | 0 | 24 | AT319 | 5.75 | 2017-10-28T07:48:00Z | 2.01 | 48
PG&E | 43039 | 0.87639 | 39.1119 | -122.9163 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Cal Fire | Structure 020/003 | Unknown | 60000 | Conductor | Overhead | Yes | 43039 | 0.87639 | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | no-match | 1513 | 2017 | 10 | 31 | 21 | 2 | INT-10325 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | 50730 | 2.5647 | 140_205 | <25mph | <15mph | HFTD - Transmission |  |  |  | 0 | 0 | E5780 | 6.35 | 2017-10-31T06:56:00Z | 3 | 12 |  |  |  | 0 | 0 | E5780 | 6.35 | 2017-10-31T07:57:00Z | 4 | 24
PG&E | 43047.2998 | 07:11 | 37.7367 | -120.3459 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 101191714 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43047.2998 | 07:11 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1516 | 2017 | 11 | 8 | 7 | 11 | 17-0093414 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 1573 | 5.3951 | 98_320 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43050.5115 | 0.49792 | 35.1191 | -120.3936 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Jordan Dayley ph#929-3911,engine#3467 | 101931190 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43050.5115 | 0.49792 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1518 | 2017 | 11 | 11 | 11 | 57 | 17-0094408 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 29093 | 5.8124 | 170_294 | <25mph | <15mph | HFTD - Distribution | AU609 | 1.13 | 2017-11-11T19:50:00Z | 12.01 | 3 | AU609 | 1.13 | 2017-11-11T19:50:00Z | 12.01 | 9 | AU609 | 1.13 | 2017-11-11T19:50:00Z | 12.01 | 5 | F0412 | 7.06 | 2017-11-11T21:15:00Z | 13 | 17
PG&E | 43059.3562 | 08:32 | 38.7584 | -120.8439 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101389405 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43059.3562 | 08:32 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1522 | 2017 | 11 | 20 | 8 | 32 | 17-0096436 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 12376 | 9.4273 | 228_225 | <25mph | <15mph | HFTD - Distribution | E5691 | 2.94 | 2017-11-20T16:29:00Z | 0 | 12 | E3165 | 6.09 | 2017-11-20T16:06:00Z | 5.99 | 109 | E5691 | 2.94 | 2017-11-20T17:29:00Z | 0 | 24 | E3165 | 6.09 | 2017-11-20T16:06:00Z | 5.99 | 219
PG&E | 43068.7326 | 17:34 | 38.6841 | -120.6546 | Vegetation | Rural | < 3 Meters | Fire Agency | Cal Fire | 101419450 | PACIFIC BELL | 21000 | Conductor | Overhead | Yes | 43068.7326 | 17:34 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1533 | 2017 | 11 | 29 | 17 | 34 | 17-0098456 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 582825 | 9.3832 | 241_163 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | GZFC1 | 7.93 | 2017-11-30T01:17:00Z | 3 | 8 |  |  |  | 0 | 0 | GZFC1 | 7.93 | 2017-11-30T02:17:00Z | 3 | 17
PG&E | 43076.5178 | 12:25 | 34.7115 | -120.1772 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | Pole 015/220 | Unknown | 115000 | Unknown | Overhead | No |  |  | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1534 | 2017 | 12 | 7 | 12 | 25 | 17-0097211 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 10.6388 | 246_130 | <25mph | <15mph | HFTD - Transmission | TT480 | 2.15 | 2017-12-07T20:20:00Z | 25.99 | 1 | SXWC1 | 7.67 | 2017-12-07T20:09:00Z | 27 | 9 | TT480 | 2.15 | 2017-12-07T20:20:00Z | 25.99 | 2 | SXWC1 | 7.67 | 2017-12-07T20:09:00Z | 27 | 23
PG&E | 43083 | 0.71944 | 34.5878 | -120.3566 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101911004 | VERIZON CALIFORNIA | 12000 | Conductor | Overhead | Yes | 43083 | 0.71944 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1538 | 2017 | 12 | 14 | 17 | 16 | 17-0101672 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 2896 | 7.0168 | 253_156 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E2332 | 7.61 | 2017-12-14T08:00:00Z | 15.99 | 7 |  |  |  | 0 | 0 | E2332 | 7.61 | 2017-12-14T08:56:00Z | 22.01 | 24
PG&E | 43085 | 0.49375 | 38.8171 | -122.7041 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Shawn Ohare | 102167231 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43085 | 0.49375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1540 | 2017 | 12 | 16 | 11 | 51 | 17-0102101 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 26120 | 6.1156 | 237_58 | <25mph | <15mph | HFTD - Distribution | LKRC1 | 2.09 | 2017-12-16T07:05:00Z | 17 | 1 | KELC1 | 6.55 | 2017-12-16T07:57:00Z | 23 | 2 | LKRC1 | 2.09 | 2017-12-16T08:05:00Z | 18.99 | 2 | KELC1 | 6.55 | 2017-12-16T07:57:00Z | 23 | 4
PG&E | 43088 | 0.82292 | 40.7271 | -122.3263 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101457738 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43088 | 0.82292 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1545 | 2017 | 12 | 19 | 19 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 14.1308 | 149_336 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | F0355 | 7.84 | 2017-12-19T07:51:00Z | 0 | 6 |  |  |  | 0 | 0 | F0355 | 7.84 | 2017-12-19T08:51:00Z | 0 | 12
PG&E | 43089.3298 | 07:54 | 37.4012 | -122.3606 | Vegetation | Rural | < 3 Meters | Fire Agency | Unknown | 100318864 | PACIFIC BELL | 12000 | Conductor | Overhead | Yes | 43089.3298 | 07:54 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1546 | 2017 | 12 | 20 | 7 | 54 | 17-0102756 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6602 | 25.9102 | 126_285 | 25-40mph | >=15mph | HFTD - Distribution | E4863 | 2.73 | 2017-12-20T15:28:00Z | 17 | 3 | E4863 | 2.73 | 2017-12-20T15:28:00Z | 17 | 13 | E4863 | 2.73 | 2017-12-20T16:38:00Z | 17 | 6 | E4863 | 2.73 | 2017-12-20T16:38:00Z | 17 | 19
PG&E | 43089.586 | 14:03 | 35.6646 | -121.244 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Cal Fire | 103857828 | Unknown | 12000 | Fuse | Overhead | No |  |  | Equipment/ Facility Failure | Insulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1547 | 2017 | 12 | 20 | 14 | 3 | 17-0102828 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 31041 | 21.133 | 172_237 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43098 | 0.68819 | 37.8517 | -122.1586 | Vegetation | Rural | < 3 Meters | Fire Agency | 925-933-1313 | 100488954 | PACIFIC BELL | 12000 | Capacitor Bank | Overhead | No |  |  | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1552 | 2017 | 12 | 29 | 16 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 9.0247 | 140_206 | <25mph | <15mph | HFTD - Distribution | E5555 | 3.67 | 2017-12-29T07:01:00Z | 23 | 31 | E5555 | 3.67 | 2017-12-29T07:01:00Z | 23 | 135 | E5555 | 3.67 | 2017-12-29T07:01:00Z | 23 | 61 | E5555 | 3.67 | 2017-12-29T07:01:00Z | 23 | 263
PG&E | 43116 | 0.60069 | 34.5703 | -119.9645 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101921689 | Verizon | 12000 | Conductor | Overhead | Yes | 43116 | 0.60069 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1556 | 2018 | 1 | 16 | 14 | 25 | 18-0006506 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 23519 | 7.2277 | 144_375 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | RHWC1 | 7.32 | 2018-01-16T07:06:00Z | 21 | 6 |  |  |  | 0 | 0 | RHWC1 | 7.32 | 2018-01-16T08:06:00Z | 21 | 11
PG&E | 43138 | 0.23889 | 40.6543 | -122.5198 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 103922730 | Unknown | 12000 | Conductor | Overhead | Yes | 43138 | 0.23889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1558 | 2018 | 2 | 7 | 5 | 44 | 18-0012073 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 9610 | 7.631 | 149_231 | <25mph | <15mph | HFTD - Distribution | AU138 | 3.45 | 2018-02-07T07:44:00Z | 10 | 5 | MMOC1 | 5.95 | 2018-02-07T08:00:00Z | 27 | 9 | AU138 | 3.45 | 2018-02-07T07:44:00Z | 10 | 9 | MMOC1 | 5.95 | 2018-02-07T09:00:00Z | 28.99 | 15
PG&E | 43138 | 0.38611 | 38.0369 | -120.2096 | Vegetation | Rural | < 3 meters | Fire Agency | Jason Podesta 209-586-3362 | 101038120 | AT&T | 17000 | Conductor | Overhead | Yes | 43138 | 0.38611 | Contact From Object | N.A. | Other | Electric Facility | Human Error | third-party caused | Other/Unknown | 1559 | 2018 | 2 | 7 | 9 | 16 | 18-0012146 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 78738 | 7.4 | 230_191 | <25mph | <15mph | HFTD - Distribution | MOUC1 | 2.73 | 2018-02-07T07:02:00Z | 18.99 | 1 | MOUC1 | 2.73 | 2018-02-07T07:02:00Z | 18.99 | 1 | MOUC1 | 2.73 | 2018-02-07T08:02:00Z | 20 | 2 | MOUC1 | 2.73 | 2018-02-07T08:02:00Z | 20 | 2
PG&E | 43143 | 0.84722 | 39.9395 | -121.6494 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430947 | Unknown | 12000 | Conductor | Overhead | Yes | 43143 | 0.84722 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1561 | 2018 | 2 | 12 | 20 | 20 | 18-0013604 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 149212 | 9.9721 | 208_94 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | CSTC1 | 7.88 | 2018-02-12T07:51:00Z | 5.99 | 19 |  |  |  | 0 | 0 | CSTC1 | 7.88 | 2018-02-12T08:51:00Z | 14.99 | 38
PG&E | 43157 | 0.68958 | 35.5302 | -118.9695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100208194 | Unknown | 21000 | Conductor | Overhead | Yes | 43157 | 0.68958 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | no-match | 1563 | 2018 | 2 | 26 | 16 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | N.A. | 1.8145 | 185_237 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43162 | 0.51042 | 39.1213 | -121.055 | Building | Urban | Structure Only | Unknown | N.A. | 100095928 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43162 | 0.51042 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1564 | 2018 | 3 | 3 | 12 | 15 | 18-0019280 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 15750 | 24.1762 | 136_386 | <25mph | >=15mph | HFTD - Distribution | C5488 | 3.59 | 2018-03-03T07:00:00Z | 10 | 22 | C5488 | 3.59 | 2018-03-03T07:00:00Z | 10 | 77 | C5488 | 3.59 | 2018-03-03T07:00:00Z | 10 | 43 | C5488 | 3.59 | 2018-03-03T07:00:00Z | 10 | 148
PG&E | 43165 | 0.74792 | 38.2811 | -120.8965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | 530-647-5220 | 101238429 | AT&T | 12000 | Conductor | Overhead | Yes | 43165 | 0.74792 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1566 | 2018 | 3 | 6 | 17 | 57 | 18-0020396 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 142000 | 3.7671 | 147_303 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | CFAC1 | 7.07 | 2018-03-06T07:05:00Z | 13 | 4 |  |  |  | 0 | 0 | CFAC1 | 7.07 | 2018-03-06T08:05:00Z | 14 | 8
PG&E | 43185 | 0.7125 | 38.7304 | -122.6215 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102166450 | AT&T | 12000 | Conductor | Overhead | Yes | 43185 | 0.7125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1569 | 2018 | 3 | 26 | 17 | 6 | 18-0026824 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3255 | 4.8801 | 291_104 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43217 | 0.53333 | 39.1717 | -120.8652 | Vegetation | Rural | < 0.25 Acres | Fire Agency | incident # 9960 ph # 530-8850111 | 100075314 | Unknown | 12000 | Conductor | Overhead | Yes | 43217 | 0.53333 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Dead | 1577 | 2018 | 4 | 27 | 12 | 48 | 18-0036310 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 28650 | 0.69339 | 172_185 | <25mph | <15mph | HFTD - Distribution | SETC1 | 1.33 | 2018-04-27T06:28:00Z | 2.01 | 1 | AT999 | 7.76 | 2018-04-27T06:02:00Z | 4 | 14 | SETC1 | 1.33 | 2018-04-27T07:28:00Z | 2.01 | 2 | AT999 | 7.76 | 2018-04-27T07:32:00Z | 4 | 27
PG&E | 43229 | 0.58333 | 38.5908 | -123.3423 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CASE# 18CALNU 005865 | 101998286 | Unknown | 12000 | Conductor | Overhead | Yes | 43229 | 0.58333 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1584 | 2018 | 5 | 9 | 14 | 0 | 18-0039683 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 29522 | 18.7683 | 264_137 | <25mph | >=15mph | HFTD - Distribution | E7021 | 3.81 | 2018-05-09T06:56:00Z | 0 | 6 | HIRWW | 5.18 | 2018-05-09T07:00:00Z | 7.9 | 8 | E7021 | 3.81 | 2018-05-09T07:36:00Z | 8.01 | 12 | E7021 | 3.81 | 2018-05-09T07:36:00Z | 8.01 | 15
PG&E | 43231 | 0.42569 | 38.387 | -122.9856 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101973909 | Unknown | 12000 | Conductor | Overhead | Yes | 43231 | 0.42569 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1585 | 2018 | 5 | 11 | 10 | 13 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 12.8787 | 222_76 | <25mph | <15mph | HFTD - Distribution | D2849 | 0.89 | 2018-05-11T06:52:00Z | 3 | 12 | BGAC1 | 6.17 | 2018-05-11T06:05:00Z | 25.99 | 55 | D2849 | 0.89 | 2018-05-11T06:52:00Z | 3 | 24 | BGAC1 | 6.17 | 2018-05-11T06:05:00Z | 25.99 | 106
PG&E | 43231 | 0.66042 | 40.3385 | -123.9137 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100989912 | Unknown | 12000 | Conductor | Overhead | Yes | 43231 | 0.66042 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1587 | 2018 | 5 | 11 | 15 | 51 | 18-0040389 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 5926 | 13.3837 | 153_302 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43231 | 0.73819 | 38.8218 | -120.9295 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Douglas Ferro. cell-530-708-2715. office-530-677-6192 | 101388939 | AT&T | 21000 | Conductor | Overhead | Yes | 43231 | 0.73819 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1588 | 2018 | 5 | 11 | 17 | 43 | 18-0040415 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 53784 | 7.4837 | 137_253 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PLTC1 | 4.34 | 2018-05-11T06:56:00Z | 2.01 | 19 |  |  |  | 0 | 0 | PLTC1 | 4.34 | 2018-05-11T07:56:00Z | 3 | 38
PG&E | 43239 | 0.82222 | 40.2665 | -122.2727 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103899310 | Unknown | 12000 | Conductor | Overhead | Yes | 43239 | 0.82222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1599 | 2018 | 5 | 19 | 19 | 44 | 18-0042559 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 31980 | 12.5399 | 286_88 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E7114 | 7.1 | 2018-05-19T06:14:00Z | 3 | 4 |  |  |  | 0 | 0 | E7114 | 7.1 | 2018-05-19T08:00:00Z | 3 | 8
PG&E | 43248 | 0.27083 | 40.4382 | -122.3001 | Building | Rural | Structure Only | Unknown | N.A. | 101495757 | Unknown | 0 – 750 | conductor | Overhead | Yes | 43248 | 0.27083 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1610 | 2018 | 5 | 28 | 6 | 30 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 14.1792 | 221_204 | <25mph | <15mph | HFTD - Distribution | AP525 | 2.99 | 2018-05-28T06:55:00Z | 0 | 6 | RRAC1 | 5.38 | 2018-05-28T06:24:00Z | 5.99 | 11 | AP525 | 2.99 | 2018-05-28T07:55:00Z | 0 | 12 | RRAC1 | 5.38 | 2018-05-28T07:24:00Z | 5.99 | 22
PG&E | 43255 | 0.39236 | 35.4593 | -120.4921 | Vegetation | Rural | < 0.25 Acres | Customer | N.A. | 101895513 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43255 | 0.39236 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1624 | 2018 | 6 | 4 | 9 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 10.7972 | 144_375 | <25mph | <15mph | HFTD - Distribution | TT469 | 2.65 | 2018-06-04T06:14:00Z | 5.99 | 1 | TT469 | 2.65 | 2018-06-04T06:14:00Z | 5.99 | 1 | TT469 | 2.65 | 2018-06-04T06:14:00Z | 5.99 | 2 | TT469 | 2.65 | 2018-06-04T06:14:00Z | 5.99 | 2
PG&E | 43256 | 0.42569 | 40.6183 | -122.3173 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JASON COLLINS 530-225-4628 | 101467801 | None | 12000 | Conductor | Overhead | Yes | 43256 | 0.42569 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1631 | 2018 | 6 | 5 | 10 | 13 | 18-0047539 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 277 | 16.4025 | 244_185 | <25mph | >=15mph | HFTD - Distribution | C5599 | 1.27 | 2018-06-05T06:46:00Z | 4 | 8 | RRAC1 | 7.21 | 2018-06-05T06:24:00Z | 12.01 | 9 | C5599 | 1.27 | 2018-06-05T07:36:00Z | 8.01 | 20 | RRAC1 | 7.21 | 2018-06-05T07:24:00Z | 14 | 22
PG&E | 43256 | 0.57292 | 38.5432 | -122.7202 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 102031673 | Unknown | 12000 | Conductor | Overhead | Yes | 43256 | 0.57292 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1633 | 2018 | 6 | 5 | 13 | 45 | 18-0047625 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 40599 | 0.57098 | 268_81 | <25mph | <15mph | HFTD - Distribution | E1553 | 2.52 | 2018-06-05T06:14:00Z | 12.01 | 24 | E1553 | 2.52 | 2018-06-05T06:14:00Z | 12.01 | 86 | E1553 | 2.52 | 2018-06-05T06:14:00Z | 12.01 | 45 | E1553 | 2.52 | 2018-06-05T06:14:00Z | 12.01 | 165
PG&E | 43256 | 0.69861 | 38.7245 | -120.802 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 103667302 | AT&T | 12000 | Conductor | Overhead | Yes | 43256 | 0.69861 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1634 | 2018 | 6 | 5 | 16 | 46 | 18-0047702 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 40590 | 22.3947 | 200_151 | <25mph | >=15mph | HFTD - Distribution | C6129 | 3.23 | 2018-06-05T06:04:00Z | 2.01 | 30 | E3165 | 6.15 | 2018-06-05T07:00:00Z | 5.99 | 50 | C6129 | 3.23 | 2018-06-05T06:04:00Z | 2.01 | 60 | E3165 | 6.15 | 2018-06-05T07:00:00Z | 5.99 | 99
PG&E | 43259 | 0.79375 | 35.154 | -120.594 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101852092 | AT&T | 12000 | Conductor | Overhead | Yes | 43259 | 0.79375 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1644 | 2018 | 6 | 8 | 19 | 3 | 18-0049130 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2473 | 16.6738 | 179_283 | <25mph | >=15mph | HFTD - Distribution | F0194 | 1.62 | 2018-06-08T06:41:00Z | 3 | 24 | E8214 | 6.18 | 2018-06-08T06:27:00Z | 4.99 | 32 | F0194 | 1.62 | 2018-06-08T06:41:00Z | 3 | 45 | E8214 | 6.18 | 2018-06-08T06:27:00Z | 4.99 | 61
PG&E | 43260 | 0.031944 | 35.0745 | -120.5167 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101927520 | Unknown | 12000 | Conductor | Overhead | Yes | 43260 | 0.031944 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1645 | 2018 | 6 | 9 | 0 | 46 | 18-0049171 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 16825 | 8.735 | 190_243 | <25mph | <15mph | HFTD - Distribution | F0412 | 2.71 | 2018-06-09T06:30:00Z | 3 | 16 | F0412 | 2.71 | 2018-06-09T06:30:00Z | 3 | 36 | F0412 | 2.71 | 2018-06-09T06:30:00Z | 3 | 33 | F0412 | 2.71 | 2018-06-09T06:30:00Z | 3 | 73
PG&E | 43261 | 0.72153 | 38.4157 | -122.9184 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101978419 | AT&T | 12000 | Conductor | Overhead | Yes | 43261 | 0.72153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1647 | 2018 | 6 | 10 | 17 | 19 | 18-0049445 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2386 | 16.9824 | 195_239 | <25mph | >=15mph | HFTD - Distribution | GRWWW | 1.77 | 2018-06-10T06:00:00Z | 14.29 | 43 | DENWW | 6.15 | 2018-06-10T06:00:00Z | 16.4 | 106 | GRWWW | 1.77 | 2018-06-10T06:00:00Z | 14.29 | 87 | DENWW | 6.15 | 2018-06-10T06:00:00Z | 16.4 | 208
PG&E | 43262 | 0.74236 | 34.7329 | -120.0861 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103015183 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43262 | 0.74236 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1649 | 2018 | 6 | 11 | 17 | 49 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 13.4941 | 215_100 | <25mph | <15mph | HFTD - Distribution | UCSE | 3.69 | 2018-06-11T06:50:00Z | 7.81 | 7 | FGMC1 | 4.52 | 2018-06-11T06:35:00Z | 20 | 9 | UCSE | 3.69 | 2018-06-11T07:30:00Z | 8.3 | 13 | FGMC1 | 4.52 | 2018-06-11T06:35:00Z | 20 | 17
PG&E | 43264 | 0.47083 | 35.2927 | -120.429 | Vegetation | Rural | < 3 meters | Customer | N.A. | 101884565 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 0.47083 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1654 | 2018 | 6 | 13 | 11 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 4.3035 | 186_288 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43264 | 0.94444 | 38.4901 | -122.6661 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SRS181640125 | 101966547 | Unknown | 12000 | Conductor | Overhead | Yes | 43264 | 0.94444 | Equipment/ Facility Failure | Voltage Regulator | N.A. | N.A. | Unknown |  | Other/Unknown | 1656 | 2018 | 6 | 13 | 22 | 40 | 18-0050782 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Voltage Regulator | 295146 | 15.1291 | 208_252 | <25mph | >=15mph | HFTD - Distribution | E1582 | 2.84 | 2018-06-13T06:43:00Z | 3 | 15 | CRIWW | 6.91 | 2018-06-13T06:00:00Z | 3.8 | 69 | E1582 | 2.84 | 2018-06-13T06:43:00Z | 3 | 30 | CRIWW | 6.91 | 2018-06-13T06:00:00Z | 3.8 | 134
PG&E | 43265 | 0.675 | 40.4419 | -124.0197 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 101005522 | AT&T | 12000 | Conductor | Overhead | Yes | 43265 | 0.675 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1658 | 2018 | 6 | 14 | 16 | 12 | 18-0051223 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 19601 | 5.2934 | 177_272 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43266 | 0.12222 | 37.4869 | -122.4223 | Vegetation | Rural | < 0.25 Acres | Utility: PG&E | N.A. | Pole 10/5 | None | 60000 | Conductor | Overhead | Yes | 43266 | 0.12222 | Contamination | N.A. | N.A. | N.A. | Unknown |  | no-match | 1659 | 2018 | 6 | 15 | 2 | 56 | INT-11115 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 0 | 11.9619 | 163_178 | <25mph | <15mph | HFTD - Transmission | C3295 | 3.73 | 2018-06-15T06:23:00Z | 3 | 1 | HSPC1 | 5.28 | 2018-06-15T06:18:00Z | 18.99 | 78 | C3295 | 3.73 | 2018-06-15T07:13:00Z | 8.99 | 4 | HSPC1 | 5.28 | 2018-06-15T07:18:00Z | 21 | 154
PG&E | 43266 | 0.41042 | 37.1986 | -119.4709 | Vegetation | Rural | < 0.25 Acres | Fire Agency | RANCHARIA ENGINE 4255 USFS ENG 52 | 101058060 | Unknown | 12000 | Conductor | Overhead | Yes | 43266 | 0.41042 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1660 | 2018 | 6 | 15 | 9 | 51 | 18-0051354 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 35146 | 5.1841 | 225_90 | <25mph | <15mph | HFTD - Distribution | NFRC1 | 3.06 | 2018-06-15T06:55:00Z | 8.01 | 1 | NFRC1 | 3.06 | 2018-06-15T06:55:00Z | 8.01 | 1 | NFRC1 | 3.06 | 2018-06-15T06:55:00Z | 8.01 | 2 | NFRC1 | 3.06 | 2018-06-15T06:55:00Z | 8.01 | 2
PG&E | 43266 | 0.42014 | 38.6238 | -121.0221 | Vegetation | Rural | < 3 meters | Customer | N.A. | 101376538 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43266 | 0.42014 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | no-match | 1661 | 2018 | 6 | 15 | 10 | 5 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | N.A. | 11.5397 | 244_164 | <25mph | <15mph | HFTD - Distribution | E8856 | 3.9 | 2018-06-15T07:00:00Z | 0 | 13 | FSLC1 | 7.47 | 2018-06-15T06:25:00Z | 9.26 | 57 | E8856 | 3.9 | 2018-06-15T08:00:00Z | 0 | 25 | FSLC1 | 7.47 | 2018-06-15T07:25:00Z | 10.63 | 112
PG&E | 43267 | 0.83194 | 37.907 | -121.8063 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 100483910 | Unknown | 21000 | Conductor | Overhead | Yes | 43267 | 0.83194 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1670 | 2018 | 6 | 16 | 19 | 58 | 18-0051687 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 3322 | 12.5495 | 235_188 | <25mph | <15mph | HFTD - Distribution | PG071 | 2.97 | 2018-06-16T06:00:00Z | 33.11 | 14 | PG071 | 2.97 | 2018-06-16T06:00:00Z | 33.11 | 106 | PG071 | 2.97 | 2018-06-16T06:00:00Z | 33.11 | 26 | PG071 | 2.97 | 2018-06-16T06:00:00Z | 33.11 | 219
PG&E | 43267 | 0.85625 | 38.0494 | -122.206 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Contra Costa FD | 101423963 | Unknown | 21000 | Conductor | Overhead | Yes | 43267 | 0.85625 | Wire-Wire Contact | N.A. | N.A. | N.A. | Unknown |  | no-match | 1671 | 2018 | 6 | 16 | 20 | 33 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Unknown | N.A. | 15.0089 | 147_245 | <25mph | >=15mph | HFTD - Distribution | DPXC1 | 2.96 | 2018-06-16T06:42:00Z | 20.98 | 15 | PG064 | 7.4 | 2018-06-16T06:10:00Z | 35.95 | 95 | DPXC1 | 2.96 | 2018-06-16T07:30:00Z | 20.98 | 28 | PG064 | 7.4 | 2018-06-16T06:10:00Z | 35.95 | 190
PG&E | 43270 | 0.01875 | 38.7604 | -120.8224 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101388356 | Unknown | 12000 | Conductor | Overhead | Yes | 43270 | 0.01875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1675 | 2018 | 6 | 19 | 0 | 27 | 18-0052111 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 141652 | 1.004 | 164_234 | <25mph | <15mph | HFTD - Distribution | E5691 | 1.82 | 2018-06-19T06:59:00Z | 0 | 12 | TS903 | 6.68 | 2018-06-19T06:37:00Z | 2.01 | 75 | E5691 | 1.82 | 2018-06-19T07:59:00Z | 0 | 24 | E3165 | 5.03 | 2018-06-19T07:41:00Z | 2.01 | 147
PG&E | 43270 | 0.42847 | 38.5918 | -120.7097 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101395943 | AT&T | 21000 | Conductor | Overhead | Yes | 43270 | 0.42847 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1677 | 2018 | 6 | 19 | 10 | 17 | 18-0052222 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 4094 | 23.6519 | 147_242 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43270 | 0.61181 | 37.2158 | -119.6811 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JOE QUINSTORFF 559-683-8008 | 103372829 | Unknown | 21000 | Conductor | Overhead | Yes | 43270 | 0.61181 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1679 | 2018 | 6 | 19 | 14 | 41 | 18-0052327 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 123838 | 7.0997 | 215_103 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E5766 | 6.85 | 2018-06-19T06:58:00Z | 0 | 20 |  |  |  | 0 | 0 | E5766 | 6.85 | 2018-06-19T07:53:00Z | 0 | 33
PG&E | 43271 | 0.35417 | 34.7561 | -120.2281 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101858890 | None | 0 – 750 | Conductor | Overhead | Yes | 43271 | 0.35417 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1680 | 2018 | 6 | 20 | 8 | 30 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 12.0354 | 183_228 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43272 | 0.79028 | 35.1224 | -120.3938 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101878933 | AT&T | 12000 | Conductor | Overhead | Yes | 43272 | 0.79028 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1683 | 2018 | 6 | 21 | 18 | 58 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 10.7167 | 212_272 | <25mph | <15mph | HFTD - Distribution | AU609 | 1.36 | 2018-06-21T06:48:00Z | 0 | 4 | F0412 | 7.22 | 2018-06-21T07:00:00Z | 4 | 11 | AU609 | 1.36 | 2018-06-21T07:48:00Z | 0 | 8 | F0412 | 7.22 | 2018-06-21T08:00:00Z | 4 | 21
PG&E | 43273 | 0.73889 | 37.2485 | -119.5625 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Madera County | 101117749 | None | 0 – 750 | Conductor | Overhead | Yes | 43273 | 0.73889 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1686 | 2018 | 6 | 22 | 17 | 44 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 4.1836 | 235_60 | <25mph | <15mph | HFTD - Distribution | NFRC1 | 3.29 | 2018-06-22T06:55:00Z | 8.01 | 1 | NFRC1 | 3.29 | 2018-06-22T06:55:00Z | 8.01 | 42 | NFRC1 | 3.29 | 2018-06-22T07:55:00Z | 8.01 | 2 | NFRC1 | 3.29 | 2018-06-22T07:55:00Z | 8.01 | 84
PG&E | 43274 | 0.39653 | 40.8632 | -122.3962 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | RYAN MEANS 530-238-2416 | 101472252 | AT&T | 12000 | Conductor | Overhead | Yes | 43274 | 0.39653 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1688 | 2018 | 6 | 23 | 9 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 5.2159 | 191_283 | <25mph | <15mph | HFTD - Distribution | CTANT | 1.62 | 2018-06-23T06:15:00Z | 9.93 | 4 | SLFC1 | 4.17 | 2018-06-23T06:19:00Z | 21 | 9 | CTANT | 1.62 | 2018-06-23T06:15:00Z | 9.93 | 7 | SLFC1 | 4.17 | 2018-06-23T06:19:00Z | 21 | 17
PG&E | 43278 | 0.78194 | 40.218 | -123.7989 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TJ alderpoint fire | 100990381 | Unknown | 12000 | Conductor | Overhead | Yes | 43278 | 0.78194 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1700 | 2018 | 6 | 27 | 18 | 46 | 18-0055205 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 21357 | 11.02 | 175_322 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | ERCC1 | 5.65 | 2018-06-27T06:28:00Z | 8.99 | 1 |  |  |  | 0 | 0 | ERCC1 | 5.65 | 2018-06-27T06:28:00Z | 8.99 | 2
PG&E | 43278 | 0.88819 | 39.8714 | -123.7119 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 103775148 | Verizon | 12000 | Conductor | Overhead | Yes | 43278 | 0.88819 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1701 | 2018 | 6 | 27 | 21 | 19 | 18-0055211 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 75544 | 8.4543 | 226_238 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43279 | 0.51875 | 38.5982 | -121.0081 | Vegetation | Rural | < 0.25 Acres | Fire Agency | John Reis, 530-622-3858 | 101376954 | Unknown | 21000 | Conductor | Overhead | Yes | 43279 | 0.51875 | Contact From Object | N.A. | Vehicle | Electric Facility | Human Error | third-party caused | Other/Unknown | 1702 | 2018 | 6 | 28 | 12 | 27 | 18-0055479 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 24671 | 4.0055 | 121_265 | <25mph | <15mph | HFTD - Distribution | E8856 | 2.62 | 2018-06-28T07:00:00Z | 7 | 13 | BENC1 | 4.05 | 2018-06-28T06:59:00Z | 8.01 | 28 | E8856 | 2.62 | 2018-06-28T07:15:00Z | 7 | 25 | BENC1 | 4.05 | 2018-06-28T06:59:00Z | 8.01 | 55
PG&E | 43279 | 0.82014 | 38.5575 | -122.5043 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Brian Coffee | 102267918 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43279 | 0.82014 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1704 | 2018 | 6 | 28 | 19 | 41 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 6.6653 | 169_327 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43281 | 0.46806 | 39.3621 | -121.0809 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ENGINEER YUREK | 100091354 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 0.46806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1713 | 2018 | 6 | 30 | 11 | 14 | 18-0055945 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5724 | 7.068 | 177_318 | <25mph | <15mph | HFTD - Distribution | E3651 | 2.44 | 2018-06-30T06:30:00Z | 2.01 | 13 | RRRC1 | 4.49 | 2018-06-30T06:13:00Z | 7 | 28 | E3651 | 2.44 | 2018-06-30T07:50:00Z | 3 | 25 | PG030 | 6.5 | 2018-06-30T08:00:00Z | 10.51 | 54
PG&E | 43281 | 0.92917 | 40.6043 | -122.24 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101469808 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43281 | 0.92917 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1716 | 2018 | 6 | 30 | 22 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 5.9401 | 123_268 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | C5599 | 4.85 | 2018-06-30T06:17:00Z | 12.01 | 10 |  |  |  | 0 | 0 | C5599 | 4.85 | 2018-06-30T06:17:00Z | 12.01 | 23
PG&E | 43281 | 0.94167 | 39.1141 | -121.077 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Matt Wallen (530) 277-3312 Incident # NEU015486 | 100105380 | AT&T | 12000 | Conductor | Overhead | Yes | 43281 | 0.94167 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1717 | 2018 | 6 | 30 | 22 | 36 | 18-0056039 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 8004 | 13.4658 | 240_131 | <25mph | <15mph | HFTD - Distribution | E1789 | 3.68 | 2018-06-30T06:30:00Z | 4 | 21 | E1789 | 3.68 | 2018-06-30T06:30:00Z | 4 | 64 | E1789 | 3.68 | 2018-06-30T07:48:00Z | 4 | 41 | AT999 | 5.18 | 2018-06-30T07:57:00Z | 8.99 | 121
PG&E | 43282 | 0.015972 | 40.2697 | -124.2386 | Vegetation | Rural | < 3 meters | Fire Agency | fire chief | 100986962 | Unknown | 12000 | Conductor | Overhead | Yes | 43282 | 0.015972 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1718 | 2018 | 7 | 1 | 0 | 23 | 18-0056043 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 22872 | 8.1598 | 289_99 | <25mph | <15mph | HFTD - Distribution | PTEC1 | 1.7 | 2018-07-01T06:08:00Z | 44.98 | 1 | PTEC1 | 1.7 | 2018-07-01T06:08:00Z | 44.98 | 1 | PTEC1 | 1.7 | 2018-07-01T06:08:00Z | 44.98 | 2 | PTEC1 | 1.7 | 2018-07-01T06:08:00Z | 44.98 | 2
PG&E | 43282 | 0.03125 | 38.8842 | -120.847 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Brian Mackwood (530)708-2711 | 100109003 | None | 21000 | Conductor | Overhead | Yes | 43282 | 0.03125 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1719 | 2018 | 7 | 1 | 0 | 45 | 18-0056045 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 5760 | 11.7533 | 196_314 | <25mph | <15mph | HFTD - Distribution | PG033 | 2.7 | 2018-07-01T07:00:00Z | 3.29 | 33 | BDMC1 | 7.75 | 2018-07-01T06:36:00Z | 10 | 41 | PG033 | 2.7 | 2018-07-01T07:00:00Z | 3.29 | 63 | BDMC1 | 7.75 | 2018-07-01T07:36:00Z | 21 | 79
PG&E | 43282 | 0.34236 | 39.4154 | -121.5122 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100430344 | AT&T | 12000 | Conductor | Overhead | Yes | 43282 | 0.34236 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1720 | 2018 | 7 | 1 | 8 | 13 | 18-0056061 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 7848 | 1.9617 | 207_277 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | TT309 | 6.67 | 2018-07-01T06:45:00Z | 5.99 | 2 |  |  |  | 0 | 0 | TT309 | 6.67 | 2018-07-01T06:45:00Z | 5.99 | 4
PG&E | 43283 | 0.21667 | 38.6092 | -122.4595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 707-967-1467 | 102252558 | AT&T | 21000 | Conductor | Overhead | Yes | 43283 | 0.21667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1722 | 2018 | 7 | 2 | 5 | 12 | 18-0056178 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 403 | 22.7012 | 147_383 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | PG045 | 7.68 | 2018-07-02T06:30:00Z | 5.48 | 11 |  |  |  | 0 | 0 | PG045 | 7.68 | 2018-07-02T07:50:00Z | 10.09 | 21
PG&E | 43285 | 0.64306 | 39.5538 | -123.4255 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102196183 | Verizon | 12000 | Conductor | Overhead | Yes | 43285 | 0.64306 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1726 | 2018 | 7 | 4 | 15 | 26 | 18-0056986 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 32269 | 8.4554 | 178_317 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43290 | 0.31042 | 35.0785 | -120.3948 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101861366 | Unknown | 12000 | Conductor | Overhead | Yes | 43290 | 0.31042 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1735 | 2018 | 7 | 9 | 7 | 27 | 18-0057904 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 21045 | 17.9744 | 216_205 | <25mph | >=15mph | HFTD - Distribution | AU609 | 1.69 | 2018-07-09T06:48:00Z | 0 | 4 | AU609 | 1.69 | 2018-07-09T06:48:00Z | 0 | 4 | AU609 | 1.69 | 2018-07-09T07:48:00Z | 0 | 8 | F0412 | 5.4 | 2018-07-09T07:55:00Z | 1.01 | 10
PG&E | 43291 | 0.28125 | 37.085 | -122.0744 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 101675262 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43291 | 0.28125 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | no-match | 1737 | 2018 | 7 | 10 | 6 | 45 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | N.A. | 11.2401 | 171_309 | <25mph | <15mph | HFTD - Distribution | E1576 | 2.63 | 2018-07-10T06:58:00Z | 4 | 39 | BNDC1 | 6.27 | 2018-07-10T06:50:00Z | 15.99 | 103 | E1576 | 2.63 | 2018-07-10T07:03:00Z | 4 | 81 | BNDC1 | 6.27 | 2018-07-10T07:50:00Z | 15.99 | 198
PG&E | 43294 | 0.45764 | 39.4836 | -123.7924 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102184869 | AT&T | 12000 | Conductor | Overhead | Yes | 43294 | 0.45764 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1742 | 2018 | 7 | 13 | 10 | 59 | 18-0059522 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 328 | 9.5867 | 192_286 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43295 | 0.48194 | 38.4026 | -122.5489 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 103141862 | Verizon | 12000 | Conductor | Overhead | Yes | 43295 | 0.48194 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1745 | 2018 | 7 | 14 | 11 | 34 | 18-0059821 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 6426 | 39.2776 | 179_223 | 25-40mph | >=15mph | HFTD - Distribution | KENWW | 0.52 | 2018-07-14T06:00:00Z | 9.19 | 2 | BVYWW | 5.16 | 2018-07-14T06:00:00Z | 11.79 | 16 | KENWW | 0.52 | 2018-07-14T06:00:00Z | 9.19 | 3 | BVYWW | 5.16 | 2018-07-14T06:00:00Z | 11.79 | 29
PG&E | 43295 | 0.52778 | 38.5793 | -122.878 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103122744 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 0.52778 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1746 | 2018 | 7 | 14 | 12 | 40 | 18-0059799 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 20804 | 30.5596 | 202_188 | 25-40mph | >=15mph | HFTD - Distribution | R08WW | 2.26 | 2018-07-14T06:00:00Z | 8.59 | 11 | DRYWW | 5.04 | 2018-07-14T06:00:00Z | 10.69 | 57 | R08WW | 2.26 | 2018-07-14T06:00:00Z | 8.59 | 20 | DRYWW | 5.04 | 2018-07-14T06:00:00Z | 10.69 | 103
PG&E | 43295 | 0.53889 | 39.2093 | -121.197 | Vegetation | Rural | < 0.25 Acres | Fire Agency | FIRE DEPT LEFT BEFORE UPTAINING THAT INFO | 100086833 | None | 21000 | Conductor | Overhead | Yes | 43295 | 0.53889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1747 | 2018 | 7 | 14 | 12 | 56 | 18-0059841 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 3720 | 12.5941 | 207_189 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | RRRC1 | 7.78 | 2018-07-14T06:13:00Z | 4.99 | 35 |  |  |  | 0 | 0 | RRRC1 | 7.78 | 2018-07-14T07:13:00Z | 5.99 | 70
PG&E | 43295 | 0.61389 | 38.9524 | -121.2467 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100035452 | AT&T | 12000 | Conductor | Overhead | Yes | 43295 | 0.61389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1748 | 2018 | 7 | 14 | 14 | 44 | 18-0059847 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2430 | 1.1884 | 81_323 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | LICC1 | 5.05 | 2018-07-14T06:13:00Z | 4 | 6 |  |  |  | 0 | 0 | E6168 | 5.24 | 2018-07-14T07:13:00Z | 4 | 11
PG&E | 43295 | 0.90139 | 36.3314 | -121.8829 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | ASSISTED JAIMIE | 101672234 | Unknown | 12000 | Conductor | Overhead | Yes | 43295 | 0.90139 | Contact From Object | N.A. | Animal | Pole | Other | bull rubbing pole | Other/Unknown | 1751 | 2018 | 7 | 14 | 21 | 38 | 18-0059900 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 493416 | 9.1931 | 133_262 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43298 | 0.46597 | 35.6986 | -120.9777 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | dennis byrnes 8055434244 inc # = 18ca-slu-007640 | 103886652 | Unknown | 21000 | Conductor | Overhead | Yes | 43298 | 0.46597 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1755 | 2018 | 7 | 17 | 11 | 11 | 18-0060637 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 9121 | 12.6745 | 199_230 | <25mph | <15mph | HFTD - Distribution | E9175 | 3.58 | 2018-07-17T06:15:00Z | 4.99 | 12 | D4060 | 6.73 | 2018-07-17T06:25:00Z | 8.01 | 17 | E9175 | 3.58 | 2018-07-17T07:25:00Z | 5.99 | 24 | D4060 | 6.73 | 2018-07-17T07:10:00Z | 8.99 | 34
PG&E | 43298 | 0.49861 | 37.2217 | -121.6778 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Luis Morado state arson fire fighter | 100601345 | Unknown | 12000 | Conductor | Overhead | Yes | 43298 | 0.49861 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1756 | 2018 | 7 | 17 | 11 | 58 | 18-0060617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 5865 | 10.4828 | 287_98 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | C7794 | 7.07 | 2018-07-17T06:00:00Z | 1.01 | 23 |  |  |  | 0 | 0 | C7794 | 7.07 | 2018-07-17T06:00:00Z | 1.01 | 45
PG&E | 43298 | 0.70347 | 38.3955 | -122.9212 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 101978449 | AT&T | 12000 | Conductor | Overhead | Yes | 43298 | 0.70347 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1759 | 2018 | 7 | 17 | 16 | 53 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.2118 | 216_106 | <25mph | <15mph | HFTD - Distribution | DUTWW | 3.53 | 2018-07-17T07:00:00Z | 9.19 | 36 | DUTWW | 3.53 | 2018-07-17T07:00:00Z | 9.19 | 80 | DUTWW | 3.53 | 2018-07-17T08:00:00Z | 10.69 | 68 | DUTWW | 3.53 | 2018-07-17T08:00:00Z | 10.69 | 154
PG&E | 43298 | 0.81944 | 40.5927 | -122.4886 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101477082 | AT&T | 12000 | Conductor | Overhead | Yes | 43298 | 0.81944 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | Other/Unknown | 1760 | 2018 | 7 | 17 | 19 | 40 | 18-0060840 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 30162 | 6.2637 | 134_236 | <25mph | <15mph | HFTD - Distribution | MMOC1 | 1.8 | 2018-07-17T07:00:00Z | 10 | 7 | MMOC1 | 1.8 | 2018-07-17T07:00:00Z | 10 | 13 | MMOC1 | 1.8 | 2018-07-17T07:00:00Z | 10 | 12 | MMOC1 | 1.8 | 2018-07-17T07:00:00Z | 10 | 23
PG&E | 43299 | 0.051389 | 38.3671 | -120.5578 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101247987 | Unknown | 12000 | Conductor | Overhead | Yes | 43299 | 0.051389 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1761 | 2018 | 7 | 18 | 1 | 14 | 18-0060882 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6420 | 5.3917 | 170_196 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | ESPC1 | 6.8 | 2018-07-18T06:13:00Z | 8.01 | 14 |  |  |  | 0 | 0 | ESPC1 | 6.8 | 2018-07-18T06:13:00Z | 8.01 | 28
PG&E | 43300 | 0.0055556 | 36.9372 | -119.4557 | Vegetation | Rural | < 0.25 Acres | Fire Agency | incident # 10559 | 100677019 | AT&T | 12000 | Conductor | Overhead | Yes | 43300 | 0.0055556 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1766 | 2018 | 7 | 19 | 0 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 5.6181 | 137_382 | <25mph | <15mph | HFTD - Distribution | FCHC1 | 3.86 | 2018-07-19T07:00:00Z | 5.99 | 2 | FCHC1 | 3.86 | 2018-07-19T07:00:00Z | 5.99 | 2 | FCHC1 | 3.86 | 2018-07-19T07:00:00Z | 5.99 | 3 | FCHC1 | 3.86 | 2018-07-19T07:00:00Z | 5.99 | 3
PG&E | 43300 | 0.22847 | 40.1918 | -123.5373 | Vegetation | Rural | < 0.25 Acres | Fire Agency | fire captain | 103909820 | Unknown | 12000 | Conductor | Overhead | Yes | 43300 | 0.22847 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1767 | 2018 | 7 | 19 | 5 | 29 | 18-0061308 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 73380 | 10.1867 | 219_259 | <25mph | <15mph | HFTD - Distribution | ALDC1 | 2.86 | 2018-07-19T06:51:00Z | 4 | 1 | ALDC1 | 2.86 | 2018-07-19T06:51:00Z | 4 | 1 | ALDC1 | 2.86 | 2018-07-19T07:51:00Z | 4 | 2 | ALDC1 | 2.86 | 2018-07-19T07:51:00Z | 4 | 2
PG&E | 43301 | 0.27153 | 37.4318 | -119.9441 | Vegetation | Rural | < 0.25 Acres | Fire Agency | ZACH RUTHERFORD 209-966-3621 | 103909942 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43301 | 0.27153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1771 | 2018 | 7 | 20 | 6 | 31 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 3.6688 | 186_294 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E9110 | 6.48 | 2018-07-20T06:47:00Z | 5.99 | 9 |  |  |  | 0 | 0 | E9110 | 6.48 | 2018-07-20T07:02:00Z | 5.99 | 18
PG&E | 43302 | 0.015972 | 38.6927 | -120.7921 | Vegetation | Rural | < 3 meters | Fire Agency | CAMINO | 101415904 | AT&T | 12000 | Conductor | Overhead | Yes | 43302 | 0.015972 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1774 | 2018 | 7 | 21 | 0 | 23 | 18-0062206 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 107552 | 6.3124 | 254_141 | <25mph | <15mph | HFTD - Distribution | C6129 | 3.07 | 2018-07-21T06:24:00Z | 2.01 | 30 | C6129 | 3.07 | 2018-07-21T06:24:00Z | 2.01 | 60 | C6129 | 3.07 | 2018-07-21T06:24:00Z | 2.01 | 60 | E3165 | 7.94 | 2018-07-21T07:58:00Z | 3 | 120
PG&E | 43302 | 0.61875 | 35.6846 | -120.9427 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | 101943190 | Unknown | 21000 | Conductor | Overhead | Yes | 43302 | 0.61875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1775 | 2018 | 7 | 21 | 14 | 51 | 18-0062364 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 110814 | 23.7634 | 150_252 | <25mph | >=15mph | HFTD - Distribution | TABC1 | 2.21 | 2018-07-21T06:07:00Z | 3 | 1 | E9175 | 5.16 | 2018-07-21T06:50:00Z | 4 | 18 | TABC1 | 2.21 | 2018-07-21T06:07:00Z | 3 | 2 | E9175 | 5.16 | 2018-07-21T06:50:00Z | 4 | 35
PG&E | 43302 | 0.67778 | 40.3439 | -123.7092 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 101009789 | Unknown | 12000 | Conductor | Overhead | Yes | 43302 | 0.67778 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1776 | 2018 | 7 | 21 | 16 | 16 | 18-0062375 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 5184 | 3.1025 | 260_163 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43304 | 0.63264 | 39.4911 | -123.7844 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 102184598 | Yes | 12000 | Conductor | Overhead | Yes | 43304 | 0.63264 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1781 | 2018 | 7 | 23 | 15 | 11 | 18-0062842 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 44840 | 2.821 | 202_111 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43304 | 0.72708 | 39.734 | -121.4965 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103843963 | AT&T | 12000 | Conductor | Overhead | Yes | 43304 | 0.72708 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1782 | 2018 | 7 | 23 | 17 | 27 | 18-0062874 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 183629 | 3.7692 | 85_370 | <25mph | <15mph | HFTD - Distribution | JBGC1 | 0.42 | 2018-07-23T06:13:00Z | 5.99 | 1 | JBGC1 | 0.42 | 2018-07-23T06:13:00Z | 5.99 | 3 | JBGC1 | 0.42 | 2018-07-23T07:13:00Z | 11.01 | 2 | JBGC1 | 0.42 | 2018-07-23T07:13:00Z | 11.01 | 5
PG&E | 43305 | 0.57431 | 39.0606 | -123.4456 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102212216 | Unknown | 12000 | Conductor | Overhead | Yes | 43305 | 0.57431 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1786 | 2018 | 7 | 24 | 13 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 15.1063 | 147_333 | <25mph | >=15mph | HFTD - Distribution | E1763 | 3.79 | 2018-07-24T06:13:00Z | 1.01 | 4 | BNVC1 | 7.27 | 2018-07-24T06:50:00Z | 4 | 8 | E1763 | 3.79 | 2018-07-24T06:13:00Z | 1.01 | 8 | BNVC1 | 7.27 | 2018-07-24T06:50:00Z | 4 | 17
PG&E | 43306 | 0.029167 | 39.7791 | -121.6173 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 100327443 | Unknown | 12000 | Conductor | Overhead | Yes | 43306 | 0.029167 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1788 | 2018 | 7 | 25 | 0 | 42 | 18-0063320 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6742 | 10.3521 | 178_335 | <25mph | <15mph | HFTD - Distribution | PDEC1 | 1.8 | 2018-07-25T07:00:00Z | 1.01 | 2 | JBGC1 | 7.44 | 2018-07-25T06:13:00Z | 10 | 21 | PDEC1 | 1.8 | 2018-07-25T08:00:00Z | 1.01 | 3 | JBGC1 | 7.44 | 2018-07-25T07:13:00Z | 10 | 37
PG&E | 43308 | 0.96667 | 37.18 | -122.029 | Vegetation | Rural | < 3 meters | Fire Agency | Jeremy Wise 408-378-4010 Incident # C182080066 | 100518365 | Unknown | 12000 | Conductor | Overhead | Yes | 43308 | 0.96667 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1793 | 2018 | 7 | 27 | 23 | 12 | 18-0064525 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 30475 | 20.4003 | 138_204 | <25mph | >=15mph | HFTD - Distribution | PG050 | 2.33 | 2018-07-27T06:10:00Z | 12.93 | 11 | PG050 | 2.33 | 2018-07-27T06:10:00Z | 12.93 | 125 | PG050 | 2.33 | 2018-07-27T06:10:00Z | 12.93 | 21 | PG050 | 2.33 | 2018-07-27T06:10:00Z | 12.93 | 240
PG&E | 43309 | 0.28542 | 38.7473 | -120.7866 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 101418155 | AT&T | 21000 | Conductor | Overhead | Yes | 43309 | 0.28542 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1794 | 2018 | 7 | 28 | 6 | 51 | 18-0064545 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 15429 | 8.664 | 173_337 | <25mph | <15mph | HFTD - Distribution | E5691 | 0.5 | 2018-07-28T06:01:00Z | 2.01 | 16 | E3165 | 4.37 | 2018-07-28T06:55:00Z | 4.99 | 54 | E5691 | 0.5 | 2018-07-28T06:01:00Z | 2.01 | 25 | E3165 | 4.37 | 2018-07-28T07:35:00Z | 8.01 | 97
PG&E | 43310 | 0.48542 | 39.0968 | -123.5018 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 102177329 | Unknown | 12000 | Conductor | Overhead | Yes | 43310 | 0.48542 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1796 | 2018 | 7 | 29 | 11 | 39 | 18-0064779 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4329 | 15.5342 | 159_261 | <25mph | >=15mph | HFTD - Distribution | E1763 | 2 | 2018-07-29T06:59:00Z | 0 | 2 | E1763 | 2 | 2018-07-29T06:59:00Z | 0 | 2 | E1763 | 2 | 2018-07-29T07:29:00Z | 2.01 | 6 | E1763 | 2 | 2018-07-29T07:29:00Z | 2.01 | 6
PG&E | 43310 | 0.72847 | 38.5777 | -120.8556 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101383255 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43310 | 0.72847 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1797 | 2018 | 7 | 29 | 17 | 29 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 7.4096 | 136_309 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | BENC1 | 4.31 | 2018-07-29T06:59:00Z | 4.99 | 30 |  |  |  | 0 | 0 | BENC1 | 4.31 | 2018-07-29T07:59:00Z | 4.99 | 58
PG&E | 43311 | 0.60833 | 38.1987 | -120.3638 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | NICK WEBB ( 209) 532-7424 | 103336176 | Unknown | 17000 | Conductor | Overhead | Yes | 43311 | 0.60833 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1800 | 2018 | 7 | 30 | 14 | 36 | 18-0065131 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 18530 | 10.6529 | 209_280 | <25mph | <15mph | HFTD - Distribution | E8204 | 0 | 2018-07-30T06:48:00Z | 0 | 4 | E9838 | 7.59 | 2018-07-30T06:39:00Z | 4.99 | 20 | E8204 | 0 | 2018-07-30T07:48:00Z | 0 | 7 | E9838 | 7.59 | 2018-07-30T06:39:00Z | 4.99 | 37
PG&E | 43312 | 0.33125 | 38.9559 | -122.7274 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102162351 | AT&T | 12000 | Conductor | Overhead | Yes | 43312 | 0.33125 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1803 | 2018 | 7 | 31 | 7 | 57 | 18-0065276 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 89832 | 5.1967 | 206_271 | <25mph | <15mph | HFTD - Distribution | KELC1 | 3.24 | 2018-07-31T06:57:00Z | 17 | 1 | KELC1 | 3.24 | 2018-07-31T06:57:00Z | 17 | 1 | KELC1 | 3.24 | 2018-07-31T07:57:00Z | 18.99 | 2 | KELC1 | 3.24 | 2018-07-31T07:57:00Z | 18.99 | 2
PG&E | 43313 | 0.74861 | 38.9155 | -122.799 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102156435 | Unknown | 12000 | Conductor | Overhead | Yes | 43313 | 0.74861 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1805 | 2018 | 8 | 1 | 17 | 58 | 18-0065921 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 2744 | 11.3872 | 85_357 | <25mph | <15mph | HFTD - Distribution | E4393 | 3.97 | 2018-08-01T06:15:00Z | 7 | 4 | KELC1 | 4.99 | 2018-08-01T06:57:00Z | 14.99 | 5 | E4393 | 3.97 | 2018-08-01T06:15:00Z | 7 | 8 | KELC1 | 4.99 | 2018-08-01T06:57:00Z | 14.99 | 10
PG&E | 43315 | 0.40625 | 40.4988 | -121.8381 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | ZEIGGLER | 101492431 | Frontier | 12000 | Conductor | Overhead | Yes | 43315 | 0.40625 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1812 | 2018 | 8 | 3 | 9 | 45 | 18-0066484 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 4625 | 15.6081 | 66_397 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43316 | 0.30694 | 37.9756 | -122.5537 | Building | Urban | Structure Only | Fire Agency | ROSS VALLEY | 102241252 | AT&T | 12000 | Conductor | Overhead | Yes | 43316 | 0.30694 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1817 | 2018 | 8 | 4 | 7 | 22 | 18-0066666 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 6260 | 15.2351 | 241_183 | <25mph | >=15mph | HFTD - Distribution | MDEC1 | 3.77 | 2018-08-04T06:36:00Z | 28.99 | 18 | MDEC1 | 3.77 | 2018-08-04T06:36:00Z | 28.99 | 52 | MDEC1 | 3.77 | 2018-08-04T07:36:00Z | 28.99 | 35 | E9939 | 4.61 | 2018-08-04T07:44:00Z | 30 | 99
PG&E | 43317 | 0.58056 | 37.4005 | -119.7532 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | JIM FORGA 209-966-3621 | 101017235 | Unknown | 12000 | Conductor | Overhead | Yes | 43317 | 0.58056 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1821 | 2018 | 8 | 5 | 13 | 56 | 18-0066905 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 7325 | 8.1058 | 299_99 | <25mph | <15mph | HFTD - Distribution | MIAC1 | 1.36 | 2018-08-05T06:59:00Z | 10 | 2 | MIAC1 | 1.36 | 2018-08-05T06:59:00Z | 10 | 28 | MIAC1 | 1.36 | 2018-08-05T06:59:00Z | 10 | 4 | MIAC1 | 1.36 | 2018-08-05T06:59:00Z | 10 | 56
PG&E | 43319 | 0.40764 | 38.6556 | -121.0226 | Vegetation | Urban | < 3 meters | Fire Agency | CAL FIRE | 103902317 | AT&T | 21000 | Conductor | Overhead | Yes | 43319 | 0.40764 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1823 | 2018 | 8 | 7 | 9 | 47 | 18-0067412 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 243 | 7.5936 | 132_238 | <25mph | <15mph | HFTD - Distribution | E4740 | 2.54 | 2018-08-07T07:00:00Z | 1.01 | 20 | BENC1 | 6.56 | 2018-08-07T06:59:00Z | 8.01 | 87 | E4740 | 2.54 | 2018-08-07T08:00:00Z | 3 | 40 | PG073 | 4.79 | 2018-08-07T07:50:00Z | 8.99 | 174
PG&E | 43319 | 0.42986 | 38.1052 | -120.4978 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101282323 | Unknown | 17000 | Lightning Arrestor | Overhead | Yes | 43319 | 0.42986 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1824 | 2018 | 8 | 7 | 10 | 19 | 18-0067659 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 388 | 10.5296 | 181_290 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43319 | 0.65694 | 40.4465 | -122.446 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101464611 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43319 | 0.65694 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1826 | 2018 | 8 | 7 | 15 | 46 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 2.2502 | 162_201 | <25mph | <15mph | HFTD - Distribution | E6886 | 2.81 | 2018-08-07T06:31:00Z | 2.01 | 4 | E6886 | 2.81 | 2018-08-07T06:31:00Z | 2.01 | 4 | E6886 | 2.81 | 2018-08-07T07:16:00Z | 2.01 | 8 | E6886 | 2.81 | 2018-08-07T07:16:00Z | 2.01 | 8
PG&E | 43319 | 0.71875 | 37.1181 | -122.1093 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101670606 | AT&T | 12000 | Conductor | Overhead | Yes | 43319 | 0.71875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1827 | 2018 | 8 | 7 | 17 | 15 | 18-0067641 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 1988 | 12.1363 | 254_206 | <25mph | <15mph | HFTD - Distribution | BNDC1 | 3.6 | 2018-08-07T06:50:00Z | 18.01 | 34 | BNDC1 | 3.6 | 2018-08-07T06:50:00Z | 18.01 | 67 | BNDC1 | 3.6 | 2018-08-07T07:50:00Z | 20 | 65 | BNDC1 | 3.6 | 2018-08-07T07:50:00Z | 20 | 124
PG&E | 43319 | 0.87708 | 38.2129 | -120.9184 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102042811 | Unknown | 12000 | Conductor | Overhead | Yes | 43319 | 0.87708 | Equipment/ Facility Failure | Transformer | N.A. | N.A. | Unknown |  | no-match | 1828 | 2018 | 8 | 7 | 21 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 4.3727 | 174_313 | <25mph | <15mph | HFTD - Distribution | CMAC1 | 2.92 | 2018-08-07T06:59:00Z | 3 | 1 | CMAC1 | 2.92 | 2018-08-07T06:59:00Z | 3 | 1 | CMAC1 | 2.92 | 2018-08-07T07:59:00Z | 3 | 2 | CMAC1 | 2.92 | 2018-08-07T07:59:00Z | 3 | 2
PG&E | 43320 | 0.41875 | 40.7933 | -124.0242 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CHIEF | 100983089 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 0.41875 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1829 | 2018 | 8 | 8 | 10 | 3 | 18-0067921 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 27379 | 13.5277 | 198_275 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | KNNC1 | 7.13 | 2018-08-08T06:55:00Z | 7 | 30 |  |  |  | 0 | 0 | KNNC1 | 7.13 | 2018-08-08T06:55:00Z | 7 | 61
PG&E | 43320 | 0.66806 | 36.4703 | -121.7143 | Vegetation | Rural | < 3 meters | Customer | N.A. | 103910535 | None | 12000 | Conductor | Overhead | Yes | 43320 | 0.66806 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1830 | 2018 | 8 | 8 | 16 | 2 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 10.515 | 221_245 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | F1964 | 7.27 | 2018-08-08T07:00:00Z | 2.01 | 5 |  |  |  | 0 | 0 | F1964 | 7.27 | 2018-08-08T08:00:00Z | 2.01 | 8
PG&E | 43320 | 0.66875 | 37.2974 | -122.2651 | Vegetation | Rural | < 3 meters | Utility: PG&E | N.A. | 100307515 | Unknown | 12000 | Conductor | Overhead | Yes | 43320 | 0.66875 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1831 | 2018 | 8 | 8 | 16 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.7553 | 139_374 | <25mph | <15mph | HFTD - Distribution | LAHC1 | 0.77 | 2018-08-08T06:07:00Z | 4 | 1 | PG003 | 5.06 | 2018-08-08T06:00:00Z | 12.93 | 57 | LAHC1 | 0.77 | 2018-08-08T06:07:00Z | 4 | 2 | PG003 | 5.06 | 2018-08-08T06:00:00Z | 12.93 | 111
PG&E | 43322 | 0.5375 | 38.799 | -120.73 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101386272 | AT&T | 12000 | Conductor | Overhead | Yes | 43322 | 0.5375 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1832 | 2018 | 8 | 10 | 12 | 54 | 18-0068798 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 26532 | 7.5402 | 254_173 | <25mph | <15mph | HFTD - Distribution | E3165 | 0.86 | 2018-08-10T06:10:00Z | 4.99 | 8 | PG068 | 4.31 | 2018-08-10T07:00:00Z | 5.03 | 47 | E3165 | 0.86 | 2018-08-10T08:00:00Z | 4.99 | 15 | PG068 | 4.31 | 2018-08-10T07:10:00Z | 6.13 | 91
PG&E | 43322 | 0.84583 | 39.2093 | -121.0615 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 100075517 | AT&T | 12000 | Conductor | Overhead | Yes | 43322 | 0.84583 | Equipment/ Facility Failure | Splice/Clamp/Connector | N.A. | N.A. | Unknown |  | Other/Unknown | 1835 | 2018 | 8 | 10 | 20 | 18 | 18-0068886 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 581901 | 3.7784 | 73_395 | <25mph | <15mph | HFTD - Distribution | AV369 | 3.86 | 2018-08-10T06:57:00Z | 1.01 | 37 | PG059 | 7.8 | 2018-08-10T06:10:00Z | 7.25 | 76 | AV369 | 3.86 | 2018-08-10T07:57:00Z | 1.01 | 75 | PG059 | 7.8 | 2018-08-10T06:10:00Z | 7.25 | 149
PG&E | 43324 | 0.61528 | 38.6443 | -120.9211 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101410516 | Unknown | 21000 | Conductor | Overhead | Yes | 43324 | 0.61528 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1838 | 2018 | 8 | 12 | 14 | 46 | 18-0069084 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4032 | 17.1478 | 211_283 | <25mph | >=15mph | HFTD - Distribution | E8856 | 3.96 | 2018-08-12T06:35:00Z | 8.01 | 27 | PG073 | 7.47 | 2018-08-12T07:00:00Z | 14.92 | 118 | E8856 | 3.96 | 2018-08-12T06:35:00Z | 8.01 | 52 | PG073 | 7.47 | 2018-08-12T07:30:00Z | 19.06 | 228
PG&E | 43325 | 0.64792 | 38.708 | -120.9625 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101377799 | Unknown | 21000 | Conductor | Overhead | Yes | 43325 | 0.64792 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1840 | 2018 | 8 | 13 | 15 | 33 | 18-0069470 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1004 | 10.2378 | 230_116 | <25mph | <15mph | HFTD - Distribution | PG073 | 2.99 | 2018-08-13T06:40:00Z | 13.8 | 60 | PG073 | 2.99 | 2018-08-13T06:40:00Z | 13.8 | 117 | PG073 | 2.99 | 2018-08-13T06:40:00Z | 13.8 | 116 | PG073 | 2.99 | 2018-08-13T06:40:00Z | 13.8 | 226
PG&E | 43326 | 0.27986 | 40.686 | -122.141 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | j.t. zulliger 530-225-2420 | 103379843 | Unknown | 12000 | Conductor | Overhead | Yes | 43326 | 0.27986 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | Other/Unknown | 1842 | 2018 | 8 | 14 | 6 | 43 | 18-0069529 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | 37986 | 4.4465 | 214_250 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43326 | 0.6375 | 36.9656 | -121.8681 | Vegetation | Urban | < 0.25 Acres | Fire Agency | Unknown | 103128221 | AT&T | 21000 | Conductor | Overhead | Yes | 43326 | 0.6375 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1843 | 2018 | 8 | 14 | 15 | 18 | 18-0069846 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 15580 | 2.5294 | 278_109 | <25mph | <15mph | HFTD - Distribution | E8014 | 2.14 | 2018-08-14T06:15:00Z | 8.99 | 34 | E8014 | 2.14 | 2018-08-14T06:15:00Z | 8.99 | 80 | E8014 | 2.14 | 2018-08-14T06:15:00Z | 8.99 | 67 | E8014 | 2.14 | 2018-08-14T06:15:00Z | 8.99 | 158
PG&E | 43326 | 0.65694 | 38.0878 | -122.6002 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103916882 | Verizon | 0 – 750 | Conductor | Overhead | Yes | 43326 | 0.65694 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1844 | 2018 | 8 | 14 | 15 | 46 | 18-0069929 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 546 | 5.3513 | 203_274 | <25mph | <15mph | HFTD - Distribution | E0433 | 1.95 | 2018-08-14T06:35:00Z | 15.99 | 35 | WDAC1 | 7.14 | 2018-08-14T06:51:00Z | 20 | 64 | E0433 | 1.95 | 2018-08-14T06:35:00Z | 15.99 | 70 | WDAC1 | 7.14 | 2018-08-14T06:51:00Z | 20 | 125
PG&E | 43329 | 0.40139 | 40.2997 | -122.3322 | Vegetation | Rural | < 0.25 Acres | Fire Agency | chief | 101509747 | AT&T | 12000 | Conductor | Overhead | Yes | 43329 | 0.40139 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1845 | 2018 | 8 | 17 | 9 | 38 | 18-0071042 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 15510 | 13.0373 | 189_233 | <25mph | <15mph | HFTD - Distribution | E7114 | 3.57 | 2018-08-17T06:47:00Z | 4.99 | 4 | E7114 | 3.57 | 2018-08-17T06:47:00Z | 4.99 | 4 | E7114 | 3.57 | 2018-08-17T07:47:00Z | 5.99 | 8 | E7114 | 3.57 | 2018-08-17T07:47:00Z | 5.99 | 8
PG&E | 43332 | 0.39861 | 39.8014 | -121.5813 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100400441 | Unknown | 12000 | Conductor | Overhead | Yes | 43332 | 0.39861 | Contact From Object | N.A. | Other | Electric Facility | Human Error | PG&E contractor | Other/Unknown | 1849 | 2018 | 8 | 20 | 9 | 34 | 18-0071596 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 394259 | 17.1084 | 130_244 | <25mph | >=15mph | HFTD - Distribution | C4565 | 3.06 | 2018-08-20T06:53:00Z | 3 | 6 | JBGC1 | 6.67 | 2018-08-20T06:13:00Z | 11.01 | 28 | C4565 | 3.06 | 2018-08-20T07:53:00Z | 3 | 12 | JBGC1 | 6.67 | 2018-08-20T07:13:00Z | 11.01 | 54
PG&E | 43333 | 0.42569 | 38.6972 | -120.889 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101385436 | Unknown | 12000 | Conductor | Overhead | Yes | 43333 | 0.42569 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1852 | 2018 | 8 | 21 | 10 | 13 | 18-0072055 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 4572 | 7.0964 | 157_213 | <25mph | <15mph | HFTD - Distribution | PG106 | 1.36 | 2018-08-21T06:40:00Z | 9.22 | 57 | PG073 | 6.99 | 2018-08-21T06:40:00Z | 11.63 | 142 | PG106 | 1.36 | 2018-08-21T06:40:00Z | 9.22 | 111 | PG073 | 6.99 | 2018-08-21T06:40:00Z | 11.63 | 274
PG&E | 43334 | 0.725 | 37.9519 | -120.3103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101030620 | Unknown | 17000 | Conductor | Overhead | Yes | 43334 | 0.725 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown | dampeners | no-match | 1853 | 2018 | 8 | 22 | 17 | 24 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.9424 | 158_261 | <25mph | <15mph | HFTD - Distribution | PG029 | 2.2 | 2018-08-22T06:00:00Z | 4.61 | 18 | PG061 | 6.32 | 2018-08-22T06:40:00Z | 5.03 | 39 | PG031 | 2.51 | 2018-08-22T08:00:00Z | 6.58 | 34 | PG031 | 2.51 | 2018-08-22T08:00:00Z | 6.58 | 73
PG&E | 43334 | 0.91389 | 39.0425 | -120.9695 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 100024728 | Verizon | 12000 | Conductor | Overhead | Yes | 43334 | 0.91389 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1854 | 2018 | 8 | 22 | 21 | 56 | 18-0072654 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 29727 | 8.8854 | 172_191 | <25mph | <15mph | HFTD - Distribution | D9434 | 1.28 | 2018-08-22T07:00:00Z | 0 | 11 | PG032 | 6.31 | 2018-08-22T06:40:00Z | 7 | 44 | D9434 | 1.28 | 2018-08-22T08:00:00Z | 0 | 21 | PG032 | 6.31 | 2018-08-22T07:40:00Z | 7 | 84
PG&E | 43336 | 0.068056 | 39.2029 | -121.2766 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100087099 | AT&T | 21000 | Conductor | Overhead | Yes | 43336 | 0.068056 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | Other/Unknown | 1857 | 2018 | 8 | 24 | 1 | 38 | 18-0073021 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 24360 | 8.9607 | 241_188 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43336 | 0.21042 | 39.1184 | -121.0154 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JIM SMITH BATT CHIEF 3 | 100097647 | Unknown | 12000 | Conductor | Overhead | Yes | 43336 | 0.21042 | Contact From Object | N.A. | Balloons | Electric Facility | Human Error | third-party caused | Other/Unknown | 1858 | 2018 | 8 | 24 | 5 | 3 | 18-0073024 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Balloons | 4048 | 10.258 | 204_277 | <25mph | <15mph | HFTD - Distribution | AT999 | 2.07 | 2018-08-24T07:00:00Z | 0 | 11 | PG059 | 6.98 | 2018-08-24T06:40:00Z | 6.58 | 79 | AT999 | 2.07 | 2018-08-24T07:15:00Z | 2.01 | 21 | PG059 | 6.98 | 2018-08-24T07:10:00Z | 8.12 | 153
PG&E | 43338 | 0.64514 | 39.3599 | -121.1209 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Unknown | 100107472 | Unknown | 12000 | Conductor | Overhead | Yes | 43338 | 0.64514 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (No defect) | 1860 | 2018 | 8 | 26 | 15 | 29 | 18-0073601 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 36162 | 10.5291 | 201_296 | <25mph | <15mph | HFTD - Distribution | RRRC1 | 3.9 | 2018-08-26T06:13:00Z | 4.99 | 1 | RRRC1 | 3.9 | 2018-08-26T06:13:00Z | 4.99 | 27 | RRRC1 | 3.9 | 2018-08-26T07:13:00Z | 7 | 2 | RRRC1 | 3.9 | 2018-08-26T07:13:00Z | 7 | 52
PG&E | 43340 | 0.53472 | 40.2139 | -123.5966 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 100994840 | Unknown | 12000 | Conductor | Overhead | Yes | 43340 | 0.53472 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1866 | 2018 | 8 | 28 | 12 | 50 | 18-0074371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 82754 | 5.0493 | 194_314 | <25mph | <15mph | HFTD - Distribution | ALDC1 | 1.95 | 2018-08-28T06:51:00Z | 3 | 1 | ALDC1 | 1.95 | 2018-08-28T06:51:00Z | 3 | 1 | ALDC1 | 1.95 | 2018-08-28T06:51:00Z | 3 | 2 | ALDC1 | 1.95 | 2018-08-28T06:51:00Z | 3 | 2
PG&E | 43343 | 0.54306 | 40.4775 | -122.4847 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 103918932 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 0.54306 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1872 | 2018 | 8 | 31 | 13 | 2 | 18-0075616 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18300 | 2.6194 | 90_363 | <25mph | <15mph | HFTD - Distribution | PG086 | 3.07 | 2018-08-31T07:00:00Z | 0 | 12 | MMOC1 | 6.41 | 2018-08-31T06:00:00Z | 11.01 | 14 | PG086 | 3.07 | 2018-08-31T08:00:00Z | 1.74 | 22 | MMOC1 | 6.41 | 2018-08-31T06:00:00Z | 11.01 | 25
PG&E | 43343 | 0.75278 | 39.5785 | -123.3842 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 102196393 | Unknown | 12000 | Conductor | Overhead | Yes | 43343 | 0.75278 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1873 | 2018 | 8 | 31 | 18 | 4 | 18-0075741 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 18540 | 2.6744 | 105_308 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | RDVC1 | 7.03 | 2018-08-31T06:28:00Z | 7 | 1 |  |  |  | 0 | 0 | RDVC1 | 7.03 | 2018-08-31T07:28:00Z | 7 | 2
PG&E | 43343 | 0.75625 | 37.0548 | -122.0472 | Vegetation | Urban | < 0.25 Acres | Fire Agency | CAL FIRE | 101803212 | Unknown | 21000 | Conductor | Overhead | Yes | 43343 | 0.75625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1874 | 2018 | 8 | 31 | 18 | 9 | 18-0075730 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 197397 | 10.8852 | 181_282 | <25mph | <15mph | HFTD - Distribution | E3439 | 3.12 | 2018-08-31T06:39:00Z | 1.01 | 16 | D8979 | 7.19 | 2018-08-31T06:21:00Z | 12.01 | 158 | E3439 | 3.12 | 2018-08-31T07:54:00Z | 1.01 | 33 | D8979 | 7.19 | 2018-08-31T06:21:00Z | 12.01 | 305
PG&E | 43344 | 0.60069 | 36.8088 | -121.5916 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | Twr 35/222 | None | 115000 | Conductor | Overhead | Yes | 43344 | 0.60069 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1875 | 2018 | 9 | 1 | 14 | 25 | INT-11331 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 702145 | 8.4404 | 131_254 | <25mph | <15mph | HFTD - Transmission |  |  |  | 0 | 0 | AP200 | 7.05 | 2018-09-01T06:58:00Z | 0 | 3 |  |  |  | 0 | 0 | AP200 | 7.05 | 2018-09-01T07:53:00Z | 0 | 6
PG&E | 43345 | 0.65 | 37.4714 | -122.4248 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Arie Delay 659-740-4636 | 103808872 | Unknown | 12000 | Capacitor Bank | Overhead | Yes | 43345 | 0.65 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1876 | 2018 | 9 | 2 | 15 | 36 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 14.2035 | 259_173 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | HSPC1 | 6.33 | 2018-09-02T06:18:00Z | 13 | 45 |  |  |  | 0 | 0 | HSPC1 | 6.33 | 2018-09-02T07:18:00Z | 13 | 90
PG&E | 43346 | 0.77014 | 39.4547 | -121.4955 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 100395672 | Unknown | 12000 | Conductor | Overhead | Yes | 43346 | 0.77014 | Unknown | N.A. | N.A. | N.A. | Unknown |  | no-match | 1880 | 2018 | 9 | 3 | 18 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | N.A. | 10.1463 | 153_187 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | TT309 | 4.73 | 2018-09-03T06:45:00Z | 4 | 2 |  |  |  | 0 | 0 | TT309 | 4.73 | 2018-09-03T06:45:00Z | 4 | 4
PG&E | 43348 | 0.70486 | 37.4655 | -119.9005 | Vegetation | Rural | < 0.25 Acres | Fire Agency | JON BERRY 209-966-4700 | 101087053 | Unknown | 21000 | Conductor | Overhead | Yes | 43348 | 0.70486 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1882 | 2018 | 9 | 5 | 16 | 55 | 18-0076909 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 4017 | 2.5862 | 137_210 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | E9110 | 4.85 | 2018-09-05T06:36:00Z | 8.01 | 6 |  |  |  | 0 | 0 | E9110 | 4.85 | 2018-09-05T06:36:00Z | 8.01 | 12
PG&E | 43349 | 0.67986 | 39.0904 | -120.9464 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 100020676 | Unknown | 12000 | Conductor | Overhead | Yes | 43349 | 0.67986 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1886 | 2018 | 9 | 6 | 16 | 19 | 18-0077280 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 30780 | 6.7204 | 178_319 | <25mph | <15mph | HFTD - Distribution | D9434 | 3.62 | 2018-09-06T06:00:00Z | 4 | 9 | PG032 | 7.62 | 2018-09-06T06:50:00Z | 7 | 46 | D9434 | 3.62 | 2018-09-06T06:00:00Z | 4 | 17 | PG032 | 7.62 | 2018-09-06T07:10:00Z | 7.25 | 89
PG&E | 43352 | 0.18403 | 38.6534 | -122.8538 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Pole 13/1 | None | 60000 | Conductor | Overhead | Yes | 43352 | 0.18403 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1887 | 2018 | 9 | 9 | 4 | 25 | INT-11353 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 0 | 13.6761 | 176_294 | <25mph | <15mph | HFTD - Transmission | PICWW | 2.16 | 2018-09-09T06:00:00Z | 11.21 | 15 | PG082 | 5.77 | 2018-09-09T06:30:00Z | 19.95 | 38 | PICWW | 2.16 | 2018-09-09T06:00:00Z | 11.21 | 26 | PG082 | 5.77 | 2018-09-09T06:30:00Z | 19.95 | 65
PG&E | 43353 | 0.85903 | 38.0188 | -122.7225 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Unknown | 102252760 | Unknown | 12000 | Conductor | Overhead | Yes | 43353 | 0.85903 | Unknown | N.A. | N.A. | N.A. | Unknown |  | Other/Unknown | 1889 | 2018 | 9 | 10 | 20 | 37 | 18-0078359 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 219903 | 4.9153 | 105_309 | <25mph | <15mph | HFTD - Distribution | BBEC1 | 1.27 | 2018-09-10T06:11:00Z | 14.99 | 8 | WDAC1 | 4.66 | 2018-09-10T06:51:00Z | 18.99 | 50 | BBEC1 | 1.27 | 2018-09-10T06:11:00Z | 14.99 | 15 | WDAC1 | 4.66 | 2018-09-10T07:51:00Z | 22.01 | 95
PG&E | 43354 | 0.22431 | 37.376 | -119.6304 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | TROY CHEEK 209-966-3621 | 101023184 | Unknown | 12000 | Conductor | Overhead | Yes | 43354 | 0.22431 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1891 | 2018 | 9 | 11 | 5 | 23 | 18-0078387 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 288 | 37.7814 | 199_187 | 25-40mph | >=15mph | HFTD - Distribution | BSNC1 | 0.17 | 2018-09-11T06:48:00Z | 8.01 | 23 | MIAC1 | 6.99 | 2018-09-11T06:59:00Z | 8.99 | 67 | BSNC1 | 0.17 | 2018-09-11T07:48:00Z | 10 | 49 | MIAC1 | 6.99 | 2018-09-11T07:59:00Z | 10 | 134
PG&E | 43357 | 0.63056 | 35.328 | -120.6982 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Sean Hernandez Cell # 805 903 3423 | 103400199 | Unknown | 12000 | Conductor | Overhead | Yes | 43357 | 0.63056 | Equipment/ Facility Failure | Fuse | N.A. | N.A. | Unknown |  | no-match | 1898 | 2018 | 9 | 14 | 15 | 8 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Fuse | N.A. | 1.3314 | 206_97 | <25mph | <15mph | HFTD - Distribution | ARGC1 | 2.05 | 2018-09-14T06:54:00Z | 2.01 | 1 | F2489 | 7.42 | 2018-09-14T06:30:00Z | 8.01 | 17 | ARGC1 | 2.05 | 2018-09-14T07:54:00Z | 3 | 2 | F2489 | 7.42 | 2018-09-14T06:30:00Z | 8.01 | 35
PG&E | 43359 | 0.35139 | 35.3046 | -120.6389 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | Unknown | Pole 4/23A | None | 70000 | Conductor | Overhead | Yes | 43359 | 0.35139 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1903 | 2018 | 9 | 16 | 8 | 26 | INT-11371 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 29925 | 0.57476 | 149_357 | <25mph | <15mph | HFTD - Transmission | ARGC1 | 2.25 | 2018-09-16T06:54:00Z | 2.01 | 1 | ARGC1 | 2.25 | 2018-09-16T06:54:00Z | 2.01 | 5 | ARGC1 | 2.25 | 2018-09-16T07:54:00Z | 3 | 2 | ARGC1 | 2.25 | 2018-09-16T07:54:00Z | 3 | 10
PG&E | 43359 | 0.43194 | 39.4627 | -123.7837 | Vegetation | Rural | < 3 meters | Fire Agency | Unknown | 102184303 | AT&T | 12000 | Conductor | Overhead | Yes | 43359 | 0.43194 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | no-match | 1904 | 2018 | 9 | 16 | 10 | 22 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 11.3941 | 213_92 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43364 | 0.88194 | 39.0273 | -122.6627 | Vegetation | Rural | < 3 meters | Customer | N.A. | 102147414 | Unknown | 12000 | Conductor | Overhead | Yes | 43364 | 0.88194 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1908 | 2018 | 9 | 21 | 21 | 10 | 18-0082278 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 281055 | 7.5535 | 144_239 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PG097 | 7.92 | 2018-09-21T06:50:00Z | 2.19 | 14 |  |  |  | 0 | 0 | PG115 | 4.77 | 2018-09-21T07:20:00Z | 3.51 | 26
PG&E | 43364 | 0.95972 | 38.6428 | -122.7453 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 102218862 | Unknown | 12000 | Conductor | Overhead | Yes | 43364 | 0.95972 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1909 | 2018 | 9 | 21 | 23 | 2 | 18-0082304 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 9470 | 25.633 | 216_90 | 25-40mph | >=15mph | HFTD - Distribution | E3235 | 2.39 | 2018-09-21T06:59:00Z | 0 | 12 | PG038 | 6.21 | 2018-09-21T07:00:00Z | 3.51 | 41 | E3235 | 2.39 | 2018-09-21T07:59:00Z | 0 | 23 | PG038 | 6.21 | 2018-09-21T07:40:00Z | 3.51 | 78
PG&E | 43366 | 0.66458 | 37.335 | -121.7679 | Vegetation | Urban | 10 - 99 Acres | Fire Agency | San Jose FD | 100576722 | AT&T | 21000 | Conductor | Overhead | Yes | 43366 | 0.66458 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1912 | 2018 | 9 | 23 | 15 | 57 | 18-0082586 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 231441 | 9.1969 | 229_213 | <25mph | <15mph | HFTD - Distribution | UCBO | 3.66 | 2018-09-23T06:40:00Z | 2.01 | 25 | MIPC1 | 7.47 | 2018-09-23T06:19:00Z | 8.99 | 85 | UCBO | 3.66 | 2018-09-23T06:40:00Z | 2.01 | 49 | MIPC1 | 7.47 | 2018-09-23T06:19:00Z | 8.99 | 165
PG&E | 43367 | 0.024306 | 39.8152 | -121.6438 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Pole 3/42B | None | 60000 | Conductor | Overhead | Yes | 43367 | 0.024306 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1913 | 2018 | 9 | 24 | 0 | 35 | INT-11388 | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | 2407691 | 10.7907 | 177_225 | <25mph | <15mph | HFTD - Transmission | C8878 | 3.93 | 2018-09-24T06:58:00Z | 3 | 25 | CSTC1 | 7.71 | 2018-09-24T06:51:00Z | 5.99 | 40 | C8878 | 3.93 | 2018-09-24T07:43:00Z | 4 | 47 | CSTC1 | 7.71 | 2018-09-24T07:51:00Z | 8.01 | 75
PG&E | 43370 | 0.15278 | 37.5473 | -120.3255 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | Twr 12/2 | None | 70000 | Conductor | Overhead | Yes | 43370 | 0.15278 | Contact From Object | N.A. | Other | Electric Facility | Unknown | guano | no-match | 1916 | 2018 | 9 | 27 | 3 | 40 | INT-11393 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Unk or Other | Unk or Other - Other | 0 | 5.6633 | 206_185 | <25mph | <15mph | HFTD - Transmission |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43370 | 0.52986 | 38.5148 | -122.4463 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Twr 000/010 | None | 60000 | Conductor | Overhead | Yes | 43370 | 0.52986 | Contact From Object | N.A. | Other | Electric Facility | Human Error | helicopter | no-match | 1917 | 2018 | 9 | 27 | 12 | 43 | INT-11394 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1488992 | 15.276 | 168_262 | <25mph | >=15mph | HFTD - Transmission |  |  |  | 0 | 0 | PG018 | 4.41 | 2018-09-27T06:10:00Z | 3.51 | 21 |  |  |  | 0 | 0 | PG018 | 4.41 | 2018-09-27T08:00:00Z | 3.51 | 39
PG&E | 43372 | 0.67778 | 41.0219 | -123.655 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Hoopa Fire Dept | 100962165 | Unknown | 12000 | Conductor | Overhead | Yes | 43372 | 0.67778 | Contact From Object | N.A. | Vegetation | Electric Facility | Human Error | third-party caused | Other/Unknown | 1923 | 2018 | 9 | 29 | 16 | 16 | 18-0084877 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 16028 | 1.1171 | 137_268 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | BHTC1 | 7.5 | 2018-09-29T06:46:00Z | 13 | 6 |  |  |  | 0 | 0 | BHTC1 | 7.5 | 2018-09-29T07:46:00Z | 21 | 9
PG&E | 43380 | 0.072222 | 37.178 | -122.0267 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Mike Mathiesen 408-472-1613 Incident # SCU7096 | 100518363 | Unknown | 12000 | Conductor | Overhead | Yes | 43380 | 0.072222 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1929 | 2018 | 10 | 7 | 1 | 44 | 18-0087807 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 224444 | 2.1469 | 89_407 | <25mph | <15mph | HFTD - Distribution | PG050 | 2.46 | 2018-10-07T06:30:00Z | 14.25 | 11 | PG057 | 6.61 | 2018-10-07T06:20:00Z | 21.92 | 140 | PG050 | 2.46 | 2018-10-07T07:50:00Z | 16.67 | 21 | PG057 | 6.61 | 2018-10-07T07:40:00Z | 23.67 | 274
PG&E | 43381 | 0.46042 | 38.2621 | -122.7881 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAL FIRE | 101987186 | AT&T | 12000 | Conductor | Overhead | No | N.A. | N.A. | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | no-match | 1933 | 2018 | 10 | 8 | 11 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 12.638 | 148_346 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | F2270 | 5.08 | 2018-10-08T06:04:00Z | 10 | 16 |  |  |  | 0 | 0 | F2270 | 5.08 | 2018-10-08T06:04:00Z | 10 | 32
PG&E | 43387 | 0.48611 | 40.3598 | -122.4388 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TOM STROING 530-200-5113 | 101506416 | AT&T | 12000 | Conductor | Overhead | Yes | 43387 | 0.48611 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (Not overhanging, Distance Unknown) | 1938 | 2018 | 10 | 14 | 11 | 40 | 18-0090193 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 945 | 27.4784 | 151_222 | 25-40mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | E7114 | 4.61 | 2018-10-14T06:00:00Z | 10 | 5 |  |  |  | 0 | 0 | E7114 | 4.61 | 2018-10-14T07:45:00Z | 10 | 8
PG&E | 43387 | 0.81875 | 38.446 | -120.5147 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | IC- Dillon Gissell- 209-295-7735 | 103384485 | Unknown | 12000 | Conductor | Overhead | Yes | 43387 | 0.81875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (slight defect) | 1939 | 2018 | 10 | 14 | 19 | 39 | 18-0090288 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3497327 | 3.8374 | 122_254 | <25mph | <15mph | HFTD - Distribution | C9148 | 3.52 | 2018-10-14T06:34:00Z | 22.01 | 18 | C9148 | 3.52 | 2018-10-14T06:34:00Z | 22.01 | 37 | C9148 | 3.52 | 2018-10-14T06:34:00Z | 22.01 | 34 | C9148 | 3.52 | 2018-10-14T06:34:00Z | 22.01 | 69
PG&E | 43387 | 0.83889 | 38.8935 | -120.8497 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 103674516 | Unknown | 21000 | Conductor | Overhead | Yes | 43387 | 0.83889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1940 | 2018 | 10 | 14 | 20 | 8 | 18-0090299 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 48095 | 7.96 | 176_269 | <25mph | <15mph | HFTD - Distribution | PG033 | 2.11 | 2018-10-14T07:00:00Z | 6.13 | 27 | BDMC1 | 7.81 | 2018-10-14T06:36:00Z | 17 | 35 | PG033 | 2.11 | 2018-10-14T07:00:00Z | 6.13 | 51 | BDMC1 | 7.81 | 2018-10-14T06:36:00Z | 17 | 66
PG&E | 43388 | 0.14097 | 38.2897 | -120.5803 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL FIRE | 103378003 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43388 | 0.14097 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1941 | 2018 | 10 | 15 | 3 | 23 | 18-0090342 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 1464 | 9.1874 | 163_314 | <25mph | <15mph | HFTD - Distribution | AT317 | 3.74 | 2018-10-15T06:50:00Z | 23 | 13 | ESPC1 | 4.93 | 2018-10-15T06:13:00Z | 44.98 | 26 | AT317 | 3.74 | 2018-10-15T06:50:00Z | 23 | 25 | ESPC1 | 4.93 | 2018-10-15T07:13:00Z | 47 | 50
PG&E | 43389 | 0.44722 | 40.5097 | -124.1624 | Vegetation | Rural | < 3 meters | Fire Agency | CAL FIRE | 101004106 | Unknown | 12000 | Conductor | Overhead | Yes | 43389 | 0.44722 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1942 | 2018 | 10 | 16 | 10 | 44 | 18-0090952 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 2081 | 5.6665 | 166_277 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | C5061 | 4.32 | 2018-10-16T07:00:00Z | 0 | 7 |  |  |  | 0 | 0 | C5061 | 4.32 | 2018-10-16T07:59:00Z | 0 | 14
PG&E | 43389 | 0.6875 | 38.7754 | -122.8976 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | MARK GRADEK (707) 889-4303 | 101962692 | AT&T | 12000 | Conductor | Overhead | Yes | 43389 | 0.6875 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1943 | 2018 | 10 | 16 | 16 | 30 | 18-0091127 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 744 | 14.3383 | 156_183 | <25mph | <15mph | HFTD - Distribution | PG090 | 1.05 | 2018-10-16T06:20:00Z | 4.38 | 7 | PG125 | 5.67 | 2018-10-16T07:00:00Z | 14.25 | 26 | PG090 | 1.05 | 2018-10-16T07:20:00Z | 10.29 | 13 | HWKC1 | 4.29 | 2018-10-16T07:56:00Z | 18.99 | 49
PG&E | 43393 | 0.60486 | 40.5218 | -124.1137 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | Str. 003/000 | None | 60000 | Conductor | Overhead | Yes | 43393 | 0.60486 | Equipment/ Facility Failure | Other | N.A. | N.A. | Unknown |  | no-match | 1947 | 2018 | 10 | 20 | 14 | 31 | INT-11477 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 410982 | 15.6973 | 218_255 | <25mph | >=15mph | HFTD - Transmission | AT493 | 3.34 | 2018-10-20T06:58:00Z | 4.99 | 22 | AT493 | 3.34 | 2018-10-20T06:58:00Z | 4.99 | 22 | AT493 | 3.34 | 2018-10-20T07:18:00Z | 4.99 | 43 | AT493 | 3.34 | 2018-10-20T07:18:00Z | 4.99 | 43
PG&E | 43394 | 0.022222 | 35.5035 | -120.6025 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101886776 | Unknown | 21000 | Conductor | Overhead | Yes | 43394 | 0.022222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1948 | 2018 | 10 | 21 | 0 | 32 | 18-0092526 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 302559 | 0.30731 | 67_380 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | TT469 | 4.38 | 2018-10-21T06:14:00Z | 4 | 28 |  |  |  | 0 | 0 | TT469 | 4.38 | 2018-10-21T07:14:00Z | 4 | 55
PG&E | 43397 | 0.29722 | 37.9475 | -120.2671 | Vegetation | Rural | < 0.25 Acres | Fire Agency | SCOTT PITTMAN 209-768-8182 TCU INCIDENT# 012528 | 101047865 | Unknown | 17000 | Conductor | Overhead | Yes | 43397 | 0.29722 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1949 | 2018 | 10 | 24 | 7 | 8 | 18-0093599 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 13433 | 10.0852 | 118_282 | <25mph | <15mph | HFTD - Distribution | PG031 | 1.92 | 2018-10-24T07:00:00Z | 6.35 | 19 | PG166 | 7.04 | 2018-10-24T06:50:00Z | 11.83 | 54 | PG031 | 1.92 | 2018-10-24T07:40:00Z | 7.9 | 35 | PG166 | 7.04 | 2018-10-24T06:50:00Z | 11.83 | 100
PG&E | 43397 | 0.59583 | 36.7265 | -119.1086 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CHRIS CHRISTOPHERSON (559)493-4320 I.C #18CAFKUO15649 | 100691946 | None | 12000 | Conductor | Overhead | Yes | 43397 | 0.59583 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | no-match | 1950 | 2018 | 10 | 24 | 14 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | N.A. | 5.8362 | 159_241 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PHRC1 | 5.37 | 2018-10-24T06:58:00Z | 8.99 | 17 |  |  |  | 0 | 0 | PHRC1 | 5.37 | 2018-10-24T07:58:00Z | 10 | 34
PG&E | 43398 | 0.78264 | 35.5566 | -118.8168 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | GREG BLACK (661)391-7000 | 100203660 | None | 0 – 750 | Conductor | Overhead | Yes | 43398 | 0.78264 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1951 | 2018 | 10 | 25 | 18 | 47 | 18-0094369 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 1309 | 15.6464 | 223_76 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43399 | 0.87153 | 40.1528 | -122.3634 | Vegetation | Rural | < 0.25 Acres | Fire Agency | CAPT. ROB WAELTY 530-527-6113 | 101553579 | Unknown | 12000 | Conductor | Overhead | Yes | 43399 | 0.87153 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Fell into (Moderate-Severe defect) | 1953 | 2018 | 10 | 26 | 20 | 55 | 18-0094702 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4812 | 1.3833 | 69_380 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43401 | 0.36806 | 36.3792 | -121.8454 | Vegetation | Rural | < 0.25 Acres | Fire Agency | TONY (831) 625-6415 | 101672342 | Unknown | 12000 | Conductor | Overhead | Yes | 43401 | 0.36806 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Branch (OverHanging) | 1954 | 2018 | 10 | 28 | 8 | 50 | 18-0094889 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 3046 | 16.096 | 217_101 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43405 | 0.86458 | 38.372 | -123.0507 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 103852431 | AT&T | 12000 | Conductor | Overhead | Yes | 43405 | 0.86458 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1958 | 2018 | 11 | 1 | 20 | 45 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 21.5695 | 137_226 | <25mph | >=15mph | HFTD - Distribution | BBYC1 | 3.77 | 2018-11-01T07:00:00Z | 0.51 | 2 | BDZC1 | 4.05 | 2018-11-01T06:10:00Z | 6.51 | 20 | BBYC1 | 3.77 | 2018-11-01T08:00:00Z | 0.85 | 3 | BDZC1 | 4.05 | 2018-11-01T08:00:00Z | 7.02 | 38
PG&E | 43411 | 0.65903 | 37.0003 | -121.9802 | Vegetation | Urban | < 0.25 Acres | Unknown | N.A. | 101684527 | Unknown | 21000 | Capacitor Bank | Overhead | Yes | 43411 | 0.65903 | Equipment/ Facility Failure | Capacitor Bank | N.A. | N.A. | Unknown |  | no-match | 1959 | 2018 | 11 | 7 | 15 | 49 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Capacitor Bank | N.A. | 2.5393 | 142_358 | <25mph | <15mph | HFTD - Distribution | C8539 | 3.2 | 2018-11-07T07:57:00Z | 5.99 | 56 | E7291 | 5.58 | 2018-11-07T07:17:00Z | 8.99 | 130 | C9585 | 2.14 | 2018-11-07T08:12:00Z | 11.01 | 109 | C9585 | 2.14 | 2018-11-07T08:12:00Z | 11.01 | 251
PG&E | 43413 | 0.20069 | 39.8234 | -121.8382 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100402367 | AT&T | 12000 | Conductor | Overhead | Yes | 43413 | 0.20069 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1963 | 2018 | 11 | 9 | 4 | 49 | 18-0098482 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 11900 | 1.6773 | 158_202 | <25mph | <15mph | HFTD - Distribution | D8132 | 3.69 | 2018-11-09T07:15:00Z | 2.01 | 5 | CSTC1 | 4.96 | 2018-11-09T07:51:00Z | 8.01 | 13 | D8132 | 3.69 | 2018-11-09T08:45:00Z | 3 | 8 | CSTC1 | 4.96 | 2018-11-09T07:51:00Z | 8.01 | 23
PG&E | 43413 | 0.37431 | 37.2809 | -122.1214 | Vegetation | Rural | .26 - 9.99 Acres | Unknown | N.A. | 100546562 | AT&T | 12000 | Conductor | Overhead | Yes | 43413 | 0.37431 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Other/Unknown | 1964 | 2018 | 11 | 9 | 8 | 59 | 18-0098521 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 77077 | 7.1129 | 111_260 | <25mph | <15mph | HFTD - Distribution | E0516 | 1.72 | 2018-11-09T08:00:00Z | 17 | 39 | PG152 | 4.64 | 2018-11-09T07:20:00Z | 31.14 | 172 | E0516 | 1.72 | 2018-11-09T09:00:00Z | 21 | 75 | PG152 | 4.64 | 2018-11-09T07:20:00Z | 31.14 | 331
PG&E | 43414 | 0.56319 | 37.0467 | -121.9853 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL FIRE | 101671641 | Unknown | 21000 | Conductor | Overhead | Yes | 43414 | 0.56319 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | Dead | 1966 | 2018 | 11 | 10 | 13 | 31 | 18-0098856 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 1482 | 20.6863 | 181_339 | <25mph | >=15mph | HFTD - Distribution | PG062 | 2.37 | 2018-11-10T08:00:00Z | 9.86 | 45 | PG004 | 7.89 | 2018-11-10T07:10:00Z | 11.83 | 186 | PG062 | 2.37 | 2018-11-10T08:20:00Z | 10.96 | 84 | PG004 | 7.89 | 2018-11-10T07:10:00Z | 11.83 | 356
PG&E | 43415 | 0.17917 | 38.4341 | -122.5522 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102032588 | Unknown | 0 – 750 | Conductor | Overhead | Yes | 43415 | 0.17917 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1967 | 2018 | 11 | 11 | 4 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.4656 | 230_66 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PG091 | 4.41 | 2018-11-11T07:10:00Z | 23.24 | 26 |  |  |  | 0 | 0 | PG091 | 4.41 | 2018-11-11T07:10:00Z | 23.24 | 50
PG&E | 43417 | 0.65347 | 37.0644 | -121.9578 | Vegetation | Rural | < 0.25 Acres | Fire Agency | Unknown | 101680441 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43417 | 0.65347 | Other | N.A. | N.A. | N.A. | Human Error | Grow house | Other/Unknown | 1973 | 2018 | 11 | 13 | 15 | 41 | 18-0099492 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Unk or Other | Unk or Other - Unknown | 21484 | 9.4329 | 156_187 | <25mph | <15mph | HFTD - Distribution | PG062 | 0.72 | 2018-11-13T08:00:00Z | 5.91 | 41 | PG057 | 4.36 | 2018-11-13T07:20:00Z | 9.86 | 181 | PG062 | 0.72 | 2018-11-13T08:10:00Z | 6.35 | 79 | PG057 | 4.36 | 2018-11-13T07:20:00Z | 9.86 | 351
PG&E | 43419 | 0.25625 | 38.3599 | -122.3682 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 102241814 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43419 | 0.25625 | Equipment/ Facility Failure | Conductor | N.A. | N.A. | Unknown |  | Other/Unknown | 1974 | 2018 | 11 | 15 | 6 | 9 | 18-0099862 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 441 | 0.37625 | 132_263 | <25mph | <15mph | HFTD - Distribution | PG021 | 1.9 | 2018-11-15T07:20:00Z | 2.42 | 7 | PG021 | 1.9 | 2018-11-15T07:20:00Z | 2.42 | 21 | PG021 | 1.9 | 2018-11-15T08:20:00Z | 2.64 | 13 | PG021 | 1.9 | 2018-11-15T08:20:00Z | 2.64 | 39
PG&E | 43419 | 0.27361 | 38.6082 | -120.9532 | Vegetation | Rural | < 0.25 Acres | Self Extinguished | N.A. | 101414740 | Unknown | 12000 | Conductor | Overhead | Yes | 43419 | 0.27361 | Contact From Object | N.A. | Animal | Electric Facility | Unknown |  | Other/Unknown | 1975 | 2018 | 11 | 15 | 6 | 34 | 18-0099901 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 5325 | 7.2449 | 211_189 | <25mph | <15mph | HFTD - Distribution | BENC1 | 1.6 | 2018-11-15T07:59:00Z | 7 | 21 | BENC1 | 1.6 | 2018-11-15T07:59:00Z | 7 | 108 | BENC1 | 1.6 | 2018-11-15T08:59:00Z | 7 | 40 | E4740 | 7.49 | 2018-11-15T08:58:00Z | 8.99 | 206
PG&E | 43420 | 0.70972 | 38.7574 | -120.9012 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101409894 | AT&T | 21000 | Conductor | Overhead | Yes | 43420 | 0.70972 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1976 | 2018 | 11 | 16 | 17 | 2 | 18-0100490 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 119860 | 9.3935 | 156_202 | <25mph | <15mph | HFTD - Distribution | PG106 | 3.02 | 2018-11-16T07:40:00Z | 5.03 | 33 | PG068 | 7.29 | 2018-11-16T08:00:00Z | 6.8 | 136 | PG106 | 3.02 | 2018-11-16T09:00:00Z | 5.26 | 63 | PG068 | 7.29 | 2018-11-16T08:10:00Z | 8.55 | 264
PG&E | 43421 | 0.72222 | 38.7082 | -120.6927 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101421319 | Unknown | 12000 | Conductor | Overhead | Yes | 43421 | 0.72222 | Contact From Object | N.A. | Vehicle | Pole | Human Error | third-party caused | Other/Unknown | 1977 | 2018 | 11 | 17 | 17 | 20 | 18-0100697 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 35749 | 5.1336 | 122_266 | <25mph | <15mph | HFTD - Distribution | PG077 | 1.14 | 2018-11-17T07:50:00Z | 1.32 | 14 | PG104 | 6.43 | 2018-11-17T08:00:00Z | 13.8 | 72 | PG077 | 1.14 | 2018-11-17T07:50:00Z | 1.32 | 25 | PG104 | 6.43 | 2018-11-17T08:10:00Z | 14.03 | 137
PG&E | 43425 | 0.094444 | 40.4383 | -124.3847 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101005309 | Frontier | 12000 | Conductor | Overhead | Yes | 43425 | 0.094444 | Vandalism/Theft | N.A. | N.A. | N.A. | Human Error | gun-shot conductor | Other/Unknown | 1982 | 2018 | 11 | 21 | 2 | 16 | 18-0101683 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Unknown | 4834 | 14.51 | 201_273 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43446 | 0.50625 | 38.727 | -120.7947 | Vegetation | Rural | < 3 meters | Unknown | N.A. | 101404403 | AT&T | 0 – 750 | Conductor | Overhead | Yes | 43446 | 0.50625 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1984 | 2018 | 12 | 12 | 12 | 9 | No ILIS or TOTL available | Zone 1 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.7011 | 213_278 | <25mph | <15mph | HFTD - Distribution | PG068 | 1.89 | 2018-12-12T08:00:00Z | 4.16 | 37 | PG027 | 6.17 | 2018-12-12T08:00:00Z | 7 | 76 | PG068 | 1.89 | 2018-12-12T08:00:00Z | 4.16 | 73 | PG027 | 6.17 | 2018-12-12T08:50:00Z | 8.32 | 148
PG&E | 43448 | 0.43889 | 40.4379 | -123.7834 | Vegetation | Rural | < 0.25 Acres | Unknown | N.A. | 101009136 | Unknown | 12000 | Conductor | Overhead | Yes | 43448 | 0.43889 | Contact From Object | N.A. | Vegetation | Electric Facility | Unknown |  | no-match | 1985 | 2018 | 12 | 14 | 10 | 32 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 7.4933 | 225_71 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PG204 | 5.47 | 2018-12-14T07:50:00Z | 2.64 | 7 |  |  |  | 0 | 0 | PG204 | 5.47 | 2018-12-14T08:40:00Z | 3.51 | 13
1. Butte | 42256 | 0.60139 | 38.3297 | -120.7042 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1987 | 2015 | 9 | 9 | 14 | 26 |  | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 1353755 | 6.6041 | 169_267 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | MTZC1 | 5.02 | 2015-09-09T06:56:00Z | 7 | 1 |  |  |  | 0 | 0 | MTZC1 | 5.02 | 2015-09-09T07:56:00Z | 8.99 | 2
2. Cascade (Neu Wind Complex) | 43016 | 0.98958 | 39.322 | -121.4021 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1988 | 2017 | 10 | 8 | 23 | 45 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Equip Failure | Conductor | 0 | 7.1971 | 208_90 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | BNGC1 | 4.15 | 2017-10-08T06:51:00Z | 3 | 1 |  |  |  | 0 | 0 | BNGC1 | 4.15 | 2017-10-08T07:51:00Z | 3 | 2
3. Redwood Valley (Mendocino Lake Complex) | 43016 | 0.98333 | 39.2487 | -123.1663 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1989 | 2017 | 10 | 8 | 23 | 36 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 19.9148 | 57_376 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | E7513 | 5.24 | 2017-10-08T06:28:00Z | 3 | 25 |  |  |  | 0 | 0 | E7513 | 5.24 | 2017-10-08T06:28:00Z | 3 | 49
4. Nuns (Central LNU Complex) | 43016 | 0.91667 | 38.4041 | -122.5209 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1990 | 2017 | 10 | 8 | 22 | 0 |  | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 9.3371 | 155_254 | <25mph | <15mph | HFTD - Distribution | KENWW | 1.15 | 2017-10-08T07:00:00Z | 4.61 | 6 | F11WW | 4.55 | 2017-10-08T07:00:00Z | 14.2 | 16 | KENWW | 1.15 | 2017-10-08T07:00:00Z | 4.61 | 11 | F11WW | 4.55 | 2017-10-08T07:00:00Z | 14.2 | 29
5. Atlas (Southern LNU Complex) | 43016 | 0.91111 | 38.3921 | -122.2437 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | [5 empty] | Contact From Object | N.A. | Vegetation |  |  |  | no-match | 1991 | 2017 | 10 | 8 | 21 | 52 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Greater than 300 Acres | Vegetation | Other/Unknown | 0 | 13.5134 | 208_279 | <25mph | <15mph | HFTD - Distribution | F0187 | 3.03 | 2017-10-08T07:00:00Z | 2.01 | 5 | ATLC1 | 5.83 | 2017-10-08T06:29:00Z | 10 | 6 | F0187 | 3.03 | 2017-10-08T07:00:00Z | 2.01 | 8 | ATLC1 | 5.83 | 2017-10-08T06:29:00Z | 10 | 15
7. Camp Fire | 43412 | 0.27292 | 39.8134 | -121.4347 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 60000 | [5 empty] | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1993 | 2018 | 11 | 8 | 6 | 33 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Conductor | 826291590 | 18.2809 | 156_335 | <25mph | >=15mph | HFTD - Transmission |  |  |  | 0 | 0 | JBGC1 | 6.08 | 2018-11-08T07:13:00Z | 44 | 1 |  |  |  | 0 | 0 | JBGC1 | 6.08 | 2018-11-08T08:13:00Z | 44.98 | 2
PG&E | 43481 | 0.011806 | 38.0621 | -120.1964 | Vegetation | Conifer Forest | Structure Only | Cal Fire |  | 163661701 |  | 17000 | Conductor | Overhead | Yes | 43481 | 0.011806 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-01 | 2019 | 1 | 16 | 0 | 17 | 19-0010443 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 1041827 | 24.1103 | 234_243 | <25mph | >=15mph | HFTD - Distribution | MOUC1 | 2.77 | 2019-01-16T07:02:00Z | 38.01 | 1 | MOUC1 | 2.77 | 2019-01-16T07:02:00Z | 38.01 | 22 | MOUC1 | 2.77 | 2019-01-16T07:02:00Z | 38.01 | 2 | MOUC1 | 2.77 | 2019-01-16T07:02:00Z | 38.01 | 41
PG&E | 43537 | 0.67222 | 39.8831 | -122.5498 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 6Fn0313191607 |  | 12000 | Conductor | Overhead | Yes | 43537 | 0.67222 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-194 | 2019 | 3 | 13 | 16 | 8 | 19-0033617 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 21012 | 19.1124 | 134_343 | <25mph | >=15mph | HFTD - Distribution | TCKC1 | 3.76 | 2019-03-13T06:28:00Z | 13 | 1 | EPKC1 | 5.75 | 2019-03-13T06:03:00Z | 28.01 | 9 | TCKC1 | 3.76 | 2019-03-13T07:28:00Z | 15.99 | 2 | EPKC1 | 5.75 | 2019-03-13T06:03:00Z | 28.01 | 17
PG&E | 43543 | 0.53611 | 37.9956 | -120.3244 | Tree - cutting, 3rd party | Hardwood Forest | 1 meter - < 3 meters | Self Extinguished |  | 101045032 |  | 17000 | Conductor | Overhead | Yes | 43543 | 0.53611 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-187 | 2019 | 3 | 19 | 12 | 52 | 19-0035101 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 70602 | 13.0291 | 229_239 | <25mph | <15mph | HFTD - Distribution | PG061 | 3.8 | 2019-03-19T07:00:00Z | 8.99 | 21 | PG166 | 7.85 | 2019-03-19T07:00:00Z | 18.86 | 68 | PG061 | 3.8 | 2019-03-19T08:00:00Z | 9.22 | 39 | PG166 | 7.85 | 2019-03-19T07:50:00Z | 20.4 | 127
PG&E | 43564 | 0.58819 | 34.6311 | -119.9813 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Fire Dept | Santa Barbra County FD | 101863014 |  | 12000 | Conductor | Overhead | Yes | 43564 | 0.58819 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-263 | 2019 | 4 | 9 | 14 | 7 | 19-0040969 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 70756 | 15.9085 | 246_53 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | SXWC1 | 5.08 | 2019-04-09T06:09:00Z | 7 | 13 |  |  |  | 0 | 0 | UCSE | 5.53 | 2019-04-09T07:40:00Z | 7.2 | 23
PG&E | 43564 | 0.64375 | 37.7341 | -120.0776 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 101076921 |  | 21000 | Pole | Overhead | Yes | 43564 | 0.64375 | Vegetation |  | Veg. contact | Pole |  |  | Branch (Not overhanging, > 12ft) | 2019-313 | 2019 | 4 | 9 | 15 | 27 | 19-0041008 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, > 12ft) | 179862 | 22.6475 | 241_182 | <25mph | >=15mph | HFTD - Distribution | PG112 | 3.29 | 2019-04-09T06:20:00Z | 10.51 | 14 | PG155 | 7.32 | 2019-04-09T06:50:00Z | 12.71 | 29 | PG112 | 3.29 | 2019-04-09T07:50:00Z | 13.8 | 26 | PG155 | 7.32 | 2019-04-09T07:50:00Z | 19.51 | 54
PG&E | 43575 | 0.28958 | 37.8686 | -121.6843 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | East County FD | Unknown |  | 17000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-321 | 2019 | 4 | 20 | 6 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 22.6108 | 170_232 | <25mph | >=15mph | HFTD - Distribution | D3588 | 2.98 | 2019-04-20T07:00:00Z | 10 | 6 | PG066 | 6.23 | 2019-04-20T06:30:00Z | 37.04 | 109 | D3588 | 2.98 | 2019-04-20T07:51:00Z | 18.01 | 11 | KC83 | 4.32 | 2019-04-20T07:35:00Z | 43.73 | 207
PG&E | 43583 | 0.525 | 39.6756 | -121.5677 |  | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 100404366 |  | 12000 | Conductor | Overhead | Yes | 43583 | 0.525 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-166 | 2019 | 4 | 28 | 12 | 36 | 19-0046853 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 79810 | 8.9649 | 175_331 | <25mph | <15mph | HFTD - Distribution | PG295 | 0.21 | 2019-04-28T06:50:00Z | 9.22 | 7 | PG295 | 0.21 | 2019-04-28T06:50:00Z | 9.22 | 25 | PG295 | 0.21 | 2019-04-28T06:50:00Z | 9.22 | 13 | JBGC1 | 5.9 | 2019-04-28T07:13:00Z | 11.01 | 46
PG&E | 43593 | 0.43264 | 39.3851 | -122.557 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Fire Dept | Colusa FD | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-312 | 2019 | 5 | 8 | 10 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 9.7314 | 133_316 | <25mph | <15mph | HFTD - Distribution | SYWC1 | 1.49 | 2019-05-08T06:26:00Z | 4 | 1 | PG294 | 6.56 | 2019-05-08T06:00:00Z | 10.74 | 16 | SYWC1 | 1.49 | 2019-05-08T07:26:00Z | 4.99 | 2 | PG294 | 6.56 | 2019-05-08T06:00:00Z | 10.74 | 30
PG&E | 43595 | 0.61944 | 40.704 | -122.8314 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Fire Dept | Lewiston FD | Keswick-Trinity 60Kv Line |  | 60000 | Conductor | Overhead | Yes | 43595 | 0.61944 | Vegetation |  | Contact from Object - Other | Electric Facility |  |  | no-match | 2019-301 | 2019 | 5 | 10 | 14 | 52 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.6998 | 123_389 | <25mph | <15mph | HFTD - Transmission |  |  |  | 0 | 0 | TCAC1 | 5.87 | 2019-05-10T06:28:00Z | 14.99 | 5 |  |  |  | 0 | 0 | TCAC1 | 5.87 | 2019-05-10T06:28:00Z | 14.99 | 8
PG&E | 43600 | 0.89653 | 38.5731 | -122.9603 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Unknown |  | 103931177 |  | 12000 | Conductor | Overhead | Yes | 43600 | 0.89653 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-316 | 2019 | 5 | 15 | 21 | 31 | 19-0052480 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 27780 | 17.9493 | 115_271 | <25mph | >=15mph | HFTD - Distribution | D9841 | 3.34 | 2019-05-15T07:00:00Z | 1.01 | 5 | AR798 | 4.72 | 2019-05-15T06:56:00Z | 10 | 43 | D9841 | 3.34 | 2019-05-15T07:00:00Z | 1.01 | 8 | AR798 | 4.72 | 2019-05-15T06:56:00Z | 10 | 84
PG&E | 43602 | 0.63333 | 38.4797 | -123.1486 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 42811111 |  | 12000 | Conductor | Overhead | Yes | 43602 | 0.63333 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-200 | 2019 | 5 | 17 | 15 | 12 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 11.8024 | 107_266 | <25mph | <15mph | HFTD - Distribution | E8483 | 3.61 | 2019-05-17T06:30:00Z | 8.99 | 5 | E8483 | 3.61 | 2019-05-17T06:30:00Z | 8.99 | 17 | E8483 | 3.61 | 2019-05-17T06:30:00Z | 8.99 | 9 | E8483 | 3.61 | 2019-05-17T06:30:00Z | 8.99 | 29
PG&E | 43602 | 0.7875 | 38.0476 | -122.2064 | Bird Found | Urban | 3 meters - 0.25 Acres | Fire Dept | Crockett FD | 2Jt0517191854 |  | 21000 | Pole | Overhead | Yes | 43602 | 0.7875 | Contact - Animal - Bird |  | Animal contact | Pole | Animal Contact |  | Other/Unknown | 2019-02 | 2019 | 5 | 17 | 18 | 54 | 19-0053464 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 17.125 | 147_242 | <25mph | >=15mph | HFTD - Distribution | DPXC1 | 2.96 | 2019-05-17T06:24:00Z | 21.99 | 17 | UPBC1 | 4.72 | 2019-05-17T06:42:00Z | 32.97 | 102 | DPXC1 | 2.96 | 2019-05-17T06:24:00Z | 21.99 | 32 | UPBC1 | 4.72 | 2019-05-17T06:42:00Z | 32.97 | 192
PG&E | 43609 | 0.62708 | 35.1696 | -120.5103 |  | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 40589503 |  | 500000 | Pole | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-100 | 2019 | 5 | 24 | 15 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 8.7091 | 205_188 | <25mph | <15mph | HFTD - Transmission | C9687 | 3.56 | 2019-05-24T06:55:00Z | 0 | 12 | PG168 | 5.97 | 2019-05-24T07:00:00Z | 4.83 | 46 | C9687 | 3.56 | 2019-05-24T07:55:00Z | 0 | 24 | PG168 | 5.97 | 2019-05-24T07:00:00Z | 4.83 | 90
PG&E | 43614 | 0.70417 | 37.0371 | -119.5209 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 100680674 |  | 12000 | Pole | Overhead | Yes | 43614 | 0.70417 | Vegetation |  | Veg. contact | Pole |  |  | Dead | 2019-202 | 2019 | 5 | 29 | 16 | 54 | 19-0059237 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 6780 | 6.2481 | 265_186 | <25mph | <15mph | HFTD - Distribution | PG219 | 2.84 | 2019-05-29T06:40:00Z | 3.06 | 8 | PG202 | 6.2 | 2019-05-29T06:30:00Z | 7.25 | 57 | PG219 | 2.84 | 2019-05-29T08:00:00Z | 4.16 | 15 | PG202 | 6.2 | 2019-05-29T06:30:00Z | 7.25 | 97
PG&E | 43614 | 0.85069 | 39.0194 | -121.0608 |  | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match |  | 2019 | 5 | 29 | 20 | 25 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 10.0293 | 197_295 | <25mph | <15mph | HFTD - Distribution | PG349 | 3.78 | 2019-05-29T06:50:00Z | 4.83 | 23 | PG367 | 7.83 | 2019-05-29T06:20:00Z | 7 | 59 | PG349 | 3.78 | 2019-05-29T07:50:00Z | 5.91 | 42 | PG332 | 6.22 | 2019-05-29T07:40:00Z | 8.77 | 111
PG&E | 43615 | 0.34583 | 35.7005 | -120.8104 | Vehicle | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 101871463 |  | 12000 | Pole | Overhead | Yes | 43615 | 0.34583 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-274 | 2019 | 5 | 30 | 8 | 18 | 19-0059906 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 171603 | 3.7561 | 208_112 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | D4060 | 4.58 | 2019-05-30T06:02:00Z | 8.01 | 12 |  |  |  | 0 | 0 | D4060 | 4.58 | 2019-05-30T06:02:00Z | 8.01 | 23
PG&E | 43616 | 0.64236 | 40.4431 | -121.8211 |  | Hardwood Woodland | 1 meter - < 3 meters | Self Extinguished |  | 101556319 |  | 12000 | Conductor | Overhead | Yes | 43616 | 0.64236 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-88 | 2019 | 5 | 31 | 15 | 25 | 19-0060901 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 55546 | 3.729 | 165_374 | <25mph | <15mph | HFTD - Distribution | PG313 | 2.94 | 2019-05-31T06:50:00Z | 16.22 | 15 | PG193 | 6.12 | 2019-05-31T06:40:00Z | 18.41 | 22 | PG130 | 1.76 | 2019-05-31T07:50:00Z | 17.54 | 33 | PG193 | 6.12 | 2019-05-31T08:00:00Z | 22.57 | 52
PG&E | 43619 | 0.60486 | 40.6822 | -122.2806 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 101466598 |  | 12000 | Transformer | Overhead | Yes | 43619 | 0.60486 | Equipment - Overloaded | Transformer |  |  |  |  | no-match | 2019-161 | 2019 | 6 | 3 | 14 | 31 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | N.A. | 9.6637 | 145_374 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PG307 | 4.7 | 2019-06-03T06:50:00Z | 2.42 | 19 |  |  |  | 0 | 0 | PG307 | 4.7 | 2019-06-03T08:00:00Z | 3.94 | 38
PG&E | 43619 | 0.61597 | 40.4419 | -122.3036 |  | Herbaceous | 1 meter - < 3 meters | Fire Dept | Anderson FD | 101495889 |  | 12000 | Insulator | Overhead | No |  |  | Equipment - PG&E | [5 empty] | no-match | 2019-456 | 2019 | 6 | 3 | 14 | 47 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 7.2059 | 146_387 | <25mph | <15mph | HFTD - Distribution | AP525 | 3.17 | 2019-06-03T06:55:00Z | 0 | 6 | PG174 | 6.35 | 2019-06-03T06:00:00Z | 10.29 | 17 | AP525 | 3.17 | 2019-06-03T07:55:00Z | 0 | 12 | PG174 | 6.35 | 2019-06-03T06:00:00Z | 10.29 | 33
PG&E | 43622 | 0.37569 | 35.6384 | -118.9687 | Bird Found | Herbaceous | 0.25 - 10 Acres | Fire Dept | Kern County FD | 100216096 |  | 21000 | Conductor | Overhead | No |  |  | Contact - Animal - Other |  | Animal contact |  | Animal Contact |  | no-match | 2019-228 | 2019 | 6 | 6 | 9 | 1 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 8.7714 | 291_110 | <25mph | <15mph | HFTD - Distribution | PG159 | 2.52 | 2019-06-06T06:50:00Z | 9.86 | 14 | PG159 | 2.52 | 2019-06-06T06:50:00Z | 9.86 | 28 | PG159 | 2.52 | 2019-06-06T06:50:00Z | 9.86 | 26 | PG159 | 2.52 | 2019-06-06T06:50:00Z | 9.86 | 52
PG&E | 43622 | 0.85417 | 38.4969 | -122.6435 |  | Barren/Other | < 1 meter | Self Extinguished |  | Unknown |  | 230000 | Circuit Breaker | Overhead | Yes | 43622 | 0.85417 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | no-match | 2019-102 | 2019 | 6 | 6 | 20 | 30 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | N.A. | 20.0966 | 129_267 | <25mph | >=15mph | HFTD - Transmission | RSAC1 | 3.91 | 2019-06-06T06:29:00Z | 8.01 | 17 | PG162 | 5.7 | 2019-06-06T06:00:00Z | 23.02 | 91 | RSAC1 | 3.91 | 2019-06-06T07:29:00Z | 11.01 | 34 | PG162 | 5.7 | 2019-06-06T06:00:00Z | 23.02 | 172
PG&E | 43623 | 0.41528 | 38.7285 | -123.3528 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 042861101 |  | 21000 | Conductor | Overhead | Yes | 43623 | 0.41528 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-358 | 2019 | 6 | 7 | 9 | 58 | 19-0064216 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 5301 | 9.4575 | 98_280 | <25mph | <15mph | HFTD - Distribution | OAAC1 | 2.48 | 2019-06-07T06:33:00Z | 35.99 | 1 | OAAC1 | 2.48 | 2019-06-07T06:33:00Z | 35.99 | 13 | OAAC1 | 2.48 | 2019-06-07T06:33:00Z | 35.99 | 2 | OAAC1 | 2.48 | 2019-06-07T06:33:00Z | 35.99 | 25
PG&E | 43624 | 0.78542 | 38.6105 | -122.9732 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 42751113 |  | 12000 | Conductor | Overhead | Yes | 43624 | 0.78542 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-355 | 2019 | 6 | 8 | 18 | 51 | 19-0064689 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 44664 | 19.8533 | 114_273 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | PG243 | 5.7 | 2019-06-08T06:20:00Z | 12.48 | 51 |  |  |  | 0 | 0 | PG243 | 5.7 | 2019-06-08T07:10:00Z | 14.47 | 100
PG&E | 43626 | 0.56181 | 38.8137 | -120.9433 | Vegetation | Hardwood Woodland | 1 meter - < 3 meters | Other | Customer | 153652109 |  | 21000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-243 | 2019 | 6 | 10 | 13 | 29 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.416 | 202_284 | <25mph | <15mph | HFTD - Distribution | PLTC1 | 3.76 | 2019-06-10T06:56:00Z | 4 | 15 | PG073 | 7.24 | 2019-06-10T07:00:00Z | 11.18 | 62 | PLTC1 | 3.76 | 2019-06-10T07:56:00Z | 4 | 28 | PG073 | 7.24 | 2019-06-10T07:10:00Z | 14.25 | 117
PG&E | 43626 | 0.67917 | 38.1107 | -122.9025 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 42291101 |  | 12000 | Conductor | Overhead | Yes | 43626 | 0.67917 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-401 | 2019 | 6 | 10 | 16 | 18 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 2.4799 | 159_198 | <25mph | <15mph | HFTD - Distribution | PG046 | 2.87 | 2019-06-10T06:40:00Z | 12.93 | 21 | PG046 | 2.87 | 2019-06-10T06:40:00Z | 12.93 | 21 | PG046 | 2.87 | 2019-06-10T06:40:00Z | 12.93 | 39 | PG046 | 2.87 | 2019-06-10T06:40:00Z | 12.93 | 39
PG&E | 43626 | 0.69028 | 38.821 | -120.846 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Garden Valley FD | 153082106 |  | 21000 | Conductor | Overhead | Yes | 43626 | 0.69028 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-372 | 2019 | 6 | 10 | 16 | 34 | 19-0065481 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 14169 | 3.2821 | 206_284 | <25mph | <15mph | HFTD - Distribution | PG180 | 3.67 | 2019-06-10T07:00:00Z | 6.35 | 14 | PG104 | 6.61 | 2019-06-10T07:00:00Z | 14.47 | 81 | PG180 | 3.67 | 2019-06-10T08:00:00Z | 6.58 | 26 | PG104 | 6.61 | 2019-06-10T07:00:00Z | 14.47 | 154
PG&E | 43629 | 0.020833 | 36.5759 | -121.7284 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire |  | 182222104 |  | 21000 | Conductor | Overhead | Yes | 43629 | 0.020833 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-341 | 2019 | 6 | 13 | 0 | 30 | 19-0067072 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 148986 | 13.4853 | 167_161 | <25mph | <15mph | HFTD - Distribution | PG268 | 1.87 | 2019-06-13T06:50:00Z | 4.61 | 11 | PG318 | 7.33 | 2019-06-13T07:00:00Z | 12.28 | 29 | PG268 | 1.87 | 2019-06-13T07:30:00Z | 6.8 | 21 | PG318 | 7.33 | 2019-06-13T08:00:00Z | 15.99 | 55
PG&E | 43630 | 0.19306 | 37.5525 | -120.3254 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 011/008 |  | 70000 | Insulator | Overhead | No |  |  | Equipment - PG&E | Insulator |  |  |  |  | no-match | 2019-79 | 2019 | 6 | 14 | 4 | 38 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | N.A. | 16.3246 | 229_214 | <25mph | >=15mph | HFTD - Transmission |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43631 | 0.58889 | 38.8802 | -122.6125 | Tree - cutting, 3rd party | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | 43361103 |  | 12000 | Pole | Overhead | Yes | 43631 | 0.58889 | Contact - 3rd Party |  | Contact from Object - Other |  | Human Error |  | Other/Unknown | 2019-19 | 2019 | 6 | 15 | 14 | 8 | 19-0068074 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 259562 | 3.4453 | 130_288 | <25mph | <15mph | HFTD - Distribution | PG110 | 3.62 | 2019-06-15T06:00:00Z | 7 | 14 | KELC1 | 5.5 | 2019-06-15T06:57:00Z | 14.99 | 58 | PG110 | 3.62 | 2019-06-15T06:00:00Z | 7 | 26 | KELC1 | 5.5 | 2019-06-15T07:57:00Z | 14.99 | 106
PG&E | 43633 | 0.43403 | 38.511 | -122.2134 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 43051101 |  | 12000 | Conductor | Overhead | Yes | 43633 | 0.43403 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-84 | 2019 | 6 | 17 | 10 | 25 | 19-0068579 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 306900 | 7.2677 | 147_267 | <25mph | <15mph | HFTD - Distribution | PG048 | 0.14 | 2019-06-17T06:30:00Z | 11.63 | 8 | PG048 | 0.14 | 2019-06-17T06:30:00Z | 11.63 | 50 | PG048 | 0.14 | 2019-06-17T06:30:00Z | 11.63 | 15 | PG048 | 0.14 | 2019-06-17T06:30:00Z | 11.63 | 93
PG&E | 43634 | 0.82569 | 35.8876 | -120.9217 | Bird Found | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Pole | Overhead | Yes | 43634 | 0.82569 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | no-match | 2019-55 | 2019 | 6 | 18 | 19 | 49 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 18.1842 | 145_332 | <25mph | >=15mph | HFTD - Distribution |  |  |  | 0 | 0 | PG360 | 6.27 | 2019-06-18T06:10:00Z | 16.89 | 15 |  |  |  | 0 | 0 | RBYC1 | 6.84 | 2019-06-18T07:12:00Z | 17 | 28
PG&E | 43635 | 0.48889 | 39.8612 | -121.6907 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100400933 |  | 12000 | Conductor | Overhead | Yes | 43635 | 0.48889 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-224 | 2019 | 6 | 19 | 11 | 44 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.3558 | 187_228 | <25mph | <15mph | HFTD - Distribution | PG337 | 3.36 | 2019-06-19T06:10:00Z | 5.48 | 26 | PG339 | 7.65 | 2019-06-19T06:40:00Z | 10.29 | 73 | PG337 | 3.36 | 2019-06-19T07:20:00Z | 7.25 | 50 | CSTC1 | 4.21 | 2019-06-19T07:51:00Z | 11.01 | 132
PG&E | 43642 | 0.55139 | 40.0185 | -122.4107 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | Circuit Id 103331101 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43642 | 0.55139 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-331 | 2019 | 6 | 26 | 13 | 14 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.2962 | 140_351 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PG276 | 6.5 | 2019-06-26T07:00:00Z | 13.6 | 14 |  |  |  | 0 | 0 | PG276 | 6.5 | 2019-06-26T07:00:00Z | 13.6 | 26
PG&E | 43643 | 0.099306 | 36.8198 | -119.3334 | Bird Found | Hardwood Woodland | 0.25 - 10 Acres | Self Extinguished |  | Kings River-Sanger-Reedley 115Kv At 16/089 |  | 115000 | Insulator | Overhead | Yes | 43643 | 0.099306 | Equipment - PG&E | Insulator |  |  |  |  | no-match | 2019-104 | 2019 | 6 | 27 | 2 | 23 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Insulator | N.A. | 12.3568 | 273_175 | <25mph | <15mph | HFTD - Transmission | PG408 | 3.33 | 2019-06-27T06:40:00Z | 4.83 | 7 | PG233 | 6.47 | 2019-06-27T06:20:00Z | 7.67 | 21 | PG408 | 3.33 | 2019-06-27T06:40:00Z | 4.83 | 13 | PG233 | 6.47 | 2019-06-27T06:20:00Z | 7.67 | 40
PG&E | 43647 | 0.09375 | 38.2955 | -120.8335 |  | Shrub | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-252 | 2019 | 7 | 1 | 2 | 15 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 14.0071 | 207_255 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | TS389 | 4.67 | 2019-07-01T06:53:00Z | 14 | 32 |  |  |  | 0 | 0 | TS389 | 4.67 | 2019-07-01T06:53:00Z | 14 | 60
PG&E | 43652 | 0.59861 | 34.6388 | -119.9695 |  | Herbaceous | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | 182721104 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43652 | 0.59861 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-153 | 2019 | 7 | 6 | 14 | 22 | 19-0074960 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 14213 | 3.9067 | 181_224 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | FGMC1 | 6.93 | 2019-07-06T06:35:00Z | 8.99 | 22 |  |  |  | 0 | 0 | FGMC1 | 6.93 | 2019-07-06T07:35:00Z | 8.99 | 42
PG&E | 43657 | 0.64375 | 39.5657 | -120.6614 | Vegetation | Conifer Forest | 0.25 - 10 Acres | Unknown |  | 100102596 |  | 12000 | Pole | Overhead | Yes | 43657 | 0.64375 | Vegetation |  | Veg. contact | Pole |  |  | no-match | 2019-03 | 2019 | 7 | 11 | 15 | 27 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.2742 | 214_325 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43659 | 0.55069 | 34.7273 | -120.4357 |  | Shrub | 0.25 - 10 Acres | Fire Dept | Santa Barbara FD | Y44 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43659 | 0.55069 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-154 | 2019 | 7 | 13 | 13 | 13 | 19-0077070 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 18256 | 8.9126 | 216_205 | <25mph | <15mph | HFTD - Distribution | VDBC1 | 3.58 | 2019-07-13T06:22:00Z | 4.99 | 5 | VDBC1 | 3.58 | 2019-07-13T06:22:00Z | 4.99 | 24 | VDBC1 | 3.58 | 2019-07-13T07:22:00Z | 4.99 | 10 | VDBC1 | 3.58 | 2019-07-13T07:22:00Z | 4.99 | 47
PG&E | 43661 | 0.32708 | 38.3266 | -122.568 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 42721104 |  | 12000 | Conductor | Overhead | Yes | 43661 | 0.32708 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-343 | 2019 | 7 | 15 | 7 | 51 | 19-0077351 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 2348 | 34.6382 | 132_257 | 25-40mph | >=15mph | HFTD - Distribution | PG177 | 1.33 | 2019-07-15T07:00:00Z | 23.02 | 11 | PG177 | 1.33 | 2019-07-15T07:00:00Z | 23.02 | 46 | PG177 | 1.33 | 2019-07-15T08:00:00Z | 23.24 | 21 | PG177 | 1.33 | 2019-07-15T08:00:00Z | 23.24 | 90
PG&E | 43662 | 0.72986 | 40.1691 | -122.3053 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103541103 |  | 12000 | Conductor | Overhead | Yes | 43662 | 0.72986 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-375 | 2019 | 7 | 16 | 17 | 31 | 19-0078094 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 45533 | 11.6886 | 144_359 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43663 | 0.32569 | 34.5066 | -120.2247 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Santa Barbara County FD | 4Bx0717190747 |  | 12000 | Other | Overhead | Yes | 43663 | 0.32569 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-425 | 2019 | 7 | 17 | 7 | 49 | 19-0078239 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 19608 | 28.1419 | 235_46 | 25-40mph | >=15mph | HFTD - Distribution | GVTC1 | 1.4 | 2019-07-17T06:09:00Z | 40 | 8 | GVTC1 | 1.4 | 2019-07-17T06:09:00Z | 40 | 8 | GVTC1 | 1.4 | 2019-07-17T07:09:00Z | 40 | 15 | GVTC1 | 1.4 | 2019-07-17T07:09:00Z | 40 | 15
PG&E | 43664 | 0.83125 | 37.081 | -119.4865 |  | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | No |  |  | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-09 | 2019 | 7 | 18 | 19 | 57 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 2.894 | 217_203 | <25mph | <15mph | HFTD - Distribution | PG389 | 1.62 | 2019-07-18T06:00:00Z | 8.77 | 39 | SE370 | 7.06 | 2019-07-18T06:10:00Z | 11.41 | 104 | PG389 | 1.62 | 2019-07-18T06:00:00Z | 8.77 | 74 | SE370 | 7.06 | 2019-07-18T06:10:00Z | 11.41 | 195
PG&E | 43664 | 0.43542 | 38.3033 | -120.6718 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | B561 |  | 12000 | Other | Overhead | Yes | 43664 | 0.43542 | Equipment - PG&E | Other |  |  |  |  | Other/Unknown | 2019-68 | 2019 | 7 | 18 | 10 | 27 | 19-0078904 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45558 | 8.4459 | 253_164 | <25mph | <15mph | HFTD - Distribution | PG372 | 0.86 | 2019-07-18T07:00:00Z | 4.83 | 14 | TS389 | 7.11 | 2019-07-18T06:53:00Z | 7 | 59 | PG372 | 0.86 | 2019-07-18T07:50:00Z | 7.67 | 26 | PG372 | 0.86 | 2019-07-18T07:50:00Z | 7.67 | 110
PG&E | 43665 | 0.49931 | 37.9162 | -120.349 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 163351703 |  | 17000 | Conductor | Overhead | Yes | 43665 | 0.49931 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-376 | 2019 | 7 | 19 | 11 | 59 | 19-0079030 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 24042 | 8.2161 | 228_234 | <25mph | <15mph | HFTD - Distribution | PG166 | 2.3 | 2019-07-19T06:00:00Z | 10.96 | 32 | PG166 | 2.3 | 2019-07-19T06:00:00Z | 10.96 | 51 | PG166 | 2.3 | 2019-07-19T06:00:00Z | 10.96 | 60 | PG166 | 2.3 | 2019-07-19T06:00:00Z | 10.96 | 95
PG&E | 43667 | 0.53194 | 37.0517 | -122.1522 | Vegetation | Urban | 1 meter - < 3 meters | Cal Fire |  | 82931101 |  | 12000 | Conductor | Overhead | Yes | 43667 | 0.53194 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-377 | 2019 | 7 | 21 | 12 | 46 | 19-0079583 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 89102 | 6.0013 | 254_171 | <25mph | <15mph | HFTD - Distribution | PG047 | 1.66 | 2019-07-21T06:50:00Z | 2.19 | 7 | PG262 | 7.56 | 2019-07-21T06:50:00Z | 5.91 | 107 | PG047 | 1.66 | 2019-07-21T07:40:00Z | 2.86 | 13 | PG262 | 7.56 | 2019-07-21T06:50:00Z | 5.91 | 201
PG&E | 43667 | 0.42639 | 38.9716 | -120.9991 |  | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire | Placer Hill FD | 152241102 |  | 12000 | Splice/Clamp/Connector | Overhead | Yes | 43667 | 0.42639 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-127 | 2019 | 7 | 21 | 10 | 14 | 19-0079578 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 32850 | 2.0112 | 151_219 | <25mph | <15mph | HFTD - Distribution | C0713 | 3.87 | 2019-07-21T07:00:00Z | 0 | 16 | PG349 | 6.34 | 2019-07-21T06:40:00Z | 3.94 | 45 | C0713 | 3.87 | 2019-07-21T07:59:00Z | 0 | 31 | PG349 | 6.34 | 2019-07-21T08:00:00Z | 5.03 | 90
PG&E | 43668 | 0.34097 | 38.7687 | -120.9633 | Bird Found | Herbaceous | 3 meters - 0.25 Acres | Cal Fire | El Dorado County FD | 6Ht0722190809 |  | 21000 | Other | Overhead | Yes | 43668 | 0.34097 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-49 | 2019 | 7 | 22 | 8 | 11 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 6.9601 | 201_281 | <25mph | <15mph | HFTD - Distribution | PG027 | 3.71 | 2019-07-22T06:20:00Z | 5.48 | 14 | PG111 | 5.58 | 2019-07-22T06:00:00Z | 5.48 | 121 | PG027 | 3.71 | 2019-07-22T07:30:00Z | 8.32 | 26 | PG027 | 3.71 | 2019-07-22T07:30:00Z | 8.32 | 231
PG&E | 43668 | 0.90208 | 38.8618 | -121.1044 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 152561103 |  | 12000 | Conductor | Overhead | Yes | 43668 | 0.90208 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-336 | 2019 | 7 | 22 | 21 | 39 | 19-0080025 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 9842 | 11.9728 | 195_286 | <25mph | <15mph | HFTD - Distribution | D8862 | 2.4 | 2019-07-22T06:15:00Z | 4 | 5 | F5165 | 7.23 | 2019-07-22T06:55:00Z | 4 | 29 | D8862 | 2.4 | 2019-07-22T07:15:00Z | 4 | 8 | F5165 | 7.23 | 2019-07-22T07:40:00Z | 4 | 53
PG&E | 43669 | 0.68819 | 37.2447 | -121.9999 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Santa Clara County FD | 83371104 |  | 12000 | Conductor | Overhead | Yes | 43669 | 0.68819 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-378 | 2019 | 7 | 23 | 16 | 31 | 19-0080428 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 19250 | 3.302 | 156_198 | <25mph | <15mph | HFTD - Distribution | PG154 | 2.55 | 2019-07-23T06:50:00Z | 10.96 | 81 | PG154 | 2.55 | 2019-07-23T06:50:00Z | 10.96 | 224 | PG154 | 2.55 | 2019-07-23T06:50:00Z | 10.96 | 156 | PG154 | 2.55 | 2019-07-23T06:50:00Z | 10.96 | 439
PG&E | 43669 | 0.70486 | 37.2128 | -119.505 | Gun Shot | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | 252521103 |  | 12000 | Conductor | Overhead | Yes | 43669 | 0.70486 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-434 | 2019 | 7 | 23 | 16 | 55 | 19-0080383 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 513358 | 5.8456 | 265_196 | <25mph | <15mph | HFTD - Distribution | PG467 | 3.77 | 2019-07-23T06:40:00Z | 15.99 | 9 | PG467 | 3.77 | 2019-07-23T06:40:00Z | 15.99 | 30 | PG467 | 3.77 | 2019-07-23T07:20:00Z | 15.99 | 16 | PG467 | 3.77 | 2019-07-23T07:20:00Z | 15.99 | 55
PG&E | 43671 | 0.010417 | 39.0662 | -120.9754 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Fire Dept | Placer Hills FD | 152491101 |  | 12000 | Conductor | Overhead | Yes | 43671 | 0.010417 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-379 | 2019 | 7 | 25 | 0 | 15 | 19-0080924 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 7845 | 10.1883 | 200_298 | <25mph | <15mph | HFTD - Distribution | PG377 | 2.2 | 2019-07-25T07:00:00Z | 4.16 | 31 | PG032 | 7.47 | 2019-07-25T06:30:00Z | 5.91 | 54 | PG377 | 2.2 | 2019-07-25T07:10:00Z | 5.7 | 61 | PG032 | 7.47 | 2019-07-25T07:10:00Z | 8.55 | 108
PG&E | 43671 | 0.31875 | 39.1735 | -123.5763 | Vegetation | Hardwood Forest | 3 meters - 0.25 Acres | Cal Fire |  | Oj 2 P/Ss Of Cgc# 215532055340 |  | 12000 | Other | Overhead | Yes | 43671 | 0.31875 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-380 | 2019 | 7 | 25 | 7 | 39 | 19-0080947 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 790 | 6.0339 | 89_305 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PG485 | 4.89 | 2019-07-25T06:30:00Z | 3.74 | 18 |  |  |  | 0 | 0 | PG485 | 4.89 | 2019-07-25T06:30:00Z | 3.74 | 35
PG&E | 43672 | 0.50208 | 38.8003 | -120.8258 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire |  | 153082106 |  | 21000 | Conductor | Overhead | Yes | 43672 | 0.50208 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-381 | 2019 | 7 | 26 | 12 | 3 | 19-0081559 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 16465 | 4.5929 | 207_283 | <25mph | <15mph | HFTD - Distribution | E5691 | 3.74 | 2019-07-26T06:58:00Z | 0 | 12 | PG068 | 5.03 | 2019-07-26T06:30:00Z | 5.48 | 111 | E5691 | 3.74 | 2019-07-26T07:58:00Z | 0 | 24 | PG180 | 4.28 | 2019-07-26T07:10:00Z | 5.48 | 215
PG&E | 43673 | 0.34861 | 40.3789 | -122.1873 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Self Extinguished |  | 103461102 |  | 12000 | Conductor | Overhead | Yes | 43673 | 0.34861 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-382 | 2019 | 7 | 27 | 8 | 22 | 19-0081756 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 456 | 11.9501 | 223_236 | <25mph | <15mph | HFTD - Distribution | PG335 | 2.07 | 2019-07-27T06:00:00Z | 9.64 | 7 | PG320 | 4.66 | 2019-07-27T06:50:00Z | 11.41 | 21 | PG335 | 2.07 | 2019-07-27T06:00:00Z | 9.64 | 13 | PG320 | 4.66 | 2019-07-27T06:50:00Z | 11.41 | 39
PG&E | 43673 | 0.67847 | 37.7266 | -120.3246 | Vegetation | Urban | 0.25 - 10 Acres | Cal Fire |  | 252811102 |  | 12000 | Conductor | Overhead | Yes | 43673 | 0.67847 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-383 | 2019 | 7 | 27 | 16 | 17 | 19-0081851 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 2694 | 9.6205 | 149_370 | <25mph | <15mph | HFTD - Distribution | PG186 | 3.42 | 2019-07-27T06:40:00Z | 8.12 | 14 | PG186 | 3.42 | 2019-07-27T06:40:00Z | 8.12 | 33 | PG186 | 3.42 | 2019-07-27T06:40:00Z | 8.12 | 26 | PG186 | 3.42 | 2019-07-27T06:40:00Z | 8.12 | 61
PG&E | 43673 | 0.20208 | 37.9486 | -120.4656 | Vegetation | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 163781705 |  | 17000 | Conductor | Overhead | Yes | 43673 | 0.20208 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-385 | 2019 | 7 | 27 | 4 | 51 | 19-0081744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 1364 | 7.5204 | 229_224 | <25mph | <15mph | HFTD - Distribution | PG167 | 3.88 | 2019-07-27T06:40:00Z | 5.26 | 14 | PG166 | 6.57 | 2019-07-27T07:00:00Z | 12.06 | 35 | PG167 | 3.88 | 2019-07-27T06:40:00Z | 5.26 | 26 | PG166 | 6.57 | 2019-07-27T07:00:00Z | 12.06 | 65
PG&E | 43676 | 0.63542 | 39.1207 | -121.072 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | 152691104 |  | 12000 | Conductor | Overhead | Yes | 43676 | 0.63542 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-386 | 2019 | 7 | 30 | 15 | 15 | 19-0082713 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 31302 | 1.5622 | 72_405 | <25mph | <15mph | HFTD - Distribution | E1789 | 3.69 | 2019-07-30T06:24:00Z | 8.01 | 11 | PG429 | 7.54 | 2019-07-30T06:20:00Z | 8.32 | 88 | E1789 | 3.69 | 2019-07-30T06:24:00Z | 8.01 | 21 | PG367 | 7.57 | 2019-07-30T07:40:00Z | 16.44 | 171
PG&E | 43678 | 0.56111 | 38.5721 | -120.6803 | Equipment Failure/Involved, Overhead | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 153662102 |  | 21000 | Conductor | Overhead | Yes | 43678 | 0.56111 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-170 | 2019 | 8 | 1 | 13 | 28 | 19-0083500 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 1374 | 11.2785 | 213_271 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PG433 | 7.73 | 2019-08-01T07:00:00Z | 11.83 | 31 |  |  |  | 0 | 0 | PG433 | 7.73 | 2019-08-01T07:20:00Z | 15.77 | 59
PG&E | 43682 | 0.94306 | 37.1869 | -119.7902 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Unknown |  | 322066125092 |  | 21000 | Transformer | Overhead | Yes | 43682 | 0.94306 | Equipment - Overloaded | Transformer |  |  |  |  | Other/Unknown | 2019-134 | 2019 | 8 | 5 | 22 | 38 | 19-0084586 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Transformer | 996 | 11.4699 | 253_195 | <25mph | <15mph | HFTD - Distribution | PG434 | 0.93 | 2019-08-05T06:50:00Z | 6.13 | 19 | PG425 | 4.53 | 2019-08-05T06:30:00Z | 7.9 | 47 | PG434 | 0.93 | 2019-08-05T07:40:00Z | 6.35 | 37 | PG460 | 7.2 | 2019-08-05T07:30:00Z | 11.63 | 89
PG&E | 43683 | 0.50833 | 39.0506 | -121.0614 | Vegetation | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 100107532 |  | 12000 | Insulator | Overhead | Yes | 43683 | 0.50833 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-391 | 2019 | 8 | 6 | 12 | 12 | 19-0084799 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 60943 | 6.1843 | 167_160 | <25mph | <15mph | HFTD - Distribution | C5488 | 2.4 | 2019-08-06T06:23:00Z | 4.99 | 25 | E1789 | 7.54 | 2019-08-06T06:54:00Z | 7 | 69 | C5488 | 2.4 | 2019-08-06T06:23:00Z | 4.99 | 50 | E1789 | 7.54 | 2019-08-06T06:54:00Z | 7 | 132
PG&E | 43688 | 0.054861 | 39.1152 | -121.001 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 100097796 |  | 12000 | Other | Overhead | Yes | 43688 | 0.054861 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-387 | 2019 | 8 | 11 | 1 | 19 | 19-0086613 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 6200 | 14.6091 | 199_300 | <25mph | <15mph | HFTD - Distribution | PG377 | 1.68 | 2019-08-11T07:00:00Z | 1.52 | 13 | AV504 | 7.68 | 2019-08-11T06:55:00Z | 7 | 79 | PG377 | 1.68 | 2019-08-11T08:00:00Z | 2.86 | 25 | AV504 | 7.68 | 2019-08-11T07:05:00Z | 8.01 | 151
PG&E | 43689 | 0.8375 | 39.0952 | -123.4937 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 102177212 |  | 12000 | Conductor | Overhead | Yes | 43689 | 0.8375 | Vegetation |  | Veg. contact |  |  |  | Fell into (No defect) | 2019-400 | 2019 | 8 | 12 | 20 | 6 | 19-0087090 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 2508 | 6.9872 | 210_275 | <25mph | <15mph | HFTD - Distribution | PG256 | 1.12 | 2019-08-12T06:10:00Z | 1.74 | 10 | PG248 | 4.67 | 2019-08-12T06:10:00Z | 4.16 | 17 | PG256 | 1.12 | 2019-08-12T06:10:00Z | 1.74 | 20 | PG248 | 4.67 | 2019-08-12T07:40:00Z | 4.38 | 33
PG&E | 43689 | 0.7375 | 38.6618 | -120.7451 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 101415488, 101404439 |  | 12000 | Pole | Overhead | Yes | 43689 | 0.7375 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (slight defect) | 2019-241 | 2019 | 8 | 12 | 17 | 42 | 19-0087080 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 54604 | 15.2648 | 93_301 | <25mph | >=15mph | HFTD - Distribution | PG354 | 3.38 | 2019-08-12T07:00:00Z | 7.67 | 16 | PG354 | 3.38 | 2019-08-12T07:00:00Z | 7.67 | 57 | PG354 | 3.38 | 2019-08-12T07:40:00Z | 11.41 | 28 | PG354 | 3.38 | 2019-08-12T07:40:00Z | 11.41 | 106
PG&E | 43690 | 0.4375 | 36.6102 | -121.4452 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 40761041 |  | 115000 | Other | Overhead | Yes | 43690 | 0.4375 | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-164 | 2019 | 8 | 13 | 10 | 30 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 5.4434 | 180_162 | <25mph | <15mph | HFTD - Transmission |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43691 | 0.42778 | 35.379 | -120.4232 | Vegetation | Hardwood Woodland | < 1 meter | Cal Fire |  | 512769069280 |  | 21000 | Conductor | Overhead | Yes | 43691 | 0.42778 | Vegetation | [5 empty] | no-match |  | 2019 | 8 | 14 | 10 | 16 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.5585 | 242_183 | <25mph | <15mph | HFTD - Distribution | PG235 | 1.2 | 2019-08-14T06:30:00Z | 5.48 | 28 | PG190 | 6.24 | 2019-08-14T06:00:00Z | 12.06 | 56 | PG235 | 1.2 | 2019-08-14T06:30:00Z | 5.48 | 52 | PG190 | 6.24 | 2019-08-14T06:00:00Z | 12.06 | 104
PG&E | 43693 | 0.34653 | 40.1235 | -123.8758 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Self Extinguished |  | 192221102-2101118022{5563} |  | 12000 | Conductor | Overhead | Yes | 43693 | 0.34653 | Vegetation | [5 empty] | Other/Unknown |  | 2019 | 8 | 16 | 8 | 19 | 19-0088744 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 2979 | 4.0105 | 78_358 | <25mph | <15mph | HFTD - Distribution | ERCC1 | 2.93 | 2019-08-16T06:28:00Z | 12.01 | 1 | ERCC1 | 2.93 | 2019-08-16T06:28:00Z | 12.01 | 33 | ERCC1 | 2.93 | 2019-08-16T06:28:00Z | 12.01 | 2 | ERCC1 | 2.93 | 2019-08-16T06:28:00Z | 12.01 | 62
PG&E | 43693 | 0.43819 | 39.3714 | -121.3221 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103191101 |  | 12000 | Conductor | Overhead | Yes | 43693 | 0.43819 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-397 | 2019 | 8 | 16 | 10 | 31 | 19-0088805 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 4580 | 6.0086 | 254_161 | <25mph | <15mph | HFTD - Distribution | PG298 | 3.48 | 2019-08-16T06:50:00Z | 6.8 | 8 | PG381 | 4.94 | 2019-08-16T07:00:00Z | 14.25 | 43 | PG298 | 3.48 | 2019-08-16T08:00:00Z | 7.25 | 15 | PG381 | 4.94 | 2019-08-16T07:00:00Z | 14.25 | 80
PG&E | 43696 | 0.72708 | 40.9399 | -123.6322 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | California Department of Forestry | 192171101 |  | 12000 | Conductor | Overhead | Yes | 43696 | 0.72708 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-340 | 2019 | 8 | 19 | 17 | 27 | 19-0089645 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 410686 | 4.2049 | 90_403 | <25mph | <15mph | HFTD - Distribution | D8984 | 1.44 | 2019-08-19T06:03:00Z | 8.99 | 6 | HOAC1 | 7.73 | 2019-08-19T06:40:00Z | 11.01 | 7 | D8984 | 1.44 | 2019-08-19T06:03:00Z | 8.99 | 11 | HOAC1 | 7.73 | 2019-08-19T06:40:00Z | 11.01 | 13
PG&E | 43697 | 0.37708 | 41.1088 | -121.5034 |  | Agriculture | 3 meters - 0.25 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation | Conductor | Veg. contact | Electric Facility |  |  | no-match | 2019-297 | 2019 | 8 | 20 | 9 | 3 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 10.1717 | 178_411 | <25mph | <15mph | HFTD - Distribution | PG384 | 3.7 | 2019-08-20T06:40:00Z | 2.64 | 7 | PG499 | 7.38 | 2019-08-20T06:00:00Z | 9.42 | 14 | PG384 | 3.7 | 2019-08-20T07:20:00Z | 3.06 | 13 | PG499 | 7.38 | 2019-08-20T06:00:00Z | 9.42 | 26
PG&E | 43699 | 0.93264 | 39.139 | -121.0194 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 152481106 |  | 12000 | Conductor | Overhead | Yes | 43699 | 0.93264 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-346 | 2019 | 8 | 22 | 22 | 23 | 19-0091224 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 38628 | 10.5918 | 199_302 | <25mph | <15mph | HFTD - Distribution | PG377 | 3.46 | 2019-08-22T07:00:00Z | 5.48 | 11 | E1789 | 6.14 | 2019-08-22T07:00:00Z | 5.99 | 93 | PG377 | 3.46 | 2019-08-22T07:00:00Z | 5.48 | 21 | E1789 | 6.14 | 2019-08-22T08:00:00Z | 5.99 | 184
PG&E | 43701 | 0.79306 | 39.0497 | -121.0614 | Vehicle | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 103956556 |  | 12000 | Pole | Overhead | Yes | 43701 | 0.79306 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-114 | 2019 | 8 | 24 | 19 | 2 | 19-0091826 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 144608 | 12.5435 | 138_217 | <25mph | <15mph | HFTD - Distribution | C0713 | 2.52 | 2019-08-24T06:39:00Z | 1.01 | 26 | E1789 | 7.6 | 2019-08-24T06:48:00Z | 8.01 | 75 | C0713 | 2.52 | 2019-08-24T06:39:00Z | 1.01 | 51 | PG332 | 5.71 | 2019-08-24T07:20:00Z | 8.77 | 141
PG&E | 43702 | 0.55069 | 41.0935 | -123.6942 | Vegetation | Urban | 3 meters - 0.25 Acres | Fire Dept | Unknown | 115334464574 |  | 12000 | Transformer | Overhead | Yes | 43702 | 0.55069 | Vegetation |  | Veg. contact | Electric Facility |  |  | Other/Unknown | 2019-351 | 2019 | 8 | 25 | 13 | 13 | 19-0091921 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | 20311 | 14.3939 | 131_272 | <25mph | <15mph | HFTD - Distribution | BIIC1 | 3.05 | 2019-08-25T06:40:00Z | 5.99 | 9 | BIIC1 | 3.05 | 2019-08-25T06:40:00Z | 5.99 | 9 | BIIC1 | 3.05 | 2019-08-25T06:40:00Z | 5.99 | 17 | BIIC1 | 3.05 | 2019-08-25T06:40:00Z | 5.99 | 17
PG&E | 43708 | 0.43056 | 40.661 | -122.356 | Vehicle | Barren/Other | 3 meters - 0.25 Acres | Fire Dept | Shasta Lake FD | 103571671 | Yes | 12000 | Fuse | Overbuild | Yes | 43708 | 0.43056 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-421 | 2019 | 8 | 31 | 10 | 20 | 19-0094332 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 3050 | 11.4855 | 143_386 | <25mph | <15mph | HFTD - Distribution | F5970 | 1.07 | 2019-08-31T06:00:00Z | 3 | 23 | PG519 | 6.72 | 2019-08-31T06:30:00Z | 5.55 | 62 | F5970 | 1.07 | 2019-08-31T07:16:00Z | 4 | 45 | PG519 | 6.72 | 2019-08-31T08:00:00Z | 11.99 | 118
PG&E | 43709 | 0.70139 | 35.908 | -121.011 |  | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 103477437 |  | 12000 | Pole | Overhead | Yes | 43709 | 0.70139 | Equipment - PG&E | [5 empty] | Other/Unknown | 2019-17 | 2019 | 9 | 1 | 16 | 50 | 19-0094475 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | 45432 | 7.3653 | 133_243 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PG140 | 7.9 | 2019-09-01T06:20:00Z | 3.74 | 21 |  |  |  | 0 | 0 | PG171 | 7.31 | 2019-09-01T08:00:00Z | 4.83 | 39
PG&E | 43713 | 0.95972 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire | California Department of Forestry | 101670112 |  | 12000 | Fuse | Overhead | Yes | 43713 | 0.95972 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-388 | 2019 | 9 | 5 | 23 | 2 | 19-0095858 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 17920 | 6.5368 | 147_193 | <25mph | <15mph | HFTD - Distribution | BNDC1 | 2.84 | 2019-09-05T06:50:00Z | 3 | 15 | BNDC1 | 2.84 | 2019-09-05T06:50:00Z | 3 | 66 | BNDC1 | 2.84 | 2019-09-05T07:50:00Z | 3 | 28 | C1844 | 4.46 | 2019-09-05T07:29:00Z | 3 | 128
PG&E | 43718 | 0.30069 | 37.1653 | -122.201 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 82841102 |  | 12000 | Conductor | Overhead | Yes | 43718 | 0.30069 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (Moderate-Severe defect) | 2019-369 | 2019 | 9 | 10 | 7 | 13 | 19-0097264 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 23500 | 11.5457 | 147_193 | <25mph | <15mph | HFTD - Distribution | PG472 | 2.91 | 2019-09-10T07:00:00Z | 23.44 | 15 | PG472 | 2.91 | 2019-09-10T07:00:00Z | 23.44 | 65 | PG472 | 2.91 | 2019-09-10T07:00:00Z | 23.44 | 28 | PG472 | 2.91 | 2019-09-10T07:00:00Z | 23.44 | 125
PG&E | 43719 | 0.87708 | 38.3132 | -120.9809 | Vegetation | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 163341103 |  | 12000 | Conductor | Overhead | Yes | 43719 | 0.87708 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-370 | 2019 | 9 | 11 | 21 | 3 | 19-0098003 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 25994 | 13.1511 | 241_121 | <25mph | <15mph | HFTD - Distribution | PG401 | 2.35 | 2019-09-11T06:00:00Z | 3.06 | 7 | CFAC1 | 5.36 | 2019-09-11T06:05:00Z | 7 | 25 | PG401 | 2.35 | 2019-09-11T06:00:00Z | 3.06 | 13 | CFAC1 | 5.36 | 2019-09-11T06:05:00Z | 7 | 51
PG&E | 43719 | 0.78889 | 37.9937 | -122.137 | Bird Found | Hardwood Woodland | Other | Unknown |  | Unknown |  | 115000 | Other | Overhead | Yes | 43719 | 0.78889 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-42 | 2019 | 9 | 11 | 18 | 56 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Animal | Animal | N.A. | 11.7227 | 200_256 | <25mph | <15mph | HFTD - Transmission | PG064 | 2.53 | 2019-09-11T06:00:00Z | 16.15 | 54 | PG064 | 2.53 | 2019-09-11T06:00:00Z | 16.15 | 209 | PG064 | 2.53 | 2019-09-11T06:00:00Z | 16.15 | 103 | PG064 | 2.53 | 2019-09-11T06:00:00Z | 16.15 | 396
PG&E | 43720 | 0.60069 | 37.3144 | -122.1865 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 024131103 |  | 12000 | Conductor | Overhead | Yes | 43720 | 0.60069 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-217 | 2019 | 9 | 12 | 14 | 25 | 19-0098386 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 89097 | 11.8169 | 147_201 | <25mph | <15mph | HFTD - Distribution | PG152 | 1.17 | 2019-09-12T06:00:00Z | 9.28 | 49 | PG150 | 4.6 | 2019-09-12T06:40:00Z | 10.16 | 161 | PG152 | 1.17 | 2019-09-12T06:00:00Z | 9.28 | 100 | PG150 | 4.6 | 2019-09-12T06:40:00Z | 10.16 | 318
PG&E | 43721 | 0.27083 | 37.3348 | -121.7716 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 83392110 |  | 21000 | Splice/Clamp/Connector | Overhead | Yes | 43721 | 0.27083 | Equipment - PG&E | Splice/Clamp/Connector |  |  |  |  | Other/Unknown | 2019-444 | 2019 | 9 | 13 | 6 | 30 | 19-0098560 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Splice/Clamp/Connector | 35534 | 0.81774 | 166_202 | <25mph | <15mph | HFTD - Distribution | PG477 | 2.08 | 2019-09-13T06:30:00Z | 9.35 | 54 | PG477 | 2.08 | 2019-09-13T06:30:00Z | 9.35 | 122 | PG477 | 2.08 | 2019-09-13T06:30:00Z | 9.35 | 101 | PG477 | 2.08 | 2019-09-13T06:30:00Z | 9.35 | 231
PG&E | 43721 | 0.37014 | 39.0754 | -121.1717 | Bird Found | Herbaceous | 0.25 - 10 Acres | Fire Dept | Consolidated FD | Etr0913190810 |  | 12000 | Other | Overhead | Yes | 43721 | 0.37014 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | no-match | 2019-46 | 2019 | 9 | 13 | 8 | 53 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | N.A. | 0.13542 | 159_207 | <25mph | <15mph | HFTD - Distribution | PG367 | 1.38 | 2019-09-13T06:00:00Z | 8.68 | 10 | PG367 | 1.38 | 2019-09-13T06:00:00Z | 8.68 | 45 | PG367 | 1.38 | 2019-09-13T06:00:00Z | 8.68 | 22 | PG367 | 1.38 | 2019-09-13T06:00:00Z | 8.68 | 89
PG&E | 43723 | 0.52639 | 38.1194 | -120.8013 | Vehicle | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 103959405 |  | 12000 | Pole | Overhead | Yes | 43723 | 0.52639 | Contact - 3rd Party |  | Vehicle contact | Pole | Human Error |  | Other/Unknown | 2019-118 | 2019 | 9 | 15 | 12 | 38 | 19-0099234 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 5378 | 19.8556 | 128_245 | <25mph | >=15mph | HFTD - Distribution | F0465 | 3.04 | 2019-09-15T06:31:00Z | 2.01 | 12 | PG375 | 4.65 | 2019-09-15T06:40:00Z | 5.19 | 26 | F0465 | 3.04 | 2019-09-15T07:36:00Z | 3 | 24 | PG375 | 4.65 | 2019-09-15T08:00:00Z | 7.61 | 50
PG&E | 43724 | 0.61042 | 37.3762 | -119.8729 | Vegetation | Hardwood Woodland | 10 - 100 Acres | Cal Fire |  | 254452102 |  | 21000 | Conductor | Overhead | Yes | 43724 | 0.61042 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (Not overhanging, Distance Unknown) | 2019-417 | 2019 | 9 | 16 | 14 | 39 | 19-0099772 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (Not overhanging, Distance Unknown) | 121254 | 8.2417 | 249_205 | <25mph | <15mph | HFTD - Distribution | PG571 | 0.83 | 2019-09-16T06:10:00Z | 7.74 | 14 | MIAC1 | 7.6 | 2019-09-16T06:59:00Z | 8.01 | 55 | PG571 | 0.83 | 2019-09-16T06:10:00Z | 7.74 | 26 | MIAC1 | 7.6 | 2019-09-16T06:59:00Z | 8.01 | 103
PG&E | 43730 | 0.49722 | 37.5168 | -119.9159 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 103967994 |  | 21000 | Pole | Overhead | Yes | 43730 | 0.49722 | Equipment - PG&E | Pole |  |  |  |  | Other/Unknown | 2019-452 | 2019 | 9 | 22 | 11 | 56 | 19-0102232 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Pole | 133232 | 12.2404 | 247_213 | <25mph | <15mph | HFTD - Distribution | PG189 | 1.46 | 2019-09-22T06:10:00Z | 6.22 | 15 | PG575 | 7.53 | 2019-09-22T06:00:00Z | 6.35 | 68 | PG189 | 1.46 | 2019-09-22T06:10:00Z | 6.22 | 28 | PG575 | 7.53 | 2019-09-22T06:00:00Z | 6.35 | 127
PG&E | 43734 | 0.59167 | 36.9517 | -121.8278 | Vegetation | Shrub | 1 meter - < 3 meters | Cal Fire |  | 2287 |  | 21000 | Conductor | Overhead | Yes | 43734 | 0.59167 | Vegetation |  | Veg. contact |  |  |  | Branch (OverHanging) | 2019-352 | 2019 | 9 | 26 | 14 | 12 | 19-0104163 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 2856 | 16.0268 | 163_181 | <25mph | >=15mph | HFTD - Distribution | E7291 | 3.61 | 2019-09-26T07:00:00Z | 8.01 | 35 | E7291 | 3.61 | 2019-09-26T07:00:00Z | 8.01 | 99 | E7291 | 3.61 | 2019-09-26T07:00:00Z | 8.01 | 66 | E7291 | 3.61 | 2019-09-26T07:00:00Z | 8.01 | 188
PG&E | 43735 | 0.4375 | 36.5336 | -121.1464 | Vegetation | Barren/Other | 0.25 - 10 Acres | Cal Fire |  | 182492105 |  | 21000 | Conductor | Overhead | Yes | 43735 | 0.4375 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (slight defect) | 2019-359 | 2019 | 9 | 27 | 10 | 30 | 19-0104536 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 20631 | 7.4063 | 193_158 | <25mph | <15mph | HFTD - Distribution | PG406 | 3.05 | 2019-09-27T06:00:00Z | 11.41 | 14 | PG406 | 3.05 | 2019-09-27T06:00:00Z | 11.41 | 22 | PG406 | 3.05 | 2019-09-27T06:00:00Z | 11.41 | 26 | PG406 | 3.05 | 2019-09-27T06:00:00Z | 11.41 | 41
PG&E | 43736 | 0.55278 | 37.2553 | -119.5057 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 252531103 |  | 12000 | Conductor | Overhead | Yes | 43736 | 0.55278 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-36 | 2019 | 9 | 28 | 13 | 16 | 19-0104972 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 1296 | 9.3578 | 265_198 | <25mph | <15mph | HFTD - Distribution | PG573 | 3.43 | 2019-09-28T07:00:00Z | 8.61 | 8 | PG573 | 3.43 | 2019-09-28T07:00:00Z | 8.61 | 68 | PG573 | 3.43 | 2019-09-28T07:00:00Z | 8.61 | 16 | PG573 | 3.43 | 2019-09-28T07:00:00Z | 8.61 | 140
PG&E | 43738 | 0.60347 | 34.6139 | -120.1799 | Contact with High Voltage, 3rd party | Agriculture | 0.25 - 10 Acres | Cal Fire |  | 183041102 |  | 12000 | Conductor | Overhead | Yes | 43738 | 0.60347 | Contact - 3rd Party |  | Contact from Object - Other | Electric Facility | Human Error |  | Other/Unknown | 2019-13 | 2019 | 9 | 30 | 14 | 29 | 19-0105582 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | 3rd Party - Other | 4080 | 1.595 | 237_52 | <25mph | <15mph | HFTD - Distribution | C9206 | 2.6 | 2019-09-30T06:56:00Z | 0 | 12 | TT480 | 6.42 | 2019-09-30T06:20:00Z | 12.01 | 16 | C9206 | 2.6 | 2019-09-30T07:56:00Z | 0 | 24 | TT480 | 6.42 | 2019-09-30T06:20:00Z | 12.01 | 32
PG&E | 43742 | 0.79653 | 40.4964 | -122.0448 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Other | Overhead | Yes | 43742 | 0.79653 | Equipment - Overloaded | Other |  |  |  |  | no-match | 2019-257 | 2019 | 10 | 4 | 19 | 7 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 9.9058 | 155_377 | <25mph | <15mph | HFTD - Distribution | PG107 | 2.58 | 2019-10-04T06:10:00Z | 4.54 | 7 | PG322 | 7.46 | 2019-10-04T06:50:00Z | 6.44 | 42 | PG107 | 2.58 | 2019-10-04T06:10:00Z | 4.54 | 13 | PG322 | 7.46 | 2019-10-04T06:50:00Z | 6.44 | 78
PG&E | 43746 | 0.74931 | 35.2979 | -120.4868 |  | Hardwood Woodland | 3 meters - 0.25 Acres | Cal Fire |  | 182541103 |  | 12000 | Conductor | Overhead | Yes | 43746 | 0.74931 | Equipment - PG&E | Conductor |  |  |  |  | no-match | 2019-207 | 2019 | 10 | 8 | 17 | 59 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 3.2839 | 223_90 | <25mph | <15mph | HFTD - Distribution | PG240 | 3.72 | 2019-10-08T06:40:00Z | 1.61 | 7 | PG235 | 6.78 | 2019-10-08T06:00:00Z | 9.64 | 35 | PG240 | 3.72 | 2019-10-08T07:20:00Z | 2.77 | 13 | PG235 | 6.78 | 2019-10-08T06:00:00Z | 9.64 | 65
PG&E | 43753 | 0.028472 | 37.3237 | -119.6173 |  | Hardwood Forest | 1 meter - < 3 meters | Cal Fire |  | Circuit 254432102 |  | 21000 | Insulator | Overhead | Yes | 43753 | 0.028472 | Equipment - PG&E | Insulator |  |  |  |  | Other/Unknown | 2019-168 | 2019 | 10 | 15 | 0 | 41 | 19-0111571 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Insulator | 741 | 6.821 | 260_202 | <25mph | <15mph | HFTD - Distribution | BSNC1 | 3.84 | 2019-10-15T06:48:00Z | 8.99 | 54 | BSNC1 | 3.84 | 2019-10-15T06:48:00Z | 8.99 | 80 | BSNC1 | 3.84 | 2019-10-15T06:48:00Z | 8.99 | 106 | BSNC1 | 3.84 | 2019-10-15T06:48:00Z | 8.99 | 156
PG&E | 43755 | 0.82222 | 37.6494 | -120.357 |  | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 5Tr1017191903 |  | 12000 | Conductor | Overhead | Yes | 43755 | 0.82222 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-423 | 2019 | 10 | 17 | 19 | 44 | 19-0113175 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 10105 | 13.285 | 228_220 | <25mph | <15mph | HFTD - Distribution | PG459 | 0.92 | 2019-10-17T06:20:00Z | 15.93 | 7 | PG186 | 7.71 | 2019-10-17T06:20:00Z | 16.28 | 21 | PG459 | 0.92 | 2019-10-17T07:40:00Z | 23.17 | 13 | PG186 | 7.71 | 2019-10-17T07:50:00Z | 25.05 | 39
PG&E | 43758 | 0.71458 | 37.1585 | -122.1339 |  | Conifer Forest | 1 meter - < 3 meters | Employee |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Equipment - PG&E | Conductor |  |  |  |  | no-match |  | 2019 | 10 | 20 | 17 | 9 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | N.A. | 12.5691 | 150_193 | <25mph | <15mph | HFTD - Distribution | PG472 | 2.84 | 2019-10-20T06:30:00Z | 12.28 | 41 | AV151 | 4.67 | 2019-10-20T06:05:00Z | 14 | 104 | PG472 | 2.84 | 2019-10-20T06:30:00Z | 12.28 | 79 | AV151 | 4.67 | 2019-10-20T06:05:00Z | 14 | 201
PG&E | 43761 | 0.89375 | 38.7959 | -122.7673 |  | Herbaceous | 100+ Acres | Cal Fire |  | 001/006 |  | 230000 | Jumper | Overhead | Yes | 43761 | 0.88819 | Under Investigation | Jumper |  |  |  | This ignition relates to the Kincade Fire, which is reported in compliance with D.19-05-037. The origin and cause of the Kincade Fire is under investigation by CAL FIRE and PG&E. At this time, PG&E has not formed a conclusion about the origin or cause of the Kincade Fire. | no-match |  | 2019 | 10 | 23 | 21 | 27 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 23.9173 | 159_306 | <25mph | >=15mph | HFTD - Transmission | PG305 | 2.22 | 2019-10-23T06:40:00Z | 21.18 | 21 | PG303 | 4.59 | 2019-10-23T06:40:00Z | 30.53 | 71 | PG305 | 2.22 | 2019-10-23T06:40:00Z | 21.18 | 39 | PG303 | 4.59 | 2019-10-23T06:40:00Z | 30.53 | 132
PG&E | 43766 | 0.74167 | 37.0309 | -121.7788 | Vegetation | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 101682849 |  | 21000 | Conductor | Overhead | Yes | 43766 | 0.74167 | Vegetation |  | Veg. contact | Electric Facility |  |  | Fell into (No defect) | 2019-389 | 2019 | 10 | 28 | 17 | 48 | 19-0118112 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 16698 | 22.4395 | 172_227 | <25mph | >=15mph | HFTD - Distribution | PG370 | 3.22 | 2019-10-28T06:00:00Z | 42.17 | 22 | PG370 | 3.22 | 2019-10-28T06:00:00Z | 42.17 | 43 | PG370 | 3.22 | 2019-10-28T06:00:00Z | 42.17 | 41 | PG370 | 3.22 | 2019-10-28T06:00:00Z | 42.17 | 80
PG&E | 43766 | 0.78194 | 38.5646 | -122.4642 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 43432104 |  | 21000 | Conductor | Overhead | Yes | 43766 | 0.78194 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-357 | 2019 | 10 | 28 | 18 | 46 | 19-0118147 | Tier 3 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 496944 | 12.705 | 184_251 | <25mph | <15mph | HFTD - Distribution | PG199 | 2.69 | 2019-10-28T07:00:00Z | 32.21 | 23 | PG162 | 6.69 | 2019-10-28T06:30:00Z | 35.08 | 79 | PG199 | 2.69 | 2019-10-28T07:00:00Z | 32.21 | 44 | PG162 | 6.69 | 2019-10-28T06:30:00Z | 35.08 | 148
PG&E | 43766 | 0.54167 | 39.3208 | -121.1273 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 100099164 |  | 12000 | Transformer | Overbuild | Yes | 43766 | 0.54167 | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-398 | 2019 | 10 | 28 | 13 | 0 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 4.6326 | 165_186 | <25mph | <15mph | HFTD - Distribution | RRRC1 | 1.31 | 2019-10-28T06:13:00Z | 7 | 8 | PG348 | 4.93 | 2019-10-28T07:00:00Z | 15.28 | 62 | RRRC1 | 1.31 | 2019-10-28T06:13:00Z | 7 | 15 | PG424 | 7.74 | 2019-10-28T07:20:00Z | 23.6 | 112
PG&E | 43767 | 0.14514 | 37.0374 | -121.5207 | Animal Found | Hardwood Woodland | 0.25 - 10 Acres | Cal Fire |  | 1471 |  | 21000 | Fuse | Overhead | Yes | 43767 | 0.14514 | Contact - Animal - Other |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-283 | 2019 | 10 | 29 | 3 | 29 | 19-0118370 | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 3294 | 9.0524 | 155_199 | <25mph | <15mph | HFTD - Distribution | PG509 | 2.27 | 2019-10-29T06:00:00Z | 7.09 | 31 | PG509 | 2.27 | 2019-10-29T06:00:00Z | 7.09 | 46 | PG509 | 2.27 | 2019-10-29T06:00:00Z | 7.09 | 61 | PG509 | 2.27 | 2019-10-29T06:00:00Z | 7.09 | 88
PG&E | 43768 | 0.56389 | 38.4792 | -122.0302 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 063681102 |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact |  |  |  | no-match | 2019-338 | 2019 | 10 | 30 | 13 | 32 | No ILIS or TOTL available | Tier 2 | HFTD | Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 13.7479 | 155_266 | <25mph | <15mph | HFTD - Distribution | PG431 | 3.57 | 2019-10-30T06:20:00Z | 30.4 | 7 | PG583 | 4.98 | 2019-10-30T06:00:00Z | 32.82 | 14 | PG431 | 3.57 | 2019-10-30T06:20:00Z | 30.4 | 13 | PG583 | 4.98 | 2019-10-30T06:00:00Z | 32.82 | 26
PG&E | 43769 | 0.88958 | 39.661 | -120.6264 | Vegetation | Hardwood Forest | 1 meter - < 3 meters | Fire Dept | Sierra County FD | 152101101 |  | 12000 | Conductor | Overhead | Yes | 43769 | 0.88958 | Vegetation |  | Veg. contact | Electric Facility |  |  | Dead | 2019-390 | 2019 | 10 | 31 | 21 | 21 | 19-0115942 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Dead | 7121279 | 1.9823 | 150_204 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 0 | 0
PG&E | 43769 | 0.72431 | 38.0458 | -122.1905 |  | Herbaceous | 1 meter - < 3 meters | Fire Dept | Crockett FD | 13432207 |  | 21000 | Conductor | Overhead | Yes | 43769 | 0.72431 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-05 | 2019 | 10 | 31 | 17 | 23 | 19-0119756 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 138161 | 16.5541 | 148_260 | <25mph | >=15mph | HFTD - Distribution | DPXC1 | 3.83 | 2019-10-31T06:30:00Z | 10 | 40 | DPXC1 | 3.83 | 2019-10-31T06:30:00Z | 10 | 108 | DPXC1 | 3.83 | 2019-10-31T06:30:00Z | 10 | 74 | DPXC1 | 3.83 | 2019-10-31T06:30:00Z | 10 | 206
PG&E | 43769 | 0.67292 | 38.3845 | -122.1893 | Vegetation | Agriculture | 0.25 - 10 Acres | Cal Fire |  | Unknown |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact |  |  |  | no-match | 2019-396 | 2019 | 10 | 31 | 16 | 9 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 9.4513 | 148_242 | <25mph | <15mph | HFTD - Distribution | F0187 | 2.71 | 2019-10-31T06:15:00Z | 8.99 | 10 | PG185 | 4.03 | 2019-10-31T06:50:00Z | 17.83 | 66 | F0187 | 2.71 | 2019-10-31T06:15:00Z | 8.99 | 21 | PG185 | 4.03 | 2019-10-31T07:10:00Z | 18.99 | 126
PG&E | 43772 | 0.76806 | 36.2323 | -121.7622 | Vegetation | Hardwood Forest | 0.25 - 10 Acres | Cal Fire |  | 182941102 |  | 12000 | Conductor | Overhead | Yes | 43772 | 0.76806 | Vegetation |  | Veg. contact |  |  |  | Fell into (Moderate-Severe defect) | 2019-371 | 2019 | 11 | 3 | 18 | 26 | 19-0120570 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (Moderate-Severe defect) | 59211 | 6.5731 | 154_220 | <25mph | <15mph | HFTD - Distribution | PG362 | 1.69 | 2019-11-03T06:30:00Z | 20.18 | 13 | PG362 | 1.69 | 2019-11-03T06:30:00Z | 20.18 | 13 | PG362 | 1.69 | 2019-11-03T07:50:00Z | 20.18 | 23 | PG362 | 1.69 | 2019-11-03T07:50:00Z | 20.18 | 23
PG&E | 43773 | 0.98056 | 34.6619 | -120.0852 |  | Herbaceous | 3 meters - 0.25 Acres | Fire Dept | Unknown | 8145 |  | 12000 | Conductor | Overhead | Yes | 43773 | 0.98056 | Equipment - PG&E | Conductor |  |  |  |  | Other/Unknown | 2019-125 | 2019 | 11 | 4 | 23 | 32 | 19-0121150 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Conductor | 20066 | 12.9782 | 241_55 | <25mph | <15mph | HFTD - Distribution | SXWC1 | 2.51 | 2019-11-04T07:09:00Z | 4.99 | 15 | TT594 | 4.6 | 2019-11-04T07:46:00Z | 5.99 | 40 | SXWC1 | 2.51 | 2019-11-04T08:09:00Z | 4.99 | 28 | TT480 | 7.81 | 2019-11-04T08:20:00Z | 8.99 | 77
PG&E | 43779 | 0.40764 | 35.0787 | -120.4974 |  | Herbaceous | 1 meter - < 3 meters | Cal Fire |  | 4Bx1110190931 |  | 12000 | Conductor | Overhead | Yes | 43779 | 0.40764 | Contact - Animal - Bird |  | Animal contact |  | Animal Contact |  | Other/Unknown | 2019-431 | 2019 | 11 | 10 | 9 | 47 | 19-0123396 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 19943 | 14.5274 | 222_78 | <25mph | <15mph | HFTD - Distribution | PG168 | 0.77 | 2019-11-10T07:00:00Z | 8.05 | 14 | PG168 | 0.77 | 2019-11-10T07:00:00Z | 8.05 | 63 | PG168 | 0.77 | 2019-11-10T09:00:00Z | 11.34 | 26 | PG168 | 0.77 | 2019-11-10T09:00:00Z | 11.34 | 126
PG&E | 43780 | 0.28611 | 36.6822 | -119.1806 |  | Herbaceous | 3 meters - 0.25 Acres | Cal Fire |  | 4Tj1111191656 |  | 12000 | Other | Overhead | Yes | 43780 | 0.28611 | Contact - Animal - Bird |  | Animal contact | Electric Facility | Animal Contact |  | Other/Unknown | 2019-453 | 2019 | 11 | 11 | 6 | 52 | 19-0123468 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Animal | Animal | 109129 | 8.0472 | 280_167 | <25mph | <15mph | HFTD - Distribution | PG258 | 2.49 | 2019-11-11T07:50:00Z | 7 | 21 | PG374 | 4.84 | 2019-11-11T07:20:00Z | 7.61 | 62 | PG258 | 2.49 | 2019-11-11T07:50:00Z | 7 | 39 | PG374 | 4.84 | 2019-11-11T08:20:00Z | 7.81 | 116
PG&E | 43780 | 0.40694 | 37.8782 | -120.4596 | Vehicle | Urban | 3 meters - 0.25 Acres | Cal Fire |  | 101020184 |  | 17000 | Other | Overhead | Yes | 43780 | 0.40694 | Contact - 3rd Party |  | Vehicle contact | Electric Facility | Human Error |  | Other/Unknown | 2019-82 | 2019 | 11 | 11 | 9 | 46 | 19-0123520 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | 3rd Party | Vehicle | 38170 | 9.7973 | 223_232 | <25mph | <15mph | HFTD - Distribution | GNSC1 | 3.86 | 2019-11-11T07:03:00Z | 4.99 | 1 | PG166 | 4.81 | 2019-11-11T07:30:00Z | 6.71 | 15 | GNSC1 | 3.86 | 2019-11-11T08:03:00Z | 5.99 | 2 | PG166 | 4.81 | 2019-11-11T09:00:00Z | 9.06 | 28
PG&E | 43790 | 0.68472 | 40.3231 | -123.9202 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 192311141 |  | 12000 | Conductor | Overhead | No |  |  | Vegetation |  | Veg. contact | Electric Facility |  |  | no-match | 2019-416 | 2019 | 11 | 21 | 16 | 26 | No ILIS or TOTL available | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Other/Unknown | N.A. | 1.5362 | 77_369 | <25mph | <15mph | HFTD - Distribution |  |  |  | 0 | 0 | PG274 | 5.92 | 2019-11-21T07:30:00Z | 2.26 | 7 |  |  |  | 0 | 0 | PG274 | 5.92 | 2019-11-21T08:40:00Z | 2.55 | 13
PG&E | 43791 | 0.19653 | 39.6736 | -121.3855 | Vegetation | Conifer Forest | 1 meter - < 3 meters | Cal Fire |  | 103751102 |  | 12000 | Conductor | Overhead | Yes | 43791 | 0.19653 | Vegetation |  | Veg. contact |  |  |  | Fell into (slight defect) | 2019-428 | 2019 | 11 | 22 | 4 | 43 | 19-0127475 | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (slight defect) | 3712 | 7.2856 | 255_176 | <25mph | <15mph | HFTD - Distribution | PG099 | 3.33 | 2019-11-22T08:00:00Z | 0 | 7 | JBGC1 | 6.99 | 2019-11-22T07:13:00Z | 13 | 36 | PG099 | 3.33 | 2019-11-22T09:00:00Z | 0 | 13 | JBGC1 | 6.99 | 2019-11-22T08:13:00Z | 13 | 67
PG&E | 43795 | 0.59583 | 35.4427 | -120.7567 |  | Urban | 0.25 - 10 Acres | Cal Fire |  | 511791771829 |  | 12000 | Other | Overhead | Yes | 43795 | 0.59583 | Equipment - PG&E | Other |  |  |  |  | no-match | 2019-211 | 2019 | 11 | 26 | 14 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip Failure | Equip Failure - Other | N.A. | 15.168 | 211_98 | <25mph | >=15mph | HFTD - Distribution | PG141 | 2.39 | 2019-11-26T07:00:00Z | 31.5 | 14 | PG141 | 2.39 | 2019-11-26T07:00:00Z | 31.5 | 72 | PG141 | 2.39 | 2019-11-26T07:00:00Z | 31.5 | 26 | PG141 | 2.39 | 2019-11-26T07:00:00Z | 31.5 | 138
PG&E | 43796 | 0.65208 | 40.6579 | -122.4211 |  | Hardwood Woodland | 1 meter - < 3 meters | Cal Fire |  | 103521102-2101107406{2413} |  | 12000 | Fuse | Overhead | Yes | 43796 | 0.65208 | Other Fire: Non-PG&E related | [5 empty] | Other/Unknown |  | 2019 | 11 | 27 | 15 | 39 | 19-0130770 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Equip failure | Fuse | 8302 | 3.7534 | 142_199 | <25mph | <15mph | HFTD - Distribution | F5970 | 3 | 2019-11-27T07:47:00Z | 17 | 11 | PG265 | 7.46 | 2019-11-27T08:00:00Z | 38.07 | 75 | F5970 | 3 | 2019-11-27T09:00:00Z | 17 | 22 | PG265 | 7.46 | 2019-11-27T08:00:00Z | 38.07 | 142
PG&E | 43796 | 0.27569 | 37.2717 | -122.3078 | Vegetation | Conifer Forest | 3 meters - 0.25 Acres | Cal Fire |  | 24101103 |  | 12000 | Conductor | Overhead | Yes | 43796 | 0.27569 | Vegetation |  | Veg. contact | Electric Facility |  |  | Branch (OverHanging) | 2019-362 | 2019 | 11 | 27 | 6 | 37 | 19-0130047 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Branch (OverHanging) | 16680 | 7.6635 | 140_386 | <25mph | <15mph | HFTD - Distribution | LAHC1 | 3.7 | 2019-11-27T07:07:00Z | 11.01 | 1 | PG150 | 6.93 | 2019-11-27T07:40:00Z | 32.37 | 33 | LAHC1 | 3.7 | 2019-11-27T08:07:00Z | 14.99 | 2 | PG150 | 6.93 | 2019-11-27T08:10:00Z | 32.73 | 61
PG&E | 43798 | 0.84583 | 39.8503 | -121.6312 |  | Shrub | 1 meter - < 3 meters | Unknown |  | 40700248, 42578814, 42578813 |  | 60000 | Pole | Overhead | Yes | 43798 | 0.84583 | Equipment - PG&E | Pole |  |  |  |  | no-match | 2019-10 | 2019 | 11 | 29 | 20 | 18 | No ILIS or TOTL available | Tier 3 | HFTD | No Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Less than 300 Acres | Equip Failure | Pole | N.A. | 10.4217 | 173_341 | <25mph | <15mph | HFTD - Transmission | PG333 | 3.51 | 2019-11-29T07:00:00Z | 10.38 | 54 | PG333 | 3.51 | 2019-11-29T07:00:00Z | 10.38 | 99 | PG333 | 3.51 | 2019-11-29T07:00:00Z | 10.38 | 102 | PG333 | 3.51 | 2019-11-29T07:00:00Z | 10.38 | 185
PG&E | 43817 | 0.22569 | 38.2817 | -120.517 | Vegetation | Herbaceous | 0.25 - 10 Acres | Cal Fire |  | 101273893 |  | 12000 | Pole | Overhead | Yes | 43817 | 0.22569 | Vegetation |  | Veg. contact | Pole |  |  | Fell into (No defect) | 2019-361 | 2019 | 12 | 18 | 5 | 25 | 19-0137065 | Tier 2 | HFTD | No Fire Weather RFW Applicable | Distribution | HFTD - Distribution | Fire Less than 300 Acres | Vegetation | Fell into (No defect) | 3185 | 11.984 | 220_255 | <25mph | <15mph | HFTD - Distribution | ESPC1 | 1.49 | 2019-12-18T07:13:00Z | 15.99 | 25 | ESPC1 | 1.49 | 2019-12-18T07:13:00Z | 15.99 | 51 | ESPC1 | 1.49 | 2019-12-18T08:13:00Z | 15.99 | 48 | ESPC1 | 1.49 | 2019-12-18T08:13:00Z | 15.99 | 95
A. Kincade Fire | 2019-10-23 21:27 | 21:27 | 38.7925 | -122.7801 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 230000 | Conductor | Overhead |  |  |  | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1993 | 2019 | 10 | 23 | 21 | 27 |  | Tier 3 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Conductor | 826291590 | 18.2809 | 156_335 | <25mph | >=15mph | HFTD - Transmission | PG305 | 2.18 | 2019-10-24T04:20:00Z | 63.64 | 18 | PG305 | 2.18 | 2019-10-24T04:20:00Z | 63.64 | 65 | PG305 | 2.18 | 2019-10-24T05:10:00Z | 79.63 | 36 | PG305 | 2.18 | 2019-10-24T05:10:00Z | 79.63 | 130
B. Zogg Fire | 2020-09-27 16:03 | 16:03 | 40.5393 | -122.5666 |  |  | > 5000 Acres | Fire Agency | CalFire |  |  | 12000 | Conductor | Overhead |  |  |  | Equipment/ Facility Failure | Conductor | N.A. |  |  |  | no-match | 1993 | 2020 | 9 | 27 | 16 | 3 |  | Tier 2 | HFTD | Fire Weather RFW Applicable | Transmission | HFTD - Transmission | Fire Greater than 300 Acres | Equip Failure | Conductor | 826291590 | 18.2809 | 156_335 | <25mph | >=15mph | HFTD - Transmission | PG732 | 3.65 | 2020-09-27T22:10:00Z | 33.68 | 7 | PG732 | 3.65 | 2020-09-27T22:10:00Z | 33.68 | 67 | MMOC1 | 3.92 | 2020-09-28T00:00:00Z | 36 | 14 | MMOC1 | 3.92 | 2020-09-28T00:00:00Z | 36 | 134
Note on AM673: Chong, Yanping: was under investigation, Kincade

## Wind Analysis
0_Tranche | HFTD - Distribution
| 1_Wind Category | Values | [6 empty] | 0_HFTD | Count of Date
| <15mph | <15mph | >=15mph | >=15mph | Total Count | Total % |  |  | HFTD | 691
0_Driver | Count | % | Count | % |  |  |  |  | non-HFTD | 1511
3rd Party | 86 | 15.9% | 13 | 12.15% | 99 | 15.28% |  |  | Grand Total | 2202
Animal | 38 | 7.024% | 10 | 9.346% | 48 | 7.407%
Equip Failure | 142 | 26.25% | 27 | 25.23% | 169 | 26.08%
Unk or Other | 17 | 3.142% | 4 | 3.738% | 21 | 3.241%
Vegetation | 258 | 47.69% | 53 | 49.53% | 311 | 47.99%
Grand Total | 541 | 100% | 107 | 100% | 648 | 100%
[9 empty] | 0_Fire Greater than 300 Acres | 0_HFTD | 0_RFW Applicable | Count of Date
0_Tranche | HFTD - Distribution | [7 empty] | Fire Greater than 300 Acres | HFTD | Fire Weather RFW Applicable | 6
[11 empty] | No Fire Weather RFW Applicable | 5
| 1_Wind Categorization | Values | [7 empty] | non-HFTD | Fire Weather RFW Applicable | 1
| <25mph | <25mph | 25-40mph | 25-40mph | 40-55mph | 40-55mph | Total Count | Total % |  |  | No Fire Weather RFW Applicable | 7
0_Driver | Count | % | Count | % | Count | % |  |  | Fire Less than 300 Acres | HFTD | Fire Weather RFW Applicable | 44
3rd Party | 98 | 15.51% | 1 | 6.667% |  | 0% | 99 | 15.28% |  |  | No Fire Weather RFW Applicable | 636
Animal | 46 | 7.278% | 2 | 13.33% |  | 0% | 48 | 7.407% |  | non-HFTD | Fire Weather RFW Applicable | 80
Equip Failure | 165 | 26.11% | 4 | 26.67% |  | 0% | 169 | 26.08% |  |  | No Fire Weather RFW Applicable | 1423
Unk or Other | 21 | 3.323% |  | 0% |  | 0% | 21 | 3.241% | Grand Total |  |  | 2202
Vegetation | 302 | 47.78% | 8 | 53.33% | 1 | 100% | 311 | 47.99%
Grand Total | 632 | 100% | 15 | 100% | 1 | 100% | 648 | 100%
0_Tranche | HFTD - Distribution
0_Driver | Vegetation
| 1_Wind Categorization | Values
| <25mph | <25mph | 25-40mph | 25-40mph | 40-55mph | 40-55mph | Total Count | Total %
0_Subdriver | Count | % | Count | % | Count | %
Branch (Not overhanging, > 12ft) | 4 | 1.325% |  | 0% |  | 0% | 4 | 1.286%
Branch (Not overhanging, Distance Unknown) | 27 | 8.94% | 1 | 12.5% | 1 | 100% | 29 | 9.325%
Branch (OverHanging) | 31 | 10.26% |  | 0% |  | 0% | 31 | 9.968%
Dead | 15 | 4.967% |  | 0% |  | 0% | 15 | 4.823%
Fell into (Moderate-Severe defect) | 34 | 11.26% | 2 | 25% |  | 0% | 36 | 11.58%
Fell into (No defect) | 81 | 26.82% | 2 | 25% |  | 0% | 83 | 26.69%
Fell into (slight defect) | 35 | 11.59% |  | 0% |  | 0% | 35 | 11.25%
Grow Into | 1 | 0.3311% |  | 0% |  | 0% | 1 | 0.3215%
Other/Unknown | 74 | 24.5% | 3 | 37.5% |  | 0% | 77 | 24.76%
Grand Total | 302 | 100% | 8 | 100% | 1 | 100% | 311 | 100%
0_Tranche | HFTD - Distribution
0_Driver | Equip Failure
| 1_Wind Categorization | Values
| <25mph | <25mph | 25-40mph | 25-40mph | Total Count | Total % | Total Count | Total %
0_Subdriver | Count | % | Count | %
Capacitor Bank | 7 | 4.242% |  | 0% | 7 | 4.142% | 7 | 4.142%
Conductor | 67 | 40.61% | 2 | 50% | 69 | 40.83% | 69 | 40.83%
Crossarm | 5 | 3.03% | 1 | 25% | 6 | 3.55% | 6 | 3.55%
Equip Failure - Other | 20 | 12.12% | 1 | 25% | 21 | 12.43% | 21 | 12.43%
Equip Failure - Unknown | 5 | 3.03% |  | 0% | 5 | 2.959% | 5 | 2.959%
Fuse | 9 | 5.455% |  | 0% | 9 | 5.325% | 9 | 5.325%
Guy/Span Wire | 1 | 0.6061% |  | 0% | 1 | 0.5917% | 1 | 0.5917%
Insulator | 3 | 1.818% |  | 0% | 3 | 1.775% | 3 | 1.775%
Lightning Arrestor | 1 | 0.6061% |  | 0% | 1 | 0.5917% | 1 | 0.5917%
Pole | 6 | 3.636% |  | 0% | 6 | 3.55% | 6 | 3.55%
Splice/Clamp/Connector | 26 | 15.76% |  | 0% | 26 | 15.38% | 26 | 15.38%
Transformer | 13 | 7.879% |  | 0% | 13 | 7.692% | 13 | 7.692%
Voltage Regulator | 2 | 1.212% |  | 0% | 2 | 1.183% | 2 | 1.183%
Grand Total | 165 | 100% | 4 | 100% | 169 | 100% | 169 | 100%

## Risk Input Sheet
Pivot Tables based on All Ignition Dataset from 2015 - 2019
0_Tranche | 0_Driver | 0_Subdriver | Count of Date | 0_HFTD | Count of Date
HFTD - Distribution | 3rd Party | 3rd Party - Other | 8 | HFTD | 691
HFTD - Distribution | 3rd Party | 3rd Party - Unknown | 23 | non-HFTD | 1511
HFTD - Distribution | 3rd Party | Balloons | 9 | Grand Total | 2202
HFTD - Distribution | 3rd Party | Vehicle | 59
HFTD - Distribution | Animal | Animal | 48
HFTD - Distribution | Equip Failure | Capacitor Bank | 7
HFTD - Distribution | Equip Failure | Conductor | 69
HFTD - Distribution | Equip Failure | Crossarm | 6
HFTD - Distribution | Equip Failure | Equip Failure - Other | 21
HFTD - Distribution | Equip Failure | Equip Failure - Unknown | 5
HFTD - Distribution | Equip Failure | Fuse | 9 | 0_Fire Greater than 300 Acres | 0_HFTD | 0_RFW Applicable | Count of Date
HFTD - Distribution | Equip Failure | Guy/Span Wire | 1 | Fire Greater than 300 Acres | HFTD | Fire Weather RFW Applicable | 6
HFTD - Distribution | Equip Failure | Insulator | 3 |  |  | No Fire Weather RFW Applicable | 5
HFTD - Distribution | Equip Failure | Lightning Arrestor | 1 |  | non-HFTD | Fire Weather RFW Applicable | 1
HFTD - Distribution | Equip Failure | Pole | 6 |  |  | No Fire Weather RFW Applicable | 7
HFTD - Distribution | Equip Failure | Splice/Clamp/Connector | 26 | Fire Less than 300 Acres | HFTD | Fire Weather RFW Applicable | 44
HFTD - Distribution | Equip Failure | Transformer | 13 |  |  | No Fire Weather RFW Applicable | 636
HFTD - Distribution | Equip Failure | Voltage Regulator | 2 |  | non-HFTD | Fire Weather RFW Applicable | 80
HFTD - Distribution | Unk or Other | Unk or Other - Other | 3 |  |  | No Fire Weather RFW Applicable | 1423
HFTD - Distribution | Unk or Other | Unk or Other - Unknown | 18 | Grand Total |  |  | 2202
HFTD - Distribution | Vegetation | Branch (Not overhanging, > 12ft) | 4
HFTD - Distribution | Vegetation | Branch (Not overhanging, Distance Unknown) | 29
HFTD - Distribution | Vegetation | Branch (OverHanging) | 31
HFTD - Distribution | Vegetation | Dead | 15
HFTD - Distribution | Vegetation | Fell into (Moderate-Severe defect) | 36
HFTD - Distribution | Vegetation | Fell into (No defect) | 83
HFTD - Distribution | Vegetation | Fell into (slight defect) | 35
HFTD - Distribution | Vegetation | Grow Into | 1
HFTD - Distribution | Vegetation | Other/Unknown | 77
HFTD - Transmission | 3rd Party | 3rd Party - Other | 3
HFTD - Transmission | 3rd Party | 3rd Party - Unknown | 2
HFTD - Transmission | 3rd Party | Balloons | 1
HFTD - Transmission | Animal | Animal | 17
HFTD - Transmission | Equip Failure | Conductor | 5
HFTD - Transmission | Equip Failure | Equip Failure - Other | 6
HFTD - Transmission | Equip Failure | Insulator | 3
HFTD - Transmission | Equip Failure | Pole | 1
HFTD - Transmission | Equip Failure | Splice/Clamp/Connector | 1
HFTD - Transmission | Unk or Other | Unk or Other - Other | 1
HFTD - Transmission | Unk or Other | Unk or Other - Unknown | 2
HFTD - Transmission | Vegetation | Other/Unknown | 1
non-HFTD - Distribution | 3rd Party | 3rd Party - Other | 30
non-HFTD - Distribution | 3rd Party | 3rd Party - Unknown | 39
non-HFTD - Distribution | 3rd Party | Balloons | 65
non-HFTD - Distribution | 3rd Party | Vehicle | 157
non-HFTD - Distribution | Animal | Animal | 192
non-HFTD - Distribution | Equip Failure | Capacitor Bank | 40
non-HFTD - Distribution | Equip Failure | Conductor | 206
non-HFTD - Distribution | Equip Failure | Crossarm | 18
non-HFTD - Distribution | Equip Failure | Equip Failure - Other | 73
non-HFTD - Distribution | Equip Failure | Equip Failure - Unknown | 8
non-HFTD - Distribution | Equip Failure | Fuse | 28
non-HFTD - Distribution | Equip Failure | Guy/Span Wire | 2
non-HFTD - Distribution | Equip Failure | Insulator | 22
non-HFTD - Distribution | Equip Failure | Lightning Arrestor | 16
non-HFTD - Distribution | Equip Failure | Pole | 35
non-HFTD - Distribution | Equip Failure | Recloser | 12
non-HFTD - Distribution | Equip Failure | Sectionalizer | 1
non-HFTD - Distribution | Equip Failure | Splice/Clamp/Connector | 115
non-HFTD - Distribution | Equip Failure | Switch | 8
non-HFTD - Distribution | Equip Failure | Transformer | 62
non-HFTD - Distribution | Equip Failure | Voltage Regulator | 5
non-HFTD - Distribution | Unk or Other | Unk or Other - Other | 12
non-HFTD - Distribution | Unk or Other | Unk or Other - Unknown | 52
non-HFTD - Distribution | Vegetation | Branch (Not overhanging, > 12ft) | 3
non-HFTD - Distribution | Vegetation | Branch (Not overhanging, 4-12ft) | 2
non-HFTD - Distribution | Vegetation | Branch (Not overhanging, Distance Unknown) | 34
non-HFTD - Distribution | Vegetation | Branch (OverHanging) | 37
non-HFTD - Distribution | Vegetation | Dead | 5
non-HFTD - Distribution | Vegetation | Fell into (Moderate-Severe defect) | 5
non-HFTD - Distribution | Vegetation | Fell into (No defect) | 40
non-HFTD - Distribution | Vegetation | Fell into (slight defect) | 9
non-HFTD - Distribution | Vegetation | Grow Into | 7
non-HFTD - Distribution | Vegetation | Other/Unknown | 114
non-HFTD - Transmission | 3rd Party | 3rd Party - Other | 3
non-HFTD - Transmission | 3rd Party | 3rd Party - Unknown | 1
non-HFTD - Transmission | 3rd Party | Balloons | 2
non-HFTD - Transmission | 3rd Party | Vehicle | 7
non-HFTD - Transmission | Animal | Animal | 16
non-HFTD - Transmission | Equip Failure | Conductor | 3
non-HFTD - Transmission | Equip Failure | Crossarm | 1
non-HFTD - Transmission | Equip Failure | Equip Failure - Other | 1
non-HFTD - Transmission | Equip Failure | Insulator | 3
non-HFTD - Transmission | Equip Failure | Pole | 1
non-HFTD - Transmission | Equip Failure | Transformer | 2
non-HFTD - Transmission | Unk or Other | Unk or Other - Other | 8
non-HFTD - Transmission | Unk or Other | Unk or Other - Unknown | 8
non-HFTD - Substation | 3rd Party | 3rd Party - Other | 1
Grand Total |  |  | 2202

## HFTD-Distribution Pivots
Pivot Tables based on All Ignition Dataset from 2015 - 2019 for HFTD-Distribution Tranche
2019 |  |  | 2015-2019 |  |  | 2015-2018
0_Year | 2019 |  | 0_Year | (All) |  | 0_Year | (Multiple Items)
0_Tranche | HFTD - Distribution |  | 0_Tranche | HFTD - Distribution |  | 0_Tranche | HFTD - Distribution
0_Driver | 0_Subdriver | Count | 0_Driver | 0_Subdriver | Count | 0_Driver | 0_Subdriver | Count
3rd Party | 3rd Party - Other | 5 | Vegetation | Branch (Not overhanging, > 12ft) | 4 | Vegetation | Branch (Not overhanging, > 12ft) | 3
| Vehicle | 5 | Vegetation | Branch (Not overhanging, Distance Unknown) | 29 | Vegetation | Branch (Not overhanging, Distance Unknown) | 25
Animal | Animal | 11 | Vegetation | Branch (OverHanging) | 31 | Vegetation | Branch (OverHanging) | 25
Equip Failure | Conductor | 10 | Vegetation | Dead | 15 | Vegetation | Dead | 10
| Equip Failure - Other | 6 | Vegetation | Fell into (Moderate-Severe defect) | 36 | Vegetation | Fell into (Moderate-Severe defect) | 29
| Fuse | 1 | Vegetation | Fell into (No defect) | 83 | Vegetation | Fell into (No defect) | 70
| Insulator | 1 | Vegetation | Fell into (slight defect) | 35 | Vegetation | Fell into (slight defect) | 28
| Pole | 1 | Vegetation | Grow Into | 1 | Vegetation | Grow Into | 1
| Splice/Clamp/Connector | 4 | Vegetation | Other/Unknown | 77 | Vegetation | Other/Unknown | 61
| Transformer | 2 | 3rd Party | 3rd Party - Other | 8 | 3rd Party | 3rd Party - Other | 3
Vegetation | Branch (Not overhanging, > 12ft) | 1 | 3rd Party | 3rd Party - Unknown | 23 | 3rd Party | 3rd Party - Unknown | 23
| Branch (Not overhanging, Distance Unknown) | 4 | 3rd Party | Balloons | 9 | 3rd Party | Balloons | 9
| Branch (OverHanging) | 6 | 3rd Party | Vehicle | 59 | 3rd Party | Vehicle | 54
| Dead | 5 | Animal | Animal | 48 | Animal | Animal | 37
| Fell into (Moderate-Severe defect) | 7 | Equip Failure | Capacitor Bank | 7 | Equip Failure | Capacitor Bank | 7
| Fell into (No defect) | 13 | Equip Failure | Conductor | 69 | Equip Failure | Conductor | 59
| Fell into (slight defect) | 7 | Equip Failure | Crossarm | 6 | Equip Failure | Crossarm | 6
| Other/Unknown | 16 | Equip Failure | Equip Failure - Other | 21 | Equip Failure | Equip Failure - Other | 15
Grand Total |  | 105 | Equip Failure | Equip Failure - Unknown | 5 | Equip Failure | Equip Failure - Unknown | 5
|  |  | Equip Failure | Fuse | 9 | Equip Failure | Fuse | 8
|  |  | Equip Failure | Guy/Span Wire | 1 | Equip Failure | Guy/Span Wire | 1
|  |  | Equip Failure | Insulator | 3 | Equip Failure | Insulator | 2
|  |  | Equip Failure | Lightning Arrestor | 1 | Equip Failure | Lightning Arrestor | 1
|  |  | Equip Failure | Pole | 6 | Equip Failure | Pole | 5
|  |  | Equip Failure | Splice/Clamp/Connector | 26 | Equip Failure | Splice/Clamp/Connector | 22
|  |  | Equip Failure | Transformer | 13 | Equip Failure | Transformer | 11
|  |  | Equip Failure | Voltage Regulator | 2 | Equip Failure | Voltage Regulator | 2
|  |  | Unk or Other | Unk or Other - Other | 3 | Unk or Other | Unk or Other - Other | 3
|  |  | Unk or Other | Unk or Other - Unknown | 18 | Unk or Other | Unk or Other - Unknown | 18
|  |  | Grand Total |  | 648 | Grand Total |  | 543

## LookUps
Lookup Tables used in All Ignition Data Set sheet
Voltage2TandDTable | Used in 0_DistributionTransmission column of All Ignition Data Set | EquipSubdriverTable | Used in 0_Subdriver column of All Ignition Data Set.
Voltage Type | Assign to Distribution or Transmission | Equipment /Facility Failure | Equip Failure Subdriver Names | Note
0 – 750 | Distribution | Pole | Pole
4000 | Distribution | Fuse | Fuse
12000 | Distribution | Splice/Clamp/Connector | Splice/Clamp/Connector
17000 | Distribution | Conductor | Conductor
21000 | Distribution | Other | Equip Failure - Other | (modified so that this can be differentiated with Other subdriver of other drivers)
60000 | Transmission | Crossarm | Crossarm
70000 | Transmission | Insulator | Insulator
115000 | Transmission | Lightning Arrestor | Lightning Arrestor
230000 | Transmission | Transformer | Transformer
500000 | Transmission | Switch | Switch
|  | Capacitor Bank | Capacitor Bank
|  | Voltage Regulator | Voltage Regulator
|  | Guy/Span Wire | Guy/Span Wire
|  | Sectionalizer | Sectionalizer
|  | Recloser | Recloser
|  | Line Recloser | Recloser | (modified since this is the same as Recloser)
|  | Circuit Breaker | Equip Failure - Other | (modified because there is just one data point)
|  | Jumper | Jumper
`

## Large Fires (PGETerritory)
CalFire wildfires that were greater than 300 acres that occurred in PG&E territory (2015 - 2019)
Incident # | County | Fire Name | Start | Cont. | DPA | Total Acres Burned | Type | Cause | Dest. | Dam. | Fire | Civil | 0_Total Fatalities | 0_Fire Size Grouping | 0_Event with Fatalities | START DATE | CONTAINED DATE | PGE? | 0_Buildings Destroyed Modified | 0_Source | 0_Year | 0_Time | 0_Latitude | 0_Longitude | 0_lat/lon available | 0_HFTD | 0_Has Time available | 0_Time and Loc Data Available for RFW Analysis? | 0_RFW Applicable | 0_Customer Minutes Interrupted | 0_Buildings Destroyed >= 100
MMU-8812 | MERCED | FOREBAY | 2015-05-11 | 2015-05-12 | CAL FIRE | 692 | G | VEHICLE |  |  |  |  | 0 |  |  | 20150511 | 20150512 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/5/11/forebay-fire/ |  |  | 37.0831 | -121.0696 |  | non-HFTD |  |  | No RFW Analysis Performed
SHF-1371 | TRINITY | SADDLE | 2015-06-09 | 2015-06-25 | USFS | 1542 | T,B | LIGHTNING |  |  |  |  | 0 |  |  | 20150609 | 20150625 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/6/10/saddle-fire/ |  |  | 40.924 | -123.168 |  | HFTD |  |  | No RFW Analysis Performed
FHL-001570 | MONTEREY | PEANUT | 2015-06-11 | 2015-06-11 | DOD | 1532 | G | UNDETERMINED |  |  |  |  | 0 |  |  | 20150611 | 20150611 | PGE Teritory |  |  |  |  | N.A. | N.A. |  | No lat/lon available |  |  | No RFW Analysis Performed
MMU-11662 | MADERA | CORRINE | 2015-06-18 | 2015-06-24 | CAL FIRE | 920 | T,B,G | ELECTRICAL POWER | 2 |  |  |  | 0 |  |  | 20150618 | 20150624 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/6/18/corrine-fire/ |  | 21:00 | 37.1658 | -119.5239 |  | HFTD |  |  | No Red Flag Warning Applicable
SNF-1058 | MADERA | SKY | 2015-06-18 | 2015-06-26 | USFS | 500 | T,B | VEHICLE |  |  |  |  | 0 |  |  | 20150618 | 20150626 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/6/18/sky-fire/ https://goldrushcam.com/sierrasuntimes/index.php/news/local-news/3595-sky-fire-in-madera-county-near-oakhurst-june-19-2015 |  | 2:00 | 0 | 0 |  | No lat/lon available |  |  | No RFW Analysis Performed
SLU-6113 | SAN LUIS OBISPO | PARKHILL | 2015-06-20 | 2015-06-20 | CAL FIRE | 1791 | B | VEHICLE | 18 | 3 |  |  | 0 |  |  | 20150620 | 20150620 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/6/20/park-hill-fire/ |  | 14:41 | 0 | 0 |  | No lat/lon available |  |  | No RFW Analysis Performed
AEU-17193 | SACRAMENTO | IONE | 2015-07-02 | 2015-07-05 | CAL FIRE | 357 | G | ARSON |  |  |  |  | 0 |  |  | 20150702 | 20150705 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/7/2/ione-fire/ |  | 1:58 | 0 | 0 |  | No lat/lon available |  |  | No RFW Analysis Performed
SKU-5078 | SISKIYOU | YORK | 2015-07-04 | 2015-07-06 | CAL FIRE | 395 | G | LIGHTNING |  |  |  |  | 0 |  |  | 20150704 | 20150706 | PGE Teritory |  |  |  |  | N.A. | N.A. |  | No lat/lon available |  |  | No RFW Analysis Performed
MMU-13970 | MERCED | MCCABE | 2015-07-18 | 2015-07-22 | CAL FIRE | 1600 | G | LIGHTNING |  |  |  |  | 0 |  |  | 20150718 | 20150722 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/7/18/mccabe-fire/ |  | 22:27 | 0 | 0 |  | No lat/lon available |  |  | No RFW Analysis Performed
SQF-2313 | TULARE | CABIN | 2015-07-19 | 2015-09-05 | USFS | 6980 | T | LIGHTNING |  |  |  |  | 0 |  |  | 20150719 | 20150905 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/7/19/cabin-fire/ |  |  | 36.24 | -118.54 |  | HFTD |  |  | No RFW Analysis Performed
TUU-383 | TULARE | TRIPLE 3 | 2015-07-21 | 2015-07-21 | CAL FIRE | 430 | G | LIGHTNING |  |  |  |  | 0 |  |  | 20150721 | 20150721 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/7/21/triple-fire/ |  | 12:35 | 36.0852 | -118.8242 |  | HFTD |  |  | No Red Flag Warning Applicable
LNU-6678 | NAPA | WRAGG | 2015-07-22 | 2015-08-06 | CAL FIRE | 8051 | B | VEHICLE | 2 | 5 |  |  | 0 |  |  | 20150722 | 20150806 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/7/22/wragg-fire/ |  | 14:24 | 38.4994 | -122.1145 |  | HFTD |  |  | No Red Flag Warning Applicable
NEU-17851 | NEVADA | LOWELL | 2015-07-25 | 2015-08-12 | CAL FIRE | 2304 | T,G | UNDETERMINED | 3 | 1 |  |  | 0 |  |  | 20150725 | 20150812 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/7/25/lowell-fire/ |  | 14:37 | 39.1921 | -120.8823 |  | HFTD |  |  | No Red Flag Warning Applicable
SNF-1689 | MADERA | WILLOW | 2015-07-25 | 2015-08-15 | USFS | 5702 | T | UNDETERMINED |  |  |  |  | 0 |  |  | 20150725 | 20150815 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/7/25/willow-fire/ |  |  | 37.2797 | -119.5001 |  | HFTD |  |  | No RFW Analysis Performed
BTU-10917 | BUTTE | SWEDES | 2015-07-29 | 2015-08-16 | CAL FIRE | 400 | B | DEBRIS BURNING | 16 |  |  |  | 0 |  |  | 20150729 | 20150816 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/7/29/swedes-fire/ |  | 11:25 | 39.4396 | -121.3879 |  | HFTD |  |  | No Red Flag Warning Applicable
LNU-6984 | LAKE | ROCKY | 2015-07-29 | 2015-08-14 | CAL FIRE | 69636 | T,B,G | EQUIPMENT | 96 | 8 |  |  | 0 |  |  | 20150729 | 20150814 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/7/29/rocky-fire/ |  | 15:29 | 38.8864 | -122.4762 |  | HFTD |  |  | No Red Flag Warning Applicable
HUU-5606 | HUMBOLDT | HUMBOLDT COMPLEX | 2015-07-30 | 2015-08-21 | CAL FIRE | 4883 | T | LIGHTNING | 7 |  |  |  | 0 |  |  | 20150730 | 20150821 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/7/30/humboldt-lightning-fires/ |  | 16:02 | 0 | 0 |  | No lat/lon available |  |  | No RFW Analysis Performed
MDF-570 | MODOC | FROG | 2015-07-30 | 2015-08-06 | USFS | 4863 | T | LIGHTNING |  |  | 1 |  | 1 |  |  | 20150730 | 20150806 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/7/30/frog-fire/ https://www.wildfirelessons.net/HigherLogic/System/DownloadDocumentFile.ashx?DocumentFileKey=c197dde6-ced5-01a2-0b0d-2b735e4934ea&forceDialog=1 |  | 17:32 | 41.399 | -121.392 |  | non-HFTD |  |  | No Red Flag Warning Applicable
SHF-2066 | TRINITY | RIVER COMPLEX | 2015-07-30 | 2015-10-15 | USFS | 77081 | T | LIGHTNING |  |  |  |  | 0 |  |  | 20150730 | 20151015 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/7/30/river-complex/ https://en.wikipedia.org/wiki/River_Complex_Fire |  |  | 40.913 | -123.437 |  | HFTD |  |  | No RFW Analysis Performed
SRF-1476 | HUMBOLDT | ROUTE COMPLEX | 2015-07-30 | 2015-08-31 | USFS | 35675 | T | LIGHTNING | 2 |  |  |  | 0 |  |  | 20150730 | 20150831 | PGE Teritory |  |  |  |  | N.A. | N.A. |  | No lat/lon available |  |  | No RFW Analysis Performed
SHF-2067 | TRINITY | FORK COMPLEX | 2015-07-30 | 2015-08-29 | USFS | 36499 | T,B,G | UNDETERMINED | 12 |  |  |  | 0 |  |  | 20150730 | 20150829 | PGE Teritory |  |  |  |  | 0 | 0 |  | No lat/lon available |  |  | No RFW Analysis Performed
SRF-1433 | TRINITY | MAD RIVER COMPLEX | 2015-07-30 | 2015-09-03 | USFS | 37462 | T | LIGHTNING | 4 |  |  |  | 0 |  |  | 20150730 | 20150903 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/7/30/mad-river-complex/ https://calfire.blogspot.com/2015/07/ca-srf-mad-river-complex-numerous.html |  | 12:00 | 40.335 | -123.383 |  | HFTD |  |  | No Red Flag Warning Applicable
MMU-14907 | MERCED | CREEK | 2015-07-31 | 2015-07-31 | CAL FIRE | 1450 | G | VEHICLE |  |  |  |  | 0 |  |  | 20150731 | 20150731 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/7/31/creek-fire/ |  |  | 0 | 0 |  | No lat/lon available |  |  | No RFW Analysis Performed
SNF-1746 | FRESNO | ROUGH | 2015-07-31 | 2015-12-01 | USFS | 151623 | T,B,G | LIGHTNING | 4 |  |  |  | 0 |  |  | 20150731 | 20151201 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/7/31/rough-fire/ |  |  | 36.874 | -118.905 |  | HFTD |  |  | No RFW Analysis Performed
SHF-2108 | TRINITY | SOUTH COMPLEX | 2015-08-01 | 2015-10-01 | USFS | 29416 | T | LIGHTNING | 3 |  |  |  | 0 |  |  | 20150801 | 20151001 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/7/30/south-complex/ |  |  | 0 | 0 |  | No lat/lon available |  |  | No RFW Analysis Performed
NOD-3806 | LASSEN | DODGE | 2015-08-03 | 2015-08-17 | BLM | 10570 | B | HUMAN |  |  |  |  | 0 |  |  | 20150803 | 20150817 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/8/3/dodge-fire/ |  |  | 40.938 | -120.105 |  | HFTD |  |  | No RFW Analysis Performed
LNU-7410 | LAKE | JERUSALEM | 2015-08-09 | 2015-08-25 | CAL FIRE | 25118 | B | UNDETERMINED | 27 |  |  |  | 0 |  |  | 20150809 | 20150825 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/8/9/jerusalem-fire/ |  | 15:34 | 38.8143 | -122.4867 |  | HFTD |  |  | No Red Flag Warning Applicable
SLU-8555 | SAN LUIS OBISPO | CUESTA | 2015-08-16 | 2015-09-03 | CAL FIRE | 2446 | G | VEHICLE | 1 |  |  |  | 0 |  |  | 20150816 | 20150903 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/8/16/cuesta-fire/ |  | 18:13 | 35.3477 | -120.6269 |  | HFTD |  |  | No Red Flag Warning Applicable
KRN-30112 | KERN | DEER | 2015-08-18 | 2015-08-20 | KRN | 311 | T,B,G | UNDETERMINED |  |  |  |  | 0 |  |  | 20150818 | 20150820 | PGE Teritory |  |  |  |  | N.A. | N.A. |  | No lat/lon available |  |  | No RFW Analysis Performed
SCU-5524 | ALAMEDA | TESLA | 2015-08-19 | 2015-08-25 | CAL FIRE | 2850 | G | UNDETERMINED | 1 |  |  |  | 0 |  |  | 20150819 | 20150825 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/8/19/tesla-fire/ |  | 14:45 | 37.3845 | -121.3732 |  | HFTD |  |  | No Red Flag Warning Applicable
LNU-8268 | LAKE | ELK | 2015-09-02 | 2015-09-06 | CAL FIRE | 700 | B | EQUIPMENT |  |  |  |  | 0 |  |  | 20150902 | 20150906 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/9/2/elk-fire/ |  | 14:57 | 55.23 | -122 |  | non-HFTD |  |  | No Red Flag Warning Applicable
YNP-123 | MARIPOSA | TENAYA | 2015-09-07 | 2015-09-16 | USFS | 415 | T,B | UNDETERMINED |  |  |  |  | 0 |  |  | 20150907 | 20150916 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/9/7/tenaya-fire/ |  |  | 0 | 0 |  | No lat/lon available |  |  | No RFW Analysis Performed
AEU-24918 | AMADOR | BUTTE | 2015-09-09 | 2015-10-23 | CAL FIRE | 70868 | T,B,G | ELECTRICAL POWER | 965 |  |  | 2 | 2 |  |  | 20150909 | 20151023 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/9/9/butte-fire/ |  | 14:26 | 38.3297 | -120.7042 |  | HFTD |  |  | No Red Flag Warning Applicable
BTU-13363 | BUTTE | LUMPKIN | 2015-09-11 | 2015-09-21 | CAL FIRE | 1040 | T,B | ARSON |  |  |  |  | 0 |  |  | 20150911 | 20150921 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/9/11/lumpkin-fire/ |  | 14:15 | 39.5218 | -121.3363 |  | HFTD |  |  | No Red Flag Warning Applicable
LNU-8670 | LAKE | VALLEY | 2015-09-12 | 2015-10-15 | CAL FIRE | 76067 | T,B,G | ELECTRICAL POWER | 1958 | 93 |  | 4 | 4 |  |  | 20150912 | 20151015 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/9/12/valley-fire/ |  | 13:24 | 38.8489 | -122.7589 |  | HFTD |  |  | No Red Flag Warning Applicable
BEU-4217 | MONTEREY | TASSAJARA | 2015-09-19 | 2015-09-29 | CAL FIRE | 1086 | B | UNDETERMINED | 20 | 1 |  |  | 0 |  |  | 20150919 | 20150929 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/9/19/tassajara-fire/ |  | 15:00 | 36.37 | -121.5896 |  | HFTD |  |  | No Red Flag Warning Applicable
BTU-14554 | BUTTE | MERIDIAN | 2015-10-03 | 2015-10-04 | CAL FIRE | 860 | G | EQUIPMENT |  |  |  |  | 0 |  |  | 20151003 | 20151004 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/10/3/meridian-fire/ |  | 21:15 | 0 | 0 |  | No lat/lon available |  |  | No RFW Analysis Performed
BEU-4582 | SAN BENITO | CIENEGA | 2015-10-12 | 2015-10-16 | CAL FIRE | 690 | T,B | ELECTRICAL POWER |  |  |  |  | 0 |  |  | 20151012 | 20151016 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2015/10/12/cienega-fire/ |  | 16:00 | 36.7085 | -121.3273 |  | non-HFTD |  |  | No Red Flag Warning Applicable
SLU-5280 | SAN LUIS OBISPO | CAMP ROBERTS | 2016-05-18 | 2016-05-20 | MIL | 3712 | G | UNDETERMINED |  |  |  |  | 0 |  |  | 20160518 | 20160520 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/5/18/roberts-fire/ |  |  | 0 | 0 |  | No lat/lon available |  |  | No RFW Analysis Performed
BEU-2369 | MONTEREY | METZ | 2016-05-22 | 2016-05-25 | CAL FIRE | 3876 | B,G | DEBRIS BURNING |  |  |  |  | 0 |  |  | 20160522 | 20160525 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/5/22/metz-fire/ |  | 15:27 | 36.3812 | -121.2006 |  | non-HFTD |  |  | No Red Flag Warning Applicable
BEU-2369 | MONTEREY | METZ | 2016-05-22 | 2016-05-25 | CAL FIRE | 3876 | B,G | DEBRIS BURNING |  |  |  |  | 0 |  |  | 20160522 | 20160525 | PGE Teritory |  |  |  |  | Duplicate | Duplicate |  | non-HFTD |  |  | No RFW Analysis Performed
CND-1134 | TULARE | CHIMNEY | 2016-06-01 | 2016-06-07 | BLM | 1324 | B,G | HUMAN |  |  |  |  | 0 |  |  | 20160601 | 20160607 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/6/1/chimney-fire/ |  |  | 35.8488 | -118.0859 |  | HFTD |  |  | No RFW Analysis Performed
FHL-1475 | MONTEREY | STONY | 2016-06-02 | 2016-06-17 | USFS | 3000 | B,G | UNDETERMINED |  |  |  |  | 0 |  |  | 20160602 | 20160617 | PGE Teritory |  |  |  |  | N.A. | N.A. |  | No lat/lon available |  |  | No RFW Analysis Performed
CND-1171 | SAN LUIS OBISPO | SODA | 2016-06-04 | 2016-06-06 | BLM | 2003 | B,G | UNDETERMINED |  |  |  |  | 0 |  |  | 20160604 | 20160606 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/6/4/soda-fire/ |  |  | 35.0138 | -119.5821 |  | non-HFTD |  |  | No RFW Analysis Performed
LPF-1504 | MONTEREY | COLEMAN | 2016-06-04 | 2016-06-17 | USFS | 2520 | B,G | UNDETERMINED | 1 |  |  |  | 0 |  |  | 20160604 | 20160617 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/6/4/coleman-fire/ |  |  | 36.0154 | -121.2503 |  | non-HFTD |  |  | No RFW Analysis Performed
KNF-4500 | SISKIYOU | PONY | 2016-06-07 | 2016-10-02 | USFS | 2860 | B,T | UNDETERMINED |  |  |  |  | 0 |  |  | 20160607 | 20161002 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/6/7/pony-fire/ |  |  | 41.623 | -123.557 |  | HFTD |  |  | No RFW Analysis Performed
SBC-7344 | SANTA BARBARA | SHERPA | 2016-06-15 | 2016-06-23 | USFS | 7474 | B,G | UNDETERMINED | 5 |  |  |  | 0 |  |  | 20160615 | 20160623 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/6/15/sherpa-fire/ |  | 15:21 | 34.776 | -119.643 |  | non-HFTD |  |  | No Red Flag Warning Applicable
CND-1415 | KERN | ERSKINE | 2016-06-23 | 2016-07-09 | USFS | 48019 | B,G,T | UNDETERMINED | 286 | 12 |  | 2 | 2 |  |  | 20160623 | 20160709 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/6/23/erskine-fire/ https://en.wikipedia.org/wiki/Erskine_Fire |  | 16:00 | 35.6115 | -118.4563 |  | HFTD |  |  | No Red Flag Warning Applicable
MMU-12363 | MERCED | DINOSAUR | 2016-06-25 | 2016-06-26 | CAL FIRE | 1246 | G | VEHICLE |  |  |  |  | 0 |  |  | 20160625 | 20160626 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/6/25/dinosaur-fire/ |  |  | 37.0715 | -121.2015 |  | non-HFTD |  |  | No RFW Analysis Performed
YNP-41 | MARIPOSA | LAKES | 2016-06-26 | 2016-10-31 | NPS | 1001 | B,T | LIGHTNING |  |  |  |  | 0 |  |  | 20160626 | 20161031 | PGE Teritory |  |  |  |  | N.A. | N.A. |  | No lat/lon available |  |  | No RFW Analysis Performed
AEU-17670 | SACRAMENTO | RANCHO | 2016-06-28 | 2016-06-30 | CAL FIRE | 372 | G | VEHICLE |  |  |  |  | 0 |  |  | 20160628 | 20160630 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/6/28/rancho-fire/ |  |  | 38.385 | -121.0036 |  | non-HFTD |  |  | No RFW Analysis Performed
NEU-15200 | PLACER | TRAILHEAD | 2016-06-28 | 2016-08-14 | CAL FIRE | 5645 | B,T | UNDETERMINED |  |  |  |  | 0 |  |  | 20160628 | 20160814 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/6/28/trailhead-fire/ |  | 13:55 | 38.9674 | -120.9375 |  | HFTD |  |  | No Red Flag Warning Applicable
TGU-5731 | TEHAMA | COLYEAR | 2016-06-30 | 2016-07-06 | CAL FIRE | 464 | B,G | ELECTRICAL POWER |  |  |  |  | 0 |  |  | 20160630 | 20160706 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/6/30/colyear-fire/ |  | 13:32 | 40.0353 | -122.5694 |  | HFTD |  |  | No Red Flag Warning Applicable
FKU-9100 | FRESNO | CURRY | 2016-07-01 | 2016-07-04 | CAL FIRE | 2944 | B,G | UNDETERMINED |  |  |  |  | 0 |  |  | 20160701 | 20160704 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/7/1/curry-fire/ |  | 17:16 | 36.0749 | -120.452 |  | non-HFTD |  |  | No Red Flag Warning Applicable
KRN-24109 | KERN | DEER | 2016-07-01 | 2016-07-10 | CC | 1785 | B,G,T | UNDETERMINED |  |  |  |  | 0 |  |  | 20160701 | 20160710 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/7/1/deer-fire/ |  | 14:05 | 35.2099 | -118.7227 |  | HFTD |  |  | No Red Flag Warning Applicable
TCU-6914 | CALAVERAS | APPALOOSA | 2016-07-02 | 2016-07-15 | CAL FIRE | 310 | B,G,T | ELECTRICAL POWER | 1 |  |  |  | 0 |  |  | 20160702 | 20160715 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/7/2/appaloosa-fire/ |  |  | 38.0284 | -120.6115 |  | HFTD |  |  | No RFW Analysis Performed
SHU-6739 | SHASTA | FIDDLER | 2016-07-08 | 2016-07-09 | CAL FIRE | 303 | B,G,T | ARSON | 1 | 1 |  |  | 0 |  |  | 20160708 | 20160709 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/7/8/fiddler-fire/ |  | 22:45 | 40.3687 | -122.7291 |  | HFTD |  |  | No Red Flag Warning Applicable
KRN-25390 | KERN | FORT | 2016-07-08 | 2016-07-09 | CC | 554 | B,G | UNDETERMINED |  |  |  |  | 0 |  |  | 20160708 | 20160709 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/7/8/fort-fire/ |  |  | 34.913 | -118.9082 |  | non-HFTD |  |  | No RFW Analysis Performed
TCU-7341 | CALAVERAS | PACHECO | 2016-07-12 | 2016-07-18 | CAL FIRE | 341 | B,G,T | EQUIPMENT | 2 |  |  |  | 0 |  |  | 20160712 | 20160718 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/7/12/pacheco-fire/ |  |  | 38.0806 | -120.8139 |  | HFTD |  |  | No RFW Analysis Performed
BEU-3422 | MONTEREY | SOBERANES | 2016-07-22 | 2016-10-13 | CAL FIRE | 132127 | B,G,T | CAMPFIRE | 68 | 5 | 1 |  | 1 |  |  | 20160722 | 20161013 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/7/22/soberanes-fire/ |  | 8:48 | 36.4599 | -121.8994 |  | HFTD |  |  | No Red Flag Warning Applicable
FKU-10852 | FRESNO | GOOSE | 2016-07-30 | 2016-08-09 | CAL FIRE | 2241 | B,G | ARSON | 9 | 1 |  |  | 0 |  |  | 20160730 | 20160809 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/7/30/goose-fire/ |  | 16:40 | 37.0159 | -119.5051 |  | HFTD |  |  | No Red Flag Warning Applicable
BTU-11608 | BUTTE | 99 | 2016-08-02 | 2016-08-08 | CAL FIRE | 520 | G | PLAYING WITH FIRE |  |  |  |  | 0 |  |  | 20160802 | 20160808 | PGE Teritory |  |  |  |  | N.A. | N.A. |  | No lat/lon available |  |  | No RFW Analysis Performed
LNU-7135 | YOLO | COLD | 2016-08-02 | 2016-08-12 | CAL FIRE | 5731 | B,G | UNDETERMINED | 2 |  |  |  | 0 |  |  | 20160802 | 20160812 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/8/2/cold-fire/ |  | 16:36 | 38.5251 | -122.0679 |  | HFTD |  |  | No Red Flag Warning Applicable
FKU-11358 | FRESNO | MINERAL | 2016-08-08 | 2016-08-19 | CAL FIRE | 7050 | B,G | ARSON | 2 |  |  |  | 0 |  |  | 20160808 | 20160819 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/8/9/mineral-fire/ |  | 13:08 | 36.0997 | -120.5106 |  | non-HFTD |  |  | No Red Flag Warning Applicable
SLU-8948 | SAN LUIS OBISPO | CHIMNEY | 2016-08-13 | 2016-09-07 | CAL FIRE | 46235 | B,T | VEHICLE | 70 | 8 |  |  | 0 |  |  | 20160813 | 20160907 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/8/13/chimney-fire/ |  | 16:03 | 35.706 | -120.9832 |  | HFTD |  |  | No Red Flag Warning Applicable
LNU-7582 | LAKE | CLAYTON | 2016-08-13 | 2016-09-03 | CAL FIRE | 3929 | B,G | ARSON | 300 | 28 |  |  | 0 |  |  | 20160813 | 20160903 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/8/13/clayton-fire/ |  | 18:03 | 38.8974 | -122.6066 |  | HFTD |  |  | No Red Flag Warning Applicable
SQF-2595 | KERN | CEDAR | 2016-08-16 | 2016-09-24 | USFS | 29322 | B,T | UNDETERMINED | 6 |  |  |  | 0 |  |  | 20160816 | 20160924 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/8/16/cedar-fire/ |  |  | 35.7506 | -118.5678 |  | HFTD |  |  | No RFW Analysis Performed
NEU-20037 | YUBA | BEALE | 2016-08-18 | 2016-08-19 | CAL FIRE | 389 | G | MISCELLANEOUS |  |  |  |  | 0 |  |  | 20160818 | 20160819 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/8/18/beale-fire/ |  |  | 36.1696 | -121.3877 |  | HFTD |  |  | No RFW Analysis Performed
LPF-2809 | SANTA BARBARA | REY | 2016-08-18 | 2016-09-15 | USFS | 32606 | B,G | UNDETERMINED | 5 |  |  |  | 0 |  |  | 20160818 | 20160915 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/8/18/rey-fire/ https://en.wikipedia.org/wiki/Rey_Fire |  | 15:15 | 34.546 | -119.805 |  | HFTD |  |  | No Red Flag Warning Applicable
STF-2257 | ALPINE | MOKELUMNE | 2016-08-19 | 2016-09-20 | USFS | 655 | B,G,T | LIGHTNING |  |  |  |  | 0 |  |  | 20160819 | 20160920 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/8/18/mokelumne-fire/ |  |  | 38.5755 | -120.0061 |  | HFTD |  |  | No RFW Analysis Performed
HUU-6956 | HUMBOLDT | TULLY | 2016-08-22 | 2016-09-09 | CAL FIRE | 599 | B,T | ARSON | 3 |  |  |  | 0 |  |  | 20160822 | 20160909 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/8/22/tully-fire/ |  | 16:03 | 41.2849 | -123.8227 |  | HFTD |  |  | No Red Flag Warning Applicable
SQF-2683 | TULARE | TULE | 2016-08-22 | 2016-08-22 | USFS | 395 | B,G,T | UNDETERMINED |  |  |  |  | 0 |  |  | 20160822 | 20160822 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/8/22/tule-fire/ |  |  | 36.1648 | -118.7391 |  | HFTD |  |  | No RFW Analysis Performed
SKU-7392 | SISKIYOU | GRADE | 2016-08-24 | 2016-09-10 | CAL FIRE | 710 | B,G,T | ELECTRICAL POWER | 10 | 1 |  |  | 0 |  |  | 20160824 | 20160910 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/8/24/grade-fire/ |  | 14:55 | 41.7813 | -122.611 |  | HFTD |  |  | No Red Flag Warning Applicable
KRN-32226 | KERN | RANGE | 2016-08-26 | 2016-08-31 | CC | 600 | B,G,T | HUMAN |  |  |  |  | 0 |  |  | 20160826 | 20160831 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/8/26/range-fire/ |  |  | 35.2013 | -118.7212 |  | HFTD |  |  | No RFW Analysis Performed
KRN-32375 | KERN | HAVILA | 2016-08-27 | 2016-08-31 | CC | 304 | B,G | UNDETERMINED |  |  |  |  | 0 |  |  | 20160827 | 20160831 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/8/28/havilah-fire/ https://yubanet.com/Fires/havilah/ |  | 2:30 | 35.4976 | -118.5097 |  | HFTD |  |  | No Red Flag Warning Applicable
KNF-7501 | SISKIYOU | GAP | 2016-08-27 | 2016-09-16 | USFS | 33867 | B,T | UNDETERMINED | 14 |  |  |  | 0 |  |  | 20160827 | 20160916 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/8/27/gap-fire/ |  |  | 41.851 | -123.118 |  | HFTD |  |  | No RFW Analysis Performed
TCU-9339 | CALAVERAS | WILLOW | 2016-08-28 | 2016-09-04 | CAL FIRE | 450 | B,G,T | VEHICLE |  | 1 |  |  | 0 |  |  | 20160828 | 20160904 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/8/28/willow-fire/ |  | 13:07 | 38.1874 | -120.6381 |  | HFTD |  |  | No Red Flag Warning Applicable
BTU-13655 | BUTTE | SADDLE | 2016-09-05 | 2016-09-22 | CAL FIRE | 800 | B,G,T | VEHICLE | 3 |  |  |  | 0 |  |  | 20160905 | 20160922 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/9/5/saddle-fire/ |  | 16:28 | 39.6871 | -121.571 |  | HFTD |  |  | No Red Flag Warning Applicable
LMU-4700 | MODOC | HOWARD | 2016-09-11 | 2016-09-15 | CAL FIRE | 380 | B,G,T | RAILROAD |  |  |  |  | 0 |  |  | 20160911 | 20160915 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/9/11/howard-fire/ |  |  | 41.4657 | -120.9066 |  | non-HFTD |  |  | No RFW Analysis Performed
LMU-4695 | LASSEN | WILLARD | 2016-09-11 | 2016-10-12 | CAL FIRE | 2575 | B,G,T | UNDETERMINED | 7 |  |  |  | 0 |  |  | 20160911 | 20161012 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/9/11/willard-fire/ |  | 11:33 | 40.3915 | -120.7845 |  | HFTD |  |  | No Red Flag Warning Applicable
SNF-2154 | FRESNO | CROWN | 2016-09-15 | 2016-10-31 | USFS | 800 | T | LIGHTNING |  |  |  |  | 0 |  |  | 20160915 | 20161031 | PGE Teritory |  |  |  |  | N.A. | N.A. |  | No lat/lon available |  |  | No RFW Analysis Performed
AFV-3151 | SANTA BARBARA | CANYON | 2016-09-17 | 2016-09-24 | MIL | 12742 | B | UNDETERMINED |  |  | 1 |  | 1 |  |  | 20160917 | 20160924 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/9/17/canyon-fire/ |  | 17:30 | 34.6345 | -120.5442 |  | HFTD |  |  | No Red Flag Warning Applicable
MDF-910 | MODOC | SOUP COMPLEX | 2016-09-17 | 2016-10-31 | USFS | 2722 | G,T | UNDETERMINED |  |  |  |  | 0 |  |  | 20160917 | 20161031 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/9/17/soup-complex/ |  |  | 41.2649 | -120.3178 |  | HFTD |  |  | No RFW Analysis Performed
KRN-35570 | KERN | FLAT | 2016-09-19 | 2016-09-22 | CC | 307 | G | EQUIPMENT |  |  |  |  | 0 |  |  | 20160919 | 20160922 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/9/19/flat-fire/ |  |  | 0 | 0 |  | No lat/lon available |  |  | No RFW Analysis Performed
LNU-9129 | SONOMA | SAWMILL | 2016-09-25 | 2016-10-01 | CAL FIRE | 1547 | B,G | UNDETERMINED |  |  |  |  | 0 |  |  | 20160925 | 20161001 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/9/25/sawmill-fire/ |  | 10:43 | 38.8002 | -122.829 |  | HFTD |  |  | Red Flag Warning Applicable
TCU-10403 | TUOLUMNE | MARSHES | 2016-09-26 | 2016-10-04 | CAL FIRE | 1080 | B,G,T | VEHICLE |  |  |  |  | 0 |  |  | 20160926 | 20161004 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/9/26/marshes-fire/ |  | 12:20 | 37.7963 | -120.3248 |  | HFTD |  |  | No Red Flag Warning Applicable
SCU-6912 | SANTA CLARA | LOMA | 2016-09-26 | 2016-11-08 | CAL FIRE | 4474 | B,T | UNDETERMINED | 28 | 1 |  |  | 0 |  |  | 20160926 | 20161108 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/9/26/loma-fire/ |  | 14:42 | 37.1063 | -121.8532 |  | HFTD |  |  | No Red Flag Warning Applicable
SQF-3261 | TULARE | SLATE | 2016-10-04 | 2016-11-05 | USFS | 2160 | B,T | LIGHTNING |  |  |  |  | 0 |  |  | 20161004 | 20161105 | PGE Teritory |  |  |  |  | N.A. | N.A. |  | No lat/lon available |  |  | No RFW Analysis Performed
SNF-2370 | FRESNO | SACATA | 2016-10-11 | 2016-10-19 | USFS | 2100 | B,G,T | UNDETERMINED |  |  |  |  | 0 |  |  | 20161011 | 20161019 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/10/11/sacata-fire/ https://www.fs.usda.gov/Internet/FSE_DOCUMENTS/fseprd521574.pdf |  | 12:58 | 36.9454 | -119.2596 |  | HFTD |  |  | No Red Flag Warning Applicable
SQF-3384 | TULARE | JACOBSON | 2016-10-20 | 2016-11-01 | USFS | 1702 | B,T | UNDETERMINED |  |  |  |  | 0 |  |  | 20161020 | 20161101 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/10/20/jacobson-fire/ |  |  | 36.217 | -118.551 |  | HFTD |  |  | No RFW Analysis Performed
SQF-3456 | TULARE | MEADOW | 2016-10-29 | 2016-11-22 | USFS | 4347 | B,T | LIGHTNING |  |  |  |  | 0 |  |  | 20161029 | 20161122 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2016/10/29/meadow-fire/ |  |  | 35.984 | -118.551 |  | HFTD |  |  | No RFW Analysis Performed
SQF-3464 | TULARE | HIDDEN | 2016-11-02 | 2016-11-23 | USFS | 2768 | B,T | LIGHTNING |  |  |  |  | 0 |  |  | 20161102 | 20161123 | PGE Teritory |  |  |  |  | N.A. | N.A. |  | No lat/lon available |  |  | No RFW Analysis Performed
NOD-1810 | MODOC | WEST | 2017-04-01 | 2017-04-01 | BLM | 401 | B, G | MISCELLANEOUS |  |  |  |  | 0 |  |  | 20170401 | 20170401 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/4/3/west-fire/ |  |  | 41.1672 | -120.5834 |  | HFTD |  |  | No RFW Analysis Performed
FKU-5281 | FRESNO | JAYNE | 2017-04-20 | 2017-04-21 | CAL FIRE | 4532 | G | EQUIPMENT USE |  |  |  |  | 0 |  |  | 20170420 | 20170421 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/4/20/jayne-fire/ |  | 15:40 | 36.0723 | -120.2656 |  | non-HFTD |  |  | No Red Flag Warning Applicable
FKU-5669 | FRESNO | EL DORADO | 2017-04-28 | 2017-04-28 | CAL FIRE | 750 | G | UNDETERMINED |  |  |  |  | 0 |  |  | 20170428 | 20170428 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/4/28/el-dorado-fire/ |  |  | 36.5308 | -120.2066 |  | non-HFTD |  |  | No RFW Analysis Performed
MMU-9464 | MERCED | WRIGHT | 2017-05-12 | 2017-05-13 | CAL FIRE | 1733 | G | UNDETERMINED |  |  |  |  | 0 |  |  | 20170512 | 20170513 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/5/12/wright-fire/ |  |  | 36.9665 | -120.8926 |  | non-HFTD |  |  | No RFW Analysis Performed
FKU-6727 | FRESNO | ELM 2 | 2017-05-18 | 2017-05-21 | CAL FIRE | 10000 | B, G | ELECTRICAL POWER |  |  |  |  | 0 |  |  | 20170518 | 20170521 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/5/18/elm-fire/ |  | 13:11 | 36.1209 | -120.3712 |  | non-HFTD |  |  | No Red Flag Warning Applicable
KRN-18713 | KERN | MING | 2017-05-20 | 2017-05-22 | CC | 506 | G | UNDETERMINED |  |  |  |  | 0 |  |  | 20170520 | 20170522 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/5/20/ming-fire/ |  |  | 35.4605 | -118.859 |  | HFTD |  |  | No RFW Analysis Performed
FHL-1267 | MONTEREY | RANGE | 2017-06-04 | 2017-06-11 | DOD | 1972 | G | MISCELLANEOUS |  |  |  |  | 0 |  |  | 20170604 | 20170611 | PGE Teritory |  |  |  |  | N.A. | N.A. |  | No lat/lon available |  |  | No RFW Analysis Performed
TUU-286 | TULARE | DINELY | 2017-06-07 | 2017-06-10 | CAL FIRE | 339 | B, G | EQUIPMENT USE |  |  |  |  | 0 |  |  | 20170607 | 20170610 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/6/7/dinely-fire/ |  | 11:55 | 36.4581 | -118.8768 |  | HFTD |  |  | No Red Flag Warning Applicable
MMU-11650 | MADERA | OAKWOOD | 2017-06-10 | 2017-06-13 | CAL FIRE | 1417 | B, G | SHOOTING |  |  |  |  | 0 |  |  | 20170610 | 20170613 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/6/10/oakwood-fire/ |  | 13:19 | 37.0825 | -119.8011 |  | non-HFTD |  |  | No Red Flag Warning Applicable
FKU-8044 | FRESNO | MONTEREY | 2017-06-11 | 2017-06-11 | CAL FIRE | 450 | G | SHOOTING |  |  |  |  | 0 |  |  | 20170611 | 20170611 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/6/11/monterey-fire/ |  |  | 36.617 | -120.3693 |  | non-HFTD |  |  | No RFW Analysis Performed
SQF-1223 | KERN | HIGHWAY | 2017-06-21 | 2017-06-25 | USFS | 1522 | G | UNDETERMINED |  |  |  |  | 0 |  |  | 20170621 | 20170625 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/6/18/highway-fire/ https://inciweb.nwcg.gov/incident/5254/ |  | 14:30 | 35.5346 | -118.6673 |  | HFTD |  |  | No Red Flag Warning Applicable
FKU-8759 | FRESNO | CREEK | 2017-06-23 | 2017-06-27 | CAL FIRE | 357 | B, G | DEBRIS BURNING | 4 |  |  |  | 0 |  |  | 20170623 | 20170627 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/6/23/creek-fire/ |  |  | 36.2731 | -120.6518 |  | non-HFTD |  |  | No RFW Analysis Performed
SQF-1317 | TULARE | SCHAEFFER | 2017-06-24 | 2017-08-05 | USFS | 16031 | B, G, T | LIGHTNING |  |  |  |  | 0 |  |  | 20170624 | 20170805 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/6/24/schaeffer-fire/ https://inciweb.nwcg.gov/incident/5285/ |  | 16:16 | 36.099 | -118.412 |  | HFTD |  |  | No Red Flag Warning Applicable
SLU-7101 | SAN LUIS OBISPO | HILL | 2017-06-26 | 2017-06-28 | CAL FIRE | 1626 | B, G | VEHICLE | 7 |  |  |  | 0 |  |  | 20170626 | 20170628 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/6/26/hill-fire/ |  | 15:37 | 35.4025 | -120.4992 |  | HFTD |  |  | No Red Flag Warning Applicable
MMU-13022 | MARIPOSA | BEN | 2017-06-28 | 2017-07-06 | CAL FIRE | 558 | B, G | VEHICLE |  |  |  |  | 0 |  |  | 20170628 | 20170706 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/6/28/ben-fire/ |  | 15:49 | 37.3762 | -119.9646 |  | HFTD |  |  | No Red Flag Warning Applicable
MDF-415 | MODOC | BATTLE | 2017-06-28 | 2017-07-01 | USFS | 640 | B, G | UNDETERMINED |  |  |  |  | 0 |  |  | 20170628 | 20170701 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/6/28/battle-fire/ https://inciweb.nwcg.gov/incident/5293/ |  | 14:00 | 41.8576 | -121.2958 |  | non-HFTD |  |  | No Red Flag Warning Applicable
KRN-24894 | KERN | TARINA | 2017-06-30 | 2017-07-01 | CC | 1200 | G | UNDETERMINED |  |  |  |  | 0 |  |  | 20170630 | 20170701 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/6/30/tarina-fire/ |  |  | 35.383 | -118.8012 |  | non-HFTD |  |  | No RFW Analysis Performed
FKU-9289 | FRESNO | DERRICK | 2017-07-02 | 2017-07-05 | CAL FIRE | 1562 | B, G | UNDETERMINED |  |  |  |  | 0 |  |  | 20170702 | 20170705 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/2/derrick-fire/ |  | 20:28 | 36.2691 | -120.6208 |  | non-HFTD |  |  | No Red Flag Warning Applicable
SKU-4779 | SISKIYOU | FAY | 2017-07-05 | 2017-07-31 | CAL FIRE | 496 | B, G, T | MISCELLANEOUS | 1 |  |  |  | 0 |  |  | 20170705 | 20170731 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/5/fay-fire/ |  | 11:05 | 41.3975 | -122.8428 |  | non-HFTD |  |  | No Red Flag Warning Applicable
LNU-6262 | YOLO | WINTER | 2017-07-06 | 2017-07-14 | CAL FIRE | 1700 | B, T | VEHICLE |  |  |  |  | 0 |  |  | 20170706 | 20170714 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/6/winters-fire/ |  | 12:41 | 38.4952 | -122.0251 |  | HFTD |  |  | No Red Flag Warning Applicable
SLU-7624 | SAN LUIS OBISPO | ALAMO | 2017-07-06 | 2017-07-18 | CAL FIRE | 28687 | B, G | UNDETERMINED | 14 | 1 |  |  | 0 |  |  | 20170706 | 20170718 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/6/alamo-fire/ |  | 15:44 | 35.0179 | -120.3223 |  | HFTD |  |  | Red Flag Warning Applicable
KRN-26708 | KERN | QUaiL COMPLEX | 2017-07-06 | 2017-07-06 | CC | 1626 | B, G | UNDETERMINED |  |  |  |  | 0 |  |  | 20170706 | 20170706 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/6/quail-fire/ |  |  | 35.599 | -119.0831 |  | non-HFTD |  |  | No RFW Analysis Performed
BTU-10975 | BUTTE | WALL | 2017-07-07 | 2017-08-03 | CAL FIRE | 6033 | B, G | ELECTRICAL POWER | 91 | 10 |  |  | 0 |  |  | 20170707 | 20170803 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/7/wall-fire/ |  | 14:52 | 39.4535 | -121.4122 |  | HFTD |  |  | No Red Flag Warning Applicable
BEU-3551 | MONTEREY | PARKFIELD | 2017-07-08 | 2017-07-08 | CAL FIRE | 1816 | B, G | ELECTRICAL POWER |  | 1 |  |  | 0 |  |  | 20170708 | 20170708 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/8/parkfield-fire/ |  |  | 35.8695 | -120.5789 |  | HFTD |  |  | No RFW Analysis Performed
LPF-1770 | SANTA BARBARA | WHITTIER | 2017-07-08 | 2017-10-05 | USFS | 18430 | B | UNDETERMINED | 40 | 7 |  |  | 0 |  |  | 20170708 | 20171005 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/8/whittier-fire/ https://inciweb.nwcg.gov/incident/5339/ |  | 13:34 | 34.551 | -119.9494 |  | HFTD |  |  | No Red Flag Warning Applicable
FKU-9755 | KINGS | GARZA | 2017-07-09 | 2017-07-25 | CAL FIRE | 48660 | B, G | EQUIPMENT USE | 1 |  |  |  | 0 |  |  | 20170709 | 20170725 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/9/garza-fire/ |  | 15:10 | 35.9327 | -120.2001 |  | non-HFTD |  |  | No Red Flag Warning Applicable
SLU-7792 | SAN LUIS OBISPO | STONE | 2017-07-09 | 2017-07-11 | CAL FIRE | 340 | B, G | EQUIPMENT USE | 3 |  |  |  | 0 |  |  | 20170709 | 20170711 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/9/stone-fire/ |  | 13:49 | 35.4243 | -120.4732 |  | HFTD |  |  | No Red Flag Warning Applicable
HTF-30363 | NEVADA | FARAD | 2017-07-10 | 2017-07-16 | USFS | 747 | B, G, T | UNDETERMINED |  |  |  |  | 0 |  |  | 20170710 | 20170716 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/10/farad-fire/ https://inciweb.nwcg.gov/incident/5350/ |  | 13:00 | 39.4397 | -120.0272 |  | HFTD |  |  | No Red Flag Warning Applicable
NOD-30366 | LASSEN | LONG VALLEY | 2017-07-11 | 2017-07-25 | BLM | 83733 | B, G | UNDETERMINED | 8 | 3 |  |  | 0 |  |  | 20170711 | 20170725 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/11/long-valley-fire/ https://inciweb.nwcg.gov/incident/5354/ |  | 13:30 | 40.0705 | -120.1401 |  | non-HFTD |  |  | No Red Flag Warning Applicable
MDF-541 | MODOC | DODE | 2017-07-13 | 2017-07-31 | USFS | 410 | B, G, T | MISCELLANEOUS | 0 |  |  |  | 0 |  |  | 20170713 | 20170731 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/13/dode-fire/ https://inciweb.nwcg.gov/incident/5362/ |  | 15:00 | 41.7216 | -121.3045 |  | non-HFTD |  |  | Red Flag Warning Applicable
MEU-8307 | MENDOCINO | GRADE | 2017-07-16 | 2017-07-18 | CAL FIRE | 900 | B, G | VEHICLE | 1 |  |  |  | 0 |  |  | 20170716 | 20170718 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/16/grade-fire/ |  | 14:51 | 39.3013 | -123.2883 |  | HFTD |  |  | No Red Flag Warning Applicable
MMU-14474 | MARIPOSA | DETWILER | 2017-07-16 | 2017-08-31 | CAL FIRE | 81826 | B, G | SHOOTING | 134 | 21 |  |  | 0 |  |  | 20170716 | 20170831 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/16/detwiler-fire/ |  | 15:56 | 37.6176 | -120.2132 |  | HFTD |  |  | No Red Flag Warning Applicable
FKU-10248 | FRESNO | PARK | 2017-07-17 | 2017-07-30 | CAL FIRE | 1649 | B, G | EQUIPMENT USE | 0 |  |  |  | 0 |  |  | 20170717 | 20170730 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/17/park-fire/ |  | 13:15 | 35.9591 | -120.5558 |  | HFTD |  |  | No Red Flag Warning Applicable
KRN-27936 | KERN | HUDSON | 2017-07-18 | 2017-07-18 | LOCAL | 1083 | G | UNDETERMINED | 0 |  |  |  | 0 |  |  | 20170718 | 20170718 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/18/hudson-fire/ |  |  | 34.9437 | -119.4475 |  | non-HFTD |  |  | No RFW Analysis Performed
SRF-703 | SISKIYOU | MARBLE | 2017-07-19 | 2017-07-28 | USFS | 319 | T | UNDETERMINED | 0 |  |  |  | 0 |  |  | 20170719 | 20170728 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/19/marble-fire/ https://inciweb.nwcg.gov/incident/5395/ |  | 14:00 | 41.478 | -123.506 |  | HFTD |  |  | No Red Flag Warning Applicable
TUU-420 | TULARE | ELEPHANT 2 | 2017-07-20 | 2017-07-21 | CAL FIRE | 416 | G | ARSON | 0 |  |  |  | 0 |  |  | 20170720 | 20170721 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/20/elephant-fire/ |  |  | 36.2227 | -119.066 |  | non-HFTD |  |  | No RFW Analysis Performed
MDF-671 | MODOC | MODOC JULY COMPLEX | 2017-07-24 | 2017-08-13 | USFS | 83120 | B, G, T | UNDETERMINED | 0 |  |  |  | 0 |  |  | 20170724 | 20170813 | PGE Teritory |  | https://inciweb.nwcg.gov/incident/5415/ |  | 17:15 | 41.829 | -120.824 |  | HFTD |  |  | Red Flag Warning Applicable
SRF-741 | SISKIYOU | ORLEANS COMPLEX | 2017-07-25 | 2017-10-12 | USFS | 27276 | B, G, T | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170725 | 20171012 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/26/orleans-complex/ https://inciweb.nwcg.gov/incident/5430/ |  | 21:00 | 41.59 | -123.501 |  | HFTD |  |  | No Red Flag Warning Applicable
AEU-21652 | SACRAMENTO | LATROBE | 2017-07-26 | 2017-07-28 | CAL FIRE | 1268 | G | DEBRIS BURNING | 0 |  |  |  | 0 |  |  | 20170726 | 20170728 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/26/latrobe-fire/ |  |  | 38.5181 | -121.104 |  | non-HFTD |  |  | No RFW Analysis Performed
PNF-1043 | PLUMAS | MINERVA 5 | 2017-07-29 | 2017-08-16 | USFS | 4310 | T | UNDETERMINED | 0 |  |  |  | 0 |  |  | 20170729 | 20170816 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/29/minerva-fire/ |  |  | 39.9034 | -120.9761 |  | HFTD |  |  | No RFW Analysis Performed
TUU-441 | TULARE | ROADRUNNER | 2017-07-30 | 2017-07-31 | CAL FIRE | 2289 | G | ARSON | 0 |  |  |  | 0 |  |  | 20170730 | 20170731 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/30/roadrunner-fire/ |  |  | 36.0226 | -118.9425 |  | HFTD |  |  | No RFW Analysis Performed
SQF-1989 | KERN | GARDEN | 2017-07-30 | 2017-08-09 | USFS | 450 | B | MISCELLANEOUS | 0 |  |  |  | 0 |  |  | 20170730 | 20170809 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/30/garden-fire/ https://inciweb.nwcg.gov/incident/5436/ |  | 16:17 | 35.543 | -118.654 |  | HFTD |  |  | No Red Flag Warning Applicable
STF-2452 | TUOLUMNE | SUMMIT COMPLEX | 2017-07-31 | 2017-11-30 | USFS | 5248 | B, T | UNDETERMINED | 0 |  |  |  | 0 |  |  | 20170731 | 20171130 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/7/31/summit-complex/ https://inciweb.nwcg.gov/incident/5546/ |  | 13:44 | 38.329 | -119.782 |  | non-HFTD |  |  | No Red Flag Warning Applicable
YNP-84 | MARIPOSA | EMPIRE | 2017-08-01 | 2017-10-31 | NPS | 6370 | B, T | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170801 | 20171031 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/1/empire-fire/ https://en.wikipedia.org/wiki/Empire_Fire |  | 8:45 | 37.644 | -119.618 |  | HFTD |  |  | No Red Flag Warning Applicable
LPF-2123 | SAN LUIS OBISPO | RED | 2017-08-02 | 2017-08-03 | USFS | 450 | B, G | UNDETERMINED | 0 |  |  |  | 0 |  |  | 20170802 | 20170803 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/2/red-fire/ |  |  | 35.4036 | -120.2804 |  | HFTD |  |  | No RFW Analysis Performed
MDF-862 | MODOC | PARKER 2 | 2017-08-03 | 2017-08-14 | USFS | 7697 | B, T | LIGHTNING | 1 |  |  |  | 0 |  |  | 20170803 | 20170814 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/3/parker-2-fire/ https://inciweb.nwcg.gov/incident/5462/ |  | 14:00 | 41.466 | -120.321 |  | HFTD |  |  | Red Flag Warning Applicable
INF-1264 | TULARE | INDIAN | 2017-08-03 | 2017-08-29 | USFS | 2295 | B, T | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170803 | 20170829 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/2/indian-fire/ https://inciweb.nwcg.gov/incident/5469/ |  | 18:00 | 36.257 | -118.296 |  | HFTD |  |  | No Red Flag Warning Applicable
TNF-992 | PLUMAS | CHILCOOT | 2017-08-06 | 2017-08-08 | USFS | 1021 | B, G | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170806 | 20170808 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/6/chilcoot-fire/ |  |  | 39.7537 | -120.1397 |  | HFTD |  |  | No RFW Analysis Performed
PNF-1145 | LASSEN | POSLIN | 2017-08-06 | 2017-08-09 | USFS | 860 | B, G | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170806 | 20170809 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/6/poslin-fire/ |  |  | 39.888 | -120.066 |  | HFTD |  |  | No RFW Analysis Performed
SNF-1476 | MADERA | BUTTE | 2017-08-07 | 2017-08-17 | USFS | 635 | B, T, | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170807 | 20170817 | PGE Teritory |  | https://inciweb.nwcg.gov/incident/5480 |  | -7 | 37.55 | -119.15 |  | HFTD |  |  | No Red Flag Warning Applicable
SRF-897 | TRINITY | RUTH COMPLEX | 2017-08-09 | 2017-08-25 | USFS | 4736 | B, G, T | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170809 | 20170825 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/7/ruth-complex/ |  |  | 40.176 | -123.3688 |  | HFTD |  |  | No RFW Analysis Performed
KRN-31474 | KERN | ROSE | 2017-08-10 | 2017-08-10 | CC | 338 | G | MISCELLANEOUS | 0 |  |  |  | 0 |  |  | 20170810 | 20170810 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/10/rose-fire/ |  | 14:32 | 34.9291 | -118.9267 |  | non-HFTD |  |  | No Red Flag Warning Applicable
KNF-6081 | SISKIYOU | SALMON AUGUST COMPLEX | 2017-08-13 | 2017-10-20 | USFS | 65889 | B, T | UNDETERMINED | 1 |  |  |  | 0 |  |  | 20170813 | 20171020 | PGE Teritory |  | https://inciweb.nwcg.gov/incident/5501/ |  | 0:01 | 41.263 | -123.099 |  | HFTD |  |  | No Red Flag Warning Applicable
YNP-108 | MARIPOSA | SOUTH FORK | 2017-08-13 | 2017-11-30 | NPS | 7000 | B, T | UNDETERMINED | 0 |  |  |  | 0 |  |  | 20170813 | 20171130 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/14/south-fork-fire/ https://www.nps.gov/yose/blogs/south-fork-fire-august-14-2017.htm |  | 14:30 | 37.538 | -119.598 |  | HFTD |  |  | No Red Flag Warning Applicable
KNF-6098 | SISKIYOU | ECLIPSE COMPLEX | 2017-08-15 | 2017-10-10 | USFS | 78698 | B, T | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170815 | 20171010 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/15/eclipse-complex/ https://inciweb.nwcg.gov/incident/5511/ |  | 7:57 | 41.841 | -123.474 |  | HFTD |  |  | No Red Flag Warning Applicable
NEU-21927 | YUBA | BEALE | 2017-08-20 | 2017-08-20 | DOD | 950 | G | UNDETERMINED | 0 |  |  |  | 0 |  |  | 20170820 | 20170820 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/20/beale-fire/ |  |  | 39.1234 | -121.3296 |  | non-HFTD |  |  | No RFW Analysis Performed
MDF-1101 | MODOC | JONES | 2017-08-23 | 2017-08-27 | USFS | 375 | B, G, T | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170823 | 20170827 | PGE Teritory |  |  |  |  | N.A. | N.A. |  | No lat/lon available |  |  | No RFW Analysis Performed
MDF-1102 | MODOC | BOLES | 2017-08-23 | 2017-09-04 | USFS | 371 | G, T | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170823 | 20170904 | PGE Teritory |  |  |  |  | N.A. | N.A. |  | No lat/lon available |  |  | No RFW Analysis Performed
BTU-13737 | BUTTE | PONDEROSA | 2017-08-29 | 2017-10-28 | CAL FIRE | 4016 | B, T | CAMPFIRE | 55 |  |  |  | 0 |  |  | 20170829 | 20171028 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/29/ponderosa-fire/ https://en.wikipedia.org/wiki/Ponderosa_Fire_(2017) |  | 13:16 | 39.577 | -121.3021 |  | HFTD |  |  | No Red Flag Warning Applicable
NOD-5152 | LASSEN | MUD | 2017-08-29 | 2017-09-01 | BLM | 6042 | G | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170829 | 20170901 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/29/mud-fire/ https://en.wikipedia.org/wiki/Mud_Fire |  | 14:30 | 40.4396 | -120.2221 |  | non-HFTD |  |  | Red Flag Warning Applicable
SNF-1743 | MADERA | RAILROAD | 2017-08-29 | 2017-09-15 | USFS | 12407 | B, T | UNDETERMINED | 8 | 1 | 1 |  | 1 |  |  | 20170829 | 20170915 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/29/railroad-fire/ https://inciweb.nwcg.gov/incident/5553/ |  | 13:00 | 37.4466 | -119.6462 |  | HFTD |  |  | No Red Flag Warning Applicable
SQF-2385 | TULARE | PIER | 2017-08-29 | 2017-09-24 | USFS | 36556 | B, T | MISCELLANEOUS | 2 |  |  |  | 0 |  |  | 20170829 | 20170924 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/29/pier-fire/ |  | 8:29 | 36.1536 | -118.741 |  | HFTD |  |  | No Red Flag Warning Applicable
NEU-22877 | NEVADA | PLEASANT | 2017-08-30 | 2017-09-06 | CAL FIRE | 392 | B, T | UNDETERMINED | 1 | 1 |  |  | 0 |  |  | 20170830 | 20170906 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/30/pleasant-fire/ |  | 15:38 | 39.3429 | -121.12 |  | HFTD |  |  | No Red Flag Warning Applicable
SHF-1770 | TRINITY | HELENA | 2017-08-30 | 2017-10-19 | USFS | 21449 | B, T | MISCELLANEOUS | 131 |  |  |  | 0 |  |  | 20170830 | 20171019 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/8/30/helena-fork-fire/ https://inciweb.nwcg.gov/incident/5564/ |  | 17:15 | 40.7602 | -123.1 |  | HFTD |  |  | No Red Flag Warning Applicable
SQF-2435 | KERN | CALDWELL | 2017-09-01 | 2017-09-06 | USFS | 1319 | B, G | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170901 | 20170906 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/9/1/caldwell-fire/ https://inciweb.nwcg.gov/incident/5579/ |  | 14:37 | 35.76 | -118.406 |  | HFTD |  |  | No Red Flag Warning Applicable
MMU-18115 | MADERA | MISSION | 2017-09-03 | 2017-09-13 | CAL FIRE | 1037 | B, T | ELECTRICAL POWER | 7 | 4 |  |  | 0 |  |  | 20170903 | 20170913 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/9/3/mission-fire/ |  | 13:06 | 37.2162 | -119.4807 |  | HFTD |  |  | No Red Flag Warning Applicable
MMU-18116 | MADERA | PEAK | 2017-09-03 | 2017-09-09 | CAL FIRE | 680 | B, T | VEHICLE | 4 |  |  |  | 0 |  |  | 20170903 | 20170909 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/9/3/peak-fire/ |  | 13:10 | 37.374 | -119.8356 |  | HFTD |  |  | No Red Flag Warning Applicable
STF-2590 | TUOLUMNE | CREEK | 2017-09-03 | 2017-11-20 | USFS | 1749 | B, T | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170903 | 20171120 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/9/3/creek-fire/ https://inciweb.nwcg.gov/incident/5596/ |  | 19:22 | 38.12 | -119.941 |  | non-HFTD |  |  | No Red Flag Warning Applicable
PNF-1488 | PLUMAS | EUREKA | 2017-09-05 | 2017-10-31 | USFS | 437 | B, T | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170905 | 20171031 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/9/5/eureka-fire/ |  |  | 39.7531 | -120.7549 |  | HFTD |  |  | No RFW Analysis Performed
ENF-26677 | EL DORADO | TABLE | 2017-09-08 | 2017-10-17 | USFS | 426 | T | UNDETERMINED | 0 |  |  |  | 0 |  |  | 20170908 | 20171017 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/10/13/table-fire/ https://inciweb.nwcg.gov/incident/5638/ |  | 18:45 | 38.848 | -120.287 |  | HFTD |  |  | No Red Flag Warning Applicable
SHU-9460 | SHASTA | BERRY | 2017-09-12 | 2017-10-04 | CAL FIRE | 900 | B | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170912 | 20171004 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/9/12/berry-fire/ |  | 6:58 | 40.9835 | -121.8162 |  | HFTD |  |  | No Red Flag Warning Applicable
SHF-1850 | TRINITY | BUCK | 2017-09-12 | 2017-11-05 | USFS | 13434 | B, G, T | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170912 | 20171105 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/9/12/buck-fire/ https://inciweb.nwcg.gov/incident/5614/ |  | 18:45 | 40.2275 | -123.0358 |  | HFTD |  |  | No Red Flag Warning Applicable
MMU-19222 | MADERA | EASTMAN | 2017-09-18 | 2017-09-19 | CAL FIRE | 483 | G | ELECTRICAL POWER | 0 |  |  |  | 0 |  |  | 20170918 | 20170919 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/9/18/eastman-fire/ https://abc30.com/fire-crews-work-quickly-to-control-eastman-fire-in-madera-county/2432668/ |  | 14:00 | 37.1462 | -120.0155 |  | non-HFTD |  |  | No Red Flag Warning Applicable
SQF-2753 | TULARE | LION | 2017-09-24 | 2017-11-27 | USFS | 19215 | B, G, T | LIGHTNING | 0 |  |  |  | 0 |  |  | 20170924 | 20171127 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/9/27/lion-fire/ |  | 17:00 | 36.2714 | -118.4856 |  | HFTD |  |  | No Red Flag Warning Applicable
SBC-12621 | SANTA BARBARA | RUCKER | 2017-09-29 | 2017-10-04 | CC | 444 | B, G | MISCELLANEOUS | 0 |  |  |  | 0 |  |  | 20170929 | 20171004 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/9/29/rucker-fire/ |  |  | 34.674 | -120.4393 |  | non-HFTD |  |  | No RFW Analysis Performed
BTU-15933 | BUTTE | CHEROKEE | 2017-10-08 | 2017-11-05 | CAL FIRE | 8500 | B, G | ELECTRICAL POWER | 6 | 1 |  |  | 0 |  |  | 20171008 | 20171105 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/10/8/cherokee-fire/ |  | 21:45 | 39.625 | -121.5297 |  | HFTD |  |  | Red Flag Warning Applicable
NEU-26269 | YUBA | CASCADE (NEU WIND COMPLEX)* | 2017-10-08 | 2017-10-19 | CAL FIRE | 9989 | B, T | ELECTRICAL POWER | 264 | 10 |  | 4 | 4 |  |  | 20171008 | 20171019 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/10/9/mccourtney-fire-wind-complex/ |  | 23:45 | 39.322 | -121.4021 |  | HFTD |  |  | Red Flag Warning Applicable
NEU-26279 | NEVADA | MCCOURTNEY (NEU WIND COMPLEX) | 2017-10-08 | 2017-10-21 | CAL FIRE | 76 | B, T | ELECTRICAL POWER | 13 | 2 |  |  | 0 |  |  | 20171008 | 20171021 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/10/9/mccourtney-fire-wind-complex/ |  | -7 | 39.1932 | -121.0841 |  | HFTD |  |  | Red Flag Warning Applicable
NEU-26275 | NEVADA | LOBO (NEU WIND COMPLEX) | 2017-10-08 | 2017-10-22 | CAL FIRE | 821 | B, T | ELECTRICAL POWER | 47 | 2 |  |  | 0 |  |  | 20171008 | 20171022 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/10/9/lobo-fire-wind-complex/ |  | 0:01 | 39.2455 | -121.1279 |  | HFTD |  |  | Red Flag Warning Applicable
LNU-10045 | NAPA | TUBBS (CENTRAL LNU COMPLEX) | 2017-10-08 | 2017-10-31 | CAL FIRE | 36807 | B, G, T | ELECTRICAL POWER | 5636 | 317 | 1 | 21 | 22 |  |  | 20171008 | 20171031 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/10/8/tubbs-fire-central-lnu-complex/ |  | 21:45 | 38.609 | -122.6288 |  | HFTD |  |  | Red Flag Warning Applicable
LNU-10050 | SONOMA | ADOBE (CENTRAL LNU COMPLEX - NUNS) | 2017-10-08 | 2017-10-31 | CAL FIRE | 3700 | B, G, T | ELECTRICAL POWER | 0 |  |  |  | 0 |  |  | 20171008 | 20171031 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/10/8/nuns-adobe-norrbom-pressley-partrick-fires-oakmont-central-lnu-complex/ |  | 1:00 | 0 | 0 |  | No lat/lon available |  |  | No RFW Analysis Performed
LNU-10051 | NAPA | PARTRICK (CENTRAL LNU COMPLEX - NUNS) | 2017-10-08 | 2017-10-31 | CAL FIRE | 8283 | B, G, T | ELECTRICAL POWER | 0 |  |  |  | 0 |  |  | 20171008 | 20171031 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/10/8/nuns-adobe-norrbom-pressley-partrick-fires-oakmont-central-lnu-complex/ |  |  | N.A. | N.A. |  | No lat/lon available |  |  | No RFW Analysis Performed
MEU-12169 | MENDOCINO | REDWOOD VALLEY (MENDOCINO LAKE COMPLEX) | 2017-10-08 | 2017-10-26 | CAL FIRE | 36523 | G, T | ELECTRICAL POWER | 543 | 41 |  | 9 | 9 |  |  | 20171008 | 20171026 | PGE Teritory |  |  |  | 23:36 | 39.2487 | -123.1663 |  | HFTD |  |  | Red Flag Warning Applicable
LNU-10049 | SONOMA | NUNS (CENTRAL LNU COMPLEX) | 2017-10-08 | 2017-10-31 | CAL FIRE | 44573 | B, G, T | ELECTRICAL POWER | 1355 | 172 |  | 3 | 3 |  |  | 20171008 | 20171031 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/10/8/nuns-adobe-norrbom-pressley-partrick-fires-oakmont-central-lnu-complex/ |  | 22:00 | 38.4041 | -122.5209 |  | HFTD |  |  | Red Flag Warning Applicable
MRN-2957 | MARIN | THIRTY SEVEN | 2017-10-09 | 2017-10-12 | CC | 1660 | B, G | ELECTRICAL POWER | 3 | 1 |  |  | 0 |  |  | 20171009 | 20171012 | PGE Teritory |  |  |  |  | N.A. | N.A. |  | No lat/lon available |  |  | No RFW Analysis Performed
BTU-15954 | BUTTE | LA PORTE (NEU WIND COMPLEX) | 2017-10-09 | 2017-10-20 | CAL FIRE | 6151 | B, T | ELECTRICAL POWER | 74 | 2 |  |  | 0 |  |  | 20171009 | 20171020 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/10/9/laporte-fire-wind-complex/ |  | 0:57 | 39.3946 | -121.4061 |  | HFTD |  |  | Red Flag Warning Applicable
LNU-10046 | NAPA | ATLAS (SOUTHERN LNU COMPLEX) | 2017-10-08 | 2017-10-28 | CAL FIRE | 51624 | B, G, T | ELECTRICAL POWER | 783 | 120 |  | 6 | 6 |  |  | 20171008 | 20171028 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/10/8/atlas-fire-southern-lnu-complex/ |  | 21:52 | 38.3921 | -122.2437 |  | HFTD |  |  | Red Flag Warning Applicable
LNU-10055 | LAKE | SULPHUR (MENDOCINO LAKE COMPLEX) | 2017-10-08 | 2017-10-26 | CAL FIRE | 2207 | G, T | ELECTRICAL POWER | 162 | 8 |  |  | 0 |  |  | 20171008 | 20171026 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/10/8/sulphur-fire-mendocino-lake-complex/ |  | 23:59 | 39.0139 | -122.6454 |  | non-HFTD |  |  | Red Flag Warning Applicable
LNU-10057 | SONOMA | POCKET 2 (CENTRAL LNU COMPLEX) | 2017-10-09 | 2017-10-31 | CAL FIRE | 17357 | B, G, T | ELECTRICAL POWER | 6 | 2 |  |  | 0 |  |  | 20171009 | 20171031 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/10/9/pocket-fire-central-lnu-complex/ |  | 3:30 | 38.7655 | -122.9094 |  | HFTD |  |  | Red Flag Warning Applicable
CZU-7822 | SANTA CRUZ | BEAR | 2017-10-16 | 2017-10-29 | CAL FIRE | 391 | T | ARSON | 6 |  |  |  | 0 |  |  | 20171016 | 20171029 | PGE Teritory |  | https://www.fire.ca.gov/incidents/2017/10/16/bear-fire/ |  | 22:30 | 37.1836 | -122.0701 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-01 | Merced | Nees Fire | 2018-05-02 |  |  | 1756 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/5/2/nees-fire/ |  |  | 36.8516 | -120.7721 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-02 | Alameda | Grant Fire | 2018-05-30 |  |  | 484 |  |  | 1 |  |  |  | 0 |  |  |  |  | PGE Teritory |  |  |  |  | 37.7537 | -121.5792 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-03 | Madera | ONeals Fire | 2018-06-04 |  |  | 300 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  |  |  |  | 37.1018 | -119.624 |  | HFTD |  |  | No RFW Analysis Performed
F2018-04 | San Benito | Eastern Fire | 2018-06-04 |  |  | 513 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/6/4/eastern-fire/ |  | 17:30 | 36.3783 | -120.9012 |  | non-HFTD |  |  | No Red Flag Warning Applicable
F2018-05 | San Benito | Airline Fire | 2018-06-04 |  |  | 1314 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/6/4/airline-fire/ |  | 17:01 | 36.4076 | -120.9932 |  | non-HFTD |  |  | No Red Flag Warning Applicable
F2018-06 | Glenn | Chrome Fire | 2018-06-09 |  |  | 2290 |  |  | 1 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/6/9/chrome-fire/ |  | 15:32 | 39.6498 | -122.5822 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-07 | Tehama | Apple Fire | 2018-06-09 |  |  | 2956 |  |  | 5 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/6/9/apple-fire/ |  | 14:10 | 39.9436 | -122.3571 |  | non-HFTD |  |  | No Red Flag Warning Applicable
F2018-08 | Madera | Lions Fire | 2018-06-11 |  |  | 4064 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://inciweb.nwcg.gov/incident/5850/ |  | 12:00 | 37.571 | -119.118 |  | non-HFTD |  |  | No Red Flag Warning Applicable
F2018-09 | Lassen | Tumbleweed Fire | 2018-06-14 |  |  | 646 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/6/14/tumbleweed-fire/ |  |  | 40.3768 | -120.364 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-10 | Merced | Planada Fire | 2018-06-15 |  |  | 4564 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/6/15/planada-fire/ |  |  | 37.3934 | -120.3421 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-11 | San Luis Obispo | Yankee Fire | 2018-06-20 |  |  | 1500 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/6/20/yankee-fire/ |  |  | 35.7363 | -120.7559 |  | HFTD |  |  | No RFW Analysis Performed
F2018-12 | Lake | Pawnee Fire | 2018-06-23 |  |  | 15185 |  |  | 22 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/6/23/pawnee-fire/ |  | 17:21 | 39.0674 | -122.5985 |  | non-HFTD |  |  | Red Flag Warning Applicable
F2018-13 | Shasta | Bascom Fire | 2018-06-23 |  |  | 328 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/6/23/bascom-fire/ |  |  | 40.5291 | -122.1746 |  | HFTD |  |  | No RFW Analysis Performed
F2018-14 | Tehama | Lane Fire | 2018-06-23 |  |  | 3716 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/6/23/lane-fire/ |  | 11:38 | 40.3507 | -121.7787 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-15 | Shasta | Creek Fire | 2018-06-24 |  |  | 1678 |  |  | 11 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/6/24/creek-fire/ |  | 12:29 | 40.5032 | -122.4231 |  | non-HFTD |  |  | Red Flag Warning Applicable
F2018-16 | Butte | Shippee Fire | 2018-06-26 |  |  | 347 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  |  |  |  | 39.5987 | -121.7821 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-17 | Lassen | Hyatt Fire | 2018-06-27 |  |  | 441 |  |  | 4 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/6/27/hyatt-fire/ |  |  | 40.3161 | -120.4505 |  | HFTD |  |  | No RFW Analysis Performed
F2018-18 | Trinity | Flat Fire | 2018-06-28 |  |  | 300 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/6/28/flat-fire/ |  | 18:01 | 40.604 | -122.9144 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-19 | San Joaquin | Waverly Fire | 2018-06-29 |  |  | 12300 |  |  | 1 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/6/29/waverly-fire/ |  |  | 38.0521 | -120.9455 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-20 | Napa and Yolo | County Fire | 2018-06-30 |  |  | 90288 |  |  | 29 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/6/30/county-fire/ |  | 14:12 | 38.8058 | -122.1818 |  | non-HFTD |  |  | Red Flag Warning Applicable
F2018-21 | El Dorado | Shingle Fire | 2018-07-04 |  |  | 316 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/7/4/shingle-fire/ |  |  | 38.5398 | -121.06 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-22 | Siskiyou | Klamathon Fire | 2018-07-05 |  |  | 38008 |  |  | 83 |  |  |  | 1 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/7/5/klamathon-fire/ |  | 12:31 | 41.8933 | -122.5347 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-23 | Amador | Irish Fire | 2018-07-06 |  |  | 825 |  |  | 1 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/7/6/irish-fire/ |  | 14:42 | 38.4262 | -120.9541 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-24 | San Bernardino | Valley Fire | 2018-07-06 |  |  | 1350 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/7/6/valley-fire/ |  | 13:29 | 34.0956 | -116.9588 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-25 | Alameda | Grant Fire | 2018-07-08 |  |  | 640 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/7/8/grant-fire/ |  | 17:38 | 37.7565 | -121.6065 |  | non-HFTD |  |  | No Red Flag Warning Applicable
F2018-26 | Tehama | Dale Fire | 2018-07-09 |  |  | 856 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/7/9/dale-fire/ |  |  | 40.3368 | -121.9391 |  | HFTD |  |  | No RFW Analysis Performed
F2018-27 | Butte | Stoney Fire | 2018-07-12 |  |  | 962 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/7/12/stoney-fire/ |  | 20:45 | 39.7712 | -121.7686 |  | non-HFTD |  |  | No Red Flag Warning Applicable
F2018-28 | Modoc | Eagle Fire | 2018-07-13 |  |  | 2100 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://inciweb.nwcg.gov/incident/5926/ |  | 20:00 | 41.285 | -120.115 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-29 | Mariposa | Ferguson Fire | 2018-07-13 |  |  | 96901 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://inciweb.nwcg.gov/incident/5927/ |  | 20:30 | 37.652 | -119.881 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-30 | Yolo | Eighty Eight Fire | 2018-07-18 |  |  | 822 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/7/18/eighty-eight-fire/ |  |  | 38.5969 | -121.9939 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-31 | Santa Clara | Country Fire | 2018-07-22 |  |  | 320 |  |  | 1 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/7/22/country-fire/ |  | 13:06 | 37.4494 | -121.8881 |  | non-HFTD |  |  | No Red Flag Warning Applicable
F2018-32 | Shasta and Trinity | Carr Fire | 2018-07-23 |  |  | 229651 |  |  | 1614 |  |  |  | 3 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/7/23/carr-fire/ |  | 13:15 | 40.6543 | -122.6236 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-33 | Kern | Breckenridge Fire | 2018-07-27 |  |  | 993 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/7/27/breckenridge-fire/ |  |  | 35.3874 | -118.8179 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-34 | Lassen | Whaleback Fire | 2018-07-27 |  |  | 18703 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://inciweb.nwcg.gov/incident/6048/ https://www.fire.ca.gov/incidents/2018/7/27/whaleback-fire/ |  | 13:30 | 40.6335 | -120.8681 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-35 | Colusa, Lake and Mendocino | River Fire (Mendocino Complex) | 2018-07-27 |  |  | 48920 |  |  | 35 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/7/27/river-fire-mendocino-complex/ |  | 13:01 | 39.0479 | -123.1197 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-36 | Colusa, Glenn, Lake and Mendocino | Ranch Fire (Mendocino Complex) | 2018-07-27 |  |  | 410203 |  |  | 246 |  |  |  | 1 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/7/27/ranch-fire-mendocino-complex/ |  | 12:05 | 39.2433 | -123.1034 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-37 | Sutter | Butte Fire | 2018-07-31 |  |  | 1200 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/7/31/butte-fire/ |  |  | 39.1861 | -121.7929 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-38 | Mendocino | Eel Fire | 2018-07-31 |  |  | 972 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://inciweb.nwcg.gov/incident/6083/ |  | 13:00 | 39.832 | -123.048 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-39 | Tuolumne | Donnell Fire | 2018-08-01 |  |  | 36450 |  |  | 54 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://inciweb.nwcg.gov/incident/6092/ |  | 17:49 | 38.349 | -119.929 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-40 | Placer | Sunset Fire | 2018-08-01 |  |  | 700 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/8/1/sunset-fire/ |  |  | 38.8243 | -121.4513 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-41 | Kern | Tarina Fire | 2018-08-03 |  |  | 2950 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/8/3/tarina-fire/ |  |  | 35.3744 | -118.8356 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-42 | Kings | Five Fire | 2018-08-06 |  |  | 2995 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/8/6/five-fire/ |  |  | 35.979 | -119.9833 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-43 | Monterey | Turkey Fire | 2018-08-06 |  |  | 2225 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/8/6/turkey-fire/ |  |  | 35.8478 | -120.3431 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-44 | Shasta | Hirz Fire | 2018-08-08 |  |  | 46150 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/8/9/hirz-fire/ |  | 1:55 | 40.896 | -122.219 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-45 | Shasta | Hat Fire | 2018-08-09 |  |  | 1900 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/8/9/hat-fire/ |  | 14:34 | 40.9934 | -121.5222 |  | HFTD |  |  | Red Flag Warning Applicable
F2018-46 | Solano | Nelson Fire | 2018-08-10 |  |  | 2162 |  |  | 1 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/8/10/nelson-fire/ |  | 16:57 | 38.4313 | -122.0437 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-47 | Monterey | Gulch Fire | 2018-08-11 |  |  | 650 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/8/11/gulch-fire/ |  |  | 36.0091 | -120.8223 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-48 | Modoc | Stone Fire | 2018-08-15 |  |  | 39387 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://inciweb.nwcg.gov/incident/6148/ |  | 8:00 | 41.395 | -121.057 |  | HFTD |  |  | Red Flag Warning Applicable
F2018-49 | Tulare | River Fire | 2018-08-15 |  |  | 668 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/8/15/river-fire/ |  |  | 35.7901 | -118.7393 |  | HFTD |  |  | No RFW Analysis Performed
F2018-50 | Humboldt | Mill Creek 1 Fire | 2018-08-16 |  |  | 3674 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/8/16/mill-creek-1-fire/ https://inciweb.nwcg.gov/incident/6161/ |  | 7:30 | 41.14 | -123.66 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-51 | Kern | Call Fire | 2018-08-18 |  |  | 367 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://inciweb.nwcg.gov/incident/6155/ |  | 15:00 | 35.524 | -118.669 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-52 | Santa Barbara | Front Fire | 2018-08-19 |  |  | 1014 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/8/19/front-fire/ |  |  | 35.1142 | -120.0922 |  | HFTD |  |  | No RFW Analysis Performed
F2018-53 | Placer | North Fire | 2018-09-03 |  |  | 1120 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/9/3/north-fire/ |  | 16:38 | 39.2686 | -120.6583 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-54 | Trinity | Kerlin Fire | 2018-09-04 |  |  | 1751 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/9/4/kerlin-fire/ |  |  | 40.6163 | -123.5202 |  | HFTD |  |  | No RFW Analysis Performed
F2018-55 | Shasta | Delta Fire | 2018-09-05 |  |  | 63311 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://inciweb.nwcg.gov/incident/6191/ |  | 12:51 | 40.923 | -122.408 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-56 | Napa | Snell Fire | 2018-09-08 |  |  | 2490 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/9/8/snell-fire/ |  | 14:29 | 38.696 | -122.4447 |  | HFTD |  |  | No Red Flag Warning Applicable
F2018-57 | Tuolumne | Tulloch Fire | 2018-09-08 |  |  | 573 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/9/8/tulloch-fire/ |  |  | 37.8339 | -120.6175 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-58 | Monterey | Metz Fire | 2018-09-13 |  |  | 400 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/9/13/metz-fire/ |  |  | 36.355 | -121.1563 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-59 | Madera | Oak Fire | 2018-09-22 |  |  | 360 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/9/22/oak-fire/ |  |  | 37.3879 | -119.6891 |  | HFTD |  |  | No RFW Analysis Performed
F2018-60 | Solano | Branscombe Fire | 2018-10-07 |  |  | 4500 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/10/7/branscombe-fire/ | [5 empty] | No lat/lon available |  |  | No RFW Analysis Performed
F2018-61 | Tehama | Sun Fire | 2018-10-07 |  |  | 3889 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/10/7/sun-fire/ |  | 12:51 | 40.2203 | -122.18 |  | HFTD |  |  | Red Flag Warning Applicable
F2018-62 | Butte | June Fire | 2018-10-30 |  |  | 550 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/10/30/june-fire/ |  |  | 39.3653 | -121.5171 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-63 | Solano | Nurse Fire | 2018-11-08 |  |  | 1500 |  |  | 0 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/11/8/nurse-fire/ |  |  | 38.214 | -121.9424 |  | non-HFTD |  |  | No RFW Analysis Performed
F2018-64 | Butte | Camp Fire | 2018-11-08 |  |  | 153336 |  | ELECTRICAL POWER | 18804 |  |  |  | 85 |  |  |  |  | PGE Teritory |  | https://www.fire.ca.gov/incidents/2018/11/8/camp-fire/ |  | 6:33 | 39.8134 | -121.4347 |  | HFTD |  |  | Red Flag Warning Applicable
F2019-01 | San Luis Obispo | Belmont Fire | 2019-05-29 |  |  | 835 |  | Unknown |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 35.3076 | -119.965 |  | non-HFTD |  |  | No RFW Analysis Performed
F2019-02 | Kern | Refuge Fire | 2019-05-07 |  |  | 2500 |  | Unknown |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 35.7206 | -119.6276 |  | non-HFTD |  |  | No RFW Analysis Performed
F2019-03 | San Luis Obispo | Boulder Fire | 2019-06-05 |  |  | 1127 |  | Unknown |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 35.3438 | -119.9137 |  | non-HFTD |  |  | No RFW Analysis Performed
F2019-04 | Yolo | Sand Fire | 2019-06-08 |  |  | 2512 |  | Unknown | 7 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  | 14:50 | 38.8898 | -122.2392 |  | non-HFTD |  |  | Red Flag Warning Applicable
F2019-05 | Sutter | West Butte Fire | 2019-06-08 |  |  | 1350 |  | Unknown |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 39.2893 | 121.8591 |  | non-HFTD |  |  | No RFW Analysis Performed
F2019-06 | Stanislaus | Stuhr Fire | 2019-06-07 |  |  | 600 |  | Unknown |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 37.2599 | -121.0938 |  | non-HFTD |  |  | No RFW Analysis Performed
F2019-07 | San Luis Obispo | McMillan Fire | 2019-06-12 |  |  | 1764 |  | Unknown |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 35.6632 | -120.4113 |  | non-HFTD |  |  | No RFW Analysis Performed
F2019-08 | Monterey | Lonoak Fire | 2019-06-26 |  |  | 2546 |  | Under Investigation |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 36.2843 | -120.9477 |  | non-HFTD |  |  | No RFW Analysis Performed
F2019-09 | Stanislaus | Rock Fire | 2019-06-26 |  |  | 2422 |  | Under Investigation |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 37.4658 | -121.2831 |  | HFTD |  |  | No RFW Analysis Performed
F2019-10 | San Luis Obispo | Gillis Fire | 2019-07-08 |  |  | 974 |  | Under Investigation |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 35.6311 | -120.2692 |  | non-HFTD |  |  | No RFW Analysis Performed
F2019-11 | Modoc | Tucker Fire | 2019-07-28 |  |  | 14217 |  | Under Investigation |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 41.7959 | -121.2603 |  | non-HFTD |  |  | No RFW Analysis Performed
F2019-12 | Kern | Mesa Fire | 2019-07-31 |  |  | 448 |  | Under Investigation |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  | 14:42 | 35.6099 | -118.412 |  | HFTD |  |  | No Red Flag Warning Applicable
F2019-13 | Lassen | W1 McDonald Fire | 2019-08-08 |  |  | 1020 |  | Under Investigation |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 40.9438 | -120.2753 |  | HFTD |  |  | No RFW Analysis Performed
F2019-14 | Lassen | Long Valley Fire | 2019-08-24 |  |  | 2438 |  | Under Investigation |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  | 15:00 | 39.8922 | -120.0297 |  | HFTD |  |  | No Red Flag Warning Applicable
F2019-15 | Mariposa | Gaines Fire | 2019-08-16 |  |  | 1300 |  | Under Investigation |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 37.5361 | -120.177 |  | HFTD |  |  | No RFW Analysis Performed
F2019-16 | Mariposa | Hunter Fire | 2019-08-15 |  |  | 423 |  | Under Investigation |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 37.532 | -120.208 |  | non-HFTD |  |  | No RFW Analysis Performed
F2019-17 | Tulare | Creek Fire | 2019-08-31 |  |  | 756 |  | Under Investigation |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 36.4019 | -119.0306 |  | non-HFTD |  |  | No RFW Analysis Performed
F2019-18 | Tehama | Red Bank Fire | 2019-09-05 |  |  | 8838 |  | Lightning | 2 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  | 13:19 | 40.12 | -122.64 |  | HFTD |  |  | No Red Flag Warning Applicable
F2019-19 | Plumas | Walker Fire | 2019-09-04 |  |  | 54612 |  | Under Investigation |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  | 17:45 | 40.0614 | -120.6806 |  | HFTD |  |  | No Red Flag Warning Applicable
F2019-20 | Siskiyou | Lime Fire | 2019-09-05 |  |  | 1872 |  | Lightning |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  | 11:19 | 41.8622 | -122.6623 |  | HFTD |  |  | Red Flag Warning Applicable
F2019-21 | Tulare | Broder Fire | 2019-08-08 |  |  | 381 |  | Lightning |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  | 8:00 | 36.151 | -118.185 |  | HFTD |  |  | No Red Flag Warning Applicable
F2019-22 | Modoc | Lone Fire | 2019-09-05 |  |  | 5737 |  | Lightning |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  | 16:14 | 41.748 | -121.056 |  | non-HFTD |  |  | Red Flag Warning Applicable
F2019-23 | Butte | Swedes Fire | 2019-09-07 |  |  | 496 |  | Under Investigation | 2 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  | 15:06 | 35.453 | -121.4126 |  | non-HFTD |  |  | No Red Flag Warning Applicable
F2019-24 | Placer | Baseline Fire | 2019-09-20 |  |  | 604 |  | Under Investigation |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 38.7516 | -121.4326 |  | non-HFTD |  |  | No RFW Analysis Performed
F2019-25 | Butte | Hwy Fire | 2019-09-28 |  |  | 300 |  | Under Investigation |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 39.6221 | -121.6935 |  | non-HFTD |  |  | No RFW Analysis Performed
F2019-26 | Napa | American Fire | 2019-10-06 |  |  | 526 |  | - | 1 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 38.1659 | -122.2117 |  | non-HFTD |  |  | No RFW Analysis Performed
F2019-27 | Mariposa | Briceburg Fire | 2019-10-06 |  |  | 5563 |  | - | 1 |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  | 16:15 | 37.6046 | -119.9661 |  | HFTD |  |  | No Red Flag Warning Applicable
F2019-28 | Santa Barbara | Real Fire | 2019-10-17 |  |  | 420 |  | - |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 34.4847 | -120.1908 |  | HFTD |  |  | No RFW Analysis Performed
F2019-29 | El Dorado | Caples Fire | 2019-10-11 |  |  | 3435 |  | - |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  | 14:00 | 38.724 | -120.145 |  | HFTD |  |  | No Red Flag Warning Applicable
F2019-30 | Sonoma | Kincade Fire | 2019-10-23 |  |  | 77758 |  | Under Investigation | 374 | 60 |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  | 21:27 | 38.7925 | -122.7801 |  | HFTD |  |  | Red Flag Warning Applicable
F2019-31 | Mendocino | Burris Fire | 2019-10-27 |  |  | 703 |  | - |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 39.2243 | -123.1289 |  | HFTD |  |  | No RFW Analysis Performed
F2019-32 | Tehama | Rawson Fire | 2019-10-26 |  |  | 605 |  | - |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 40.0017 | -122.2542 |  | non-HFTD |  |  | No RFW Analysis Performed
F2019-33 | Placer | Foothills Fire | 2019-11-25 |  |  | 355 |  | - |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  |  | 38.839 | -121.3258 |  | non-HFTD |  |  | No RFW Analysis Performed
F2019-34 | Tehama | Ranch Fire | 2019-11-03 |  |  | 2534 |  | - |  |  |  |  | 0 |  |  |  |  | PGE Teritory |  | Click on Fire name |  | 14:16 | 40.0364 | -122.6378 |  | HFTD |  |  | No Red Flag Warning Applicable
Note on X38: Oum, Yumi: mannually added searching the google

## EventTree
Large Fires Summary by HFTD / Red Flag Warning / Destructive
Used in REF_EventTree tab of Risk Input File | [5 empty] | Start Row (Do not change) | End Row (Do not change)
|  |  |  | Start Year | 2015
|  |  |  | End Year | 2019
|  |  |  | Destructive: | 100 | structures destroyed
|  |  |  | column P | [5 empty] | Yes | Yes
column T
[5 empty] | destructive | non-destructive | Total | destructive | non-destructive | destructive | non-destructive | #Fatal | %Fatal¦Destructive | %Fatal¦non-Destructive | %Fatal | %Destructive¦Fatal
column AA | column AB | column AD |  |  | count | count | count | % | % | fatal | fatal
HFTD | Time Available | Red Flag Warning Applicable | HFTD | w/ Redflag
HFTD | Time Available | No Red Flag Warning Applicable |  | wo/ Redflag
HFTD | No Time Available | No RFW Analysis Performed |  | no Redflag info
total
non-HFTD | Time Available | Red Flag Warning Applicable | non HFTD | w/ Redflag
non-HFTD | Time Available | No Red Flag Warning Applicable |  | wo/ Redflag
non-HFTD | No Time Available | No RFW Analysis Performed |  | no Redflag info
total
No lat/lon available | Time Available | Red Flag Warning Applicable | unknown | w/ Redflag
No lat/lon available | Time Available | No Red Flag Warning Applicable |  | wo/ Redflag
No lat/lon available | No Time Available | No RFW Analysis Performed |  | no Redflag info
total
|  |  | Total | w/ Redflag
wo/ Redflag
no Redflag info
total

## Fire Names & ILIS
Mapping of ILIS Rpt# to Fire Name
ILIS Rpt# | Fire Name | 0_Fire Name | match fire name with Large Fires (PGE Territory) | match w Calfire revised
14-0001794 | Cal Fire requests PG&E to de-energize facilities | Miscellenious 1
14-0003531 | Atwater PD request PG&E de-enrgize facilities due to 3rd party climing tower | Miscellenious 2
14-0003532 | Atwater PD request PG&E de-enrgize facilities due to 3rd party climing tower | Miscellenious 2
14-0003530 | Atwater PD request PG&E de-enrgize facilities due to 3rd party climing tower | Miscellenious 2
14-0003010 | San Jose PD request lines de-energized due to warehouse fire | Miscellenious 5
14-0003745 | declined. Raod construction does not meet non-restore criteria | Miscellenious 6
14-0011563 | Shasta county Fire request PG&E de-energize facilities due to structure fire | Miscellenious 7
14-0031529 | Declined. Unable to obtain contact information for fire department | Miscellenious 8
14-0009119 | Declined. Updates for single transformer can be completed in ILIS> Not approved for all customers in outage | Miscellenious 9
14-0002158 | Declined. Unable to obtain contact information for fire department | Miscellenious 10
14-0036755 | Cal Fire requests PG&E to de-energize facilities | Miscellenious 11
14-0039781 | Steelhead fire. CalFire request PG&E to de-energize facilities | Miscellenious 12
14-0041859 | Butts Fire. Cal Fire request PG&E to de-energize facilities | BUTTS
14-0041844 | Butts Fire. Cal Fire request PG&E to de-energize facilities | BUTTS
14-0042590 | Monticello Fire. Cal Fire request PG&E to de-energize facilties for fire activity | MONTICELLO
14-0038731 | CalTrans ask PG&E to stand down of Crane set on HWY 17 due to traffic issues | Miscellenious 16
14-0043722 | BridgeportFire. Cal Fire request PG&E to de-energize facilities | Bridgeport
14-0052714 | PG&E Denergized facilities at request of Fire Dept. | Miscellenious 18
14-0052618 | PG&E Denergized facilities at request of Fire Dept. | Miscellenious 19
14-0047150 | Sand Fire. Cal Fire reqeust PG&E de-energize facilities | SAND
14-0047157 | Sand Fire. Cal Fire reqeust PG&E de-energize facilities | SAND
14-0047154 | Sand Fire. Cal Fire reqeust PG&E de-energize facilities | SAND
14-0055397.1 | Bridge Fire. Cal Fire request PG&E to de-energize facilities | Bridge fire
14-0055397.2 | Bridge Fire. Cal Fire request PG&E to de-energize facilities | Bridge fire
14-0055397.3 | Bridge Fire. Cal Fire request PG&E to de-energize facilities | Bridge fire
14-0055397.4 | Bridge Fire. Cal Fire request PG&E to de-energize facilities | Bridge fire
14-0047155 | Sand Fire. Cal Fire reqeust PG&E de-energize facilities | SAND
14-0053446 | Pines Fire. Cal Fire request PG&E de-energized facitlies due to fire fighting activigties | Pine
14-0051664 | Junction Fire. Cal Fire request PG&E de-energize facilties due to large fire in the town of Oakhurst | Junction
14-0056791 | Black fire. Cal Fire request PG&E de-energized facitlies due to fire fighting activities. | black
14-0048674 | Eiler Fire. Cal Fire request PG&E de-energize facilities due to fire fighting activities | Eiler
14-0047160 | Sand Fire. Cal Fire reqeust PG&E de-energize facilities | SAND
14-0047167 | Sand Fire. Cal Fire reqeust PG&E de-energize facilities | SAND
14-0047164 | Sand Fire. Cal Fire reqeust PG&E de-energize facilities | SAND
14-0056877 | Courtney Fire. Cal Fire request PG&E de-energize facilities due to fire fighting activities. | Courtney
14-0056871 | King Fire. Cal Fire requested PG&E de-energize facilities due to firefighting activities. | king
14-0044102 | Cal Fire requests PG&E to de-energize facilities due to grass fire. | Miscellenious 37
14-0070317 | Cal Fire requests PG&E to de-energize line due to structure fire. | Structure fire 38
14-0062318 | Applegate Fire. Cal Fire request PG&E to de-energize facilitiies. | Applegate
15-0070732 | Lightning/mudslides | Miscellenious 41
15-0070510 | Lightning/mudslides | Miscellenious 41
15-0070421 | Lightning/mudslides | Miscellenious 41
15-0070671 | Mudslides/Flooding | Miscellenious 41
15-0070661 | Mudslides/Flooding | Miscellenious 41
15-0070563 | Mudslides/Flooding | Miscellenious 41
15-0070595 | Mudslides/Flooding | Miscellenious 41
15-0070672 | Mudslides/Flooding | Miscellenious 41
15-0070798 | Mudslides/Flooding | Miscellenious 41
15-0077680 | 3rd party dig-in-Fire | Miscellenious 50
15-0079002 | Customer(US Forest Service) agreed to power restoration the next day. Building were unoccupied. | Miscellenious 51
15-0087236 | Customer refused access to PG&E for repairs to Transmission Line | Miscellenious 52
15-0087173 | Customer refused access to PG&E for repairs to Transmission Line | Miscellenious 52
15-0087248 | Customer refused access to PG&E for repairs to Transmission Line | Miscellenious 52
15-0087228 | Customer refused access to PG&E for repairs to Transmission Line | Miscellenious 52
15-0086232 | Private plane crash with fatalities. Kern County Sheriff denied access until the investigation was completed. | Miscellenious 56
15-0073135 | Peat Fire on Bradford Island in Delta | Peat Fire
15-0087424 | San Luis Obispo Fire Dept requested line to be de-energized for the safety of the firefighters. | Miscellenious 58
15-0087875 | Landslide off Hwy 299 | Miscellenious 59
16-0004162 | Mudslide | Miscellenious 60
16-0011637 | Car theft | Miscellenious 61
16-0004234 | Flooding | Miscellenious 62
16-0002510 | Flooding | Miscellenious 63
16-0018478 | Flooding | Miscellenious 64
16-0017884 | Flooding | Miscellenious 65
16-0020532 | Customer request | Miscellenious 66
16-0032787 | Railrooad tie fire | Miscellenious 67
16-0025387 | Customer request | Miscellenious 68
16-0037914 | Police actvity | Miscellenious 69
16-0047576 | Appaloosa Fire Cal Fire chief asked T-Lines be de-energized. | Appaloosa
16-0047576 | Appaloosa Fire Cal Fire chief asked T-Lines be de-energized. | Appaloosa
16-0047576 | Appaloosa Fire Cal Fire chief asked T-Lines be de-energized. | Appaloosa
16-0040254 | WAPA T-Line | Miscellenious 73
16-0044338 | Structure fire | Structure fire 74
16-0041119 | Tree failure | Miscellenious 75
16-0047488 | Curry Fire | Curry
16-0046084 | Fraiser Fire | Fraiser Fire
16-0048021 | Structure fire | Structure fire 78
16-0046756 | 3rd party climber | Miscellenious 79
16-0053724 | Fork Fire | fork fire
16-0050315 | Green Fire | green
16-0052248 | Sobrantes Fire | Soberanes
16-0053130 | Sobrantes Fire | Soberanes
16-0053995 | Sobrantes Fire | Soberanes
16-0052404 | Sobrantes Fire | Soberanes
16-0052405 | Sobrantes Fire | Soberanes
16-0053970` | Sobrantes Fire | Soberanes
16-0052690 | Sobrantes Fire | Soberanes
16-0053969 | Sobrantes Fire | Soberanes
16-0054217 | Sobrantes Fire | Soberanes
16-0054975 | Sobrantes Fire | Soberanes
16-0053671 | Extention Fire#2 | Miscellenious 92
16-0055140 | Grub Fire | Grub
16-0056103 | Clayton Fire | Clayton
16-0057195 | Sobrantes Fire | Soberanes
16-0053861 | Goose Fire | Goose
16-0057291 | Sobrantes Fire | Soberanes
16-0052073 | Initiative Foods Fire | Miscellenious 98
16-0040870 | N/A | Miscellenious 99
16-0057128 | Clayton Fire | Clayton
16-0056103 | Clayton Fire | Clayton
16-0052175 | N/A | Miscellenious 102
16-0058308 | N/A | Miscellenious 103
16-0057745 | N/A | Miscellenious 104
16-0057200 | Chimney Fire | Chimney
16-0055868 | Mineral Fire | Mineral fire
16-0053958 | Goose Fire | Goose
16-0057036 | N/A | Miscellenious 108
16-0057128 | Clayton Fire | Clayton
16-0057722 | Clayton Fire | Clayton
16-0059078 | Chimney Fire | Chimney
16-0059175 | N/A | Miscellenious 112
16-0058863 | N/A | Miscellenious 113
16-0057194 | Clayton Fire | Clayton
16-0057199 | Clayton Fire | Clayton
16-0057511 | Clayton Fire | Clayton
16-0060402 | Chimney Fire | Chimney
16-0058864 | Chimney Fire | Chimney
16-0057512 | Clayton Fire | Clayton
16-0056667 | Structure Fire | Structure Fire 120
16-0060552 | Wildfire | Miscellenious 121
16-0059182 | Tulley Fire | Tully
16-0057129 | Clayton Fire | Clayton
16-0049398 | Grass fire | Miscellenious 124
16-0047764 | Grass fire | Miscellenious 125
16-0051570 | Serpa fire | Serpa
16-0047754 | Broken Bit | Miscellenious 127
16-0039882 | Riverbed fire | Riverbed
16-0061386 | Chimney Fire | Chimney
16-0047215 | Grass fire | Miscellenious 130
16-0045471 | Grass fire | Miscellenious 131
16-0044590 | Cole fire | cole
16-0058633 | Chimney Fire | chimney
16-0064043 | McDonald Fire | McDonald
16-0062269 | Sunny Fire | sunny
16-0062398 | Saddle Fire | saddle
16-0060410 | Grass fire | Miscellenious 137
16-0068775 | Structure Fire | Structure Fire 138
16-0067537 | Marshes Fire | Marshes
16-0069410 | Chumash Fire | Chumash
16-0065816 | 2 House Fire | Miscellenious 141
16-0064801 | Car pole | Miscellenious 142
16-0064801 | Car pole | Miscellenious 143
16-0067829 | Loma Prieta Fire | Loma
16-0074199 | Car Pole | Miscellenious 145
16-0067551 | Vegetation fire | Miscellenious 146
16-0073622 | Vegetation fire | Miscellenious 147
16-0073608 | Vegetation fire | Miscellenious 148
16-0076880 | Structure fire | Structure fire 149
16-0078004 | Water Leak | Water Leak
16-0083969 | Ghost ship fire | ghost ship
16-0083236 | Structure Fire | Structure Fire 152
16-0085841 | Warehouse Fire | Miscellenious 153
17-0008766 | Snow | Miscellenious 154
17-0013316 | Flood | Miscellenious 155
17-0007051 | Mudslide | Miscellenious 156
17-0011077 | Mudslide | Miscellenious 157
17-0019777 | Flooding | Miscellenious 158
17-0020790 | Structure Fire | Structure Fire 159
17-0020988 | Flooding | Miscellenious 160
17-0016146 | Flooding | Miscellenious 161
17-0015705 | Flooding | Miscellenious 162
17-0020911 | Evacuation | Miscellenious 163
17-0020911 | Evacuation | Miscellenious 164
17/0018799 | Mudslide | Miscellenious 165
17-0022537 | Flooding | Miscellenious 166
17-0026736 | Mudslide | Miscellenious 167
17-0019194 | Flooding | Miscellenious 168
17-0019348 | Flooding | Miscellenious 169
17-0029467 | Flood | Miscellenious 170
17-0030194 | Flood | Miscellenious 171
17-0009642 | Extreme weather | Miscellenious 172
17-0028569 | Muslide | Miscellenious 173
17-0026897 | Fallen tree | Miscellenious 174
17-0034484 | Structure Fire | Structure Fire 175
17-0033989 | Structure Fire | Structure Fire 176
17-0037870 | Flood | Miscellenious 177
17-0040504 | Road Closure | Miscellenious 178
17-0046642 | Acre Fire | Acre Fire
17-0047697 | Structure Fire | Structure Fire 180
17-0047696 | Structure Fire | Structure Fire 181
17-0050806 | Pallet Fire | Pallet Fire
17-0058297 | Levy break | Levy break
17-0060132 | Derrick Fire | derrick
17-0060425 | Grass Fire | Grass Fire
17-0060085 | Spring Fire | Spring Fire
17-0061069 | Structure Fire | Structure Fire 187
17-0059475 | Grass Fire | Grass Fire
17-0062403 | fire | Miscellenious 189
17-0055795 | Structure Fire | Structure Fire 190
17-0062157 | Alum Rock Fire | Alum Rock Fire
17-0061315 | Wall Fire | Wall
17-0061299 | Wall Fire | Wall
17-0061473 | Wall Fire | Wall
17-0061515 | Wall Fire | Wall
17-0061315 | Wall Fire | Wall
17-0063520 | Saratoga Hills Fire | Saratoga Hills Fire
17-0061219 | Dig in | Miscellenious 198
17-0063296 | Grade Fire | Grade
17-0061351 | Alamo Fire | Alamo
17-0061428 | Alamo Fire | Alamo
17-0062054 | Alamo Fire | Alamo
17-0058751 | Santa margarita Fire | Santa margarita Fire
17-0061560 | Stone Fire | Stone
17-0061453 | Whittier fire | Whittier
17-0066480 | Jacksonville Fire | Jacksonville
17-0066473 | Jacksonville Fire | Jacksonville
17-0063781 | Structure Fire | Structure Fire 208
17-0063754 | Hogback Fire | Hogback Fire
17-0061015 | Winters Fire | Winters Fire
17-0061526 | Alamo Fire | alamo
17-0064288.1 | Canyon-auburn Fire | Canyon-auburn Fire
17-0052970 | Stockton Fire | Stockton Fire
17-0050777 | Property Owner | Miscellenious 214
17-0062495 | Levee Break | Levee Break
17-0063258 | Detwiler Fire | Detwiler
17-0063494 | Detwiler Fire | Detwiler
17-0063694 | Detwiler Fire | Detwiler
17-0063698 | Detwiler Fire | Detwiler
17-0054202 | Oakwood Fire | Oakwood
17-0066571 | Twist Fire | Twist Fire
17-0067270 | Sandy Bar Fire | Sandy Bar Fire
17-0067765 | Saw Fire | Saw Fire
17-0069729 | Sage Canyon Fire | Sage Canyon Fire
17-0071136 | Corner Fire | Corner Fire
17-0072686 | I-5 Fire | I-5 Fire
17-0063460 | Maria Fire | maria
17-0067490 | Brush Fire | brush
17-0075412 | Customer Complaint | Miscellenious 229
17-0073847 | Ponderosa Fire | Ponderosa
17-0075566 | Peak Fire | Peak
17-0074305 | Pleasaant Fire | Pleasant
17-0075546 | Mission Fire | mission
17-0083565 | Structure Fire | Structure Fire 234
17-0082949 | Rucker Fire | rucker
17-0073645 | Alder Fire | alder
17-0087209 | Coal Fire | coal
17-0093129 | Customer OK | Miscellenious 238
17-0100400 | Salt Springs 2101 | Salt Springs 2101
17-0092708 | McFarland 1101 | McFarland 1101
18-0003644 | Road Block | Road Block
18-0010374 | Emergency shutdown | Miscellenious 242
18-0035576 | Structure Fire | Structure Fire 243
18-0040771 | Customer consent | Miscellenious 244
18-0051211 | Table Fire | Table Fire
18-0051211 | Table Fire | Table Fire
18-0053910 | Stoll Fire | Stoll Fire
18-0053936 | Stoll Fire | Stoll Fire
18-0053896 | Stoll Fire | Stoll Fire
18-0053898 | Stoll Fire | Stoll Fire
18-0054060 | Pawnee Fire | Pawnee Fire
18-0058587 | Schoolhouse fire | School fire
18-0059709 | Fergusson Fire | Fergusson Fire
18-0060332 | Fergusson Fire | Fergusson Fire
18-0061189 | Las Cruses Fire | Cruces Fire
18-0062515 | Country Fire | Country Fire
18-0063765 | Church Fire | Church Fire
18-0058419 | Hale Fire | Hale Fire
18-0058989 | Panoche fire | Panoche fire
18-0056845 | Anderson Island Fire | Anderson Island Fire
18-0049327 | Chrome Fire | Chrome Fire
18-0056884 | County Fire | County Fire
18-0067233 | Grass Fire | Grass Fire
18-0053879 | Bascom Fire | Bascom Fire
18-0063745 | Marsh Fire | Marsh Fire
18-0058389 | Antioch Townhome Complex Fire | Antioch Townhome Complex Fire
18-0056724 | County Fire | County Fire
18-0056864 | County Fire | County Fire
18-0068879.1 | Nelson Fire - Solano County | Nelson Fire
18-0068879.2 | Nelson Fire - Solano County | Nelson Fire
18-0059408 | Stoney Fire | Stoney Fire
18-0067277 | Murphy Fire | Murphy Fire
18-0067277 | Murphy Fire | Murphy Fire
18-0068472 | Hat Fire | Hat Fire
18-0068518 | Hat Fire | Hat Fire
18-0068475 | Hat Fire | Hat Fire
18-0068479 | Hat Fire | Hat Fire
18-0068473 | Hat Fire | Hat Fire
18-0061257 | Structure Fire | Structure Fire 279
18-0061257 | Structure Fire | Structure Fire 280
18-0058117 | Grass Wildfire | Grass Wildfire
18-0053956 | Wildland Fire | Miscellenious 282
18-0071446 | Gorge Fire | Gorge Fire
18-0054039 | Creek Fire | Creek Fire
18-0059873 | Grassland Wild Fire | Miscellenious 285
18-0051506 | Grassland House Fire | Grassland House Fire
18-0065171 | Grass Fire | Miscellenious 287
18-0053899 | Stoll Fire | Stoll Fire
18-0055989 | Pawnee Fire | Pawnee Fire
18-0056007 | Pawnee Fire | Pawnee Fire
18-0053984 | Pawnee Fire | Pawnee Fire
18-0056062 | County Fire | County Fire
18-0069085 | Grass Valley Fire | Grass Valley Fire
18-0062435 | Carder Fire | Carder Fire
18-0062363 | Carder Fire | Carder Fire
18-0062362 | Carder Fire | Carder Fire
18-0055982 | Ridge Fire | Ridge Fire
18-0065890 | Omega Fire | Omega Fire
18-0059965 | Fergusson Fire | Fergusson Fire
18-0060332 | Fergusson Fire | Fergusson Fire
18-0060332 | Fergusson Fire | Fergusson Fire
18-0060332 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0063405 | Fergusson Fire | Fergusson Fire
18-0066361 | Fergusson Fire | Fergusson Fire
18-0066361 | Fergusson Fire | Fergusson Fire
18-0066361 | Fergusson Fire | Fergusson Fire
18-0066361 | Fergusson Fire | Fergusson Fire
18-0066638 | Fergusson Fire | Fergusson Fire
18-0066638 | Fergusson Fire | Fergusson Fire
18-0066638 | Fergusson Fire | Fergusson Fire
18-0062759 | Carr Fire | Carr Fire
18-0063814 | Carr Fire | Carr Fire
18-0063814 | Carr Fire | Carr Fire
18-0063814 | Carr Fire | Carr Fire
18-0063845 | Carr Fire | Carr Fire
18-0064182 | Carr Fire | Carr Fire
18-0064182 | Carr Fire | Carr Fire
18-0064196 | Carr Fire | Carr Fire
18-0064530 | Carr Fire | Carr Fire
18-0064533 | Carr Fire | Carr Fire
18-0064533 | Carr Fire | Carr Fire
18-0064546 | Carr Fire | Carr Fire
18-0065074 | Carr Fire | Carr Fire
18-0065096 | Carr Fire | Carr Fire
18-0065129 | Carr Fire | Carr Fire
18-0065159 | Carr Fire | Carr Fire
18-0065160 | Carr Fire | Carr Fire
18-0065161 | Carr Fire | Carr Fire
18-0065164 | Carr Fire | Carr Fire
18-0065168 | Carr Fire | Carr Fire
18-0065331 | Carr Fire | Carr Fire
18-0065333 | Carr Fire | Carr Fire
18-0065462 | Carr Fire | Carr Fire
18-0065468 | Carr Fire | Carr Fire
18-0065470 | Carr Fire | Carr Fire
18-0065530 | Carr Fire | Carr Fire
18-0065530 | Carr Fire | Carr Fire
18-0065886 | Carr Fire | Carr Fire
18-0065894 | Carr Fire | Carr Fire
18-0065991 | Carr Fire | Carr Fire
18-0066118 | Carr Fire | Carr Fire
18-0066134 | Carr Fire | Carr Fire
18-0066139 | Carr Fire | Carr Fire
18-0066146 | Carr Fire | Carr Fire
18-0066170 | Carr Fire | Carr Fire
18-0066173 | Carr Fire | Carr Fire
18-0066174 | Carr Fire | Carr Fire
18-0066181 | Carr Fire | Carr Fire
18-0066261 | Carr Fire | Carr Fire
18-0066262 | Carr Fire | Carr Fire
18-0066263 | Carr Fire | Carr Fire
18-0066264 | Carr Fire | Carr Fire
18-0066265 | Carr Fire | Carr Fire
18-0066266 | Carr Fire | Carr Fire
18-0066267 | Carr Fire | Carr Fire
18-0066268 | Carr Fire | Carr Fire
18-0066269 | Carr Fire | Carr Fire
18-0066270 | Carr Fire | Carr Fire
18-0066271 | Carr Fire | Carr Fire
18-0066272 | Carr Fire | Carr Fire
18-0066273 | Carr Fire | Carr Fire
18-0066274 | Carr Fire | Carr Fire
18-0066275 | Carr Fire | Carr Fire
18-0066276 | Carr Fire | Carr Fire
18-0066278 | Carr Fire | Carr Fire
18-0066279 | Carr Fire | Carr Fire
18-0066280 | Carr Fire | Carr Fire
18-0066281 | Carr Fire | Carr Fire
18-0066528 | Carr Fire | Carr Fire
18-0066591 | Carr Fire | Carr Fire
18-0066592 | Carr Fire | Carr Fire
18-0066597 | Carr Fire | Carr Fire
18-0066705 | Carr Fire | Carr Fire
18-0066711 | Carr Fire | Carr Fire
18-0066714 | Carr Fire | Carr Fire
18-0066715 | Carr Fire | Carr Fire
18-0066736 | Carr Fire | Carr Fire
18-0066737 | Carr Fire | Carr Fire
18-0066738 | Carr Fire | Carr Fire
18-0066739 | Carr Fire | Carr Fire
18-0066740 | Carr Fire | Carr Fire
18-0066744 | Carr Fire | Carr Fire
18-0066745 | Carr Fire | Carr Fire
18-0066746 | Carr Fire | Carr Fire
18-0066751 | Carr Fire | Carr Fire
18-0066757 | Carr Fire | Carr Fire
18-0066766 | Carr Fire | Carr Fire
18-0066767 | Carr Fire | Carr Fire
18-0066774 | Carr Fire | Carr Fire
18-0066775 | Carr Fire | Carr Fire
18-0066776 | Carr Fire | Carr Fire
18-0066778 | Carr Fire | Carr Fire
18-0066779 | Carr Fire | Carr Fire
18-0066780 | Carr Fire | Carr Fire
18-0066889 | Carr Fire | Carr Fire
18-0066890 | Carr Fire | Carr Fire
18-0066891 | Carr Fire | Carr Fire
18-0066892 | Carr Fire | Carr Fire
18-0066895 | Carr Fire | Carr Fire
18-0066908 | Carr Fire | Carr Fire
18-0067219 | Carr Fire | Carr Fire
18-0067240 | Carr Fire | Carr Fire
18-0067241 | Carr Fire | Carr Fire
18-0067460 | Carr Fire | Carr Fire
18-0067480 | Carr Fire | Carr Fire
18-0067510 | Carr Fire | Carr Fire
18-0067576 | Carr Fire | Carr Fire
18-0067623 | Carr Fire | Carr Fire
18-0067625 | Carr Fire | Carr Fire
18-0067639 | Carr Fire | Carr Fire
18-0067651 | Carr Fire | Carr Fire
18-0067662 | Carr Fire | Carr Fire
18-0067916 | Carr Fire | Carr Fire
18-0068080 | Carr Fire | Carr Fire
18-0068084 | Carr Fire | Carr Fire
18-0068441 | Carr Fire | Carr Fire
18-0068481 | Carr Fire | Carr Fire
18-0068482 | Carr Fire | Carr Fire
18-0070315 | Carr Fire | Carr Fire
18-0070333 | Carr Fire | Carr Fire
18-0064489 | Mendocino Complex | Mendocino Complex
18-0065124 | Mendocino Complex | Mendocino Complex
18-0065152 | Mendocino Complex | Mendocino Complex
18-0065124 | Mendocino Complex | Mendocino Complex
18-0064491 | Mendocino Complex | Mendocino Complex
18-0064611 | Mendocino Complex | Mendocino Complex
18-0064619 | Mendocino Complex | Mendocino Complex
18-0064619 | Mendocino Complex | Mendocino Complex
18-0064789 | Mendocino Complex | Mendocino Complex
18-0064789 | Mendocino Complex | Mendocino Complex
18-0064789 | Mendocino Complex | Mendocino Complex
18-0064789 | Mendocino Complex | Mendocino Complex
18-0064789 | Mendocino Complex | Mendocino Complex
18-0064789 | Mendocino Complex | Mendocino Complex
18-0064789 | Mendocino Complex | Mendocino Complex
18-0064789 | Mendocino Complex | Mendocino Complex
18-0064789 | Mendocino Complex | Mendocino Complex
18-0064789 | Mendocino Complex | Mendocino Complex
18-0064789 | Mendocino Complex | Mendocino Complex
18-0064789 | Mendocino Complex | Mendocino Complex
18-0064798 | Mendocino Complex | Mendocino Complex
18-0064803 | Mendocino Complex | Mendocino Complex
18-0064805 | Mendocino Complex | Mendocino Complex
18-0064812 | Mendocino Complex | Mendocino Complex
18-0064814 | Mendocino Complex | Mendocino Complex
18-0065090 | Mendocino Complex | Mendocino Complex
18-0065124 | Mendocino Complex | Mendocino Complex
18-0065124 | Mendocino Complex | Mendocino Complex
18-0065143 | Mendocino Complex | Mendocino Complex
18-0065144 | Mendocino Complex | Mendocino Complex
18-0065145 | Mendocino Complex | Mendocino Complex
18-0088901 | Paint Warehouse Structure Fire | Structure Fire 470
18-0097264 | Structure Fire | Structure Fire 471
18-0087987 | Sun Fire | Sun Fire
18-0097076 | Rincon Fire | Rincon Fire
18-0105902 | AT&T alley arm broke on PG&E joint pole | Structure Fire 474
18-0076434 | North Fire | North Fire
18-0098448 | CAMP FIRE | CAMP FIRE
18-0099077 | CAMP FIRE | CAMP FIRE
18-0099075 | CAMP FIRE | CAMP FIRE
18-0099076 | CAMP FIRE | CAMP FIRE
18-0098445 | CAMP FIRE | CAMP FIRE
18-0099184 | CAMP FIRE | CAMP FIRE
18-0099187 | CAMP FIRE | CAMP FIRE
18-0098446 | CAMP FIRE | CAMP FIRE
18-0098487 | CAMP FIRE | CAMP FIRE
18-0098440 | CAMP FIRE | CAMP FIRE
18-0098436 | CAMP FIRE | CAMP FIRE
18-0098438 | CAMP FIRE | CAMP FIRE
18-0098432 | CAMP FIRE | CAMP FIRE
18-0098432 | CAMP FIRE | CAMP FIRE
18-0098215 | CAMP FIRE | CAMP FIRE
18-0099171 | CAMP FIRE | CAMP FIRE
18-0099386 | CAMP FIRE | CAMP FIRE
18-0099168 | CAMP FIRE | CAMP FIRE
18-0099164 | CAMP FIRE | CAMP FIRE
18-0099404 | CAMP FIRE | CAMP FIRE
18-0099167 | CAMP FIRE | CAMP FIRE
18-0099382 | CAMP FIRE | CAMP FIRE
18-0099388 | CAMP FIRE | CAMP FIRE
18-0099166 | CAMP FIRE | CAMP FIRE
18-0099169 | CAMP FIRE | CAMP FIRE
18-0099384 | CAMP FIRE | CAMP FIRE
18-0100110 | CAMP FIRE | CAMP FIRE
18-0100113 | CAMP FIRE | CAMP FIRE
18-0101874 | CAMP FIRE | CAMP FIRE
18-0102119 | CAMP FIRE | CAMP FIRE
18-0102121 | CAMP FIRE | CAMP FIRE
18-0102125 | CAMP FIRE | CAMP FIRE
18-0102138 | CAMP FIRE | CAMP FIRE
18-0101609 | CAMP FIRE | CAMP FIRE
18-0102123 | CAMP FIRE | CAMP FIRE
18-0102120 | CAMP FIRE | CAMP FIRE
18-0102332 | CAMP FIRE | CAMP FIRE
18-0102111 | CAMP FIRE | CAMP FIRE
18-0103077 | CAMP FIRE | CAMP FIRE
18-0100823 | CAMP FIRE | CAMP FIRE
18-0098215 | CAMP FIRE | CAMP FIRE
18-0099374 | CAMP FIRE | CAMP FIRE
18-0099373 | CAMP FIRE | CAMP FIRE
18-0099375 | CAMP FIRE | CAMP FIRE
18-0099437 | CAMP FIRE | CAMP FIRE
18-0099351 | CAMP FIRE | CAMP FIRE
18-0099356 | CAMP FIRE | CAMP FIRE
18-0099361 | CAMP FIRE | CAMP FIRE
18-0100458 | CAMP FIRE | CAMP FIRE
18-0100455 | CAMP FIRE | CAMP FIRE
18-0098209 | CAMP FIRE | CAMP FIRE
18-0098209 | CAMP FIRE | CAMP FIRE
18-0100660 | CAMP FIRE | CAMP FIRE
18-0100453 | CAMP FIRE | CAMP FIRE
18-0099204 | CAMP FIRE | CAMP FIRE
18-0100450 | CAMP FIRE | CAMP FIRE
18-0102627 | CAMP FIRE | CAMP FIRE
18-0100826 | CAMP FIRE | CAMP FIRE
18-0100824 | CAMP FIRE | CAMP FIRE
18-0098208 | CAMP FIRE | CAMP FIRE
18-0102324 | CAMP FIRE | CAMP FIRE
18-0103365 | CAMP FIRE | CAMP FIRE
18-0103371 | CAMP FIRE | CAMP FIRE
18-0103363 | CAMP FIRE | CAMP FIRE
18-0102333 | CAMP FIRE | CAMP FIRE
18-0102334 | CAMP FIRE | CAMP FIRE
18-0102339 | CAMP FIRE | CAMP FIRE
18-0107814 | CAMP FIRE | CAMP FIRE
18-0098211 | CAMP FIRE | CAMP FIRE
18-0100487 | CAMP FIRE | CAMP FIRE
18-0100505 | CAMP FIRE | CAMP FIRE
18-0100493 | CAMP FIRE | CAMP FIRE
18-0098211 | CAMP FIRE | CAMP FIRE
18-0102337 | CAMP FIRE | CAMP FIRE
18-0103572 | CAMP FIRE | CAMP FIRE
18-0103608 | CAMP FIRE | CAMP FIRE
18-0103582 | CAMP FIRE | CAMP FIRE
18-0103567 | CAMP FIRE | CAMP FIRE
18-0103590 | CAMP FIRE | CAMP FIRE
18-0103737 | CAMP FIRE | CAMP FIRE
18-0103216 | CAMP FIRE | CAMP FIRE
18-0098513 | CAMP FIRE | CAMP FIRE
18-0100798 | CAMP FIRE | CAMP FIRE
18-0100799 | CAMP FIRE | CAMP FIRE
18-0100803 | CAMP FIRE | CAMP FIRE
18-0100790 | CAMP FIRE | CAMP FIRE
18-0100794 | CAMP FIRE | CAMP FIRE
18-0100787 | CAMP FIRE | CAMP FIRE
18-0100796 | CAMP FIRE | CAMP FIRE
18-0100802 | CAMP FIRE | CAMP FIRE
18-0100797 | CAMP FIRE | CAMP FIRE
18-0100806 | CAMP FIRE | CAMP FIRE
18-0100812 | CAMP FIRE | CAMP FIRE
18-0100815 | CAMP FIRE | CAMP FIRE
18-0100817 | CAMP FIRE | CAMP FIRE
18-0100814 | CAMP FIRE | CAMP FIRE
18-0100818 | CAMP FIRE | CAMP FIRE
18-0100869 | CAMP FIRE | CAMP FIRE
18-0100874 | CAMP FIRE | CAMP FIRE
18-0100804 | CAMP FIRE | CAMP FIRE
18-0100857 | CAMP FIRE | CAMP FIRE
18-0100807 | CAMP FIRE | CAMP FIRE
18-0100872 | CAMP FIRE | CAMP FIRE
18-0100867 | CAMP FIRE | CAMP FIRE
18-0100877 | CAMP FIRE | CAMP FIRE
18-0100829 | CAMP FIRE | CAMP FIRE
18-0100875 | CAMP FIRE | CAMP FIRE
18-0100866 | CAMP FIRE | CAMP FIRE
18-0100889 | CAMP FIRE | CAMP FIRE
18-0100884 | CAMP FIRE | CAMP FIRE
18-0100886 | CAMP FIRE | CAMP FIRE
18-0100862 | CAMP FIRE | CAMP FIRE
18-0100861 | CAMP FIRE | CAMP FIRE
18-0100878 | CAMP FIRE | CAMP FIRE
18-0100880 | CAMP FIRE | CAMP FIRE
18-0100870 | CAMP FIRE | CAMP FIRE
18-0100868 | CAMP FIRE | CAMP FIRE
18-0100876 | CAMP FIRE | CAMP FIRE
18-0100885 | CAMP FIRE | CAMP FIRE
18-0100882 | CAMP FIRE | CAMP FIRE
18-0100860 | CAMP FIRE | CAMP FIRE
18-0100864 | CAMP FIRE | CAMP FIRE
18-0100891 | CAMP FIRE | CAMP FIRE
18-0100887 | CAMP FIRE | CAMP FIRE
18-0100831 | CAMP FIRE | CAMP FIRE
18-0100883 | CAMP FIRE | CAMP FIRE
18-0100865 | CAMP FIRE | CAMP FIRE
18-0100888 | CAMP FIRE | CAMP FIRE
18-0100879 | CAMP FIRE | CAMP FIRE
18-0100892 | CAMP FIRE | CAMP FIRE
18-0100890 | CAMP FIRE | CAMP FIRE
18-0100881 | CAMP FIRE | CAMP FIRE
18-0100830 | CAMP FIRE | CAMP FIRE
18-0100871 | CAMP FIRE | CAMP FIRE
18-0098552 | CAMP FIRE | CAMP FIRE
18-0100902 | CAMP FIRE | CAMP FIRE
18-0100905 | CAMP FIRE | CAMP FIRE
18-0100907 | CAMP FIRE | CAMP FIRE
18-0100906 | CAMP FIRE | CAMP FIRE
18-0100904 | CAMP FIRE | CAMP FIRE
18-0100921 | CAMP FIRE | CAMP FIRE
18-0100918 | CAMP FIRE | CAMP FIRE
18-0103210 | CAMP FIRE | CAMP FIRE
18-0100788 | CAMP FIRE | CAMP FIRE
18-0100820 | CAMP FIRE | CAMP FIRE
18-0103197 | CAMP FIRE | CAMP FIRE
18-0103207 | CAMP FIRE | CAMP FIRE
18-0100789 | CAMP FIRE | CAMP FIRE
18-0100800 | CAMP FIRE | CAMP FIRE
18-0105480 | CAMP FIRE | CAMP FIRE
18-0103199 | CAMP FIRE | CAMP FIRE
18-0100792 | CAMP FIRE | CAMP FIRE
18-0100785 | CAMP FIRE | CAMP FIRE
18-0103202 | CAMP FIRE | CAMP FIRE
18-0103198 | CAMP FIRE | CAMP FIRE
18-0101286 | CAMP FIRE | CAMP FIRE
18-0101274 | CAMP FIRE | CAMP FIRE
18-0101279 | CAMP FIRE | CAMP FIRE
18-0101263 | CAMP FIRE | CAMP FIRE
18-0101254 | CAMP FIRE | CAMP FIRE
18-0101257 | CAMP FIRE | CAMP FIRE
18-0101260 | CAMP FIRE | CAMP FIRE
18-0101261 | CAMP FIRE | CAMP FIRE
18-0101252 | CAMP FIRE | CAMP FIRE
18-0101341 | CAMP FIRE | CAMP FIRE
18-0101334 | CAMP FIRE | CAMP FIRE
18-0101353 | CAMP FIRE | CAMP FIRE
18-0101315 | CAMP FIRE | CAMP FIRE
18-0101318 | CAMP FIRE | CAMP FIRE
18-0101323 | CAMP FIRE | CAMP FIRE
18-0101310 | CAMP FIRE | CAMP FIRE
18-0101330 | CAMP FIRE | CAMP FIRE
18-0101321 | CAMP FIRE | CAMP FIRE
18-0101364 | CAMP FIRE | CAMP FIRE
18-0101405 | CAMP FIRE | CAMP FIRE
18-0101414 | CAMP FIRE | CAMP FIRE
18-0101430 | CAMP FIRE | CAMP FIRE
18-0101454 | CAMP FIRE | CAMP FIRE
18-0101446 | CAMP FIRE | CAMP FIRE
18-0101502 | CAMP FIRE | CAMP FIRE
18-0101513 | CAMP FIRE | CAMP FIRE
18-0101476 | CAMP FIRE | CAMP FIRE
18-0101490 | CAMP FIRE | CAMP FIRE
18-0101508 | CAMP FIRE | CAMP FIRE
18-0101495 | CAMP FIRE | CAMP FIRE
18-0101482 | CAMP FIRE | CAMP FIRE
18-0101468 | CAMP FIRE | CAMP FIRE
18-0101463 | CAMP FIRE | CAMP FIRE
18-0101457 | CAMP FIRE | CAMP FIRE
18-0101648 | CAMP FIRE | CAMP FIRE
18-0101647 | CAMP FIRE | CAMP FIRE
18-0101649 | CAMP FIRE | CAMP FIRE
18-0101652 | CAMP FIRE | CAMP FIRE
18-0101646 | CAMP FIRE | CAMP FIRE
18-0101651 | CAMP FIRE | CAMP FIRE
18-0101579 | CAMP FIRE | CAMP FIRE
18-0103206 | CAMP FIRE | CAMP FIRE
18-0103212 | CAMP FIRE | CAMP FIRE
18-0103247 | CAMP FIRE | CAMP FIRE
18-0103346 | CAMP FIRE | CAMP FIRE
18-0103348 | CAMP FIRE | CAMP FIRE
18-0103376 | CAMP FIRE | CAMP FIRE
18-0103369 | CAMP FIRE | CAMP FIRE
18-0103342 | CAMP FIRE | CAMP FIRE
18-0103335 | CAMP FIRE | CAMP FIRE
18-0103358 | CAMP FIRE | CAMP FIRE
18-0103373 | CAMP FIRE | CAMP FIRE
18-0103331 | CAMP FIRE | CAMP FIRE
18-0103696 | CAMP FIRE | CAMP FIRE
18-0103700 | CAMP FIRE | CAMP FIRE
18-0103693 | CAMP FIRE | CAMP FIRE
18-0103702 | CAMP FIRE | CAMP FIRE
18-0103780 | CAMP FIRE | CAMP FIRE
18-0103757 | CAMP FIRE | CAMP FIRE
18-0103778 | CAMP FIRE | CAMP FIRE
18-0103765 | CAMP FIRE | CAMP FIRE
18-0103783 | CAMP FIRE | CAMP FIRE
18-0103821 | CAMP FIRE | CAMP FIRE
18-0103788 | CAMP FIRE | CAMP FIRE
18-0103798 | CAMP FIRE | CAMP FIRE
18-0103705 | CAMP FIRE | CAMP FIRE
18-0103774 | CAMP FIRE | CAMP FIRE
18-0103794 | CAMP FIRE | CAMP FIRE
18-0103695 | CAMP FIRE | CAMP FIRE
18-0103776 | CAMP FIRE | CAMP FIRE
18-0103726 | CAMP FIRE | CAMP FIRE
18-0103697 | CAMP FIRE | CAMP FIRE
18-0103825 | CAMP FIRE | CAMP FIRE
18-0103769 | CAMP FIRE | CAMP FIRE
18-0103719 | CAMP FIRE | CAMP FIRE
18-0103709 | CAMP FIRE | CAMP FIRE
18-0103715 | CAMP FIRE | CAMP FIRE
18-0103728 | CAMP FIRE | CAMP FIRE
18-0103711 | CAMP FIRE | CAMP FIRE
18-0103749 | CAMP FIRE | CAMP FIRE
18-0103738 | CAMP FIRE | CAMP FIRE
18-0103771 | CAMP FIRE | CAMP FIRE
18-0103759 | CAMP FIRE | CAMP FIRE
18-0103703 | CAMP FIRE | CAMP FIRE
18-0103692 | CAMP FIRE | CAMP FIRE
18-0103211 | CAMP FIRE | CAMP FIRE
18-0103203 | CAMP FIRE | CAMP FIRE
18-0101581 | CAMP FIRE | CAMP FIRE
18-0103205 | CAMP FIRE | CAMP FIRE
18-0101580 | CAMP FIRE | CAMP FIRE
18-0101526 | CAMP FIRE | CAMP FIRE
18-0101644 | CAMP FIRE | CAMP FIRE
18-0103379 | CAMP FIRE | CAMP FIRE
18-0103204 | CAMP FIRE | CAMP FIRE
18-0098518 | CAMP FIRE | CAMP FIRE
18-0098518 | CAMP FIRE | CAMP FIRE
18-0101418 | CAMP FIRE | CAMP FIRE
18-0101424 | CAMP FIRE | CAMP FIRE
18-0101247 | CAMP FIRE | CAMP FIRE
18-0101530 | CAMP FIRE | CAMP FIRE
18-0103375 | CAMP FIRE | CAMP FIRE
18-0103213 | CAMP FIRE | CAMP FIRE
18-0103614 | CAMP FIRE | CAMP FIRE
18-0098513 | CAMP FIRE | CAMP FIRE
18-0101022 | CAMP FIRE | CAMP FIRE
18-0101061 | CAMP FIRE | CAMP FIRE
18-0101012 | CAMP FIRE | CAMP FIRE
18-0100989 | CAMP FIRE | CAMP FIRE
18-0100997 | CAMP FIRE | CAMP FIRE
18-0101011 | CAMP FIRE | CAMP FIRE
18-0101003 | CAMP FIRE | CAMP FIRE
18-0101082 | CAMP FIRE | CAMP FIRE
18-0101085 | CAMP FIRE | CAMP FIRE
18-0101121 | CAMP FIRE | CAMP FIRE
18-0101126 | CAMP FIRE | CAMP FIRE
18-0101090 | CAMP FIRE | CAMP FIRE
18-0101102 | CAMP FIRE | CAMP FIRE
18-0101151 | CAMP FIRE | CAMP FIRE
18-0101130 | CAMP FIRE | CAMP FIRE
18-0101337 | CAMP FIRE | CAMP FIRE
18-0101348 | CAMP FIRE | CAMP FIRE
18-0101340 | CAMP FIRE | CAMP FIRE
18-0101342 | CAMP FIRE | CAMP FIRE
18-0101333 | CAMP FIRE | CAMP FIRE
18-0101351 | CAMP FIRE | CAMP FIRE
18-0101331 | CAMP FIRE | CAMP FIRE
18-0101335 | CAMP FIRE | CAMP FIRE
18-0101355 | CAMP FIRE | CAMP FIRE
18-0101365 | CAMP FIRE | CAMP FIRE
18-0101370 | CAMP FIRE | CAMP FIRE
18-0101377 | CAMP FIRE | CAMP FIRE
18-0101375 | CAMP FIRE | CAMP FIRE
18-0101381 | CAMP FIRE | CAMP FIRE
18-0101396 | CAMP FIRE | CAMP FIRE
18-0101399 | CAMP FIRE | CAMP FIRE
18-0101391 | CAMP FIRE | CAMP FIRE
18-0101389 | CAMP FIRE | CAMP FIRE
18-0101401 | CAMP FIRE | CAMP FIRE
18-0101404 | CAMP FIRE | CAMP FIRE
18-0101411 | CAMP FIRE | CAMP FIRE
18-0101480 | CAMP FIRE | CAMP FIRE
18-0101500 | CAMP FIRE | CAMP FIRE
18-0101493 | CAMP FIRE | CAMP FIRE
18-0101507 | CAMP FIRE | CAMP FIRE
18-0101509 | CAMP FIRE | CAMP FIRE
18-0101472 | CAMP FIRE | CAMP FIRE
18-0101465 | CAMP FIRE | CAMP FIRE
18-0101519 | CAMP FIRE | CAMP FIRE
18-0101475 | CAMP FIRE | CAMP FIRE
18-0101140 | CAMP FIRE | CAMP FIRE
18-0098524 | CAMP FIRE | CAMP FIRE
18-0101104 | CAMP FIRE | CAMP FIRE
18-0103565 | CAMP FIRE | CAMP FIRE
18-0103568 | CAMP FIRE | CAMP FIRE
18-0103585 | CAMP FIRE | CAMP FIRE
18-0103598 | CAMP FIRE | CAMP FIRE
18-0103587 | CAMP FIRE | CAMP FIRE
18-0103611 | CAMP FIRE | CAMP FIRE
18-0103592 | CAMP FIRE | CAMP FIRE
18-0103610 | CAMP FIRE | CAMP FIRE
18-0103609 | CAMP FIRE | CAMP FIRE
18-0103612 | CAMP FIRE | CAMP FIRE
18-0103607 | CAMP FIRE | CAMP FIRE
18-0103613 | CAMP FIRE | CAMP FIRE
18-0103570 | CAMP FIRE | CAMP FIRE
18-0103605 | CAMP FIRE | CAMP FIRE
18-0106216 | CAMP FIRE | CAMP FIRE
18-0101488 | CAMP FIRE | CAMP FIRE
18-0101469 | CAMP FIRE | CAMP FIRE
18-0108636 | CAMP FIRE | CAMP FIRE
18-0106391 | CAMP FIRE | CAMP FIRE
18-0106388 | CAMP FIRE | CAMP FIRE
18-0101484 | CAMP FIRE | CAMP FIRE
18-0101147 | CAMP FIRE | CAMP FIRE
18-0101132 | CAMP FIRE | CAMP FIRE
18-0101417 | CAMP FIRE | CAMP FIRE
18-0103528 | CAMP FIRE | CAMP FIRE
18-0101129 | CAMP FIRE | CAMP FIRE
18-0101125 | CAMP FIRE | CAMP FIRE
18-0101144 | CAMP FIRE | CAMP FIRE
18-0101044 | CAMP FIRE | CAMP FIRE
18-0106396 | CAMP FIRE | CAMP FIRE
18-0101149 | CAMP FIRE | CAMP FIRE
18-0101118 | CAMP FIRE | CAMP FIRE
18-0103530 | CAMP FIRE | CAMP FIRE
18-0106394 | CAMP FIRE | CAMP FIRE
18-0101143 | CAMP FIRE | CAMP FIRE
18-0101136 | CAMP FIRE | CAMP FIRE
18-0101440 | CAMP FIRE | CAMP FIRE
18-0101139 | CAMP FIRE | CAMP FIRE
18-0101123 | CAMP FIRE | CAMP FIRE
18-0101111 | CAMP FIRE | CAMP FIRE
18-0098503 | CAMP FIRE | CAMP FIRE
18-0101514 | CAMP FIRE | CAMP FIRE
18-0101511 | CAMP FIRE | CAMP FIRE
18-0101517 | CAMP FIRE | CAMP FIRE
18-0101520 | CAMP FIRE | CAMP FIRE
18-0101536 | CAMP FIRE | CAMP FIRE
18-0101532 | CAMP FIRE | CAMP FIRE
18-0101538 | CAMP FIRE | CAMP FIRE
18-0101562 | CAMP FIRE | CAMP FIRE
18-0101555 | CAMP FIRE | CAMP FIRE
18-0101568 | CAMP FIRE | CAMP FIRE
18-0101570 | CAMP FIRE | CAMP FIRE
18-0101573 | CAMP FIRE | CAMP FIRE
18-0101812 | CAMP FIRE | CAMP FIRE
18-0101773 | CAMP FIRE | CAMP FIRE
18-0101727 | CAMP FIRE | CAMP FIRE
18-0101803 | CAMP FIRE | CAMP FIRE
18-0101758 | CAMP FIRE | CAMP FIRE
18-0101753 | CAMP FIRE | CAMP FIRE
18-0101774 | CAMP FIRE | CAMP FIRE
18-0101770 | CAMP FIRE | CAMP FIRE
18-0101794 | CAMP FIRE | CAMP FIRE
18-0101744 | CAMP FIRE | CAMP FIRE
18-0101809 | CAMP FIRE | CAMP FIRE
18-0101799 | CAMP FIRE | CAMP FIRE
18-0101720 | CAMP FIRE | CAMP FIRE
18-0101686 | CAMP FIRE | CAMP FIRE
18-0101788 | CAMP FIRE | CAMP FIRE
18-0101722 | CAMP FIRE | CAMP FIRE
18-0101754 | CAMP FIRE | CAMP FIRE
18-0101711 | CAMP FIRE | CAMP FIRE
18-0101756 | CAMP FIRE | CAMP FIRE
18-0101732 | CAMP FIRE | CAMP FIRE
18-0101749 | CAMP FIRE | CAMP FIRE
18-0101724 | CAMP FIRE | CAMP FIRE
18-0101707 | CAMP FIRE | CAMP FIRE
18-0101688 | CAMP FIRE | CAMP FIRE
18-0101705 | CAMP FIRE | CAMP FIRE
18-0101700 | CAMP FIRE | CAMP FIRE
18-0101695 | CAMP FIRE | CAMP FIRE
18-0101691 | CAMP FIRE | CAMP FIRE
18-0101698 | CAMP FIRE | CAMP FIRE
18-0101710 | CAMP FIRE | CAMP FIRE
18-0106199 | CAMP FIRE | CAMP FIRE
18-0106172 | CAMP FIRE | CAMP FIRE
18-0106174 | CAMP FIRE | CAMP FIRE
18-0106210 | CAMP FIRE | CAMP FIRE
18-0106168 | CAMP FIRE | CAMP FIRE
18-0106167 | CAMP FIRE | CAMP FIRE
18-0106163 | CAMP FIRE | CAMP FIRE
18-0106204 | CAMP FIRE | CAMP FIRE
18-0106208 | CAMP FIRE | CAMP FIRE
18-0106161 | CAMP FIRE | CAMP FIRE
18-0106165 | CAMP FIRE | CAMP FIRE
18-0106173 | CAMP FIRE | CAMP FIRE
18-0106170 | CAMP FIRE | CAMP FIRE
18-0101582 | CAMP FIRE | CAMP FIRE
18-0106192 | CAMP FIRE | CAMP FIRE
18-0106166 | CAMP FIRE | CAMP FIRE
18-0106164 | CAMP FIRE | CAMP FIRE
18-0102420 | CAMP FIRE | CAMP FIRE
18-0102423 | CAMP FIRE | CAMP FIRE
18-0102421 | CAMP FIRE | CAMP FIRE
18-0102422 | CAMP FIRE | CAMP FIRE
18-0102424 | CAMP FIRE | CAMP FIRE
18-0098503 | CAMP FIRE | CAMP FIRE
18-0101053 | CAMP FIRE | CAMP FIRE
18-0101051 | CAMP FIRE | CAMP FIRE
18-0101290 | CAMP FIRE | CAMP FIRE
18-0101285 | CAMP FIRE | CAMP FIRE
18-0101264 | CAMP FIRE | CAMP FIRE
18-0101291 | CAMP FIRE | CAMP FIRE
18-0101287 | CAMP FIRE | CAMP FIRE
18-0101266 | CAMP FIRE | CAMP FIRE
18-0101289 | CAMP FIRE | CAMP FIRE
18-0101292 | CAMP FIRE | CAMP FIRE
18-0101278 | CAMP FIRE | CAMP FIRE
18-0101077 | CAMP FIRE | CAMP FIRE
18-0101071 | CAMP FIRE | CAMP FIRE
18-0101074 | CAMP FIRE | CAMP FIRE
18-0098524 | CAMP FIRE | CAMP FIRE
18-0101236 | CAMP FIRE | CAMP FIRE
18-0101248 | CAMP FIRE | CAMP FIRE
18-0101256 | CAMP FIRE | CAMP FIRE
18-0101238 | CAMP FIRE | CAMP FIRE
18-0101242 | CAMP FIRE | CAMP FIRE
18-0101243 | CAMP FIRE | CAMP FIRE
18-0101246 | CAMP FIRE | CAMP FIRE
18-0101233 | CAMP FIRE | CAMP FIRE
18-0101251 | CAMP FIRE | CAMP FIRE
18-0101259 | CAMP FIRE | CAMP FIRE
18-0101253 | CAMP FIRE | CAMP FIRE
18-0101239 | CAMP FIRE | CAMP FIRE
18-0101250 | CAMP FIRE | CAMP FIRE
18-0098524 | CAMP FIRE | CAMP FIRE
18-0106155 | CAMP FIRE | CAMP FIRE
18-0106145 | CAMP FIRE | CAMP FIRE
18-0106153 | CAMP FIRE | CAMP FIRE
18-0106154 | CAMP FIRE | CAMP FIRE
18-0101245 | CAMP FIRE | CAMP FIRE
18-0106143 | CAMP FIRE | CAMP FIRE
18-0106146 | CAMP FIRE | CAMP FIRE
18-0106151 | CAMP FIRE | CAMP FIRE
18-0106150 | CAMP FIRE | CAMP FIRE
18-0106149 | CAMP FIRE | CAMP FIRE
18-0106152 | CAMP FIRE | CAMP FIRE
18-0106156 | CAMP FIRE | CAMP FIRE
18-0106144 | CAMP FIRE | CAMP FIRE
18-0106148 | CAMP FIRE | CAMP FIRE
18-0101344 | CAMP FIRE | CAMP FIRE
18-0101338 | CAMP FIRE | CAMP FIRE
18-0101329 | CAMP FIRE | CAMP FIRE
18-0101327 | CAMP FIRE | CAMP FIRE
18-0101361 | CAMP FIRE | CAMP FIRE
18-0101369 | CAMP FIRE | CAMP FIRE
18-0101374 | CAMP FIRE | CAMP FIRE
18-0101395 | CAMP FIRE | CAMP FIRE
18-0101400 | CAMP FIRE | CAMP FIRE
18-0101407 | CAMP FIRE | CAMP FIRE
18-0101431 | CAMP FIRE | CAMP FIRE
18-0101448 | CAMP FIRE | CAMP FIRE
18-0101455 | CAMP FIRE | CAMP FIRE
18-0101456 | CAMP FIRE | CAMP FIRE
18-0101452 | CAMP FIRE | CAMP FIRE
18-0101479 | CAMP FIRE | CAMP FIRE
18-0101471 | CAMP FIRE | CAMP FIRE
18-0101489 | CAMP FIRE | CAMP FIRE
18-0101824 | CAMP FIRE | CAMP FIRE
18-0101778 | CAMP FIRE | CAMP FIRE
18-0101786 | CAMP FIRE | CAMP FIRE
18-0101806 | CAMP FIRE | CAMP FIRE
18-0102509 | CAMP FIRE | CAMP FIRE
18-0102505 | CAMP FIRE | CAMP FIRE
18-0102510 | CAMP FIRE | CAMP FIRE
18-0102455 | CAMP FIRE | CAMP FIRE
18-0102512 | CAMP FIRE | CAMP FIRE
18-0102457 | CAMP FIRE | CAMP FIRE
18-0102503 | CAMP FIRE | CAMP FIRE
18-0102495 | CAMP FIRE | CAMP FIRE
18-0102466 | CAMP FIRE | CAMP FIRE
18-0102486 | CAMP FIRE | CAMP FIRE
18-0102464 | CAMP FIRE | CAMP FIRE
18-0102507 | CAMP FIRE | CAMP FIRE
18-0102472 | CAMP FIRE | CAMP FIRE
18-0102493 | CAMP FIRE | CAMP FIRE
18-0102483 | CAMP FIRE | CAMP FIRE
18-0102469 | CAMP FIRE | CAMP FIRE
18-0102470 | CAMP FIRE | CAMP FIRE
18-0102501 | CAMP FIRE | CAMP FIRE
18-0102492 | CAMP FIRE | CAMP FIRE
18-0102482 | CAMP FIRE | CAMP FIRE
18-0102526 | CAMP FIRE | CAMP FIRE
18-0102518 | CAMP FIRE | CAMP FIRE
18-0102522 | CAMP FIRE | CAMP FIRE
18-0102525 | CAMP FIRE | CAMP FIRE
18-0102523 | CAMP FIRE | CAMP FIRE
18-0102513 | CAMP FIRE | CAMP FIRE
18-0102519 | CAMP FIRE | CAMP FIRE
18-0102516 | CAMP FIRE | CAMP FIRE
18-0098113 | CAMP FIRE | CAMP FIRE
18-0098096 | CAMP FIRE | CAMP FIRE
18-0098098 | CAMP FIRE | CAMP FIRE
18-0098097 | CAMP FIRE | CAMP FIRE
18-0098099 | CAMP FIRE | CAMP FIRE
18-0098096 | CAMP FIRE | CAMP FIRE
18-0107823 | CAMP FIRE | CAMP FIRE
18-0107818 | CAMP FIRE | CAMP FIRE
18-0098064 | CAMP FIRE | CAMP FIRE
18-0098087 | CAMP FIRE | CAMP FIRE
18-0098064 | CAMP FIRE | CAMP FIRE
17-0085448 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086285 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086224 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088673 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086438 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086475 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085239 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088360 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086487 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0089648 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087211 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087988 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086477 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0089778 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087768 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087769 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087770 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088411 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085387 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088410 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088055 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087197 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086491 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086662 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087180 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087141 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085369 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085135 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085731 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085370 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086797 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087310 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088013 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087305 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087599 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087598 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086784 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088060 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086753 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085211 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088578 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086614 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086615 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086618 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086697 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087467 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087571 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087717 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087572 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086612 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086613 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086616 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086617 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086187 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086187 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086187 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086187 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086186 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088680 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088688 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085289 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087658 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088697 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087655 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086890 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087660 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087662 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088678 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088692 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088696 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088695 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088709 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085247 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087654 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085247 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085295 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087219 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087213 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086201 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087984 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087199 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087369 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086116 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087579 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086187 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086189 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087198 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087202 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086200 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086198 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087222 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085320 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085275 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085283 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086129 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086090 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086104 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086121 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086130 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086119 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088007 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086140 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088043 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086154 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085372 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087584 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0089515 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087839 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085958 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085372 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085367 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085438 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086445 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086414 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086374 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086770 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086281 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087359 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086821 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086698 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085950 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0089258 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0089338 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085957 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088422 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086782 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086790 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0089082 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087504 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087413 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087206 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0089398 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085262 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085901 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087351 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086863 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087090 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087398 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087515 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087122 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088276 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088417 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085330 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088264 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087498 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085286 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086861 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088425 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088432 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088420 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088426 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087541 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088416 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087582 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087205 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087580 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086458 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086466 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086481 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086444 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088020 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086872 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086338 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087154 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088022 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088418 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088419 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087779 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086912 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087578 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087154 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087154 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088085 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087214 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086453 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086454 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086456 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086457 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086858 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087156 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087235 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087252 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087425 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087590 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086451 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086451 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086901 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087233 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087854 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085414 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086327 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086999 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088623 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086745 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087182 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087187 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087188 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087190 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087576 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087990 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087407 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0089079 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088086 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088093 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088104 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088106 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088108 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088109 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088114 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088117 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088118 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088120 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087991 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087128 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0090215 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086975 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087550 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087552 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087989 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0089660 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0089686 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088087 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088088 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088090 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088110 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088102 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088091 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087038 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086910 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086917 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086485 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086488 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086067 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086676 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087099 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087238 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087748 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085392 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087563 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087565 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087566 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088473 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088474 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086913 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086873 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085400 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085400 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085400 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085400 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086274 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087421 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088306 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088309 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085432 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085432 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086915 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086911 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086786 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086666 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087223 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087200 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087396 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0089205 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087394 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087420 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087422 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087954 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087954 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087372 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087371 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086905 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087477 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087395 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085450 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088279 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088409 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088413 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087084 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087373 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087716 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087774 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088404 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088710 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0089365 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0089413 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088415 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0089353 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088408 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087763 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0089504 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087384 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087517 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087553 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087940 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088077 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088207 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086287 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087523 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087522 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087524 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087723 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0086895 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087508 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087512 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087513 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087518 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087520 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085803 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088700 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087381 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088428 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088433 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088434 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088299 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087473 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085341 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088707 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087531 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087533 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087527 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087528 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087529 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087557 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087532 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087556 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087559 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087560 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087530 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087555 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085371 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085894 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087423 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088097 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087126 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087760 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087762 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087766 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087163 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087806 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087978 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088111 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088115 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0088103 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085407 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087166 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0087757 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
17-0085434 | TUBBS (CENTRAL LNU COMPLEX) | TUBBS (CENTRAL LNU COMPLEX)
15-0061377 | VALLEY | VALLEY
15-0062436 | VALLEY | VALLEY
15-0062437 | VALLEY | VALLEY
15-0062442 | VALLEY | VALLEY
15-0062438 | VALLEY | VALLEY
15-0062435 | VALLEY | VALLEY
15-0061085 | VALLEY | VALLEY
15-0060607 | VALLEY | VALLEY
15-0061082 | VALLEY | VALLEY
15-0061084 | VALLEY | VALLEY
15-0061089 | VALLEY | VALLEY
15-0061092 | VALLEY | VALLEY
15-0061100 | VALLEY | VALLEY
15-0061102 | VALLEY | VALLEY
15-0061112 | VALLEY | VALLEY
15-0062316 | VALLEY | VALLEY
15-0062324 | VALLEY | VALLEY
15-0062431 | VALLEY | VALLEY
15-0062432 | VALLEY | VALLEY
15-0062433 | VALLEY | VALLEY
15-0062439 | VALLEY | VALLEY
15-0062212 | VALLEY | VALLEY
15-0062739 | VALLEY | VALLEY
15-0061595 | VALLEY | VALLEY
15-0062213 | VALLEY | VALLEY
15-0061066 | VALLEY | VALLEY
15-0061279 | VALLEY | VALLEY
15-0061338 | VALLEY | VALLEY
15-0061348 | VALLEY | VALLEY
15-0061445 | VALLEY | VALLEY
15-0061533 | VALLEY | VALLEY
15-0061568 | VALLEY | VALLEY
15-0062214 | VALLEY | VALLEY
15-0062395 | VALLEY | VALLEY
15-0062799 | VALLEY | VALLEY
15-0062994 | VALLEY | VALLEY
15-0062998 | VALLEY | VALLEY
15-0060626 | VALLEY | VALLEY
15-0061701 | VALLEY | VALLEY
15-0061175 | VALLEY | VALLEY
15-0061038 | VALLEY | VALLEY
15-0061064 | VALLEY | VALLEY
15-0061312 | VALLEY | VALLEY
15-0061342 | VALLEY | VALLEY
15-0061038 | VALLEY | VALLEY
15-0061038 | VALLEY | VALLEY
15-0061937 | VALLEY | VALLEY
15-0062003 | VALLEY | VALLEY
15-0062376 | VALLEY | VALLEY
15-0060882 | VALLEY | VALLEY
15-0061564 | VALLEY | VALLEY
15-0060275 | VALLEY | VALLEY
15-0060975 | VALLEY | VALLEY
15-0061436 | VALLEY | VALLEY
15-0061437 | VALLEY | VALLEY
15-0061432 | VALLEY | VALLEY
15-0061529 | VALLEY | VALLEY
15-0060275 | VALLEY | VALLEY
15-0060284 | VALLEY | VALLEY
15-0061562 | VALLEY | VALLEY
15-0061563 | VALLEY | VALLEY
15-0061771 | VALLEY | VALLEY
15-0060275 | VALLEY | VALLEY
15-0061590 | VALLEY | VALLEY
15-0061551 | VALLEY | VALLEY
15-0062204 | VALLEY | VALLEY
15-0061682 | VALLEY | VALLEY
15-0062312 | VALLEY | VALLEY
15-0062812 | VALLEY | VALLEY
15-0062313 | VALLEY | VALLEY
15-0061232 | VALLEY | VALLEY
15-0062818 | VALLEY | VALLEY
15-0061195 | VALLEY | VALLEY
15-0061347 | VALLEY | VALLEY
15-0061547 | VALLEY | VALLEY
15-0062314 | VALLEY | VALLEY
15-0062315 | VALLEY | VALLEY
15-0062317 | VALLEY | VALLEY
15-0062318 | VALLEY | VALLEY
15-0062319 | VALLEY | VALLEY
15-0062320 | VALLEY | VALLEY
15-0062321 | VALLEY | VALLEY
15-0062322 | VALLEY | VALLEY
15-0062323 | VALLEY | VALLEY
15-0062325 | VALLEY | VALLEY
15-0062326 | VALLEY | VALLEY
15-0062327 | VALLEY | VALLEY
15-0060626 | VALLEY | VALLEY
15-0062810 | VALLEY | VALLEY
15-0062817 | VALLEY | VALLEY
15-0062319 | VALLEY | VALLEY
15-0062312 | VALLEY | VALLEY
15-0062399 | VALLEY | VALLEY
15-0062400 | VALLEY | VALLEY
15-0062401 | VALLEY | VALLEY
15-0062402 | VALLEY | VALLEY
15-0062419 | VALLEY | VALLEY
15-0061043 | BUTTE | BUTTE
15-0061062 | BUTTE | BUTTE
15-0062113 | BUTTE | BUTTE
15-0062793 | BUTTE | BUTTE
15-0061117 | BUTTE | BUTTE
15-0061062 | BUTTE | BUTTE
15-0062274 | BUTTE | BUTTE
15-0061031 | BUTTE | BUTTE
15-0062273 | BUTTE | BUTTE
15-0063490 | BUTTE | BUTTE
15-0061025 | BUTTE | BUTTE
15-0061487 | BUTTE | BUTTE
15-0062706 | BUTTE | BUTTE
15-0062702 | BUTTE | BUTTE
15-0062704 | BUTTE | BUTTE
15-0062709 | BUTTE | BUTTE
15-0061059 | BUTTE | BUTTE
15-0062089 | BUTTE | BUTTE
15-0061061 | BUTTE | BUTTE
15-0062069 | BUTTE | BUTTE
15-0061902 | BUTTE | BUTTE
15-0062528 | BUTTE | BUTTE
15-0061014 | BUTTE | BUTTE
15-0061890 | BUTTE | BUTTE
15-0062139 | BUTTE | BUTTE
15-0063087 | BUTTE | BUTTE
15-0063496 | BUTTE | BUTTE
15-0063524 | BUTTE | BUTTE
15-0063556 | BUTTE | BUTTE
15-0063557 | BUTTE | BUTTE
15-0063597 | BUTTE | BUTTE
15-0063625 | BUTTE | BUTTE
15-0063663 | BUTTE | BUTTE
15-0065145 | BUTTE | BUTTE
15-0062008 | BUTTE | BUTTE
15-0061936 | BUTTE | BUTTE
15-0062007 | BUTTE | BUTTE
15-0062299 | BUTTE | BUTTE
15-0062119 | BUTTE | BUTTE
15-0061044 | BUTTE | BUTTE
15-0061985 | BUTTE | BUTTE
15-0061991 | BUTTE | BUTTE
15-0062038 | BUTTE | BUTTE
15-0061103 | BUTTE | BUTTE
15-0061104 | BUTTE | BUTTE
15-0061110 | BUTTE | BUTTE
15-0061981 | BUTTE | BUTTE
15-0061986 | BUTTE | BUTTE
15-0061988 | BUTTE | BUTTE
15-0061989 | BUTTE | BUTTE
15-0061990 | BUTTE | BUTTE
15-0062357 | BUTTE | BUTTE
15-0062360 | BUTTE | BUTTE
15-0062409 | BUTTE | BUTTE
15-0061963 | BUTTE | BUTTE
15-0061113 | BUTTE | BUTTE
15-0061034 | BUTTE | BUTTE
15-0062813 | BUTTE | BUTTE
15-0061992 | BUTTE | BUTTE
15-0061994 | BUTTE | BUTTE
15-0061995 | BUTTE | BUTTE
15-0061996 | BUTTE | BUTTE
15-0062001 | BUTTE | BUTTE
15-0062002 | BUTTE | BUTTE
15-0062010 | BUTTE | BUTTE
15-0062013 | BUTTE | BUTTE
15-0062014 | BUTTE | BUTTE
15-0062022 | BUTTE | BUTTE
15-0062023 | BUTTE | BUTTE
15-0062024 | BUTTE | BUTTE
15-0062027 | BUTTE | BUTTE
15-0062041 | BUTTE | BUTTE
15-0061045 | BUTTE | BUTTE
19-0026318 | Snow | Snow2019
19-004112 | Compost Fire | Miscellenious1511
19-0071251 | Structure Fire | Structure1512
19-0072923 | Toxic Crop Dusting | Miscellenious1513
19-0079932 | Canyon Fire | Canyon2019
19-0085888 | Preston Fire | Preston Fire
19-0085782 | Golf Fire | Golf Fire
19-0090149 | Vegetation Fire | Miscellenious1517
19-0108106 | Dinosaur Point Fire | Dinosaur Point
19-0130953 | Muddy conditions | Miscellenious1519