## RuralHFTD - Chart
Size | Count of Size - HFTD | Count of Size - UI
Less Than .25 Acres | 83
.26 - 9.99 Acres | 30
10 - 99 Acres | 7 | 4
100 - 299 Acres | 2 | 2
300 - 999 Acres | 1 | 3
1000 - 4999 Acres |  | 4
Greater than 5000 Acres | 2 | 6

## RuralHFTD
ID | Name | Circuit | Date | Year | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Size - HFTD | Size - UI | Suppressed by | Suppressing Agency | Facility Identification | FLOC | HFRA | cGIS HFRA | HFTD | Other Companies | Voltage (Volts) | Business Line | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor
1 |  | Birchim | 2015-02-06 | 2015 | 13:15 | 37.454 | -118.5842 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Various Fire Agencies | Between Poles 1854107E & 1854106E | OH-1854107E | Tier 2 | T2 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-02-06 | 13:15 | Unknown |  |  |  | Unknown
2 |  | Sexton | 2015-02-22 | 2015 | 9:52 | 34.2849 | -119.2173 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura Fire Department | Pole 1718768E | OH-1718768E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-02-22 | 10:49 | Unknown |  |  |  | None
3 |  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown
4 |  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown
5 |  | Maguire | 2015-04-17 | 2015 | 16:41 | 34.0851 | -118.8044 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles County Fire | Maguire 16kV out of Latigo Sub | OH-1199311E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2015-04-17 | 16:41 | Contact From Object |  | Vehicle | Pole | None
6 |  | Zone | 2015-04-27 | 2015 | 19:09 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | 9372 STOCKTON RD PMP MOORPARK | OH-4734128E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-04-27 | 19:09 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
7 |  | Zone | 2015-04-27 | 2015 | 19:10 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 4734128E | OH-4734128E | Tier 3 | T3 | Y |  | 16 | Distribution | Other | Overhead | Yes | 2015-04-27 | 19:10 | Equipment/Facility Failure | Other |  |  | Unknown
8 |  | Atlanta | 2015-05-05 | 2015 | 16:00 | 33.711 | -117.7089 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 4229158E | OH-4229158E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vehicle | Electric Facility | None
9 |  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None
10 |  | Soda Springs | 2015-05-14 | 2015 | 22:24 | 36.1318 | -118.7784 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | Soda Springs 12kV out of Boxwood Sub | OH-4464511E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-14 | 22:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown
11 |  | Lopez | 2015-05-23 | 2015 | 11:57 | 34.3006 | -118.3613 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | Pole 1261671E | OH-1261671E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Conductor | Overhead | Yes | 2015-05-23 | 11:05 | Unknown |  |  |  | Unknown
12 |  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown
13 |  | Pawley | 2015-05-29 | 2015 | 7:29 | 36.387 | -118.9536 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare County Fire | Lemon Cove and Three Rivers Sub. Venida 66kV | OH-4434944E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-05-29 | 7:29 | Contact From Object |  | Animal | Electric Facility | None
14 |  | Atento | 2015-05-30 | 2015 | 15:26 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | Unknown
15 |  | Atento | 2015-05-30 | 2015 | 15:30 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | None
16 |  | Python | 2015-06-06 | 2015 | 10:00 | 34.4043 | -118.4234 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | 16450 Alamo Canyon Rd, Canyon Country | OH-4779534E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-06-06 | 10:13 | Contact From Object |  | Animal | Electric Facility | None
17 |  | Keller | 2015-06-09 | 2015 | 5:46 | 33.5986 | -117.1311 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 4401960E | OH-2297077E | Tier 2 | T2 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2015-06-09 | 5:46 | Contact From Object |  | Animal | Electric Facility | None
18 |  | SPRINGVILLE-LINDSAY-VENIDA/ET-07230,SPRINGVILLE-STRATHMORE/ET-07256 | 2015-06-17 | 2015 | 17:29 | 36.1086 | -118.9425 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 722603E | OH-722604E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-06-17 | 17:29 | Contact From Object |  | Animal | Electric Facility | None
19 |  | Zone | 2015-06-23 | 2015 | 17:21 | 34.279 | -118.9072 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura Fire Department | Primary splice box at base of pole 2115918e | OH-2115918E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Subsurface | No | <Null> |  | Equipment/Facility Failure | Other |  |  | Unknown
20 |  | Taiwan | 2015-07-13 | 2015 | 11:15 | 33.7678 | -117.7207 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | Cal Fire | Pole 960439E | OH-960439E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-07-13 | 13:30 | Unknown |  |  |  | Unknown
21 |  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error
22 |  | BIG CREEK 3-RECTOR NO.1/ET-01046 | 2015-09-03 | 2015 | 17:00 | 36.8936 | -119.4571 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | East of Watts Valley Rd and Pittman Hill Rd, East of Clovis | OH-7020930 | Tier 2 | T2 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2015-09-03 | 16:15 | Contact From Object |  | Balloons | Electric Facility | None
23 |  | PALOMINO | 2015-10-09 | 2015 | 14:00 | 33.5752 | -117.17 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | BEHIND ADDRESS 28151 CELIA RD / PROPERTY LINE., STR 212903S | OH-212903S | Tier 2 | T2 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown
24 |  | GUITAR | 2016-01-16 | 2016 | 15:20 | 34.4096 | -118.6816 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-848266E | OH-848266E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-01-16 | 15:20 | Equipment/Facility Failure | Other |  |  | Unknown
25 |  | SHEFFIELD | 2016-02-22 | 2016 | 17:04 | 34.4492 | -119.5845 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Montecito Fire Department | OH-1082380E | OH-1082380E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-02-22 | 17:04 | Equipment/Facility Failure | Conductor |  |  | Unknown
26 |  | POPPET FLATS | 2016-02-27 | 2016 | 0:49 | 33.9134 | -116.8003 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1989045E | OH-1989045E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-02-27 | 0:49 | Contact From Object |  | Vehicle | Pole | Unknown
27 |  | SANTA CLARA-TAYSHELL/ET-00423 | 2016-04-21 | 2016 | 12:20 | 34.3339 | -119.2748 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4434916E | OH-4434916E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2016-04-21 | 12:20 | Contact From Object |  | Animal | Electric Facility | Unknown
28 |  | WELCH | 2016-04-25 | 2016 | 15:23 | 35.8387 | -118.9147 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1078325E | OH-1078325E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 15:23 | Equipment/Facility Failure | Insulator |  |  | Unknown
29 |  | ELSTER | 2016-04-25 | 2016 | 19:15 | 36.1372 | -118.8615 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-X16345E | OH-X16345E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 120/240 V | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 19:15 | Equipment/Facility Failure | Conductor |  |  | Unknown
30 |  | TICO | 2016-04-28 | 2016 | 14:00 | 34.357 | -119.314 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura County FD | OH-1604151E | OH-1604151E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-04-28 | 14:00 | Equipment/Facility Failure | Other |  |  | Unknown
31 |  | CONCEPCION | 2016-05-02 | 2016 | 7:03 | 34.4736 | -120.2153 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-4041841E | OH-4041841E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-02 | 7:03 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
32 |  | CONCEPCION | 2016-05-12 | 2016 | 8:55 | 34.4736 | -120.216 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-708452E | OH-708452E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-12 | 8:55 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
33 |  | SKINKLE | 2016-05-29 | 2016 | 22:25 | 36.0091 | -118.9563 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-4566417E | OH-4566417E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-05-29 | 22:25 | Contact From Object |  | Other | Electric Facility | Unknown
34 |  | BRUMFIELD | 2016-06-04 | 2016 | 10:17 | 33.5947 | -117.1387 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-2206630E | OH-2206630E | Tier 2 | T2 | Y |  | 12 | Distribution | Transformer | Overhead | Yes | 2016-06-04 | 10:17 | Equipment/Facility Failure | Transformer |  |  | Unknown
35 |  | PYTHON | 2016-06-05 | 2016 | 15:59 | 34.4208 | -118.4218 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4154960E | OH-4154960E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-06-05 | 15:59 | Unknown |  |  |  | Unknown
36 |  | VIENTO | 2016-06-06 | 2016 | 17:44 | 35.1355 | -118.4771 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1373165E | OH-1373165E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-06 | 17:44 | Contact From Object |  | Other | Pole | Unknown
37 |  | SHOWDOWN | 2016-06-09 | 2016 | 11:28 | 34.5862 | -118.196 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4267121E | OH-4267121E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-09 | 11:28 | Contact From Object |  | Balloons | Electric Facility | Unknown
38 |  | SODA SPRINGS | 2016-06-21 | 2016 | 21:47 | 36.2515 | -118.7809 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4391218E | OH-4391218E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-21 | 21:47 | Contact From Object |  | Vegetation | Electric Facility | Unknown
39 |  | KINSEY | 2016-07-08 | 2016 | 11:15 | 34.7906 | -118.8256 | Vegetation | Rural | 300 - 999 Acres | 300 - 999 Acres |  | Fire Agency | Kern County Fire Department | 1-5, Gorman | OH-4539401E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown
40 |  | CACHUMA | 2016-08-18 | 2016 | 14:52 | 34.5356 | -119.8523 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-1413051E | OH-1413051E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-18 | 14:52 | Contact From Object |  | Vegetation | Communication Facility | Unknown
41 |  | VALLECITO | 2016-08-18 | 2016 | 19:00 | 34.4214 | -119.5964 | Other | Rural | Structure Only | Structure Only |  | Fire Agency | Santa Barbara County Fire Department | 2400 block of Whitney Avenue in Summerland | OH-1523986E | Tier 2 | T2 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown
42 |  | MIST | 2016-08-24 | 2016 | 16:37 | 34.4665 | -120.0701 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Santa Barbara County Fire Department | Refiugio Canyon, Santa Barbara | OH-4538468E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-24 | 18:50 | Contact From Object |  | Animal | Electric Facility | Unknown
43 |  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown
44 |  | PATRICIA | 2016-09-16 | 2016 | 19:02 | 34.4851 | -119.3001 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ojai City Fire Department | OH-4797071E | OH-4797071E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-09-16 | 19:02 | Contact From Object |  | Vehicle | Pole | Unknown
45 |  | TUNA | 2016-09-19 | 2016 | 6:11 | 34.04 | -118.6687 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-1638513E | OH-1638513E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown
46 |  | CARVER | 2016-09-24 | 2016 | 14:20 | 35.7381 | -118.9546 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4784763E | OH-4784763E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-09-24 | 14:20 | Contact From Object |  | Animal | Electric Facility | Unknown
47 |  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown
48 |  | DRISKILL | 2016-10-18 | 2016 | 18:41 | 34.4687 | -119.7722 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Santa Barbara Fire Department | OH-2178476E | OH-2178476E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-18 | 18:41 | Equipment/Facility Failure | Fuse |  |  | Unknown
49 |  | PYTHON | 2016-10-22 | 2016 | 15:17 | 34.3812 | -118.4132 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | RAR 0038 | OH-4860064E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-22 | 15:17 | Contact From Object |  | Balloons | Electric Facility | Unknown
50 |  | PATRICIA | 2016-10-23 | 2016 | 9:40 | 34.4603 | -119.2853 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | 900 Rice Road Ojai | OH-786960E | Tier 3 | T3 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown
51 |  | HUGHES LAKE | 2016-10-26 | 2016 | 12:19 | 34.7081 | -118.5367 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | ELIZABETH LAKE ROAD AND KINGS CANYON ROAD, LAKE HUGHES | OH-1586523E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-26 | 12:19 | Contact From Object |  | Vegetation | Electric Facility | Unknown
52 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown
53 |  | PYTHON | 2016-12-02 | 2016 | 21:26 | 34.3812 | -118.4132 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | OH-4572770E | OH-4572770E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vegetation | Electric Facility | Unknown
54 |  | RHODA | 2016-12-30 | 2016 | 11:42 | 34.1231 | -118.723 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-1927507E | OH-1927507E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-12-30 | 11:42 | Contact From Object |  | Balloons | Electric Facility | Unknown
55 |  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown
56 |  | OAK GLEN | 2017-03-15 | 2017 | 13:23 | 34.0534 | -116.971 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-2326555E | OH-2326555E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-15 | 13:23 | Contact From Object |  | Animal | Electric Facility | Unknown
57 |  | HUCKLEBERRY | 2017-03-17 | 2017 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4493863E | OH-4493863E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown
58 |  | PATRICIA | 2017-04-16 | 2017 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4495331E | OH-4495331E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown
59 |  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown
60 |  | LEE VINING-LUNDY NO. 1/ET-01774 | 2017-05-01 | 2017 | 5:40 | 38.0209 | -119.1608 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | CAlFIre | OH-1580964E | OH-1580964E | Tier 2 | T2 | Y |  | 55 | Distribution | Conductor | Overhead | No | <Null> |  | Contamination |  |  |  | Unknown
61 |  | GUITAR | 2017-05-11 | 2017 | 12:27 | 34.4127 | -118.6702 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-848255E | OH-848255E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-05-11 | 12:27 | Contact From Object |  | Balloons | Electric Facility | Unknown
62 |  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown
63 |  | METTLER | 2017-06-02 | 2017 | 10:50 | 35.1021 | -118.5328 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4416566E | OH-4416566E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown
64 |  | ANZAR | 2017-06-04 | 2017 | 13:14 | 33.8373 | -117.4863 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-1757417E | OH-1757417E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2017-06-04 | 13:14 | Wire-Wire Contact |  |  |  | Unknown
65 |  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown
66 |  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown
67 |  | PICK | 2017-06-19 | 2017 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | 30278 Arrastre Canyon Rd., Acton | OH-699610E | Tier 3 | T3 | Y |  | 33 | Distribution | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown
68 |  | MAYBELL | 2017-07-02 | 2017 | 8:24 | 34.0804 | -117.8552 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | OH-144184E | OH-1255315E | T2 200Ft Outer Buffer | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-07-02 | 8:24 | Contact From Object |  | Animal | Electric Facility | Unknown
69 |  | DALBA | 2017-07-11 | 2017 | 18:06 | 34.2054 | -117.1143 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-919465E | OH-919465E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 2.4 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown
70 |  | CUDDEBACK | 2017-08-08 | 2017 | 17:52 | 35.1342 | -118.5607 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4179753E | OH-4179753E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-08-08 | 17:52 | Contact From Object |  | Vehicle | Electric Facility | Unknown
71 |  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown
72 |  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown
73 |  | CABANA | 2017-10-16 | 2017 | 6:11 | 34.0217 | -117.5069 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1670014E | OH-1670014E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-10-16 | 6:11 | Contact From Object |  | Balloons | Electric Facility | Unknown
74 |  | DEACON | 2017-10-18 | 2017 | 13:34 | 33.7702 | -117.2157 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1564666E | OH-1564666E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown
75 |  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown
76 |  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
77 |  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown
78 |  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown
79 |  | BENCH | 2018-06-26 | 2018 | 20:48 | 34.0158 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Holmes St/Wildwood Canyon Rd, Yucaipa | OH-4367391E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-26 | 20:48 | Contact From Object |  | Vehicle | Pole | Unknown
80 |  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown
81 |  | HUGHES LAKE/ED-08810 | 2018-07-06 | 2018 | 5:38 | 34.6744 | -118.4517 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | 465140E | OH-1938477E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-07-06 | 5:38 | Contact From Object |  | Vehicle | Pole | Unknown
82 |  | BIG CREEK 1-RECTOR/ET-01082 | 2018-08-04 | 2018 | 0:43 | 37.1895 | -119.2738 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | OH-7021454 | OH-7021454 | Tier 3 | T3 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2018-08-04 | 2:21 | Equipment/Facility Failure | Other |  |  | Unknown
83 |  | JORDAN | 2018-08-29 | 2018 | 17:32 | 35.7358 | -118.7192 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | Jack Ranch Rd/White River Rd, Kernville | OH-4635091E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-08-29 | 19:06 | Contact From Object |  | Vegetation | Electric Facility | Unknown
84 |  | POULTRY | 2018-09-21 | 2018 | 8:28 | 34.0728 | -117.0397 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Juniper St. Yucaipa | OH-129241E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown
85 |  | OAK GLEN | 2018-11-08 | 2018 | 12:09 | 34.0397 | -116.9362 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 11833 Oak Glen Rd. Yucaipa | OH-4611601E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-08 | 12:09 | Equipment/Facility Failure | Transformer |  |  | Unknown
86 |  | ARCHIE | 2018-11-13 | 2018 | 7:11 | 33.4928 | -117.2796 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | NORTH OF CARANCHO ON VIA CIELO | OH-4149859E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-13 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Unknown
87 |  | Peninsula | 2019-03-16 | 2019 | 17:58 | 33.6182 | -117.8025 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1729510E | OH-1729510E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-03-16 | 17:58 | Equipment/Facility Failure | Crossarm |  |  | Unknown
88 |  | Taggert | 2019-04-23 | 2019 | 21:06 | 34.2147 | -117.0973 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1027559E | OH-1027559E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution |  | Overhead | No |  |  | Unknown |  |  |  | Unknown
89 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error
90 |  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error
91 |  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force
92 |  | Northpark | 2019-06-20 | 2019 | 14:08 | 34.2298 | -117.4048 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | San Bern. FD | OH-201371S | OH-201371S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Human Error
93 |  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force
94 |  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather
95 |  | Saugus-Santa Susana | 2019-08-06 | 2019 | 15:03 | 34.3918 | -118.6596 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | VFD & LACFD | M6-T1 | M6-T1 | Tier 3 | T3 | Y | NA | 66 | Transmission | Other | Overhead | Yes | 2019-08-06 | 12:51 | Contact From Object |  | Animal | Electric Facility | Other
96 |  | Zone | 2019-08-10 | 2019 | 13:00 | 34.3089 | -118.9413 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | VFD | OH-4734128E | OH-4734128E | Tier 3 | T3 | Y | AT&T Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
97 |  | Enchanted | 2019-08-25 | 2019 | 8:03 | 34.301 | -118.8308 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4754475E | OH-4754475E | Tier 3 | T3 | Y | NA | 16 | Distribution | Lightning Arrestor | Overhead | Yes | 2019-08-25 | 8:03 | Contact From Object |  | Animal | Electric Facility | Other
98 |  | Hughes Lake | 2019-09-02 | 2019 | 14:02 | 34.7026 | -118.342 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4782978E | OH-4782978E | Tier 2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-02 | 14:02 | Contact From Object |  | Balloons | Electric Facility | Other
99 |  | Plateau | 2019-09-11 | 2019 | 8:08 | 34.0991 | -118.6793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4424792E | OH-4424792E | Tier 3 | T3 | Y | Verizon / AT&T / Crown Castle | 16 | Distribution | Conductor | Overhead | Yes | 2019-09-11 | 8:08 | Equipment/Facility Failure | Conductor |  | Electric Facility | Human Error
100 |  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown
101 |  | Penstock | 2019-09-18 | 2019 | 2:52 | 34.3143 | -117.3793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4066969E | OH-4066969E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Human Error
102 |  | Wildomar | 2019-09-19 | 2019 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside County FD | OH-2225310E | OH-2225310E | Tier 3 | T3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other
103 |  | Elster | 2019-09-21 | 2019 | 10:53 | 36.1026 | -118.8659 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4252581E | OH-4252581E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-21 | 10:53 | Contact From Object |  | Vehicle | Electric Facility | Human Error
104 |  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown
105 |  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other
106 |  | Medusa | 2020-03-06 | 2020 | 17:05 | 34.0802 | -117.254 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1811355E | OH-1811355E | T2 | T2 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Other
107 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
108 |  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other
109 |  | VALLEY-MAYBERRY-MORENO-VISTA | 2020-05-18 | 2020 | 12:10 | 33.8587 | -117.0203 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire Perris | OH-1979539E | OH-1979539E | T3 | T3 | Y | None | 115 | Transmission | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Other
110 |  | Bonanza | 2020-06-05 | 2020 | 17:33 | 35.7635 | -118.4218 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Kern County Fire Department | OH-4451126E | OH-4451126E | T3 | T3 | Y | None | 12 | Distribution | Other | Overhead | Yes | 2020-06-05 | 17:33 | Contact From Object |  | Animal | Electric Facility | Other
111 |  | Conestoga | 2020-06-13 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Other
112 |  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other
113 |  | La Mancha | 2020-07-05 | 2020 | 3:57 | 34.1325 | -118.8532 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1848406E | OH-1848406E | T3 | T3 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-07-05 | 3:57 | Equipment/Facility Failure | Insulator |  |  | Unknown
114 |  | Capanero | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | T2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Unknown
115 |  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force
116 |  | Mettler | 2020-08-10 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | OH-2093506E | OH-2093506E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Unknown
117 |  | Flying D | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County | OH-1761180E | OH-1761180E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown
118 |  | Calgrove | 2020-10-03 | 2020 | 17:45 | 34.357 | -118.5659 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | OH-2101062E | OH-2101062E | T3 | T3 |  | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other
119 |  | Kickapoo Trail | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1941931E | OH-1941931E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Unknown
120 |  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other
121 |  | Vicasa | 2020-11-30 | 2020 | 21:02 | 34.0723 | -118.588 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles Fire Department | OH-4535641E | OH-4535641E | T3 | T3 |  | Verizon Wireless, AT&T Mobility, Frontier Communications, Crown Castle NG West, Inc | 16 | Distribution | Other | Overhead | Yes | 2020-11-30 | 21:02 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
122 |  | Viento | 2020-06-09 | 2020 | 16:42 | 35.1384 | -118.4809 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4707894E | OH-4707894E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
123 |  | Lasker | 2020-07-26 | 2020 | 12:50 | 34.5326 | -118.0541 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4619162E | OH-4619162E | T3 | T3 |  | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other
124 |  | Morongo | 2020-08-03 | 2020 | 10:33 | 34.0758 | -116.5548 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-2107480E | OH-2107480E | T2 | T2 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-08-03 | 19:15 | Contact From Object |  | Balloons | Electric Facility | Outside Force
125 |  | Bidder | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire | OH-2023941E | OH-2023941E | T3 | T3 |  | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force
126 |  | Vicasa | 2020-10-26 | 2020 | 11:56 | 34.0998 | -118.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | OH-795990E | OH-795990E | T3 | T3 |  | Frontier Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Weather
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather
10002 | CABIN |  | 2015-08-14 | 2015 | 13:07 | 34.0299 | -118.0726 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather
10003 | EDISON |  | 2016-05-12 | 2016 | -8 | 34.3135 | -119.1865 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather
10004 | ERSKINE |  | 2016-06-23 | 2016 | 16:00 | 34.2676 | -117.844 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | BLM | [13 empty] | Contact From Object |  | Vegetation
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather
10006 | RYE |  | 2017-12-05 | 2017 | 15:00 | 34.2676 | -117.844 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather
10007 | ELLIS |  | 2017-10-18 | 2017 | 11:18 | 33.7721 | -117.2173 | Vegetation | Rural | Unknown |  | Unknown | Fire Agency | Cal Fire | [17 empty] | Weather
10008 | THOMAS |  | 2017-12-04 | 2017 | 18:28 | 34.4152 | -119.0912 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | USFS | [17 empty] | Weather
10009 | RYE |  | 2017-12-05 | 2017 | 11:31 | 34.4528 | -118.5819 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather
10010 | MEYERS |  | 2017-12-05 | 2017 | 14:00 | 34.2183 | -117.4062 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Cal Fire | [17 empty] | Weather
10011 | LIBERTY |  | 2017-12-07 | 2017 | 13:00 | 33.5926 | -117.1498 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | Murrieta Fire Department | [17 empty] | Weather
10012 | HOLIDAY |  | 2018-07-06 | 2018 | 20:40 | 34.4639 | -119.8314 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Santa Barbara Fire Department | [17 empty] | Weather
10013 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather
10014 | STAR |  | 2019-07-28 | 2019 | 14:00 | 33.9975 | -117.7698 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Chino Valley Fire Department | [13 empty] | Contact From Object |  | Bird |  | Weather
10015 | TENAJA |  | 2019-09-04 | 2019 | 16:43 | 33.5285 | -117.2732 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Cal Fire | [17 empty] | Weather
10016 | SADDLE RIDGE |  | 2019-10-10 | 2019 | 21:09 | 34.3299 | -118.4816 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather
10017 | OAK |  | 2019-10-28 | 2019 | 8:42 | 34.1489 | -118.6954 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather
10018 | EASY |  | 2019-10-30 | 2019 | 6:00 | 34.2822 | -118.8034 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather
10019 | MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather
10020 | MARIA |  | 2019-10-31 | 2019 | 20:58 | 34.3022 | -118.9971 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather
Note on D1: Date the event started (Use MM/DD/YY when inputting dates)
Note on F1: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on G1: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on H1: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on I1: Material involved in the initial fueling of the fire;
Note on J1: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on K1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on L1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on M1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on N1: Is who suppressed the fire
Note on O1: If the fire was suppressed by a fire agency or agencies, insert the lead agency when one or more agency was involved
Note on P1: Utility’s description of the pole and/or equipment involved.
Note on U1: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on V1: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on X1: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on Y1: The equipment involved in the event (overhead, padmounted or subsurface);
Note on Z1: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AA1: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AB1: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AC1: The suspected cause of the ignition;
Note on AD1: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on AE1: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on AF1: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on AG1: Factors that contributed to the ignition;

## UnderInvestigation
ID | Name | Circuit | Date | Year | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Size - HFTD | Size - UI | Suppressed by | Suppressing Agency | Facility Identification | FLOC | HFRA | cGIS HFRA | HFTD | Other Companies | Voltage (Volts) | Business Line | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather
10002 | CABIN |  | 2015-08-14 | 2015 | 13:07 | 34.0299 | -118.0726 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather
10003 | EDISON |  | 2016-05-12 | 2016 | -8 | 34.3135 | -119.1865 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather
10004 | ERSKINE |  | 2016-06-23 | 2016 | 16:00 | 34.2676 | -117.844 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | BLM | [13 empty] | Contact From Object |  | Vegetation
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather
10006 | RYE |  | 2017-12-05 | 2017 | 15:00 | 34.2676 | -117.844 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather
10007 | ELLIS |  | 2017-10-18 | 2017 | 11:18 | 33.7721 | -117.2173 | Vegetation | Rural | Unknown |  | Unknown | Fire Agency | Cal Fire | [17 empty] | Weather
10008 | THOMAS |  | 2017-12-04 | 2017 | 18:28 | 34.4152 | -119.0912 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | USFS | [17 empty] | Weather
10009 | RYE |  | 2017-12-05 | 2017 | 11:31 | 34.4528 | -118.5819 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather
10010 | MEYERS |  | 2017-12-05 | 2017 | 14:00 | 34.2183 | -117.4062 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Cal Fire | [17 empty] | Weather
10011 | LIBERTY |  | 2017-12-07 | 2017 | 13:00 | 33.5926 | -117.1498 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | Murrieta Fire Department | [17 empty] | Weather
10012 | HOLIDAY |  | 2018-07-06 | 2018 | 20:40 | 34.4639 | -119.8314 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Santa Barbara Fire Department | [17 empty] | Weather
10013 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather
10014 | STAR |  | 2019-07-28 | 2019 | 14:00 | 33.9975 | -117.7698 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Chino Valley Fire Department | [13 empty] | Contact From Object |  | Bird |  | Weather
10015 | TENAJA |  | 2019-09-04 | 2019 | 16:43 | 33.5285 | -117.2732 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Cal Fire | [17 empty] | Weather
10016 | SADDLE RIDGE |  | 2019-10-10 | 2019 | 21:09 | 34.3299 | -118.4816 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather
10017 | OAK |  | 2019-10-28 | 2019 | 8:42 | 34.1489 | -118.6954 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather
10018 | EASY |  | 2019-10-30 | 2019 | 6:00 | 34.2822 | -118.8034 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather
10019 | MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather
10020 | MARIA |  | 2019-10-31 | 2019 | 20:58 | 34.3022 | -118.9971 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather
Note on D1: Date the event started (Use MM/DD/YY when inputting dates)
Note on F1: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on G1: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on H1: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on I1: Material involved in the initial fueling of the fire;
Note on J1: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on K1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on L1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on M1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on N1: Is who suppressed the fire
Note on O1: If the fire was suppressed by a fire agency or agencies, insert the lead agency when one or more agency was involved
Note on P1: Utility’s description of the pole and/or equipment involved.
Note on U1: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on V1: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on X1: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on Y1: The equipment involved in the event (overhead, padmounted or subsurface);
Note on Z1: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AA1: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AB1: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AC1: The suspected cause of the ignition;
Note on AD1: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on AE1: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on AF1: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on AG1: Factors that contributed to the ignition;

## IgnitionsWind
ID | Name | Circuit | Date | Year | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Size - HFTD | Size - UI | Suppressed by | Suppressing Agency | Facility Identification | FLOC | HFRA | cGIS HFRA | HFTD | Other Companies | Voltage (Volts) | Business Line | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | 8m/1h stid | 8m/1h dist | 8m/1h time | 8m/1h gust mph | 8m/1h count | 8m/1h Category | Cause
1 |  | Birchim | 2015-02-06 | 2015 | 13:15 | 37.454 | -118.5842 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Various Fire Agencies | Between Poles 1854107E & 1854106E | OH-1854107E | Tier 2 | T2 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-02-06 | 13:15 | Unknown |  |  |  | Unknown | OVRC1 | 4.68 | 2015-02-06T20:54:00Z | 34 | 1 | 25-40mph | Unknown
2 |  | Sexton | 2015-02-22 | 2015 | 9:52 | 34.2849 | -119.2173 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura Fire Department | Pole 1718768E | OH-1718768E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-02-22 | 10:49 | Unknown |  |  |  | None | AT185 | 8 | 2015-02-22T18:06:00Z | 13 | 19 | < 25mph | Unknown
3 |  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | TNRC1 | 5.88 | 2015-03-26T20:57:00Z | 24 | 64 | < 25mph | Equipment
4 |  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown | CNSC1 | 7.75 | 2015-04-17T15:16:00Z | 10 | 22 | < 25mph | Unknown
5 |  | Maguire | 2015-04-17 | 2015 | 16:41 | 34.0851 | -118.8044 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles County Fire | Maguire 16kV out of Latigo Sub | OH-1199311E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2015-04-17 | 16:41 | Contact From Object |  | Vehicle | Pole | None | MBCC1 | 5.78 | 2015-04-17T23:56:00Z | 23 | 25 | < 25mph | Agent
6 |  | Zone | 2015-04-27 | 2015 | 19:09 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | 9372 STOCKTON RD PMP MOORPARK | OH-4734128E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-04-27 | 19:09 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | WLYC1 | 7.19 | 2015-04-28T01:49:00Z | 18.99 | 52 | < 25mph | Equipment
7 |  | Zone | 2015-04-27 | 2015 | 19:10 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 4734128E | OH-4734128E | Tier 3 | T3 | Y |  | 16 | Distribution | Other | Overhead | Yes | 2015-04-27 | 19:10 | Equipment/Facility Failure | Other |  |  | Unknown | WLYC1 | 7.19 | 2015-04-28T01:49:00Z | 18.99 | 53 | < 25mph | Equipment
8 |  | Atlanta | 2015-05-05 | 2015 | 16:00 | 33.711 | -117.7089 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 4229158E | OH-4229158E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.92 | 2015-05-05T22:51:00Z | 20 | 67 | < 25mph | Agent
9 |  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.54 | 2015-05-06T20:51:00Z | 20 | 57 | < 25mph | Agent
10 |  | Soda Springs | 2015-05-14 | 2015 | 22:24 | 36.1318 | -118.7784 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | Soda Springs 12kV out of Boxwood Sub | OH-4464511E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-14 | 22:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown | OORC1 | 5.23 | 2015-05-15T05:12:00Z | 4 | 1 | < 25mph | Vegetation
11 |  | Lopez | 2015-05-23 | 2015 | 11:57 | 34.3006 | -118.3613 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | Pole 1261671E | OH-1261671E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Conductor | Overhead | Yes | 2015-05-23 | 11:05 | Unknown |  |  |  | Unknown | CNIC1 | 4.89 | 2015-05-23T18:55:00Z | 42.99 | 21 | 40-55mph | Unknown
12 |  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | LCBC1 | 6.83 | 2015-05-26T21:55:00Z | 17 | 25 | < 25mph | Unknown
13 |  | Pawley | 2015-05-29 | 2015 | 7:29 | 36.387 | -118.9536 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare County Fire | Lemon Cove and Three Rivers Sub. Venida 66kV | OH-4434944E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-05-29 | 7:29 | Contact From Object |  | Animal | Electric Facility | None | D0117 | 5.17 | 2015-05-29T14:00:00Z | 2.01 | 7 | < 25mph | Agent
14 |  | Atento | 2015-05-30 | 2015 | 15:26 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | Unknown | FRCC1 | 7.87 | 2015-05-30T22:51:00Z | 18.01 | 37 | < 25mph | Agent
15 |  | Atento | 2015-05-30 | 2015 | 15:30 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | None | FRCC1 | 7.87 | 2015-05-30T22:51:00Z | 18.01 | 39 | < 25mph | Agent
16 |  | Python | 2015-06-06 | 2015 | 10:00 | 34.4043 | -118.4234 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | 16450 Alamo Canyon Rd, Canyon Country | OH-4779534E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-06-06 | 10:13 | Contact From Object |  | Animal | Electric Facility | None | CNIC1 | 3.54 | 2015-06-06T16:55:00Z | 12.01 | 24 | < 25mph | Agent
17 |  | Keller | 2015-06-09 | 2015 | 5:46 | 33.5986 | -117.1311 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 4401960E | OH-2297077E | Tier 2 | T2 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2015-06-09 | 5:46 | Contact From Object |  | Animal | Electric Facility | None | SDFRV | 2.48 | 2015-06-09T12:49:00Z | 10 | 17 | < 25mph | Agent
18 |  | SPRINGVILLE-LINDSAY-VENIDA/ET-07230,SPRINGVILLE-STRATHMORE/ET-07256 | 2015-06-17 | 2015 | 17:29 | 36.1086 | -118.9425 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 722603E | OH-722604E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-06-17 | 17:29 | Contact From Object |  | Animal | Electric Facility | None | C1000 | 6.57 | 2015-06-18T00:25:00Z | 5.99 | 12 | < 25mph | Agent
19 |  | Zone | 2015-06-23 | 2015 | 17:21 | 34.279 | -118.9072 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura Fire Department | Primary splice box at base of pole 2115918e | OH-2115918E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Subsurface | No | <Null> |  | Equipment/Facility Failure | Other |  |  | Unknown | WLYC1 | 7.44 | 2015-06-24T00:49:00Z | 21 | 47 | < 25mph | Equipment
20 |  | Taiwan | 2015-07-13 | 2015 | 11:15 | 33.7678 | -117.7207 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | Cal Fire | Pole 960439E | OH-960439E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-07-13 | 13:30 | Unknown |  |  |  | Unknown | FRCC1 | 3.07 | 2015-07-13T17:51:00Z | 17 | 42 | < 25mph | Unknown
21 |  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error | KTSP | 6.45 | 2015-08-12T18:35:00Z | 21.85 | 20 | < 25mph | Agent
22 |  | BIG CREEK 3-RECTOR NO.1/ET-01046 | 2015-09-03 | 2015 | 17:00 | 36.8936 | -119.4571 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | East of Watts Valley Rd and Pittman Hill Rd, East of Clovis | OH-7020930 | Tier 2 | T2 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2015-09-03 | 16:15 | Contact From Object |  | Balloons | Electric Facility | None | FCHC1 | 1.24 | 2015-09-04T00:00:00Z | 14.99 | 1 | < 25mph | Agent
23 |  | PALOMINO | 2015-10-09 | 2015 | 14:00 | 33.5752 | -117.17 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | BEHIND ADDRESS 28151 CELIA RD / PROPERTY LINE., STR 212903S | OH-212903S | Tier 2 | T2 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | KF70 | 2.39 | 2015-10-09T20:55:00Z | 18.41 | 30 | < 25mph | Equipment
24 |  | GUITAR | 2016-01-16 | 2016 | 15:20 | 34.4096 | -118.6816 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-848266E | OH-848266E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-01-16 | 15:20 | Equipment/Facility Failure | Other |  |  | Unknown | DLVC1 | 1.62 | 2016-01-16T22:55:00Z | 15.99 | 8 | < 25mph | Equipment
25 |  | SHEFFIELD | 2016-02-22 | 2016 | 17:04 | 34.4492 | -119.5845 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Montecito Fire Department | OH-1082380E | OH-1082380E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-02-22 | 17:04 | Equipment/Facility Failure | Conductor |  |  | Unknown | MTIC1 | 3.77 | 2016-02-23T00:47:00Z | 28.01 | 15 | 25-40mph | Equipment
26 |  | POPPET FLATS | 2016-02-27 | 2016 | 0:49 | 33.9134 | -116.8003 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1989045E | OH-1989045E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-02-27 | 0:49 | Contact From Object |  | Vehicle | Pole | Unknown | BAZC1 | 1.3 | 2016-02-27T09:14:00Z | 14 | 7 | < 25mph | Agent
27 |  | SANTA CLARA-TAYSHELL/ET-00423 | 2016-04-21 | 2016 | 12:20 | 34.3339 | -119.2748 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4434916E | OH-4434916E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2016-04-21 | 12:20 | Contact From Object |  | Animal | Electric Facility | Unknown | E8097 | 5.68 | 2016-04-21T19:40:00Z | 15.99 | 31 | < 25mph | Agent
28 |  | WELCH | 2016-04-25 | 2016 | 15:23 | 35.8387 | -118.9147 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1078325E | OH-1078325E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 15:23 | Equipment/Facility Failure | Insulator |  |  | Unknown | FTNC1 | 3.62 | 2016-04-25T22:00:00Z | 20 | 1 | < 25mph | Equipment
29 |  | ELSTER | 2016-04-25 | 2016 | 19:15 | 36.1372 | -118.8615 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-X16345E | OH-X16345E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 120/240 V | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 19:15 | Equipment/Facility Failure | Conductor |  |  | Unknown | MOLC1 | 6.51 | 2016-04-26T02:27:00Z | 13 | 1 | < 25mph | Equipment
30 |  | TICO | 2016-04-28 | 2016 | 14:00 | 34.357 | -119.314 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura County FD | OH-1604151E | OH-1604151E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-04-28 | 14:00 | Equipment/Facility Failure | Other |  |  | Unknown | LCTC1 | 6.05 | 2016-04-28T20:45:00Z | 35.99 | 18 | 25-40mph | Equipment
31 |  | CONCEPCION | 2016-05-02 | 2016 | 7:03 | 34.4736 | -120.2153 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-4041841E | OH-4041841E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-02 | 7:03 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UP481 | 0.66 | 2016-05-02T13:55:00Z | 7.02 | 15 | < 25mph | Equipment
32 |  | CONCEPCION | 2016-05-12 | 2016 | 8:55 | 34.4736 | -120.216 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-708452E | OH-708452E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-12 | 8:55 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | C6499 | 0.67 | 2016-05-12T16:13:00Z | 4 | 12 | < 25mph | Equipment
33 |  | SKINKLE | 2016-05-29 | 2016 | 22:25 | 36.0091 | -118.9563 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-4566417E | OH-4566417E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-05-29 | 22:25 | Contact From Object |  | Other | Electric Facility | Unknown | C1000 | 7.9 | 2016-05-30T05:50:00Z | 0 | 10 | < 25mph | Equipment
34 |  | BRUMFIELD | 2016-06-04 | 2016 | 10:17 | 33.5947 | -117.1387 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-2206630E | OH-2206630E | Tier 2 | T2 | Y |  | 12 | Distribution | Transformer | Overhead | Yes | 2016-06-04 | 10:17 | Equipment/Facility Failure | Transformer |  |  | Unknown | SDFRV | 2.92 | 2016-06-04T16:49:00Z | 11.01 | 17 | < 25mph | Equipment
35 |  | PYTHON | 2016-06-05 | 2016 | 15:59 | 34.4208 | -118.4218 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4154960E | OH-4154960E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-06-05 | 15:59 | Unknown |  |  |  | Unknown | SAUC1 | 5.3 | 2016-06-05T22:57:00Z | 25.99 | 34 | 25-40mph | Unknown
36 |  | VIENTO | 2016-06-06 | 2016 | 17:44 | 35.1355 | -118.4771 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1373165E | OH-1373165E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-06 | 17:44 | Contact From Object |  | Other | Pole | Unknown | KTSP | 2.14 | 2016-06-07T00:35:00Z | 28.77 | 30 | 25-40mph | Equipment
37 |  | SHOWDOWN | 2016-06-09 | 2016 | 11:28 | 34.5862 | -118.196 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4267121E | OH-4267121E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-09 | 11:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | LPDC1 | 6.32 | 2016-06-09T18:55:00Z | 28.99 | 12 | 25-40mph | Agent
38 |  | SODA SPRINGS | 2016-06-21 | 2016 | 21:47 | 36.2515 | -118.7809 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4391218E | OH-4391218E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-21 | 21:47 | Contact From Object |  | Vegetation | Electric Facility | Unknown | OORC1 | 6.87 | 2016-06-22T05:12:00Z | 13 | 2 | < 25mph | Vegetation
39 |  | KINSEY | 2016-07-08 | 2016 | 11:15 | 34.7906 | -118.8256 | Vegetation | Rural | 300 - 999 Acres | 300 - 999 Acres |  | Fire Agency | Kern County Fire Department | 1-5, Gorman | OH-4539401E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | E5906 | 7.95 | 2016-07-08T18:30:00Z | 5.99 | 3 | < 25mph | Unknown
40 |  | CACHUMA | 2016-08-18 | 2016 | 14:52 | 34.5356 | -119.8523 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-1413051E | OH-1413051E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-18 | 14:52 | Contact From Object |  | Vegetation | Communication Facility | Unknown | AS303 | 7.85 | 2016-08-18T22:00:00Z | 32.99 | 85 | 25-40mph | Vegetation
41 |  | VALLECITO | 2016-08-18 | 2016 | 19:00 | 34.4214 | -119.5964 | Other | Rural | Structure Only | Structure Only |  | Fire Agency | Santa Barbara County Fire Department | 2400 block of Whitney Avenue in Summerland | OH-1523986E | Tier 2 | T2 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | AS714 | 6.86 | 2016-08-19T01:32:00Z | 18.99 | 30 | < 25mph | Equipment
42 |  | MIST | 2016-08-24 | 2016 | 16:37 | 34.4665 | -120.0701 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Santa Barbara County Fire Department | Refiugio Canyon, Santa Barbara | OH-4538468E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-24 | 18:50 | Contact From Object |  | Animal | Electric Facility | Unknown | RHWC1 | 3.48 | 2016-08-25T00:06:00Z | 35.99 | 13 | 25-40mph | Agent
43 |  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | ROVC1 | 7.44 | 2016-09-03T17:24:00Z | 14.99 | 12 | < 25mph | Agent
44 |  | PATRICIA | 2016-09-16 | 2016 | 19:02 | 34.4851 | -119.3001 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ojai City Fire Department | OH-4797071E | OH-4797071E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-09-16 | 19:02 | Contact From Object |  | Vehicle | Pole | Unknown | ROVC1 | 7.69 | 2016-09-17T02:24:00Z | 8.01 | 6 | < 25mph | Agent
45 |  | TUNA | 2016-09-19 | 2016 | 6:11 | 34.04 | -118.6687 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-1638513E | OH-1638513E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | MBUC1 | 2.01 | 2016-09-19T12:56:00Z | 14.99 | 25 | < 25mph | Unknown
46 |  | CARVER | 2016-09-24 | 2016 | 14:20 | 35.7381 | -118.9546 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4784763E | OH-4784763E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-09-24 | 14:20 | Contact From Object |  | Animal | Electric Facility | Unknown | WOCC1 | 7.2 | 2016-09-24T21:13:00Z | 11.01 | 1 | < 25mph | Agent
47 |  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown | AU414 | 2.86 | 2016-10-03T03:04:00Z | 12.01 | 13 | < 25mph | Equipment
48 |  | DRISKILL | 2016-10-18 | 2016 | 18:41 | 34.4687 | -119.7722 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Santa Barbara Fire Department | OH-2178476E | OH-2178476E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-18 | 18:41 | Equipment/Facility Failure | Fuse |  |  | Unknown | MTIC1 | 7.03 | 2016-10-19T01:47:00Z | 59.99 | 138 | 55mph+ | Equipment
49 |  | PYTHON | 2016-10-22 | 2016 | 15:17 | 34.3812 | -118.4132 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | RAR 0038 | OH-4860064E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-22 | 15:17 | Contact From Object |  | Balloons | Electric Facility | Unknown | CNIC1 | 1.96 | 2016-10-22T21:55:00Z | 32.01 | 32 | 25-40mph | Agent
50 |  | PATRICIA | 2016-10-23 | 2016 | 9:40 | 34.4603 | -119.2853 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | 900 Rice Road Ojai | OH-786960E | Tier 3 | T3 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | OJ | 3.19 | 2016-10-23T17:00:00Z | 4.92 | 4 | < 25mph | Equipment
51 |  | HUGHES LAKE | 2016-10-26 | 2016 | 12:19 | 34.7081 | -118.5367 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | ELIZABETH LAKE ROAD AND KINGS CANYON ROAD, LAKE HUGHES | OH-1586523E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-26 | 12:19 | Contact From Object |  | Vegetation | Electric Facility | Unknown | C4614 | 6.71 | 2016-10-26T19:40:00Z | 11.01 | 8 | < 25mph | Vegetation
52 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | CRXC1 | 6.51 | 2016-11-20T19:07:00Z | 8.01 | 55 | < 25mph | Agent
53 |  | PYTHON | 2016-12-02 | 2016 | 21:26 | 34.3812 | -118.4132 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | OH-4572770E | OH-4572770E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vegetation | Electric Facility | Unknown | NHPC1 | 6.84 | 2016-12-03T05:56:00Z | 51 | 26 | 40-55mph | Vegetation
54 |  | RHODA | 2016-12-30 | 2016 | 11:42 | 34.1231 | -118.723 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-1927507E | OH-1927507E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-12-30 | 11:42 | Contact From Object |  | Balloons | Electric Facility | Unknown | CEEC1 | 4.39 | 2016-12-30T19:38:00Z | 24.99 | 43 | < 25mph | Agent
55 |  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | MSJC1 | 4.82 | 2017-01-13T18:53:00Z | 8.01 | 34 | < 25mph | Vegetation
56 |  | OAK GLEN | 2017-03-15 | 2017 | 13:23 | 34.0534 | -116.971 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-2326555E | OH-2326555E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-15 | 13:23 | Contact From Object |  | Animal | Electric Facility | Unknown | C9072 | 4.81 | 2017-03-15T20:27:00Z | 13 | 64 | < 25mph | Agent
57 |  | HUCKLEBERRY | 2017-03-17 | 2017 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4493863E | OH-4493863E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown | E1966 | 2.92 | 2017-03-18T00:42:00Z | 13 | 14 | < 25mph | Agent
58 |  | PATRICIA | 2017-04-16 | 2017 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4495331E | OH-4495331E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown | CSVC1 | 7.35 | 2017-04-16T23:09:00Z | 18.99 | 10 | < 25mph | Vegetation
59 |  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | E1966 | 3.22 | 2017-04-23T23:24:00Z | 18.01 | 11 | < 25mph | Unknown
60 |  | LEE VINING-LUNDY NO. 1/ET-01774 | 2017-05-01 | 2017 | 5:40 | 38.0209 | -119.1608 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | CAlFIre | OH-1580964E | OH-1580964E | Tier 2 | T2 | Y |  | 55 | Distribution | Conductor | Overhead | No | <Null> |  | Contamination |  |  |  | Unknown | ERYC1 | 7.12 | 2017-05-01T13:00:00Z | 25.59 | 1 | 25-40mph | Equipment
61 |  | GUITAR | 2017-05-11 | 2017 | 12:27 | 34.4127 | -118.6702 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-848255E | OH-848255E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-05-11 | 12:27 | Contact From Object |  | Balloons | Electric Facility | Unknown | TCLC1 | 6.71 | 2017-05-11T19:12:00Z | 14.99 | 5 | < 25mph | Agent
62 |  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | F0145 | 4.82 | 2017-05-21T00:27:00Z | 18.01 | 36 | < 25mph | Agent
63 |  | METTLER | 2017-06-02 | 2017 | 10:50 | 35.1021 | -118.5328 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4416566E | OH-4416566E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | C6906 | 5.06 | 2017-06-02T18:13:00Z | 12.01 | 29 | < 25mph | Agent
64 |  | ANZAR | 2017-06-04 | 2017 | 13:14 | 33.8373 | -117.4863 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-1757417E | OH-1757417E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2017-06-04 | 13:14 | Wire-Wire Contact |  |  |  | Unknown | AU409 | 5.17 | 2017-06-04T20:40:00Z | 18.01 | 43 | < 25mph | Equipment
65 |  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown | LYQC1 | 4.98 | 2017-06-10T19:18:00Z | 34 | 1 | 25-40mph | Equipment
66 |  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | E8879 | 4.39 | 2017-06-14T22:38:00Z | 11.01 | 28 | < 25mph | Agent
67 |  | PICK | 2017-06-19 | 2017 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | 30278 Arrastre Canyon Rd., Acton | OH-699610E | Tier 3 | T3 | Y |  | 33 | Distribution | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown | MLCC1 | 7.72 | 2017-06-20T01:53:00Z | 17 | 2 | < 25mph | Equipment
68 |  | MAYBELL | 2017-07-02 | 2017 | 8:24 | 34.0804 | -117.8552 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | OH-144184E | OH-1255315E | T2 200Ft Outer Buffer | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-07-02 | 8:24 | Contact From Object |  | Animal | Electric Facility | Unknown | E9402 | 7.93 | 2017-07-02T15:54:00Z | 4.99 | 68 | < 25mph | Agent
69 |  | DALBA | 2017-07-11 | 2017 | 18:06 | 34.2054 | -117.1143 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-919465E | OH-919465E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 2.4 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | AS598 | 0.82 | 2017-07-12T01:32:00Z | 126.99 | 65 | 55mph+ | Unknown
70 |  | CUDDEBACK | 2017-08-08 | 2017 | 17:52 | 35.1342 | -118.5607 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4179753E | OH-4179753E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-08-08 | 17:52 | Contact From Object |  | Vehicle | Electric Facility | Unknown | C1020 | 3.61 | 2017-08-09T00:47:00Z | 18.01 | 30 | < 25mph | Agent
71 |  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | F0063 | 5.45 | 2017-08-28T11:38:00Z | 4.99 | 114 | < 25mph | Equipment
72 |  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | CEEC1 | 6.07 | 2017-08-29T00:38:00Z | 21 | 62 | < 25mph | Equipment
73 |  | CABANA | 2017-10-16 | 2017 | 6:11 | 34.0217 | -117.5069 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1670014E | OH-1670014E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-10-16 | 6:11 | Contact From Object |  | Balloons | Electric Facility | Unknown | E7239 | 2.66 | 2017-10-16T13:28:00Z | 4.99 | 16 | < 25mph | Agent
74 |  | DEACON | 2017-10-18 | 2017 | 13:34 | 33.7702 | -117.2157 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1564666E | OH-1564666E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | F0145 | 6.41 | 2017-10-18T20:49:00Z | 20 | 27 | < 25mph | Agent
75 |  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | MTIC1 | 4.81 | 2017-10-28T06:47:00Z | 22.01 | 14 | < 25mph | Unknown
76 |  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UCMO | 4.71 | 2017-11-13T22:00:00Z | 8.01 | 32 | < 25mph | Equipment
77 |  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown | FTNC1 | 0.32 | 2018-06-02T18:00:00Z | 13 | 1 | < 25mph | Agent
78 |  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown | F0490 | 5.32 | 2018-06-16T00:17:00Z | 31 | 25 | 25-40mph | Agent
79 |  | BENCH | 2018-06-26 | 2018 | 20:48 | 34.0158 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Holmes St/Wildwood Canyon Rd, Yucaipa | OH-4367391E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-26 | 20:48 | Contact From Object |  | Vehicle | Pole | Unknown | BNJC1 | 6.9 | 2018-06-27T04:13:00Z | 18.99 | 45 | < 25mph | Agent
80 |  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | CEEC1 | 7.72 | 2018-06-29T10:38:00Z | 11.01 | 109 | < 25mph | Equipment
81 |  | HUGHES LAKE/ED-08810 | 2018-07-06 | 2018 | 5:38 | 34.6744 | -118.4517 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | 465140E | OH-1938477E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-07-06 | 5:38 | Contact From Object |  | Vehicle | Pole | Unknown | GMTC1 | 3.15 | 2018-07-06T12:59:00Z | 12.01 | 4 | < 25mph | Agent
82 |  | BIG CREEK 1-RECTOR/ET-01082 | 2018-08-04 | 2018 | 0:43 | 37.1895 | -119.2738 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | OH-7021454 | OH-7021454 | Tier 3 | T3 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2018-08-04 | 2:21 | Equipment/Facility Failure | Other |  |  | Unknown | SHVC1 | 3.7 | 2018-08-04T07:56:00Z | 1.01 | 1 | < 25mph | Equipment
83 |  | JORDAN | 2018-08-29 | 2018 | 17:32 | 35.7358 | -118.7192 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | Jack Ranch Rd/White River Rd, Kernville | OH-4635091E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-08-29 | 19:06 | Contact From Object |  | Vegetation | Electric Facility | Unknown | WOCC1 | 6.68 | 2018-08-30T00:13:00Z | 10 | 1 | < 25mph | Vegetation
84 |  | POULTRY | 2018-09-21 | 2018 | 8:28 | 34.0728 | -117.0397 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Juniper St. Yucaipa | OH-129241E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SE085 | 4.77 | 2018-09-21T15:40:00Z | 8.66 | 62 | < 25mph | Agent
85 |  | OAK GLEN | 2018-11-08 | 2018 | 12:09 | 34.0397 | -116.9362 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 11833 Oak Glen Rd. Yucaipa | OH-4611601E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-08 | 12:09 | Equipment/Facility Failure | Transformer |  |  | Unknown | BNJC1 | 4.78 | 2018-11-08T20:13:00Z | 35.99 | 71 | 25-40mph | Equipment
86 |  | ARCHIE | 2018-11-13 | 2018 | 7:11 | 33.4928 | -117.2796 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | NORTH OF CARANCHO ON VIA CIELO | OH-4149859E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-13 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Unknown | SRUC1 | 3.4 | 2018-11-13T14:54:00Z | 38.01 | 43 | 25-40mph | Equipment
87 |  | Peninsula | 2019-03-16 | 2019 | 17:58 | 33.6182 | -117.8025 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1729510E | OH-1729510E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-03-16 | 17:58 | Equipment/Facility Failure | Crossarm |  |  | Unknown | ALLC1 | 6.35 | 2019-03-17T00:50:00Z | 17 | 148 | < 25mph | Equipment
88 |  | Taggert | 2019-04-23 | 2019 | 21:06 | 34.2147 | -117.0973 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1027559E | OH-1027559E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution |  | Overhead | No |  |  | Unknown |  |  |  | Unknown | HHPC1 | 2.75 | 2019-04-24T04:15:00Z | 13 | 60 | < 25mph | Unknown
89 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error | ATNC1 | 5.18 | 2019-06-01T18:54:00Z | 20 | 58 | < 25mph | Agent
90 |  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error | SE062 | 6.86 | 2019-06-06T16:30:00Z | 12.93 | 81 | < 25mph | Agent
91 |  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force | TSHC1 | 6.99 | 2019-06-06T21:04:00Z | 12.01 | 14 | < 25mph | Agent
92 |  | Northpark | 2019-06-20 | 2019 | 14:08 | 34.2298 | -117.4048 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | San Bern. FD | OH-201371S | OH-201371S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Human Error | SE064 | 1.9 | 2019-06-20T21:00:00Z | 28.5 | 93 | 25-40mph | Agent
93 |  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force | SDMEA | 5.11 | 2019-06-23T21:49:00Z | 23 | 61 | < 25mph | Agent
94 |  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather | KBUR | 7.65 | 2019-06-25T21:53:00Z | 18.41 | 77 | < 25mph | Equipment
95 |  | Saugus-Santa Susana | 2019-08-06 | 2019 | 15:03 | 34.3918 | -118.6596 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | VFD & LACFD | M6-T1 | M6-T1 | Tier 3 | T3 | Y | NA | 66 | Transmission | Other | Overhead | Yes | 2019-08-06 | 12:51 | Contact From Object |  | Animal | Electric Facility | Other | SE040 | 2.76 | 2019-08-06T22:00:00Z | 23.31 | 61 | < 25mph | Agent
96 |  | Zone | 2019-08-10 | 2019 | 13:00 | 34.3089 | -118.9413 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | VFD | OH-4734128E | OH-4734128E | Tier 3 | T3 | Y | AT&T Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | WLYC1 | 7.19 | 2019-08-10T19:49:00Z | 24 | 177 | < 25mph | Equipment
97 |  | Enchanted | 2019-08-25 | 2019 | 8:03 | 34.301 | -118.8308 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4754475E | OH-4754475E | Tier 3 | T3 | Y | NA | 16 | Distribution | Lightning Arrestor | Overhead | Yes | 2019-08-25 | 8:03 | Contact From Object |  | Animal | Electric Facility | Other | WLYC1 | 4.92 | 2019-08-25T14:49:00Z | 14 | 123 | < 25mph | Agent
98 |  | Hughes Lake | 2019-09-02 | 2019 | 14:02 | 34.7026 | -118.342 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4782978E | OH-4782978E | Tier 2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-02 | 14:02 | Contact From Object |  | Balloons | Electric Facility | Other | PPPC1 | 3.45 | 2019-09-02T20:56:00Z | 28.99 | 42 | 25-40mph | Agent
99 |  | Plateau | 2019-09-11 | 2019 | 8:08 | 34.0991 | -118.6793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4424792E | OH-4424792E | Tier 3 | T3 | Y | Verizon / AT&T / Crown Castle | 16 | Distribution | Conductor | Overhead | Yes | 2019-09-11 | 8:08 | Equipment/Facility Failure | Conductor |  | Electric Facility | Human Error | CEEC1 | 6.47 | 2019-09-11T15:38:00Z | 8.99 | 144 | < 25mph | Agent
100 |  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown | WTPC1 | 2.77 | 2019-09-13T04:57:00Z | 12.01 | 32 | < 25mph | Equipment
101 |  | Penstock | 2019-09-18 | 2019 | 2:52 | 34.3143 | -117.3793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4066969E | OH-4066969E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Human Error | SE355 | 5.09 | 2019-09-18T09:50:00Z | 18.19 | 121 | < 25mph | Agent
102 |  | Wildomar | 2019-09-19 | 2019 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside County FD | OH-2225310E | OH-2225310E | Tier 3 | T3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other | SDMEA | 4.2 | 2019-09-19T21:49:00Z | 24 | 53 | < 25mph | Agent
103 |  | Elster | 2019-09-21 | 2019 | 10:53 | 36.1026 | -118.8659 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4252581E | OH-4252581E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-21 | 10:53 | Contact From Object |  | Vehicle | Electric Facility | Human Error | SE278 | 7.52 | 2019-09-21T18:00:00Z | 11.48 | 30 | < 25mph | Agent
104 |  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown | UCSH | 2.26 | 2019-04-25T00:10:00Z | 20.89 | 14 | < 25mph | Equipment
105 |  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | SE015 | 7.92 | 2020-01-03T14:50:00Z | 29.73 | 45 | 25-40mph | Equipment
106 |  | Medusa | 2020-03-06 | 2020 | 17:05 | 34.0802 | -117.254 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1811355E | OH-1811355E | T2 | T2 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Other | SE190 | 7.6 | 2020-03-07T00:50:00Z | 13.24 | 75 | < 25mph | Equipment
107 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | SE042 | 7.73 | 2020-04-22T22:40:00Z | 21.77 | 78 | < 25mph | Equipment
108 |  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other | SE063 | 5.85 | 2020-05-02T04:00:00Z | 31.14 | 92 | 25-40mph | Agent
109 |  | VALLEY-MAYBERRY-MORENO-VISTA | 2020-05-18 | 2020 | 12:10 | 33.8587 | -117.0203 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire Perris | OH-1979539E | OH-1979539E | T3 | T3 | Y | None | 115 | Transmission | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Other | HSGC1 | 4.08 | 2020-05-18T19:16:00Z | 25.99 | 147 | 25-40mph | Equipment
110 |  | Bonanza | 2020-06-05 | 2020 | 17:33 | 35.7635 | -118.4218 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Kern County Fire Department | OH-4451126E | OH-4451126E | T3 | T3 | Y | None | 12 | Distribution | Other | Overhead | Yes | 2020-06-05 | 17:33 | Contact From Object |  | Animal | Electric Facility | Other | WFHC1 | 5.2 | 2020-06-06T01:00:00Z | 24 | 35 | < 25mph | Agent
111 |  | Conestoga | 2020-06-13 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Other | MHEC1 | 2.44 | 2020-06-14T00:16:00Z | 26 | 96 | 25-40mph | Agent
112 |  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other | PPPC1 | 1.78 | 2020-06-14T22:56:00Z | 29 | 29 | 25-40mph | Equipment
113 |  | La Mancha | 2020-07-05 | 2020 | 3:57 | 34.1325 | -118.8532 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1848406E | OH-1848406E | T3 | T3 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-07-05 | 3:57 | Equipment/Facility Failure | Insulator |  |  | Unknown | SE146 | 4.78 | 2020-07-05T11:10:00Z | 13.37 | 166 | < 25mph | Equipment
114 |  | Capanero | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | T2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE290 | 4.95 | 2020-07-05T19:30:00Z | 12.13 | 35 | < 25mph | Vegetation
115 |  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force | SE232 | 7.53 | 2020-07-25T20:40:00Z | 26.68 | 64 | 25-40mph | Agent
116 |  | Mettler | 2020-08-10 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | OH-2093506E | OH-2093506E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Unknown | C1020 | 3.83 | 2020-08-10T22:05:00Z | 22 | 139 | < 25mph | Unknown
117 |  | Flying D | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County | OH-1761180E | OH-1761180E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown | SE304 | 1.75 | 2020-09-24T18:00:00Z | 17.76 | 38 | < 25mph | Agent
118 |  | Calgrove | 2020-10-03 | 2020 | 17:45 | 34.357 | -118.5659 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | OH-2101062E | OH-2101062E | T3 | T3 |  | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | DLVC1 | 7.65 | 2020-10-04T00:55:00Z | 21 | 224 | < 25mph | Equipment
119 |  | Kickapoo Trail | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1941931E | OH-1941931E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE349 | 2.58 | 2020-11-09T15:30:00Z | 15.49 | 102 | < 25mph | Equipment
120 |  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other | SE286 | 7.46 | 2020-05-27T06:00:00Z | 14.98 | 110 | < 25mph | Agent
121 |  | Vicasa | 2020-11-30 | 2020 | 21:02 | 34.0723 | -118.588 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles Fire Department | OH-4535641E | OH-4535641E | T3 | T3 |  | Verizon Wireless, AT&T Mobility, Frontier Communications, Crown Castle NG West, Inc | 16 | Distribution | Other | Overhead | Yes | 2020-11-30 | 21:02 | Contact From Object |  | Vehicle | Electric Facility | Outside Force | HP026 | 2.45 | 2020-12-01T05:26:00Z | 32.44 | 257 | 25-40mph | Agent
122 |  | Viento | 2020-06-09 | 2020 | 16:42 | 35.1384 | -118.4809 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4707894E | OH-4707894E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | C1020 | 1.14 | 2020-06-10T00:10:00Z | 22 | 140 | < 25mph | Equipment
123 |  | Lasker | 2020-07-26 | 2020 | 12:50 | 34.5326 | -118.0541 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4619162E | OH-4619162E | T3 | T3 |  | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | LPDC1 | 2.76 | 2020-07-26T19:55:00Z | 30 | 112 | 25-40mph | Equipment
124 |  | Morongo | 2020-08-03 | 2020 | 10:33 | 34.0758 | -116.5548 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-2107480E | OH-2107480E | T2 | T2 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-08-03 | 19:15 | Contact From Object |  | Balloons | Electric Facility | Outside Force | SE351 | 6.16 | 2020-08-03T18:00:00Z | 17.98 | 71 | < 25mph | Agent
125 |  | Bidder | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire | OH-2023941E | OH-2023941E | T3 | T3 |  | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force | 007SE | 4.03 | 2020-11-10T02:30:00Z | 26.53 | 221 | 25-40mph | Agent
126 |  | Vicasa | 2020-10-26 | 2020 | 11:56 | 34.0998 | -118.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | OH-795990E | OH-795990E | T3 | T3 |  | Frontier Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Weather | D2363 | 2.61 | 2020-10-26T18:40:00Z | 68 | 269 | 55mph+ | Equipment
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | BPOC1 | 4.63 | 2015-02-06T22:49:00Z | 72.01 | 9 | 55mph+ | Investigation
10002 | CABIN |  | 2015-08-14 | 2015 | 13:07 | 34.0299 | -118.0726 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | D7923 | 5.49 | 2015-08-14T20:33:00Z | 14.99 | 70 | < 25mph | Investigation
10003 | EDISON |  | 2016-05-12 | 2016 | -8 | 34.3135 | -119.1865 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | E8097 | 6.25 | 2016-05-12T06:31:00Z | 10 | 89 | < 25mph | Investigation
10004 | ERSKINE |  | 2016-06-23 | 2016 | 16:00 | 34.2676 | -117.844 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | BLM | [13 empty] | Contact From Object |  | Vegetation |  |  | TANC1 | 6.35 | 2016-06-23T23:01:00Z | 14 | 1 | < 25mph | Investigation
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | ERYC1 | 5.82 | 2016-06-24T12:00:00Z | 19.8 | 14 | < 25mph | Investigation
10006 | RYE |  | 2017-12-05 | 2017 | 15:00 | 34.2676 | -117.844 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | TANC1 | 6.35 | 2017-12-05T23:01:00Z | 34 | 1 | 25-40mph | Investigation
10007 | ELLIS |  | 2017-10-18 | 2017 | 11:18 | 33.7721 | -117.2173 | Vegetation | Rural | Unknown |  | Unknown | Fire Agency | Cal Fire | [17 empty] | Weather | F0145 | 6.54 | 2017-10-18T18:08:00Z | 21 | 30 | < 25mph | Investigation
10008 | THOMAS |  | 2017-12-04 | 2017 | 18:28 | 34.4152 | -119.0912 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | USFS | [17 empty] | Weather | AT184 | 6.91 | 2017-12-05T02:53:00Z | 62.01 | 81 | 55mph+ | Investigation
10009 | RYE |  | 2017-12-05 | 2017 | 11:31 | 34.4528 | -118.5819 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | SAUC1 | 4.1 | 2017-12-05T19:57:00Z | 65.01 | 18 | 55mph+ | Investigation
10010 | MEYERS |  | 2017-12-05 | 2017 | 14:00 | 34.2183 | -117.4062 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | E3127 | 5.41 | 2017-12-05T21:31:00Z | 54 | 14 | 40-55mph | Investigation
10011 | LIBERTY |  | 2017-12-07 | 2017 | 13:00 | 33.5926 | -117.1498 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | Murrieta Fire Department | [17 empty] | Weather | KF70 | 1.76 | 2017-12-07T21:15:00Z | 29.93 | 29 | 25-40mph | Investigation
10012 | HOLIDAY |  | 2018-07-06 | 2018 | 20:40 | 34.4639 | -119.8314 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Santa Barbara Fire Department | [17 empty] | Weather | SBVC1 | 7.19 | 2018-07-07T03:24:00Z | 38.99 | 146 | 25-40mph | Investigation
10013 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | AS198 | 4.48 | 2018-11-08T21:57:00Z | 38.01 | 83 | 25-40mph | Investigation
10014 | STAR |  | 2019-07-28 | 2019 | 14:00 | 33.9975 | -117.7698 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Chino Valley Fire Department | [13 empty] | Contact From Object |  | Bird |  | Weather | SE218 | 7.69 | 2019-07-28T21:30:00Z | 23.82 | 145 | < 25mph | Investigation
10015 | TENAJA |  | 2019-09-04 | 2019 | 16:43 | 33.5285 | -117.2732 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | SDMEA | 2.99 | 2019-09-04T23:49:00Z | 34 | 51 | 25-40mph | Investigation
10016 | SADDLE RIDGE |  | 2019-10-10 | 2019 | 21:09 | 34.3299 | -118.4816 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | CNIC1 | 3.94 | 2019-10-11T03:55:00Z | 53.02 | 108 | 40-55mph | Investigation
10017 | OAK |  | 2019-10-28 | 2019 | 8:42 | 34.1489 | -118.6954 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | MBUC1 | 6.68 | 2019-10-28T15:56:00Z | 52.01 | 185 | 40-55mph | Investigation
10018 | EASY |  | 2019-10-30 | 2019 | 6:00 | 34.2822 | -118.8034 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | SE277 | 5.28 | 2019-10-30T13:10:00Z | 60.06 | 156 | 55mph+ | Investigation
10019 | MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | MBUC1 | 6.39 | 2019-10-30T17:56:00Z | 58 | 195 | 55mph+ | Investigation
10020 | MARIA |  | 2019-10-31 | 2019 | 20:58 | 34.3022 | -118.9971 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | SE209 | 2.55 | 2019-11-01T03:30:00Z | 37.78 | 154 | 25-40mph | Investigation
Note on D1: Date the event started (Use MM/DD/YY when inputting dates)
Note on F1: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on G1: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on H1: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on I1: Material involved in the initial fueling of the fire;
Note on J1: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on K1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on L1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on M1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on N1: Is who suppressed the fire
Note on O1: If the fire was suppressed by a fire agency or agencies, insert the lead agency when one or more agency was involved
Note on P1: Utility’s description of the pole and/or equipment involved.
Note on U1: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on V1: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on X1: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on Y1: The equipment involved in the event (overhead, padmounted or subsurface);
Note on Z1: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AA1: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AB1: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AC1: The suspected cause of the ignition;
Note on AD1: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on AE1: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on AF1: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on AG1: Factors that contributed to the ignition;

## RandomWind
ID | Name | Circuit | Date | Year | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Size - HFTD | Size - UI | Suppressed by | Suppressing Agency | Facility Identification | FLOC | HFRA | cGIS HFRA | HFTD | Other Companies | Voltage (Volts) | Business Line | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | 8m/1h stid | 8m/1h dist | 8m/1h time | 8m/1h gust mph | 8m/1h count | 8m/1h Category
| HOLIDAY |  | 2018-07-06 | 2018 | 20:40 | 34.4639 | -119.8314 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Santa Barbara Fire Department | [17 empty] | Weather | AS303 | 6.76 | 2015-12-08T09:48:00Z | 31 | 39 | 25-40mph
|  | VALLECITO | 2016-08-18 | 2016 | 19:00 | 34.4214 | -119.5964 | Other | Rural | Structure Only | Structure Only |  | Fire Agency | Santa Barbara County Fire Department | 2400 block of Whitney Avenue in Summerland | OH-1523986E | Tier 2 | T2 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | C9548 | 7.54 | 2015-01-02T03:45:00Z | 8.01 | 33 | < 25mph
|  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown | SE535 | 3.02 | 2020-10-30T04:30:00Z | 9.86 | 94 | < 25mph
|  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE192 | 7.91 | 2019-04-12T14:10:00Z | 12.48 | 43 | < 25mph
|  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown | CNSC1 | 7.75 | 2015-01-01T05:16:00Z | 8.01 | 20 | < 25mph
|  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | E9981 | 1.54 | 2018-05-26T18:21:00Z | 15.99 | 24 | < 25mph
|  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown | LYQC1 | 4.98 | 2016-02-10T10:18:00Z | 10 | 1 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TNRC1 | 2.34 | 2016-09-06T02:57:00Z | 14.99 | 102 | < 25mph
|  | PICK | 2017-06-19 | 2017 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | 30278 Arrastre Canyon Rd., Acton | OH-699610E | Tier 3 | T3 | Y |  | 33 | Distribution | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown | SE015 | 5.04 | 2018-07-14T04:00:00Z | 14.25 | 14 | < 25mph
1 |  | Birchim | 2015-02-06 | 2015 | 13:15 | 37.454 | -118.5842 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Various Fire Agencies | Between Poles 1854107E & 1854106E | OH-1854107E | Tier 2 | T2 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-02-06 | 13:15 | Unknown |  |  |  | Unknown | OVRC1 | 4.68 | 2017-03-12T21:54:00Z | 10 | 1 | < 25mph
|  | GUITAR | 2017-05-11 | 2017 | 12:27 | 34.4127 | -118.6702 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-848255E | OH-848255E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-05-11 | 12:27 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE086 | 4.67 | 2020-11-21T01:20:00Z | 20.9 | 171 | < 25mph
|  | Medusa | 2020-03-06 | 2020 | 17:05 | 34.0802 | -117.254 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1811355E | OH-1811355E | T2 | T2 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Other | UP629 | 3.4 | 2018-10-30T10:00:00Z | 10.02 | 19 | < 25mph
|  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | NTBC1 | 7.63 | 2017-08-20T10:00:00Z | 4.99 | 15 | < 25mph
|  | CUDDEBACK | 2017-08-08 | 2017 | 17:52 | 35.1342 | -118.5607 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4179753E | OH-4179753E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-08-08 | 17:52 | Contact From Object |  | Vehicle | Electric Facility | Unknown | KTSP | 6.87 | 2017-06-11T20:55:00Z | 29.93 | 22 | 25-40mph
|  | DEACON | 2017-10-18 | 2017 | 13:34 | 33.7702 | -117.2157 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1564666E | OH-1564666E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SE033 | 6.86 | 2019-05-05T18:30:00Z | 10.96 | 42 | < 25mph
|  | KINSEY | 2016-07-08 | 2016 | 11:15 | 34.7906 | -118.8256 | Vegetation | Rural | 300 - 999 Acres | 300 - 999 Acres |  | Fire Agency | Kern County Fire Department | 1-5, Gorman | OH-4539401E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | PG241 | 5.06 | 2020-07-24T03:40:00Z | 16.81 | 42 | < 25mph
|  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SE250 | 7.27 | 2020-02-05T06:40:00Z | 20.67 | 76 | < 25mph
|  | PATRICIA | 2017-04-16 | 2017 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4495331E | OH-4495331E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown | CSVC1 | 7.35 | 2016-07-16T16:09:00Z | 7 | 13 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:26 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | Unknown | FRCC1 | 7.87 | 2017-12-12T19:51:00Z | 28.99 | 51 | 25-40mph
|  | VALLEY-MAYBERRY-MORENO-VISTA | 2020-05-18 | 2020 | 12:10 | 33.8587 | -117.0203 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire Perris | OH-1979539E | OH-1979539E | T3 | T3 | Y | None | 115 | Transmission | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Other | SE431 | 5.67 | 2019-10-09T10:50:00Z | 8.84 | 56 | < 25mph
|  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UCMO | 4.71 | 2017-12-22T16:50:00Z | 8.5 | 32 | < 25mph
|  | CACHUMA | 2016-08-18 | 2016 | 14:52 | 34.5356 | -119.8523 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-1413051E | OH-1413051E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-18 | 14:52 | Contact From Object |  | Vegetation | Communication Facility | Unknown | SE068 | 4.85 | 2020-04-08T23:50:00Z | 11.54 | 105 | < 25mph
| THOMAS |  | 2017-12-04 | 2017 | 18:28 | 34.4152 | -119.0912 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | USFS | [17 empty] | Weather | D7412 | 1.16 | 2017-09-06T03:16:00Z | 3 | 71 | < 25mph
10002 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | E1856 | 4.13 | 2017-03-18T01:18:00Z | 10 | 71 | < 25mph
|  | BENCH | 2018-06-26 | 2018 | 20:48 | 34.0158 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Holmes St/Wildwood Canyon Rd, Yucaipa | OH-4367391E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-26 | 20:48 | Contact From Object |  | Vehicle | Pole | Unknown | BNJC1 | 6.9 | 2020-01-22T05:13:00Z | 21 | 91 | < 25mph
|  | Medusa | 2020-03-06 | 2020 | 17:05 | 34.0802 | -117.254 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1811355E | OH-1811355E | T2 | T2 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Other | UP581 | 6.78 | 2017-12-14T08:50:00Z | 4.94 | 28 | < 25mph
|  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error | SAUC1 | 7.39 | 2015-05-09T05:57:00Z | 13 | 19 | < 25mph
|  | SKINKLE | 2016-05-29 | 2016 | 22:25 | 36.0091 | -118.9563 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-4566417E | OH-4566417E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-05-29 | 22:25 | Contact From Object |  | Other | Electric Facility | Unknown | C1000 | 7.9 | 2016-08-07T18:15:00Z | 3 | 8 | < 25mph
|  | PATRICIA | 2017-04-16 | 2017 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4495331E | OH-4495331E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE211 | 3.78 | 2020-02-22T01:30:00Z | 25.57 | 92 | 25-40mph
|  | Calgrove | 2020-10-03 | 2020 | 17:45 | 34.357 | -118.5659 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | OH-2101062E | OH-2101062E | T3 | T3 |  | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | NHPC1 | 2.94 | 2018-11-06T11:56:00Z | 18.01 | 43 | < 25mph
10005 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | D5145 | 7.89 | 2018-03-27T22:25:00Z | 25.99 | 58 | 25-40mph
|  | SODA SPRINGS | 2016-06-21 | 2016 | 21:47 | 36.2515 | -118.7809 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4391218E | OH-4391218E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-21 | 21:47 | Contact From Object |  | Vegetation | Electric Facility | Unknown | AV342 | 7.69 | 2017-12-30T18:52:00Z | 8.01 | 13 | < 25mph
|  | OAK GLEN | 2017-03-15 | 2017 | 13:23 | 34.0534 | -116.971 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-2326555E | OH-2326555E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-15 | 13:23 | Contact From Object |  | Animal | Electric Facility | Unknown | E6473 | 6.33 | 2017-06-07T18:00:00Z | 10 | 55 | < 25mph
|  | GUITAR | 2017-05-11 | 2017 | 12:27 | 34.4127 | -118.6702 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-848255E | OH-848255E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-05-11 | 12:27 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE040 | 2.19 | 2019-05-03T20:10:00Z | 22.79 | 64 | < 25mph
|  | Enchanted | 2019-08-25 | 2019 | 8:03 | 34.301 | -118.8308 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4754475E | OH-4754475E | Tier 3 | T3 | Y | NA | 16 | Distribution | Lightning Arrestor | Overhead | Yes | 2019-08-25 | 8:03 | Contact From Object |  | Animal | Electric Facility | Other | WLYC1 | 4.92 | 2017-11-07T21:49:00Z | 20 | 54 | < 25mph
|  | Penstock | 2019-09-18 | 2019 | 2:52 | 34.3143 | -117.3793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4066969E | OH-4066969E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Human Error | SE336 | 7.49 | 2020-07-23T05:20:00Z | 27.91 | 201 | 25-40mph
|  | TICO | 2016-04-28 | 2016 | 14:00 | 34.357 | -119.314 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura County FD | OH-1604151E | OH-1604151E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-04-28 | 14:00 | Equipment/Facility Failure | Other |  |  | Unknown | CSVC1 | 4.81 | 2015-09-11T00:09:00Z | 11.01 | 12 | < 25mph
|  | Wildomar | 2019-09-19 | 2019 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside County FD | OH-2225310E | OH-2225310E | Tier 3 | T3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other | DLZSD | 4.22 | 2020-03-22T13:40:00Z | 8.99 | 52 | < 25mph
|  | Wildomar | 2019-09-19 | 2019 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside County FD | OH-2225310E | OH-2225310E | Tier 3 | T3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other | SDMEA | 4.2 | 2018-06-21T20:49:00Z | 18.01 | 7 | < 25mph
|  | OAK GLEN | 2018-11-08 | 2018 | 12:09 | 34.0397 | -116.9362 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 11833 Oak Glen Rd. Yucaipa | OH-4611601E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-08 | 12:09 | Equipment/Facility Failure | Transformer |  |  | Unknown | SE680 | 7.97 | 2020-05-29T16:30:00Z | 23.09 | 128 | < 25mph
| LIBERTY |  | 2017-12-07 | 2017 | 13:00 | 33.5926 | -117.1498 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | Murrieta Fire Department | [17 empty] | Weather | SE192 | 6.9 | 2019-11-22T07:50:00Z | 8.05 | 55 | < 25mph
| RYE |  | 2017-12-05 | 2017 | 15:00 | 34.2676 | -117.844 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | TANC1 | 6.35 | 2016-12-07T05:01:00Z | 7 | 1 | < 25mph
| MEYERS |  | 2017-12-05 | 2017 | 14:00 | 34.2183 | -117.4062 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | SE352 | 5.78 | 2020-07-07T07:30:00Z | 21.99 | 273 | < 25mph
|  | Kickapoo Trail | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1941931E | OH-1941931E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Unknown | UCCC1 | 6.87 | 2016-10-16T16:56:00Z | 8.01 | 19 | < 25mph
|  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown | E3060 | 4.55 | 2017-10-17T10:12:00Z | 8.01 | 35 | < 25mph
| OAK |  | 2019-10-28 | 2019 | 8:42 | 34.1489 | -118.6954 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | CEEC1 | 2.95 | 2020-12-29T01:38:00Z | 22 | 290 | < 25mph
|  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown | UCSH | 2.26 | 2019-02-22T19:40:00Z | 4.7 | 10 | < 25mph
| LIBERTY |  | 2017-12-07 | 2017 | 13:00 | 33.5926 | -117.1498 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | Murrieta Fire Department | [17 empty] | Weather | F0145 | 6.97 | 2018-04-01T00:05:00Z | 20 | 28 | < 25mph
|  | Morongo | 2020-08-03 | 2020 | 10:33 | 34.0758 | -116.5548 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-2107480E | OH-2107480E | T2 | T2 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-08-03 | 19:15 | Contact From Object |  | Balloons | Electric Facility | Outside Force | UCBU | 7.55 | 2017-03-04T03:30:00Z | 7.49 | 6 | < 25mph
10003 |  | SHEFFIELD | 2016-02-22 | 2016 | 17:04 | 34.4492 | -119.5845 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Montecito Fire Department | OH-1082380E | OH-1082380E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-02-22 | 17:04 | Equipment/Facility Failure | Conductor |  |  | Unknown | AV377 | 7.98 | 2018-12-13T09:00:00Z | 12.01 | 57 | < 25mph
10004 |  | Peninsula | 2019-03-16 | 2019 | 17:58 | 33.6182 | -117.8025 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1729510E | OH-1729510E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-03-16 | 17:58 | Equipment/Facility Failure | Crossarm |  |  | Unknown | E1565 | 4.94 | 2019-08-12T22:01:00Z | 14 | 121 | < 25mph
3 |  | Bidder | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire | OH-2023941E | OH-2023941E | T3 | T3 |  | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force | MPWC1 | 5.77 | 2016-05-26T03:06:00Z | 41 | 100 | 40-55mph
| RYE |  | 2017-12-05 | 2017 | 15:00 | 34.2676 | -117.844 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | TANC1 | 6.35 | 2015-08-31T12:01:00Z | 5.99 | 1 | < 25mph
|  | PATRICIA | 2016-10-23 | 2016 | 9:40 | 34.4603 | -119.2853 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | 900 Rice Road Ojai | OH-786960E | Tier 3 | T3 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | CSVC1 | 6.08 | 2016-09-27T23:09:00Z | 15.99 | 6 | < 25mph
|  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown | LYQC1 | 4.98 | 2020-04-16T00:18:00Z | 35.99 | 37 | 25-40mph
|  | CABANA | 2017-10-16 | 2017 | 6:11 | 34.0217 | -117.5069 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1670014E | OH-1670014E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-10-16 | 6:11 | Contact From Object |  | Balloons | Electric Facility | Unknown | E7239 | 2.66 | 2016-01-14T02:38:00Z | 5.99 | 17 | < 25mph
|  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UCMO | 4.71 | 2019-06-01T21:00:00Z | 18.1 | 61 | < 25mph
|  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown | UCSH | 2.26 | 2019-02-11T01:20:00Z | 27.4 | 13 | 25-40mph
|  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown | SE338 | 7.45 | 2019-11-08T17:10:00Z | 18.7 | 68 | < 25mph
|  | Bonanza | 2020-06-05 | 2020 | 17:33 | 35.7635 | -118.4218 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Kern County Fire Department | OH-4451126E | OH-4451126E | T3 | T3 | Y | None | 12 | Distribution | Other | Overhead | Yes | 2020-06-05 | 17:33 | Contact From Object |  | Animal | Electric Facility | Other | SE113 | 7.43 | 2019-03-06T21:50:00Z | 24.34 | 18 | < 25mph
|  | LEE VINING-LUNDY NO. 1/ET-01774 | 2017-05-01 | 2017 | 5:40 | 38.0209 | -119.1608 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | CAlFIre | OH-1580964E | OH-1580964E | Tier 2 | T2 | Y |  | 55 | Distribution | Conductor | Overhead | No | <Null> |  | Contamination |  |  |  | Unknown | ERYC1 | 7.12 | 2016-06-11T22:00:00Z | 20.09 | 10 | < 25mph
|  | Conestoga | 2020-06-13 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Other | C7445 | 1.64 | 2016-04-24T20:03:00Z | 31 | 38 | 25-40mph
3 |  | Bidder | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire | OH-2023941E | OH-2023941E | T3 | T3 |  | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force | MPWC1 | 5.77 | 2019-12-11T13:06:00Z | 14.99 | 162 | < 25mph
| RYE |  | 2017-12-05 | 2017 | 11:31 | 34.4528 | -118.5819 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | C1909 | 5.98 | 2017-09-27T14:24:00Z | 12.01 | 19 | < 25mph
|  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force | SDWDM | 3.49 | 2017-07-23T17:49:00Z | 42.99 | 23 | 40-55mph
|  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE444 | 4.44 | 2019-11-09T14:00:00Z | 21.63 | 64 | < 25mph
|  | CACHUMA | 2016-08-18 | 2016 | 14:52 | 34.5356 | -119.8523 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-1413051E | OH-1413051E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-18 | 14:52 | Contact From Object |  | Vegetation | Communication Facility | Unknown | SE068 | 4.85 | 2020-02-07T10:40:00Z | 8.68 | 80 | < 25mph
|  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown | UCSH | 2.26 | 2017-09-10T18:40:00Z | 11.9 | 12 | < 25mph
|  | HUGHES LAKE/ED-08810 | 2018-07-06 | 2018 | 5:38 | 34.6744 | -118.4517 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | 465140E | OH-1938477E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-07-06 | 5:38 | Contact From Object |  | Vehicle | Pole | Unknown | GMTC1 | 3.15 | 2016-12-20T23:59:00Z | 18.99 | 6 | < 25mph
|  | DRISKILL | 2016-10-18 | 2016 | 18:41 | 34.4687 | -119.7722 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Santa Barbara Fire Department | OH-2178476E | OH-2178476E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-18 | 18:41 | Equipment/Facility Failure | Fuse |  |  | Unknown | LPOC1 | 5.34 | 2018-08-22T06:35:00Z | 5.99 | 142 | < 25mph
|  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE063 | 6.25 | 2019-01-26T11:00:00Z | 19.28 | 19 | < 25mph
|  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown | HMMC1 | 3.23 | 2017-06-15T20:14:00Z | 15.99 | 14 | < 25mph
|  | VIENTO | 2016-06-06 | 2016 | 17:44 | 35.1355 | -118.4771 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1373165E | OH-1373165E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-06 | 17:44 | Contact From Object |  | Other | Pole | Unknown | C0464 | 2.52 | 2017-08-03T02:58:00Z | 15.99 | 32 | < 25mph
|  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other | LPDC1 | 2.12 | 2017-07-04T13:55:00Z | 30 | 11 | 25-40mph
|  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error | AU563 | 7.19 | 2018-04-09T10:51:00Z | 30 | 15 | 25-40mph
|  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown | E1966 | 2.94 | 2016-07-03T10:50:00Z | 13 | 10 | < 25mph
|  | Maguire | 2015-04-17 | 2015 | 16:41 | 34.0851 | -118.8044 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles County Fire | Maguire 16kV out of Latigo Sub | OH-1199311E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2015-04-17 | 16:41 | Contact From Object |  | Vehicle | Pole | None | OOSC1 | 7.73 | 2020-01-22T16:00:00Z | 27.11 | 118 | 25-40mph
| ELLIS |  | 2017-10-18 | 2017 | 11:18 | 33.7721 | -117.2173 | Vegetation | Rural | Unknown |  | Unknown | Fire Agency | Cal Fire | [17 empty] | Weather | UCMO | 3.15 | 2018-10-16T09:20:00Z | 11.1 | 44 | < 25mph
|  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | D2363 | 4.16 | 2020-12-05T18:48:00Z | 13 | 247 | < 25mph
|  | Enchanted | 2019-08-25 | 2019 | 8:03 | 34.301 | -118.8308 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4754475E | OH-4754475E | Tier 3 | T3 | Y | NA | 16 | Distribution | Lightning Arrestor | Overhead | Yes | 2019-08-25 | 8:03 | Contact From Object |  | Animal | Electric Facility | Other | WLYC1 | 4.92 | 2017-08-05T17:49:00Z | 14 | 47 | < 25mph
|  | PYTHON | 2016-10-22 | 2016 | 15:17 | 34.3812 | -118.4132 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | RAR 0038 | OH-4860064E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-22 | 15:17 | Contact From Object |  | Balloons | Electric Facility | Unknown | CNIC1 | 1.96 | 2017-03-06T10:55:00Z | 38.01 | 35 | 25-40mph
|  | Calgrove | 2020-10-03 | 2020 | 17:45 | 34.357 | -118.5659 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | OH-2101062E | OH-2101062E | T3 | T3 |  | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | S183E | 3.95 | 2019-08-31T08:00:00Z | 11.03 | 77 | < 25mph
|  | PATRICIA | 2016-10-23 | 2016 | 9:40 | 34.4603 | -119.2853 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | 900 Rice Road Ojai | OH-786960E | Tier 3 | T3 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | OJ | 3.19 | 2015-11-02T15:00:00Z | 2.46 | 4 | < 25mph
|  | PYTHON | 2016-06-05 | 2016 | 15:59 | 34.4208 | -118.4218 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4154960E | OH-4154960E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-06-05 | 15:59 | Unknown |  |  |  | Unknown | CNIC1 | 4.67 | 2015-12-14T15:55:00Z | 44 | 22 | 40-55mph
|  | SHOWDOWN | 2016-06-09 | 2016 | 11:28 | 34.5862 | -118.196 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4267121E | OH-4267121E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-09 | 11:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE015 | 5.54 | 2019-03-14T09:20:00Z | 23.02 | 39 | < 25mph
10003 |  | SHEFFIELD | 2016-02-22 | 2016 | 17:04 | 34.4492 | -119.5845 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Montecito Fire Department | OH-1082380E | OH-1082380E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-02-22 | 17:04 | Equipment/Facility Failure | Conductor |  |  | Unknown | MTIC1 | 3.77 | 2019-11-03T20:47:00Z | 13 | 100 | < 25mph
|  | Soda Springs | 2015-05-14 | 2015 | 22:24 | 36.1318 | -118.7784 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | Soda Springs 12kV out of Boxwood Sub | OH-4464511E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-14 | 22:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown | OORC1 | 5.23 | 2017-06-23T16:12:00Z | 4.99 | 1 | < 25mph
10004 |  | HUGHES LAKE | 2016-10-26 | 2016 | 12:19 | 34.7081 | -118.5367 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | ELIZABETH LAKE ROAD AND KINGS CANYON ROAD, LAKE HUGHES | OH-1586523E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-26 | 12:19 | Contact From Object |  | Vegetation | Electric Facility | Unknown | E5794 | 1.45 | 2016-01-28T08:37:00Z | 4.99 | 10 | < 25mph
|  | PATRICIA | 2016-09-16 | 2016 | 19:02 | 34.4851 | -119.3001 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ojai City Fire Department | OH-4797071E | OH-4797071E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-09-16 | 19:02 | Contact From Object |  | Vehicle | Pole | Unknown | ROVC1 | 7.69 | 2018-08-03T00:24:00Z | 14.99 | 25 | < 25mph
|  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE254 | 3.85 | 2020-11-21T11:00:00Z | 7.67 | 184 | < 25mph
|  | PALOMINO | 2015-10-09 | 2015 | 14:00 | 33.5752 | -117.17 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | BEHIND ADDRESS 28151 CELIA RD / PROPERTY LINE., STR 212903S | OH-212903S | Tier 2 | T2 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | F0145 | 7.52 | 2018-05-02T16:31:00Z | 10 | 28 | < 25mph
|  | La Mancha | 2020-07-05 | 2020 | 3:57 | 34.1325 | -118.8532 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1848406E | OH-1848406E | T3 | T3 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-07-05 | 3:57 | Equipment/Facility Failure | Insulator |  |  | Unknown | D5145 | 6.42 | 2017-05-18T20:37:00Z | 18.01 | 43 | < 25mph
|  | CACHUMA | 2016-08-18 | 2016 | 14:52 | 34.5356 | -119.8523 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-1413051E | OH-1413051E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-18 | 14:52 | Contact From Object |  | Vegetation | Communication Facility | Unknown | SE068 | 4.85 | 2020-02-16T08:10:00Z | 11.7 | 163 | < 25mph
|  | SANTA CLARA-TAYSHELL/ET-00423 | 2016-04-21 | 2016 | 12:20 | 34.3339 | -119.2748 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4434916E | OH-4434916E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2016-04-21 | 12:20 | Contact From Object |  | Animal | Electric Facility | Unknown | AT185 | 3.56 | 2016-09-24T08:07:00Z | 5.99 | 25 | < 25mph
|  | PATRICIA | 2017-04-16 | 2017 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4495331E | OH-4495331E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown | ROVC1 | 7.28 | 2018-07-18T23:24:00Z | 18.01 | 21 | < 25mph
|  | Python | 2015-06-06 | 2015 | 10:00 | 34.4043 | -118.4234 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | 16450 Alamo Canyon Rd, Canyon Country | OH-4779534E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-06-06 | 10:13 | Contact From Object |  | Animal | Electric Facility | None | CNIC1 | 3.54 | 2015-03-23T13:55:00Z | 28.01 | 28 | 25-40mph
|  | HUCKLEBERRY | 2017-03-17 | 2017 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4493863E | OH-4493863E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown | AU715 | 5.97 | 2015-10-14T01:03:00Z | 23 | 13 | < 25mph
|  | Mettler | 2020-08-10 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | OH-2093506E | OH-2093506E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Unknown | C1020 | 3.83 | 2020-02-18T19:15:00Z | 23 | 72 | < 25mph
|  | Zone | 2019-08-10 | 2019 | 13:00 | 34.3089 | -118.9413 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | VFD | OH-4734128E | OH-4734128E | Tier 3 | T3 | Y | AT&T Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | WLYC1 | 7.19 | 2017-02-22T07:49:00Z | 13 | 42 | < 25mph
| EDISON |  | 2016-05-12 | 2016 | -8 | 34.3135 | -119.1865 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | SE794 | 4.25 | 2020-08-14T16:50:00Z | 10.16 | 199 | < 25mph
|  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown | D5868 | 6.71 | 2018-09-06T13:57:00Z | 4.99 | 11 | < 25mph
|  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.54 | 2017-11-19T09:51:00Z | 24 | 91 | < 25mph
|  | Keller | 2015-06-09 | 2015 | 5:46 | 33.5986 | -117.1311 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 4401960E | OH-2297077E | Tier 2 | T2 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2015-06-09 | 5:46 | Contact From Object |  | Animal | Electric Facility | None | SRUC1 | 7.92 | 2020-07-09T10:54:00Z | 7 | 55 | < 25mph
|  | ARCHIE | 2018-11-13 | 2018 | 7:11 | 33.4928 | -117.2796 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | NORTH OF CARANCHO ON VIA CIELO | OH-4149859E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-13 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Unknown | E4050 | 5.17 | 2015-05-17T17:59:00Z | 13 | 36 | < 25mph
|  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other | C2900 | 7.95 | 2019-02-23T14:42:00Z | 11.01 | 44 | < 25mph
10004 |  | Peninsula | 2019-03-16 | 2019 | 17:58 | 33.6182 | -117.8025 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1729510E | OH-1729510E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-03-16 | 17:58 | Equipment/Facility Failure | Crossarm |  |  | Unknown | SE024 | 6.43 | 2020-11-18T19:30:00Z | 13.08 | 166 | < 25mph
|  | PYTHON | 2016-10-22 | 2016 | 15:17 | 34.3812 | -118.4132 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | RAR 0038 | OH-4860064E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-22 | 15:17 | Contact From Object |  | Balloons | Electric Facility | Unknown | SAUC1 | 6.81 | 2020-06-18T00:57:00Z | 26 | 165 | 25-40mph
| RYE |  | 2017-12-05 | 2017 | 11:31 | 34.4528 | -118.5819 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | C1909 | 5.98 | 2016-01-13T13:54:00Z | 10 | 18 | < 25mph
|  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | F0112 | 6.36 | 2019-01-21T18:30:00Z | 28.99 | 62 | 25-40mph
|  | VALLECITO | 2016-08-18 | 2016 | 19:00 | 34.4214 | -119.5964 | Other | Rural | Structure Only | Structure Only |  | Fire Agency | Santa Barbara County Fire Department | 2400 block of Whitney Avenue in Summerland | OH-1523986E | Tier 2 | T2 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | MTIC1 | 4.08 | 2018-09-23T15:47:00Z | 8.99 | 33 | < 25mph
|  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other | SE063 | 5.85 | 2018-09-06T13:10:00Z | 10.96 | 20 | < 25mph
|  | Calgrove | 2020-10-03 | 2020 | 17:45 | 34.357 | -118.5659 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | OH-2101062E | OH-2101062E | T3 | T3 |  | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | NHPC1 | 2.94 | 2017-08-05T20:56:00Z | 21 | 42 | < 25mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | ATNC1 | 4.83 | 2018-02-20T09:54:00Z | 12.01 | 1 | < 25mph
|  | Plateau | 2019-09-11 | 2019 | 8:08 | 34.0991 | -118.6793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4424792E | OH-4424792E | Tier 3 | T3 | Y | Verizon / AT&T / Crown Castle | 16 | Distribution | Conductor | Overhead | Yes | 2019-09-11 | 8:08 | Equipment/Facility Failure | Conductor |  | Electric Facility | Human Error | D2363 | 3.42 | 2019-11-05T17:05:00Z | 10 | 162 | < 25mph
|  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other | SE344 | 5.87 | 2019-11-09T20:00:00Z | 18.41 | 77 | < 25mph
|  | GUITAR | 2016-01-16 | 2016 | 15:20 | 34.4096 | -118.6816 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-848266E | OH-848266E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-01-16 | 15:20 | Equipment/Facility Failure | Other |  |  | Unknown | PU | 7.33 | 2018-01-09T03:00:00Z | 8.72 | 5 | < 25mph
|  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None | SE658 | 5.78 | 2020-10-02T09:20:00Z | 10.38 | 213 | < 25mph
|  | SPRINGVILLE-LINDSAY-VENIDA/ET-07230,SPRINGVILLE-STRATHMORE/ET-07256 | 2015-06-17 | 2015 | 17:29 | 36.1086 | -118.9425 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 722603E | OH-722604E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-06-17 | 17:29 | Contact From Object |  | Animal | Electric Facility | None | C1000 | 6.57 | 2015-10-09T18:50:00Z | 0 | 12 | < 25mph
|  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other | SE063 | 5.85 | 2020-04-22T04:30:00Z | 22.93 | 89 | < 25mph
10006 |  | Capanero | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | T2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Unknown | UHLC1 | 1.17 | 2016-05-25T13:59:00Z | 2.01 | 13 | < 25mph
|  | PYTHON | 2016-06-05 | 2016 | 15:59 | 34.4208 | -118.4218 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4154960E | OH-4154960E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-06-05 | 15:59 | Unknown |  |  |  | Unknown | CNIC1 | 4.67 | 2015-03-03T04:55:00Z | 22.01 | 21 | < 25mph
|  | Taiwan | 2015-07-13 | 2015 | 11:15 | 33.7678 | -117.7207 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | Cal Fire | Pole 960439E | OH-960439E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-07-13 | 13:30 | Unknown |  |  |  | Unknown | FRCC1 | 3.07 | 2015-05-18T19:51:00Z | 15.99 | 62 | < 25mph
|  | HUGHES LAKE/ED-08810 | 2018-07-06 | 2018 | 5:38 | 34.6744 | -118.4517 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | 465140E | OH-1938477E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-07-06 | 5:38 | Contact From Object |  | Vehicle | Pole | Unknown | GMTC1 | 3.15 | 2019-01-24T13:59:00Z | 23 | 9 | < 25mph
2 |  | Lopez | 2015-05-23 | 2015 | 11:57 | 34.3006 | -118.3613 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | Pole 1261671E | OH-1261671E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Conductor | Overhead | Yes | 2015-05-23 | 11:05 | Unknown |  |  |  | Unknown | KBUR | 6.98 | 2016-03-07T21:53:00Z | 27.63 | 37 | 25-40mph
|  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | LCBC1 | 6.83 | 2017-02-15T17:55:00Z | 13 | 31 | < 25mph
|  | Medusa | 2020-03-06 | 2020 | 17:05 | 34.0802 | -117.254 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1811355E | OH-1811355E | T2 | T2 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Other | AU239 | 7.19 | 2018-05-12T00:30:00Z | 15.99 | 30 | < 25mph
| TENAJA |  | 2019-09-04 | 2019 | 16:43 | 33.5285 | -117.2732 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | SDMEA | 2.99 | 2018-07-01T06:49:00Z | 10 | 18 | < 25mph
|  | SANTA CLARA-TAYSHELL/ET-00423 | 2016-04-21 | 2016 | 12:20 | 34.3339 | -119.2748 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4434916E | OH-4434916E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2016-04-21 | 12:20 | Contact From Object |  | Animal | Electric Facility | Unknown | SE470 | 6.24 | 2020-01-25T08:10:00Z | 9.64 | 83 | < 25mph
|  | VALLEY-MAYBERRY-MORENO-VISTA | 2020-05-18 | 2020 | 12:10 | 33.8587 | -117.0203 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire Perris | OH-1979539E | OH-1979539E | T3 | T3 | Y | None | 115 | Transmission | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Other | HSGC1 | 4.08 | 2016-07-21T01:16:00Z | 27 | 15 | 25-40mph
10004 |  | HUGHES LAKE | 2016-10-26 | 2016 | 12:19 | 34.7081 | -118.5367 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | ELIZABETH LAKE ROAD AND KINGS CANYON ROAD, LAKE HUGHES | OH-1586523E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-26 | 12:19 | Contact From Object |  | Vegetation | Electric Facility | Unknown | C4614 | 6.71 | 2016-04-12T22:00:00Z | 23 | 11 | < 25mph
|  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown | WTPC1 | 2.77 | 2017-08-22T03:57:00Z | 11.01 | 2 | < 25mph
|  | RHODA | 2016-12-30 | 2016 | 11:42 | 34.1231 | -118.723 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-1927507E | OH-1927507E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-12-30 | 11:42 | Contact From Object |  | Balloons | Electric Facility | Unknown | MBUC1 | 6.16 | 2017-11-23T04:56:00Z | 14 | 62 | < 25mph
|  | Maguire | 2015-04-17 | 2015 | 16:41 | 34.0851 | -118.8044 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles County Fire | Maguire 16kV out of Latigo Sub | OH-1199311E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2015-04-17 | 16:41 | Contact From Object |  | Vehicle | Pole | None | D1664 | 3.65 | 2016-03-17T09:26:00Z | 14 | 24 | < 25mph
|  | BENCH | 2018-06-26 | 2018 | 20:48 | 34.0158 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Holmes St/Wildwood Canyon Rd, Yucaipa | OH-4367391E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-26 | 20:48 | Contact From Object |  | Vehicle | Pole | Unknown | BNTC1 | 7.18 | 2015-10-25T01:14:00Z | 17 | 50 | < 25mph
|  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | F0063 | 5.09 | 2018-09-30T11:38:00Z | 4.99 | 74 | < 25mph
|  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.54 | 2018-08-27T20:51:00Z | 22.01 | 49 | < 25mph
|  | BENCH | 2018-06-26 | 2018 | 20:48 | 34.0158 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Holmes St/Wildwood Canyon Rd, Yucaipa | OH-4367391E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-26 | 20:48 | Contact From Object |  | Vehicle | Pole | Unknown | BNTC1 | 7.18 | 2015-08-20T15:14:00Z | 5.99 | 39 | < 25mph
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | BPOC1 | 4.63 | 2017-06-20T21:49:00Z | 21 | 10 | < 25mph
|  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force | TSHC1 | 6.99 | 2015-05-11T10:04:00Z | 12.01 | 9 | < 25mph
|  | SHOWDOWN | 2016-06-09 | 2016 | 11:28 | 34.5862 | -118.196 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4267121E | OH-4267121E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-09 | 11:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE063 | 2.98 | 2019-01-12T03:30:00Z | 14.03 | 35 | < 25mph
| MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | D2363 | 5.89 | 2019-03-02T14:35:00Z | 24.99 | 108 | < 25mph
|  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | MLCC1 | 7.93 | 2019-10-21T17:53:00Z | 23 | 48 | < 25mph
|  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown | WTPC1 | 2.77 | 2016-09-22T00:57:00Z | 20 | 2 | < 25mph
|  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | OJ | 0.4 | 2016-03-01T18:00:00Z | 4.92 | 13 | < 25mph
|  | PYTHON | 2016-06-05 | 2016 | 15:59 | 34.4208 | -118.4218 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4154960E | OH-4154960E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-06-05 | 15:59 | Unknown |  |  |  | Unknown | SE177 | 6.54 | 2020-08-15T04:50:00Z | 15.42 | 202 | < 25mph
|  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE258 | 5.3 | 2019-05-20T06:40:00Z | 39.01 | 19 | 25-40mph
10003 |  | SHEFFIELD | 2016-02-22 | 2016 | 17:04 | 34.4492 | -119.5845 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Montecito Fire Department | OH-1082380E | OH-1082380E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-02-22 | 17:04 | Equipment/Facility Failure | Conductor |  |  | Unknown | NTBC1 | 6.39 | 2016-03-15T23:00:00Z | 15.99 | 16 | < 25mph
|  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | ROVC1 | 7.44 | 2017-08-20T00:24:00Z | 18.01 | 14 | < 25mph
|  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error | AU563 | 7.19 | 2018-08-27T13:37:00Z | 28.99 | 21 | 25-40mph
|  | Calgrove | 2020-10-03 | 2020 | 17:45 | 34.357 | -118.5659 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | OH-2101062E | OH-2101062E | T3 | T3 |  | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | NHPC1 | 2.94 | 2016-10-04T11:56:00Z | 14.99 | 52 | < 25mph
|  | PATRICIA | 2017-04-16 | 2017 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4495331E | OH-4495331E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown | CSVC1 | 7.35 | 2017-01-16T08:09:00Z | 4 | 10 | < 25mph
|  | HUCKLEBERRY | 2017-03-17 | 2017 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4493863E | OH-4493863E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown | AU715 | 5.97 | 2015-02-02T14:13:00Z | 2.01 | 17 | < 25mph
|  | BENCH | 2018-06-26 | 2018 | 20:48 | 34.0158 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Holmes St/Wildwood Canyon Rd, Yucaipa | OH-4367391E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-26 | 20:48 | Contact From Object |  | Vehicle | Pole | Unknown | BNTC1 | 7.18 | 2016-12-29T00:14:00Z | 24 | 46 | < 25mph
|  | Vicasa | 2020-10-26 | 2020 | 11:56 | 34.0998 | -118.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | OH-795990E | OH-795990E | T3 | T3 |  | Frontier Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Weather | D2363 | 2.61 | 2017-04-20T03:51:00Z | 20 | 66 | < 25mph
|  | PATRICIA | 2017-04-16 | 2017 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4495331E | OH-4495331E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown | ROVC1 | 7.28 | 2020-03-01T20:24:00Z | 18.99 | 95 | < 25mph
|  | PALOMINO | 2015-10-09 | 2015 | 14:00 | 33.5752 | -117.17 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | BEHIND ADDRESS 28151 CELIA RD / PROPERTY LINE., STR 212903S | OH-212903S | Tier 2 | T2 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | SE969 | 3.92 | 2020-12-22T20:50:00Z | 16.15 | 184 | < 25mph
|  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force | CSWC1 | 5.63 | 2017-10-31T10:35:00Z | 4 | 8 | < 25mph
10007 |  | Vicasa | 2020-11-30 | 2020 | 21:02 | 34.0723 | -118.588 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles Fire Department | OH-4535641E | OH-4535641E | T3 | T3 |  | Verizon Wireless, AT&T Mobility, Frontier Communications, Crown Castle NG West, Inc | 16 | Distribution | Other | Overhead | Yes | 2020-11-30 | 21:02 | Contact From Object |  | Vehicle | Electric Facility | Outside Force | MBUC1 | 3.36 | 2019-01-31T19:56:00Z | 28.01 | 153 | 25-40mph
|  | HUGHES LAKE/ED-08810 | 2018-07-06 | 2018 | 5:38 | 34.6744 | -118.4517 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | 465140E | OH-1938477E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-07-06 | 5:38 | Contact From Object |  | Vehicle | Pole | Unknown | PPPC1 | 4.96 | 2019-10-01T08:56:00Z | 34 | 46 | 25-40mph
|  | KINSEY | 2016-07-08 | 2016 | 11:15 | 34.7906 | -118.8256 | Vegetation | Rural | 300 - 999 Acres | 300 - 999 Acres |  | Fire Agency | Kern County Fire Department | 1-5, Gorman | OH-4539401E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | PG241 | 5.06 | 2019-11-02T10:10:00Z | 20.76 | 30 | < 25mph
|  | MAYBELL | 2017-07-02 | 2017 | 8:24 | 34.0804 | -117.8552 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | OH-144184E | OH-1255315E | T2 200Ft Outer Buffer | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-07-02 | 8:24 | Contact From Object |  | Animal | Electric Facility | Unknown | STFC1 | 6.14 | 2016-11-27T12:57:00Z | 8.99 | 94 | < 25mph
|  | ELSTER | 2016-04-25 | 2016 | 19:15 | 36.1372 | -118.8615 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-X16345E | OH-X16345E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 120/240 V | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 19:15 | Equipment/Facility Failure | Conductor |  |  | Unknown | MOLC1 | 6.51 | 2016-09-14T17:27:00Z | 8.99 | 1 | < 25mph
|  | Northpark | 2019-06-20 | 2019 | 14:08 | 34.2298 | -117.4048 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | San Bern. FD | OH-201371S | OH-201371S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Human Error | SE701 | 5.99 | 2020-05-08T02:30:00Z | 16.89 | 264 | < 25mph
|  | CARVER | 2016-09-24 | 2016 | 14:20 | 35.7381 | -118.9546 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4784763E | OH-4784763E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-09-24 | 14:20 | Contact From Object |  | Animal | Electric Facility | Unknown | WOCC1 | 7.2 | 2019-04-13T08:13:00Z | 7 | 7 | < 25mph
|  | BIG CREEK 3-RECTOR NO.1/ET-01046 | 2015-09-03 | 2015 | 17:00 | 36.8936 | -119.4571 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | East of Watts Valley Rd and Pittman Hill Rd, East of Clovis | OH-7020930 | Tier 2 | T2 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2015-09-03 | 16:15 | Contact From Object |  | Balloons | Electric Facility | None | FCHC1 | 1.24 | 2018-11-07T06:00:00Z | 5.99 | 1 | < 25mph
|  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | TNRC1 | 5.88 | 2019-04-25T02:57:00Z | 11.01 | 98 | < 25mph
|  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE444 | 4.44 | 2019-11-09T08:20:00Z | 17.9 | 64 | < 25mph
|  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown | WMSC1 | 6.6 | 2015-12-26T22:53:00Z | 55.99 | 2 | 55mph+
|  | SKINKLE | 2016-05-29 | 2016 | 22:25 | 36.0091 | -118.9563 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-4566417E | OH-4566417E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-05-29 | 22:25 | Contact From Object |  | Other | Electric Facility | Unknown |  |  |  | 0 | 0 | No data
|  | Vicasa | 2020-10-26 | 2020 | 11:56 | 34.0998 | -118.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | OH-795990E | OH-795990E | T3 | T3 |  | Frontier Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Weather | TPGC1 | 2.63 | 2016-02-19T09:57:00Z | 12.01 | 68 | < 25mph
10007 |  | Vicasa | 2020-11-30 | 2020 | 21:02 | 34.0723 | -118.588 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles Fire Department | OH-4535641E | OH-4535641E | T3 | T3 |  | Verizon Wireless, AT&T Mobility, Frontier Communications, Crown Castle NG West, Inc | 16 | Distribution | Other | Overhead | Yes | 2020-11-30 | 21:02 | Contact From Object |  | Vehicle | Electric Facility | Outside Force | MBCC1 | 6.65 | 2020-08-31T21:56:00Z | 32 | 252 | 25-40mph
|  | Mettler | 2020-08-10 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | OH-2093506E | OH-2093506E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Unknown | E3266 | 6.59 | 2017-07-24T08:34:00Z | 8.99 | 25 | < 25mph
| TENAJA |  | 2019-09-04 | 2019 | 16:43 | 33.5285 | -117.2732 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | HP012 | 7.67 | 2017-12-31T08:26:00Z | 12.75 | 20 | < 25mph
|  | Hughes Lake | 2019-09-02 | 2019 | 14:02 | 34.7026 | -118.342 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4782978E | OH-4782978E | Tier 2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-02 | 14:02 | Contact From Object |  | Balloons | Electric Facility | Other | PPPC1 | 3.45 | 2017-01-26T09:56:00Z | 13 | 20 | < 25mph
|  | Elster | 2019-09-21 | 2019 | 10:53 | 36.1026 | -118.8659 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4252581E | OH-4252581E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-21 | 10:53 | Contact From Object |  | Vehicle | Electric Facility | Human Error | SE282 | 6.36 | 2020-05-23T16:40:00Z | 11.84 | 60 | < 25mph
|  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | TNRC1 | 5.88 | 2017-01-08T04:57:00Z | 17 | 121 | < 25mph
|  | SODA SPRINGS | 2016-06-21 | 2016 | 21:47 | 36.2515 | -118.7809 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4391218E | OH-4391218E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-21 | 21:47 | Contact From Object |  | Vegetation | Electric Facility | Unknown | TT625 | 4.02 | 2020-09-11T23:49:00Z | 7 | 31 | < 25mph
10003 |  | SHEFFIELD | 2016-02-22 | 2016 | 17:04 | 34.4492 | -119.5845 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Montecito Fire Department | OH-1082380E | OH-1082380E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-02-22 | 17:04 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE234 | 5.48 | 2019-09-18T16:10:00Z | 6.87 | 95 | < 25mph
| OAK |  | 2019-10-28 | 2019 | 8:42 | 34.1489 | -118.6954 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | D2363 | 6.43 | 2015-06-19T13:08:00Z | 18.99 | 40 | < 25mph
|  | WELCH | 2016-04-25 | 2016 | 15:23 | 35.8387 | -118.9147 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1078325E | OH-1078325E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 15:23 | Equipment/Facility Failure | Insulator |  |  | Unknown | FTNC1 | 3.62 | 2017-06-22T20:00:00Z | 14.99 | 1 | < 25mph
|  | PALOMINO | 2015-10-09 | 2015 | 14:00 | 33.5752 | -117.17 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | BEHIND ADDRESS 28151 CELIA RD / PROPERTY LINE., STR 212903S | OH-212903S | Tier 2 | T2 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | SRUC1 | 5.21 | 2018-07-18T04:54:00Z | 12.01 | 27 | < 25mph
| ELLIS |  | 2017-10-18 | 2017 | 11:18 | 33.7721 | -117.2173 | Vegetation | Rural | Unknown |  | Unknown | Fire Agency | Cal Fire | [17 empty] | Weather | SE033 | 6.73 | 2019-04-11T16:30:00Z | 9.22 | 42 | < 25mph
|  | Calgrove | 2020-10-03 | 2020 | 17:45 | 34.357 | -118.5659 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | OH-2101062E | OH-2101062E | T3 | T3 |  | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | SE079 | 2.48 | 2020-10-25T12:30:00Z | 16.22 | 200 | < 25mph
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | ERYC1 | 5.82 | 2017-03-31T10:00:00Z | 37.29 | 7 | 25-40mph
| EDISON |  | 2016-05-12 | 2016 | -8 | 34.3135 | -119.1865 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | E8097 | 6.25 | 2018-07-07T08:03:00Z | 7 | 98 | < 25mph
|  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other | PPPC1 | 1.78 | 2016-06-12T01:56:00Z | 50 | 2 | 40-55mph
|  | TUNA | 2016-09-19 | 2016 | 6:11 | 34.04 | -118.6687 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-1638513E | OH-1638513E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | MBUC1 | 2.01 | 2015-01-27T21:56:00Z | 23 | 25 | < 25mph
|  | HUCKLEBERRY | 2017-03-17 | 2017 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4493863E | OH-4493863E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE608 | 3.49 | 2020-09-04T15:10:00Z | 9.72 | 172 | < 25mph
|  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force | SE232 | 7.53 | 2019-08-03T00:30:00Z | 26.75 | 53 | 25-40mph
|  | PATRICIA | 2016-09-16 | 2016 | 19:02 | 34.4851 | -119.3001 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ojai City Fire Department | OH-4797071E | OH-4797071E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-09-16 | 19:02 | Contact From Object |  | Vehicle | Pole | Unknown | CSVC1 | 6.69 | 2017-08-11T09:09:00Z | 4 | 6 | < 25mph
|  | GUITAR | 2016-01-16 | 2016 | 15:20 | 34.4096 | -118.6816 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-848266E | OH-848266E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-01-16 | 15:20 | Equipment/Facility Failure | Other |  |  | Unknown | SE693 | 2.69 | 2020-11-05T02:50:00Z | 12.64 | 183 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:26 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | Unknown | FRCC1 | 7.87 | 2019-01-23T04:51:00Z | 53.02 | 86 | 40-55mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | SE132 | 6.92 | 2019-06-12T22:30:00Z | 23.89 | 121 | < 25mph
|  | PATRICIA | 2016-10-23 | 2016 | 9:40 | 34.4603 | -119.2853 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | 900 Rice Road Ojai | OH-786960E | Tier 3 | T3 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | CSVC1 | 6.08 | 2016-05-21T16:09:00Z | 7 | 3 | < 25mph
| MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | D2363 | 5.89 | 2017-08-25T10:21:00Z | 14 | 72 | < 25mph
|  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | SE047 | 3.1 | 2019-04-22T13:50:00Z | 6.24 | 54 | < 25mph
|  | Mettler | 2020-08-10 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | OH-2093506E | OH-2093506E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Unknown | KTSP | 6.1 | 2018-06-01T20:15:00Z | 20.71 | 33 | < 25mph
|  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | OJ | 0.4 | 2017-06-23T04:00:00Z | 7.38 | 9 | < 25mph
|  | MIST | 2016-08-24 | 2016 | 16:37 | 34.4665 | -120.0701 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Santa Barbara County Fire Department | Refiugio Canyon, Santa Barbara | OH-4538468E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-24 | 18:50 | Contact From Object |  | Animal | Electric Facility | Unknown | SE241 | 2.95 | 2019-09-06T15:40:00Z | 4.03 | 27 | < 25mph
|  | Zone | 2019-08-10 | 2019 | 13:00 | 34.3089 | -118.9413 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | VFD | OH-4734128E | OH-4734128E | Tier 3 | T3 | Y | AT&T Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | AT184 | 5.07 | 2016-07-31T14:28:00Z | 20 | 50 | < 25mph
|  | CACHUMA | 2016-08-18 | 2016 | 14:52 | 34.5356 | -119.8523 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-1413051E | OH-1413051E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-18 | 14:52 | Contact From Object |  | Vegetation | Communication Facility | Unknown | F3082 | 5.83 | 2017-01-06T19:31:00Z | 11.01 | 113 | < 25mph
|  | BENCH | 2018-06-26 | 2018 | 20:48 | 34.0158 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Holmes St/Wildwood Canyon Rd, Yucaipa | OH-4367391E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-26 | 20:48 | Contact From Object |  | Vehicle | Pole | Unknown | MMKC1 | 4.65 | 2017-05-08T07:34:00Z | 11.01 | 46 | < 25mph
4 |  | PYTHON | 2016-12-02 | 2016 | 21:26 | 34.3812 | -118.4132 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | OH-4572770E | OH-4572770E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vegetation | Electric Facility | Unknown | SAUC1 | 6.81 | 2016-11-29T20:57:00Z | 32.99 | 33 | 25-40mph
|  | Python | 2015-06-06 | 2015 | 10:00 | 34.4043 | -118.4234 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | 16450 Alamo Canyon Rd, Canyon Country | OH-4779534E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-06-06 | 10:13 | Contact From Object |  | Animal | Electric Facility | None | CNIC1 | 3.54 | 2019-10-05T02:55:00Z | 18.01 | 112 | < 25mph
|  | Medusa | 2020-03-06 | 2020 | 17:05 | 34.0802 | -117.254 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1811355E | OH-1811355E | T2 | T2 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Other | AU239 | 7.19 | 2015-08-27T02:10:00Z | 14.99 | 19 | < 25mph
|  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | KNWC1 | 3.86 | 2017-07-08T18:17:00Z | 13 | 25 | < 25mph
|  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | MBCC1 | 5.33 | 2018-04-28T02:56:00Z | 13 | 60 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:26 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | Unknown | FRCC1 | 7.87 | 2019-08-16T00:51:00Z | 17 | 120 | < 25mph
|  | Enchanted | 2019-08-25 | 2019 | 8:03 | 34.301 | -118.8308 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4754475E | OH-4754475E | Tier 3 | T3 | Y | NA | 16 | Distribution | Lightning Arrestor | Overhead | Yes | 2019-08-25 | 8:03 | Contact From Object |  | Animal | Electric Facility | Other | WLYC1 | 4.92 | 2018-03-03T02:49:00Z | 24.99 | 60 | < 25mph
|  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | LPDC1 | 5.12 | 2020-06-14T01:55:00Z | 33 | 84 | 25-40mph
10006 |  | Capanero | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | T2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Unknown | UHLC1 | 1.17 | 2016-02-23T13:59:00Z | 8.99 | 13 | < 25mph
|  | POULTRY | 2018-09-21 | 2018 | 8:28 | 34.0728 | -117.0397 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Juniper St. Yucaipa | OH-129241E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | MMKC1 | 0.63 | 2017-02-02T12:34:00Z | 12.01 | 57 | < 25mph
10006 |  | CONCEPCION | 2016-05-12 | 2016 | 8:55 | 34.4736 | -120.216 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-708452E | OH-708452E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-12 | 8:55 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UP481 | 0.62 | 2017-04-01T17:55:00Z | 4.03 | 11 | < 25mph
|  | METTLER | 2017-06-02 | 2017 | 10:50 | 35.1021 | -118.5328 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4416566E | OH-4416566E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | C8288 | 2.97 | 2017-04-30T08:08:00Z | 7 | 39 | < 25mph
| MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | D2363 | 5.89 | 2019-12-08T20:12:00Z | 35.99 | 192 | 25-40mph
|  | ELSTER | 2016-04-25 | 2016 | 19:15 | 36.1372 | -118.8615 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-X16345E | OH-X16345E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 120/240 V | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 19:15 | Equipment/Facility Failure | Conductor |  |  | Unknown | MOLC1 | 6.51 | 2015-02-21T23:27:00Z | 7 | 1 | < 25mph
|  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | NTBC1 | 7.63 | 2019-01-12T07:00:00Z | 21.99 | 28 | < 25mph
|  | Atlanta | 2015-05-05 | 2015 | 16:00 | 33.711 | -117.7089 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 4229158E | OH-4229158E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.92 | 2020-08-27T20:51:00Z | 18 | 175 | < 25mph
|  | Conestoga | 2020-06-13 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Other | TR118 | 5.47 | 2017-05-02T17:26:00Z | 15.99 | 39 | < 25mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | E1966 | 3.22 | 2018-06-04T22:56:00Z | 18.99 | 4 | < 25mph
| THOMAS |  | 2017-12-04 | 2017 | 18:28 | 34.4152 | -119.0912 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | USFS | [17 empty] | Weather | AT490 | 3.89 | 2016-05-17T20:50:00Z | 14.99 | 78 | < 25mph
|  | ELSTER | 2016-04-25 | 2016 | 19:15 | 36.1372 | -118.8615 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-X16345E | OH-X16345E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 120/240 V | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 19:15 | Equipment/Facility Failure | Conductor |  |  | Unknown | MOLC1 | 6.51 | 2018-08-05T19:27:00Z | 12.01 | 1 | < 25mph
|  | BRUMFIELD | 2016-06-04 | 2016 | 10:17 | 33.5947 | -117.1387 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-2206630E | OH-2206630E | Tier 2 | T2 | Y |  | 12 | Distribution | Transformer | Overhead | Yes | 2016-06-04 | 10:17 | Equipment/Facility Failure | Transformer |  |  | Unknown | SRUC1 | 7.42 | 2016-01-28T10:54:00Z | 12.01 | 26 | < 25mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | ATNC1 | 4.83 | 2017-04-05T14:54:00Z | 8.01 | 1 | < 25mph
|  | PATRICIA | 2016-09-16 | 2016 | 19:02 | 34.4851 | -119.3001 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ojai City Fire Department | OH-4797071E | OH-4797071E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-09-16 | 19:02 | Contact From Object |  | Vehicle | Pole | Unknown | CSVC1 | 6.69 | 2016-03-24T11:09:00Z | 4 | 6 | < 25mph
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | BPOC1 | 4.63 | 2017-10-01T21:49:00Z | 30 | 12 | 25-40mph
|  | Atento | 2015-05-30 | 2015 | 15:26 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | Unknown | SE080 | 5.34 | 2019-02-23T19:50:00Z | 13.15 | 77 | < 25mph
|  | MIST | 2016-08-24 | 2016 | 16:37 | 34.4665 | -120.0701 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Santa Barbara County Fire Department | Refiugio Canyon, Santa Barbara | OH-4538468E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-24 | 18:50 | Contact From Object |  | Animal | Electric Facility | Unknown | RHWC1 | 3.48 | 2016-12-28T04:06:00Z | 23 | 11 | < 25mph
| RYE |  | 2017-12-05 | 2017 | 15:00 | 34.2676 | -117.844 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | TANC1 | 6.35 | 2019-08-29T19:01:00Z | 12.01 | 8 | < 25mph
2 |  | Lopez | 2015-05-23 | 2015 | 11:57 | 34.3006 | -118.3613 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | Pole 1261671E | OH-1261671E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Conductor | Overhead | Yes | 2015-05-23 | 11:05 | Unknown |  |  |  | Unknown | CNIC1 | 4.89 | 2018-12-01T03:55:00Z | 32.01 | 61 | 25-40mph
|  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error | SE678 | 6.69 | 2020-07-25T05:20:00Z | 11.33 | 167 | < 25mph
|  | Enchanted | 2019-08-25 | 2019 | 8:03 | 34.301 | -118.8308 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4754475E | OH-4754475E | Tier 3 | T3 | Y | NA | 16 | Distribution | Lightning Arrestor | Overhead | Yes | 2019-08-25 | 8:03 | Contact From Object |  | Animal | Electric Facility | Other | WLYC1 | 4.92 | 2017-02-15T13:49:00Z | 24.99 | 34 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | SE132 | 6.92 | 2020-04-29T03:50:00Z | 15.12 | 122 | < 25mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | SE273 | 3.51 | 2020-02-17T09:00:00Z | 13.15 | 54 | < 25mph
|  | CUDDEBACK | 2017-08-08 | 2017 | 17:52 | 35.1342 | -118.5607 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4179753E | OH-4179753E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-08-08 | 17:52 | Contact From Object |  | Vehicle | Electric Facility | Unknown | C1020 | 3.61 | 2019-04-27T03:24:00Z | 20 | 59 | < 25mph
|  | CABANA | 2017-10-16 | 2017 | 6:11 | 34.0217 | -117.5069 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1670014E | OH-1670014E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-10-16 | 6:11 | Contact From Object |  | Balloons | Electric Facility | Unknown | E7239 | 2.66 | 2016-03-04T18:55:00Z | 7 | 17 | < 25mph
10005 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | D5145 | 7.89 | 2015-05-21T14:57:00Z | 4.99 | 39 | < 25mph
|  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | MBCC1 | 6.95 | 2018-08-27T03:56:00Z | 12.01 | 119 | < 25mph
|  | TICO | 2016-04-28 | 2016 | 14:00 | 34.357 | -119.314 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura County FD | OH-1604151E | OH-1604151E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-04-28 | 14:00 | Equipment/Facility Failure | Other |  |  | Unknown | AT185 | 1.35 | 2016-01-11T17:11:00Z | 5.99 | 22 | < 25mph
|  | POULTRY | 2018-09-21 | 2018 | 8:28 | 34.0728 | -117.0397 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Juniper St. Yucaipa | OH-129241E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | MMKC1 | 0.63 | 2015-09-08T22:34:00Z | 18.99 | 52 | < 25mph
|  | Medusa | 2020-03-06 | 2020 | 17:05 | 34.0802 | -117.254 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1811355E | OH-1811355E | T2 | T2 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Other | UP629 | 3.4 | 2016-04-29T07:45:00Z | 4.94 | 29 | < 25mph
|  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather | CEKC1 | 7.88 | 2019-04-30T17:54:00Z | 14.99 | 74 | < 25mph
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | BPOC1 | 4.63 | 2018-07-25T03:49:00Z | 13 | 11 | < 25mph
|  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | TNRC1 | 5.88 | 2015-01-25T09:57:00Z | 48 | 52 | 40-55mph
|  | Zone | 2015-04-27 | 2015 | 19:10 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 4734128E | OH-4734128E | Tier 3 | T3 | Y |  | 16 | Distribution | Other | Overhead | Yes | 2015-04-27 | 19:10 | Equipment/Facility Failure | Other |  |  | Unknown | WLYC1 | 7.19 | 2015-02-26T03:49:00Z | 12.01 | 31 | < 25mph
|  | BIG CREEK 3-RECTOR NO.1/ET-01046 | 2015-09-03 | 2015 | 17:00 | 36.8936 | -119.4571 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | East of Watts Valley Rd and Pittman Hill Rd, East of Clovis | OH-7020930 | Tier 2 | T2 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2015-09-03 | 16:15 | Contact From Object |  | Balloons | Electric Facility | None | FCHC1 | 1.24 | 2015-07-09T20:00:00Z | 14.99 | 1 | < 25mph
|  | Penstock | 2019-09-18 | 2019 | 2:52 | 34.3143 | -117.3793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4066969E | OH-4066969E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Human Error | MNCC1 | 7.1 | 2017-09-06T13:16:00Z | 10 | 37 | < 25mph
| OAK |  | 2019-10-28 | 2019 | 8:42 | 34.1489 | -118.6954 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | SE204 | 5.4 | 2020-01-15T17:20:00Z | 11.54 | 194 | < 25mph
|  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error | AU563 | 7.19 | 2019-05-15T23:26:00Z | 30 | 33 | 25-40mph
|  | RHODA | 2016-12-30 | 2016 | 11:42 | 34.1231 | -118.723 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-1927507E | OH-1927507E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-12-30 | 11:42 | Contact From Object |  | Balloons | Electric Facility | Unknown | CEEC1 | 4.39 | 2016-08-16T12:38:00Z | 12.01 | 44 | < 25mph
|  | GUITAR | 2017-05-11 | 2017 | 12:27 | 34.4127 | -118.6702 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-848255E | OH-848255E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-05-11 | 12:27 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE040 | 2.19 | 2020-08-10T01:40:00Z | 20.6 | 129 | < 25mph
|  | Kickapoo Trail | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1941931E | OH-1941931E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Unknown | UCBU | 5.62 | 2016-11-26T00:00:00Z | 14.41 | 18 | < 25mph
|  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | MSJC1 | 4.82 | 2017-11-26T18:53:00Z | 14.99 | 25 | < 25mph
|  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | MBUC1 | 5.76 | 2016-01-20T12:56:00Z | 14 | 56 | < 25mph
|  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown | LYQC1 | 4.98 | 2018-07-07T06:18:00Z | 18.99 | 1 | < 25mph
|  | Conestoga | 2020-06-13 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Other | D7531 | 4.06 | 2017-12-30T18:04:00Z | 8.99 | 34 | < 25mph
|  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | CEEC1 | 6.07 | 2019-01-15T03:38:00Z | 17 | 123 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TNRC1 | 2.34 | 2015-08-06T10:57:00Z | 11.01 | 98 | < 25mph
|  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | SDPRR | 7.34 | 2015-11-22T03:49:00Z | 20 | 9 | < 25mph
|  | DRISKILL | 2016-10-18 | 2016 | 18:41 | 34.4687 | -119.7722 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Santa Barbara Fire Department | OH-2178476E | OH-2178476E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-18 | 18:41 | Equipment/Facility Failure | Fuse |  |  | Unknown | AS714 | 5.43 | 2018-05-14T22:51:00Z | 21 | 147 | < 25mph
|  | Sexton | 2015-02-22 | 2015 | 9:52 | 34.2849 | -119.2173 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura Fire Department | Pole 1718768E | OH-1718768E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-02-22 | 10:49 | Unknown |  |  |  | None | AR137 | 1.99 | 2015-06-25T02:44:00Z | 10.98 | 16 | < 25mph
|  | HUCKLEBERRY | 2017-03-17 | 2017 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4493863E | OH-4493863E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE015 | 7.17 | 2019-07-26T00:10:00Z | 12.93 | 46 | < 25mph
2 |  | Lopez | 2015-05-23 | 2015 | 11:57 | 34.3006 | -118.3613 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | Pole 1261671E | OH-1261671E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Conductor | Overhead | Yes | 2015-05-23 | 11:05 | Unknown |  |  |  | Unknown | SE099 | 3.82 | 2020-10-15T08:10:00Z | 19.44 | 127 | < 25mph
|  | CACHUMA | 2016-08-18 | 2016 | 14:52 | 34.5356 | -119.8523 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-1413051E | OH-1413051E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-18 | 14:52 | Contact From Object |  | Vegetation | Communication Facility | Unknown | MPWC1 | 4.41 | 2018-09-27T03:06:00Z | 15.99 | 122 | < 25mph
|  | BIG CREEK 1-RECTOR/ET-01082 | 2018-08-04 | 2018 | 0:43 | 37.1895 | -119.2738 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | OH-7021454 | OH-7021454 | Tier 3 | T3 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2018-08-04 | 2:21 | Equipment/Facility Failure | Other |  |  | Unknown | SHVC1 | 3.7 | 2017-01-09T12:56:00Z | 17 | 1 | < 25mph
|  | DALBA | 2017-07-11 | 2017 | 18:06 | 34.2054 | -117.1143 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-919465E | OH-919465E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 2.4 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | HHPC1 | 2.47 | 2017-07-29T17:15:00Z | 14.99 | 54 | < 25mph
|  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | SE070 | 7.19 | 2019-06-04T17:30:00Z | 10.29 | 66 | < 25mph
|  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather | KBUR | 7.65 | 2017-03-21T19:53:00Z | 19.57 | 29 | < 25mph
|  | Medusa | 2020-03-06 | 2020 | 17:05 | 34.0802 | -117.254 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1811355E | OH-1811355E | T2 | T2 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Other | SDSBO | 3.04 | 2017-07-15T04:49:00Z | 7 | 29 | < 25mph
2 |  | Lopez | 2015-05-23 | 2015 | 11:57 | 34.3006 | -118.3613 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | Pole 1261671E | OH-1261671E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Conductor | Overhead | Yes | 2015-05-23 | 11:05 | Unknown |  |  |  | Unknown | CNIC1 | 4.89 | 2020-08-30T20:55:00Z | 23 | 109 | < 25mph
|  | KINSEY | 2016-07-08 | 2016 | 11:15 | 34.7906 | -118.8256 | Vegetation | Rural | 300 - 999 Acres | 300 - 999 Acres |  | Fire Agency | Kern County Fire Department | 1-5, Gorman | OH-4539401E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | KSDB | 6.6 | 2018-05-15T19:53:00Z | 27.63 | 2 | 25-40mph
| THOMAS |  | 2017-12-04 | 2017 | 18:28 | 34.4152 | -119.0912 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | USFS | [17 empty] | Weather | AT490 | 3.89 | 2015-04-13T21:17:00Z | 15.99 | 43 | < 25mph
| STAR |  | 2019-07-28 | 2019 | 14:00 | 33.9975 | -117.7698 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Chino Valley Fire Department | [13 empty] | Contact From Object |  | Bird |  | Weather | TNRC1 | 4.58 | 2015-06-25T20:57:00Z | 18.01 | 50 | < 25mph
|  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | MBCC1 | 6.95 | 2016-03-04T03:56:00Z | 11.01 | 66 | < 25mph
|  | BIG CREEK 1-RECTOR/ET-01082 | 2018-08-04 | 2018 | 0:43 | 37.1895 | -119.2738 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | OH-7021454 | OH-7021454 | Tier 3 | T3 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2018-08-04 | 2:21 | Equipment/Facility Failure | Other |  |  | Unknown | SE818 | 1.92 | 2020-12-31T08:20:00Z | 7.24 | 53 | < 25mph
|  | SANTA CLARA-TAYSHELL/ET-00423 | 2016-04-21 | 2016 | 12:20 | 34.3339 | -119.2748 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4434916E | OH-4434916E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2016-04-21 | 12:20 | Contact From Object |  | Animal | Electric Facility | Unknown | SE230 | 3.69 | 2020-07-24T22:20:00Z | 18.06 | 141 | < 25mph
10005 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error | LPDC1 | 6.51 | 2018-01-07T06:55:00Z | 15.99 | 11 | < 25mph
|  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE193 | 5.64 | 2020-02-23T14:30:00Z | 6.58 | 60 | < 25mph
| RYE |  | 2017-12-05 | 2017 | 15:00 | 34.2676 | -117.844 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | TANC1 | 6.35 | 2016-02-08T09:01:00Z | 17 | 1 | < 25mph
|  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | CEEC1 | 7.72 | 2019-08-01T11:38:00Z | 8.01 | 171 | < 25mph
|  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.54 | 2017-02-27T14:51:00Z | 12.01 | 98 | < 25mph
|  | BRUMFIELD | 2016-06-04 | 2016 | 10:17 | 33.5947 | -117.1387 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-2206630E | OH-2206630E | Tier 2 | T2 | Y |  | 12 | Distribution | Transformer | Overhead | Yes | 2016-06-04 | 10:17 | Equipment/Facility Failure | Transformer |  |  | Unknown | SRUC1 | 7.42 | 2020-10-02T12:54:00Z | 9 | 186 | < 25mph
|  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | SDLEL | 7.13 | 2016-12-03T21:49:00Z | 12.01 | 13 | < 25mph
|  | Bonanza | 2020-06-05 | 2020 | 17:33 | 35.7635 | -118.4218 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Kern County Fire Department | OH-4451126E | OH-4451126E | T3 | T3 | Y | None | 12 | Distribution | Other | Overhead | Yes | 2020-06-05 | 17:33 | Contact From Object |  | Animal | Electric Facility | Other | SE113 | 7.43 | 2018-11-27T04:20:00Z | 12.06 | 13 | < 25mph
|  | Zone | 2015-04-27 | 2015 | 19:10 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 4734128E | OH-4734128E | Tier 3 | T3 | Y |  | 16 | Distribution | Other | Overhead | Yes | 2015-04-27 | 19:10 | Equipment/Facility Failure | Other |  |  | Unknown | WLYC1 | 7.19 | 2016-10-07T19:49:00Z | 37 | 51 | 25-40mph
|  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force | LYQC1 | 1.86 | 2017-09-16T08:18:00Z | 12.01 | 5 | < 25mph
| EDISON |  | 2016-05-12 | 2016 | -8 | 34.3135 | -119.1865 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | E8097 | 6.25 | 2017-08-05T12:47:00Z | 8.01 | 84 | < 25mph
10002 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | CEEC1 | 3.51 | 2018-08-12T15:38:00Z | 18.01 | 79 | < 25mph
10002 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | SE146 | 7.93 | 2019-12-29T12:20:00Z | 10.74 | 130 | < 25mph
|  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | SE227 | 7.96 | 2020-12-09T21:00:00Z | 14.83 | 176 | < 25mph
|  | Maguire | 2015-04-17 | 2015 | 16:41 | 34.0851 | -118.8044 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles County Fire | Maguire 16kV out of Latigo Sub | OH-1199311E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2015-04-17 | 16:41 | Contact From Object |  | Vehicle | Pole | None | OOSC1 | 7.73 | 2020-10-08T12:45:00Z | 10.1 | 205 | < 25mph
|  | DALBA | 2017-07-11 | 2017 | 18:06 | 34.2054 | -117.1143 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-919465E | OH-919465E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 2.4 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | HHPC1 | 2.47 | 2018-10-09T08:15:00Z | 8.01 | 65 | < 25mph
|  | SPRINGVILLE-LINDSAY-VENIDA/ET-07230,SPRINGVILLE-STRATHMORE/ET-07256 | 2015-06-17 | 2015 | 17:29 | 36.1086 | -118.9425 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 722603E | OH-722604E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-06-17 | 17:29 | Contact From Object |  | Animal | Electric Facility | None | SE279 | 3.12 | 2020-02-08T03:40:00Z | 9.28 | 45 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TNRC1 | 2.34 | 2016-03-16T00:57:00Z | 14.99 | 102 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:26 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | Unknown | SNPC1 | 6.52 | 2020-07-31T14:20:00Z | 17.99 | 173 | < 25mph
|  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other | UCBU | 3.92 | 2018-01-25T06:40:00Z | 19.19 | 19 | < 25mph
|  | Zone | 2015-04-27 | 2015 | 19:10 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 4734128E | OH-4734128E | Tier 3 | T3 | Y |  | 16 | Distribution | Other | Overhead | Yes | 2015-04-27 | 19:10 | Equipment/Facility Failure | Other |  |  | Unknown | WLYC1 | 7.19 | 2017-09-14T07:49:00Z | 13 | 41 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:30 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | None | E3131 | 6.3 | 2016-12-17T12:30:00Z | 14 | 41 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:30 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | None | SNPC1 | 6.52 | 2020-06-13T05:30:00Z | 16.99 | 165 | < 25mph
|  | MIST | 2016-08-24 | 2016 | 16:37 | 34.4665 | -120.0701 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Santa Barbara County Fire Department | Refiugio Canyon, Santa Barbara | OH-4538468E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-24 | 18:50 | Contact From Object |  | Animal | Electric Facility | Unknown | C6499 | 7.68 | 2015-02-03T12:33:00Z | 3 | 12 | < 25mph
|  | Hughes Lake | 2019-09-02 | 2019 | 14:02 | 34.7026 | -118.342 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4782978E | OH-4782978E | Tier 2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-02 | 14:02 | Contact From Object |  | Balloons | Electric Facility | Other | GMTC1 | 5.92 | 2017-10-23T18:59:00Z | 23 | 28 | < 25mph
|  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other | LPDC1 | 2.12 | 2018-03-03T09:55:00Z | 28.99 | 13 | 25-40mph
|  | Wildomar | 2019-09-19 | 2019 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside County FD | OH-2225310E | OH-2225310E | Tier 3 | T3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other | SE430 | 2.54 | 2020-06-21T12:10:00Z | 7.81 | 70 | < 25mph
| EASY |  | 2019-10-30 | 2019 | 6:00 | 34.2822 | -118.8034 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | E1625 | 7.52 | 2017-05-03T01:45:00Z | 13 | 44 | < 25mph
|  | Zone | 2019-08-10 | 2019 | 13:00 | 34.3089 | -118.9413 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | VFD | OH-4734128E | OH-4734128E | Tier 3 | T3 | Y | AT&T Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | WLYC1 | 7.19 | 2016-02-15T20:49:00Z | 50 | 47 | 40-55mph
|  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | D2363 | 4.48 | 2017-07-03T11:09:00Z | 11.01 | 75 | < 25mph
| OAK |  | 2019-10-28 | 2019 | 8:42 | 34.1489 | -118.6954 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | TPGC1 | 5.19 | 2015-03-26T00:57:00Z | 32.01 | 41 | 25-40mph
10005 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error | LPDC1 | 6.51 | 2019-02-15T05:55:00Z | 42.01 | 30 | 40-55mph
|  | KINSEY | 2016-07-08 | 2016 | 11:15 | 34.7906 | -118.8256 | Vegetation | Rural | 300 - 999 Acres | 300 - 999 Acres |  | Fire Agency | Kern County Fire Department | 1-5, Gorman | OH-4539401E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | KSDB | 6.6 | 2017-09-12T19:53:00Z | 26.46 | 3 | 25-40mph
|  | Plateau | 2019-09-11 | 2019 | 8:08 | 34.0991 | -118.6793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4424792E | OH-4424792E | Tier 3 | T3 | Y | Verizon / AT&T / Crown Castle | 16 | Distribution | Conductor | Overhead | Yes | 2019-09-11 | 8:08 | Equipment/Facility Failure | Conductor |  | Electric Facility | Human Error | SE284 | 3.54 | 2020-05-11T17:40:00Z | 18.19 | 208 | < 25mph
| OAK |  | 2019-10-28 | 2019 | 8:42 | 34.1489 | -118.6954 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | SE204 | 5.4 | 2020-10-21T02:50:00Z | 12.13 | 294 | < 25mph
4 |  | ANZAR | 2017-06-04 | 2017 | 13:14 | 33.8373 | -117.4863 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-1757417E | OH-1757417E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2017-06-04 | 13:14 | Wire-Wire Contact |  |  |  | Unknown | TSCC1 | 5.76 | 2015-01-31T16:41:00Z | 15.99 | 45 | < 25mph
|  | VALLECITO | 2016-08-18 | 2016 | 19:00 | 34.4214 | -119.5964 | Other | Rural | Structure Only | Structure Only |  | Fire Agency | Santa Barbara County Fire Department | 2400 block of Whitney Avenue in Summerland | OH-1523986E | Tier 2 | T2 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | NTBC1 | 5.13 | 2020-06-16T18:54:00Z | 11.99 | 244 | < 25mph
|  | GUITAR | 2016-01-16 | 2016 | 15:20 | 34.4096 | -118.6816 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-848266E | OH-848266E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-01-16 | 15:20 | Equipment/Facility Failure | Other |  |  | Unknown | SE437 | 3.94 | 2020-10-18T00:40:00Z | 18.41 | 195 | < 25mph
|  | Atlanta | 2015-05-05 | 2015 | 16:00 | 33.711 | -117.7089 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 4229158E | OH-4229158E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vehicle | Electric Facility | None | C5283 | 3.54 | 2015-08-21T18:13:00Z | 11.01 | 46 | < 25mph
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | BPOC1 | 4.63 | 2015-07-24T12:49:00Z | 13 | 12 | < 25mph
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | UNDC1 | 4.3 | 2018-04-10T00:23:00Z | 18.01 | 10 | < 25mph
10006 |  | Capanero | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | T2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Unknown | UHLC1 | 1.17 | 2019-03-04T07:59:00Z | 3 | 14 | < 25mph
|  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown | F0490 | 5.32 | 2018-02-19T02:38:00Z | 35.99 | 36 | 25-40mph
|  | Python | 2015-06-06 | 2015 | 10:00 | 34.4043 | -118.4234 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | 16450 Alamo Canyon Rd, Canyon Country | OH-4779534E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-06-06 | 10:13 | Contact From Object |  | Animal | Electric Facility | None | CNIC1 | 3.54 | 2018-01-11T00:55:00Z | 55.01 | 27 | 55mph+
|  | Zone | 2015-06-23 | 2015 | 17:21 | 34.279 | -118.9072 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura Fire Department | Primary splice box at base of pole 2115918e | OH-2115918E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Subsurface | No | <Null> |  | Equipment/Facility Failure | Other |  |  | Unknown | WLYC1 | 7.44 | 2015-01-11T06:49:00Z | 21 | 34 | < 25mph
10005 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | D5145 | 7.89 | 2015-08-12T08:05:00Z | 8.01 | 47 | < 25mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | ATNC1 | 4.83 | 2015-08-07T00:54:00Z | 20 | 3 | < 25mph
|  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown | FTNC1 | 0.32 | 2019-05-27T13:00:00Z | 4 | 1 | < 25mph
|  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force | TSHC1 | 6.99 | 2016-11-01T15:04:00Z | 11.01 | 17 | < 25mph
10005 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | F1963 | 7.5 | 2019-03-30T21:52:00Z | 18.99 | 88 | < 25mph
|  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | SE015 | 7.92 | 2018-08-07T06:00:00Z | 13.27 | 18 | < 25mph
| RYE |  | 2017-12-05 | 2017 | 15:00 | 34.2676 | -117.844 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | TANC1 | 6.35 | 2019-01-17T01:01:00Z | 7 | 1 | < 25mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | E1966 | 3.22 | 2015-07-18T16:45:00Z | 21 | 8 | < 25mph
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | ERYC1 | 5.82 | 2017-07-15T23:00:00Z | 20.49 | 1 | < 25mph
|  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | E3130 | 6.26 | 2015-02-28T04:02:00Z | 23.98 | 34 | < 25mph
|  | Plateau | 2019-09-11 | 2019 | 8:08 | 34.0991 | -118.6793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4424792E | OH-4424792E | Tier 3 | T3 | Y | Verizon / AT&T / Crown Castle | 16 | Distribution | Conductor | Overhead | Yes | 2019-09-11 | 8:08 | Equipment/Facility Failure | Conductor |  | Electric Facility | Human Error | MBCC1 | 1.73 | 2015-07-13T00:56:00Z | 27 | 14 | 25-40mph
|  | Wildomar | 2019-09-19 | 2019 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside County FD | OH-2225310E | OH-2225310E | Tier 3 | T3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other | SDWDM | 6.47 | 2015-10-16T23:49:00Z | 18.99 | 18 | < 25mph
|  | Kickapoo Trail | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1941931E | OH-1941931E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Unknown | C7929 | 7.58 | 2015-04-20T13:35:00Z | 7 | 11 | < 25mph
|  | DALBA | 2017-07-11 | 2017 | 18:06 | 34.2054 | -117.1143 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-919465E | OH-919465E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 2.4 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | HHPC1 | 2.47 | 2018-07-23T15:15:00Z | 11.01 | 46 | < 25mph
|  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | LPDC1 | 5.12 | 2016-04-25T15:55:00Z | 23 | 3 | < 25mph
| ERSKINE |  | 2016-06-23 | 2016 | 16:00 | 34.2676 | -117.844 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | BLM | [13 empty] | Contact From Object |  | Vegetation |  |  | TANC1 | 6.35 | 2015-01-20T04:01:00Z | 4.99 | 1 | < 25mph
|  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | AV011 | 5.06 | 2015-04-08T18:29:00Z | 10 | 63 | < 25mph
|  | JORDAN | 2018-08-29 | 2018 | 17:32 | 35.7358 | -118.7192 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | Jack Ranch Rd/White River Rd, Kernville | OH-4635091E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-08-29 | 19:06 | Contact From Object |  | Vegetation | Electric Facility | Unknown | WOCC1 | 6.68 | 2015-09-21T10:13:00Z | 5.99 | 1 | < 25mph
|  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown | SE074 | 3.24 | 2019-07-01T09:10:00Z | 6.8 | 57 | < 25mph
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | CBVA | 1.36 | 2017-11-15T17:20:00Z | 24 | 10 | < 25mph
| MEYERS |  | 2017-12-05 | 2017 | 14:00 | 34.2183 | -117.4062 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | E3127 | 5.41 | 2019-01-24T16:31:00Z | 49.01 | 43 | 40-55mph
|  | BENCH | 2018-06-26 | 2018 | 20:48 | 34.0158 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Holmes St/Wildwood Canyon Rd, Yucaipa | OH-4367391E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-26 | 20:48 | Contact From Object |  | Vehicle | Pole | Unknown | BNJC1 | 6.9 | 2018-04-01T08:13:00Z | 21 | 45 | < 25mph
10006 |  | Capanero | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | T2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Unknown | UHLC1 | 1.17 | 2018-08-31T03:59:00Z | 4 | 13 | < 25mph
|  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | D1941 | 4.42 | 2016-03-02T21:11:00Z | 14 | 45 | < 25mph
|  | PYTHON | 2016-06-05 | 2016 | 15:59 | 34.4208 | -118.4218 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4154960E | OH-4154960E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-06-05 | 15:59 | Unknown |  |  |  | Unknown | SAUC1 | 5.3 | 2016-09-12T23:57:00Z | 28.99 | 33 | 25-40mph
|  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | NTBC1 | 7.63 | 2015-10-06T02:30:00Z | 8.99 | 21 | < 25mph
|  | PYTHON | 2016-10-22 | 2016 | 15:17 | 34.3812 | -118.4132 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | RAR 0038 | OH-4860064E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-22 | 15:17 | Contact From Object |  | Balloons | Electric Facility | Unknown | CNIC1 | 1.96 | 2019-09-03T00:55:00Z | 24.99 | 102 | < 25mph
|  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | D2363 | 4.48 | 2020-03-10T20:21:00Z | 28.01 | 223 | 25-40mph
|  | Plateau | 2019-09-11 | 2019 | 8:08 | 34.0991 | -118.6793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4424792E | OH-4424792E | Tier 3 | T3 | Y | Verizon / AT&T / Crown Castle | 16 | Distribution | Conductor | Overhead | Yes | 2019-09-11 | 8:08 | Equipment/Facility Failure | Conductor |  | Electric Facility | Human Error | MBUC1 | 3.24 | 2015-06-15T01:56:00Z | 34 | 22 | 25-40mph
|  | DEACON | 2017-10-18 | 2017 | 13:34 | 33.7702 | -117.2157 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1564666E | OH-1564666E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SDPRR | 3.64 | 2015-08-10T21:49:00Z | 14 | 8 | < 25mph
|  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | MSJC1 | 4.82 | 2016-08-09T06:53:00Z | 17 | 29 | < 25mph
|  | Sexton | 2015-02-22 | 2015 | 9:52 | 34.2849 | -119.2173 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura Fire Department | Pole 1718768E | OH-1718768E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-02-22 | 10:49 | Unknown |  |  |  | None | SE792 | 3.36 | 2020-12-30T11:20:00Z | 13.81 | 137 | < 25mph
|  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | MLCC1 | 7.93 | 2016-04-23T16:53:00Z | 23 | 6 | < 25mph
|  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown | C5551 | 7.78 | 2018-06-01T22:06:00Z | 14.99 | 7 | < 25mph
|  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | ROVC1 | 7.44 | 2015-11-01T16:24:00Z | 5.99 | 12 | < 25mph
|  | WELCH | 2016-04-25 | 2016 | 15:23 | 35.8387 | -118.9147 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1078325E | OH-1078325E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 15:23 | Equipment/Facility Failure | Insulator |  |  | Unknown | FTNC1 | 3.62 | 2015-10-22T13:00:00Z | 5.99 | 1 | < 25mph
10007 |  | Vicasa | 2020-11-30 | 2020 | 21:02 | 34.0723 | -118.588 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles Fire Department | OH-4535641E | OH-4535641E | T3 | T3 |  | Verizon Wireless, AT&T Mobility, Frontier Communications, Crown Castle NG West, Inc | 16 | Distribution | Other | Overhead | Yes | 2020-11-30 | 21:02 | Contact From Object |  | Vehicle | Electric Facility | Outside Force | D2363 | 2.23 | 2018-12-21T01:55:00Z | 13 | 144 | < 25mph
|  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather | E8724 | 7.03 | 2018-02-01T09:29:00Z | 8.99 | 39 | < 25mph
|  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown | FTNC1 | 0.32 | 2019-01-21T12:00:00Z | 4.99 | 1 | < 25mph
|  | Pawley | 2015-05-29 | 2015 | 7:29 | 36.387 | -118.9536 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare County Fire | Lemon Cove and Three Rivers Sub. Venida 66kV | OH-4434944E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-05-29 | 7:29 | Contact From Object |  | Animal | Electric Facility | None | D0117 | 5.17 | 2016-04-29T03:10:00Z | 1.01 | 6 | < 25mph
| ELLIS |  | 2017-10-18 | 2017 | 11:18 | 33.7721 | -117.2173 | Vegetation | Rural | Unknown |  | Unknown | Fire Agency | Cal Fire | [17 empty] | Weather | SE757 | 7.45 | 2020-09-06T15:20:00Z | 8.04 | 148 | < 25mph
1 |  | Birchim | 2015-02-06 | 2015 | 13:15 | 37.454 | -118.5842 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Various Fire Agencies | Between Poles 1854107E & 1854106E | OH-1854107E | Tier 2 | T2 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-02-06 | 13:15 | Unknown |  |  |  | Unknown | OVRC1 | 4.68 | 2018-01-14T06:54:00Z | 3 | 1 | < 25mph
|  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather | E8724 | 7.03 | 2018-10-25T19:44:00Z | 10 | 58 | < 25mph
|  | BIG CREEK 3-RECTOR NO.1/ET-01046 | 2015-09-03 | 2015 | 17:00 | 36.8936 | -119.4571 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | East of Watts Valley Rd and Pittman Hill Rd, East of Clovis | OH-7020930 | Tier 2 | T2 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2015-09-03 | 16:15 | Contact From Object |  | Balloons | Electric Facility | None | FCHC1 | 1.24 | 2018-12-12T05:00:00Z | 5.99 | 1 | < 25mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | SE075 | 2.32 | 2019-04-21T00:10:00Z | 34.4 | 49 | 25-40mph
|  | WELCH | 2016-04-25 | 2016 | 15:23 | 35.8387 | -118.9147 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1078325E | OH-1078325E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 15:23 | Equipment/Facility Failure | Insulator |  |  | Unknown | FTNC1 | 3.62 | 2018-06-11T18:00:00Z | 12.01 | 1 | < 25mph
|  | HUCKLEBERRY | 2017-03-17 | 2017 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4493863E | OH-4493863E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown | E1966 | 2.92 | 2017-09-17T03:36:00Z | 23 | 10 | < 25mph
|  | TICO | 2016-04-28 | 2016 | 14:00 | 34.357 | -119.314 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura County FD | OH-1604151E | OH-1604151E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-04-28 | 14:00 | Equipment/Facility Failure | Other |  |  | Unknown | E8097 | 7.74 | 2017-06-28T07:09:00Z | 7 | 26 | < 25mph
|  | VALLECITO | 2016-08-18 | 2016 | 19:00 | 34.4214 | -119.5964 | Other | Rural | Structure Only | Structure Only |  | Fire Agency | Santa Barbara County Fire Department | 2400 block of Whitney Avenue in Summerland | OH-1523986E | Tier 2 | T2 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | SE039 | 3.3 | 2020-02-06T10:50:00Z | 8.25 | 79 | < 25mph
|  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SE061 | 3.27 | 2020-11-12T21:00:00Z | 13.74 | 151 | < 25mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | SE015 | 7.4 | 2018-12-06T13:40:00Z | 31.14 | 28 | 25-40mph
|  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | SDUNC | 3.79 | 2015-01-09T19:49:00Z | 7 | 7 | < 25mph
|  | VIENTO | 2016-06-06 | 2016 | 17:44 | 35.1355 | -118.4771 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1373165E | OH-1373165E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-06 | 17:44 | Contact From Object |  | Other | Pole | Unknown | SE681 | 7.45 | 2020-08-21T05:10:00Z | 17.68 | 150 | < 25mph
|  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UCMO | 4.71 | 2015-11-27T23:10:00Z | 14.5 | 9 | < 25mph
10005 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error | E1966 | 7.65 | 2018-03-04T14:17:00Z | 15.99 | 12 | < 25mph
|  | Medusa | 2020-03-06 | 2020 | 17:05 | 34.0802 | -117.254 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1811355E | OH-1811355E | T2 | T2 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Other | SE152 | 5.81 | 2020-07-09T16:00:00Z | 6.87 | 131 | < 25mph
10003 |  | SHEFFIELD | 2016-02-22 | 2016 | 17:04 | 34.4492 | -119.5845 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Montecito Fire Department | OH-1082380E | OH-1082380E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-02-22 | 17:04 | Equipment/Facility Failure | Conductor |  |  | Unknown | CXPC1 | 4.08 | 2019-04-30T03:42:00Z | 8.99 | 33 | < 25mph
3 |  | Bidder | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire | OH-2023941E | OH-2023941E | T3 | T3 |  | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force | SE054 | 5.44 | 2019-02-07T18:00:00Z | 10.09 | 72 | < 25mph
|  | La Mancha | 2020-07-05 | 2020 | 3:57 | 34.1325 | -118.8532 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1848406E | OH-1848406E | T3 | T3 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-07-05 | 3:57 | Equipment/Facility Failure | Insulator |  |  | Unknown | LCBC1 | 7.67 | 2019-03-25T23:55:00Z | 24.99 | 78 | < 25mph
|  | Taggert | 2019-04-23 | 2019 | 21:06 | 34.2147 | -117.0973 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1027559E | OH-1027559E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution |  | Overhead | No |  |  | Unknown |  |  |  | Unknown | SE152 | 7.14 | 2019-04-19T06:50:00Z | 14.47 | 60 | < 25mph
|  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | AT643 | 4.77 | 2016-05-20T19:06:00Z | 30 | 46 | 25-40mph
| OAK |  | 2019-10-28 | 2019 | 8:42 | 34.1489 | -118.6954 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | MBCC1 | 4.51 | 2017-07-17T21:56:00Z | 31 | 66 | 25-40mph
|  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown | LYQC1 | 4.98 | 2016-07-25T11:18:00Z | 4.99 | 1 | < 25mph
|  | CARVER | 2016-09-24 | 2016 | 14:20 | 35.7381 | -118.9546 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4784763E | OH-4784763E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-09-24 | 14:20 | Contact From Object |  | Animal | Electric Facility | Unknown | WOCC1 | 7.2 | 2018-05-12T11:13:00Z | 7 | 1 | < 25mph
|  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown | SE513 | 5.76 | 2020-10-26T22:40:00Z | 18.06 | 85 | < 25mph
| ERSKINE |  | 2016-06-23 | 2016 | 16:00 | 34.2676 | -117.844 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | BLM | [13 empty] | Contact From Object |  | Vegetation |  |  | TANC1 | 6.35 | 2016-02-03T09:01:00Z | 5.99 | 1 | < 25mph
1 |  | Birchim | 2015-02-06 | 2015 | 13:15 | 37.454 | -118.5842 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Various Fire Agencies | Between Poles 1854107E & 1854106E | OH-1854107E | Tier 2 | T2 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-02-06 | 13:15 | Unknown |  |  |  | Unknown | OVRC1 | 4.68 | 2017-09-20T17:54:00Z | 10 | 1 | < 25mph
|  | Atlanta | 2015-05-05 | 2015 | 16:00 | 33.711 | -117.7089 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 4229158E | OH-4229158E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.92 | 2018-08-09T19:51:00Z | 15.99 | 44 | < 25mph
10006 |  | Capanero | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | T2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Unknown | UHLC1 | 1.17 | 2016-03-01T15:59:00Z | 4 | 13 | < 25mph
|  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown | WMSC1 | 6.6 | 2019-12-03T11:53:00Z | 25.99 | 38 | 25-40mph
|  | Atlanta | 2015-05-05 | 2015 | 16:00 | 33.711 | -117.7089 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 4229158E | OH-4229158E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.92 | 2019-11-20T08:51:00Z | 28.01 | 169 | 25-40mph
| EASY |  | 2019-10-30 | 2019 | 6:00 | 34.2822 | -118.8034 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | WLYC1 | 6.54 | 2015-05-26T02:49:00Z | 18.99 | 58 | < 25mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | ATNC1 | 4.83 | 2016-06-10T01:54:00Z | 18.01 | 1 | < 25mph
10002 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | CEEC1 | 3.51 | 2018-08-15T13:38:00Z | 10 | 83 | < 25mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | ATNC1 | 4.83 | 2018-02-09T01:54:00Z | 13 | 1 | < 25mph
|  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | SE015 | 7.92 | 2020-01-10T22:10:00Z | 23.31 | 46 | < 25mph
|  | LEE VINING-LUNDY NO. 1/ET-01774 | 2017-05-01 | 2017 | 5:40 | 38.0209 | -119.1608 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | CAlFIre | OH-1580964E | OH-1580964E | Tier 2 | T2 | Y |  | 55 | Distribution | Conductor | Overhead | No | <Null> |  | Contamination |  |  |  | Unknown | ERYC1 | 7.12 | 2016-09-10T02:00:00Z | 30.6 | 11 | 25-40mph
|  | Mettler | 2020-08-10 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | OH-2093506E | OH-2093506E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Unknown | E1410 | 5.9 | 2016-07-02T18:03:00Z | 25.99 | 37 | 25-40mph
|  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | NTBC1 | 7.63 | 2019-09-06T16:06:00Z | 10 | 72 | < 25mph
|  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | MLCC1 | 7.93 | 2017-07-06T18:53:00Z | 14.99 | 16 | < 25mph
|  | Hughes Lake | 2019-09-02 | 2019 | 14:02 | 34.7026 | -118.342 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4782978E | OH-4782978E | Tier 2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-02 | 14:02 | Contact From Object |  | Balloons | Electric Facility | Other | SE071 | 7.61 | 2018-10-25T18:30:00Z | 12.06 | 38 | < 25mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | E1966 | 3.22 | 2015-08-31T01:00:00Z | 23 | 8 | < 25mph
|  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force | D7608 | 3.75 | 2017-10-15T07:06:00Z | 13 | 23 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:30 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | None | SE148 | 2.55 | 2020-07-16T09:50:00Z | 7.89 | 155 | < 25mph
|  | Flying D | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County | OH-1761180E | OH-1761180E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown | DEMC1 | 6.46 | 2015-01-22T16:25:00Z | 8.01 | 2 | < 25mph
|  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error | AU563 | 7.19 | 2018-04-14T12:22:00Z | 18.99 | 17 | < 25mph
|  | Kickapoo Trail | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1941931E | OH-1941931E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE344 | 4.44 | 2020-07-26T11:40:00Z | 14.91 | 90 | < 25mph
|  | Python | 2015-06-06 | 2015 | 10:00 | 34.4043 | -118.4234 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | 16450 Alamo Canyon Rd, Canyon Country | OH-4779534E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-06-06 | 10:13 | Contact From Object |  | Animal | Electric Facility | None | NHPC1 | 7.23 | 2015-08-26T18:56:00Z | 18.99 | 24 | < 25mph
|  | METTLER | 2017-06-02 | 2017 | 10:50 | 35.1021 | -118.5328 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4416566E | OH-4416566E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | KTSP | 5.76 | 2015-04-16T19:55:00Z | 21.85 | 42 | < 25mph
|  | TICO | 2016-04-28 | 2016 | 14:00 | 34.357 | -119.314 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura County FD | OH-1604151E | OH-1604151E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-04-28 | 14:00 | Equipment/Facility Failure | Other |  |  | Unknown | AT185 | 1.35 | 2015-02-07T08:25:00Z | 5.99 | 12 | < 25mph
|  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown | E1966 | 2.94 | 2017-08-14T04:11:00Z | 24 | 11 | < 25mph
10005 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error | SE063 | 1.86 | 2019-03-20T20:30:00Z | 32.01 | 37 | 25-40mph
|  | POULTRY | 2018-09-21 | 2018 | 8:28 | 34.0728 | -117.0397 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Juniper St. Yucaipa | OH-129241E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SE263 | 4.25 | 2020-09-18T04:50:00Z | 13.01 | 182 | < 25mph
|  | HUGHES LAKE/ED-08810 | 2018-07-06 | 2018 | 5:38 | 34.6744 | -118.4517 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | 465140E | OH-1938477E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-07-06 | 5:38 | Contact From Object |  | Vehicle | Pole | Unknown | PPPC1 | 4.96 | 2018-03-25T19:56:00Z | 38.01 | 5 | 25-40mph
|  | KINSEY | 2016-07-08 | 2016 | 11:15 | 34.7906 | -118.8256 | Vegetation | Rural | 300 - 999 Acres | 300 - 999 Acres |  | Fire Agency | Kern County Fire Department | 1-5, Gorman | OH-4539401E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown |  |  |  | 0 | 0 | No data
| SADDLE RIDGE |  | 2019-10-10 | 2019 | 21:09 | 34.3299 | -118.4816 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | SE177 | 4.53 | 2019-11-12T14:10:00Z | 19.66 | 139 | < 25mph
|  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | MSJC1 | 4.82 | 2018-10-30T11:53:00Z | 14.99 | 48 | < 25mph
|  | MAYBELL | 2017-07-02 | 2017 | 8:24 | 34.0804 | -117.8552 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | OH-144184E | OH-1255315E | T2 200Ft Outer Buffer | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-07-02 | 8:24 | Contact From Object |  | Animal | Electric Facility | Unknown | STFC1 | 6.14 | 2018-12-19T10:57:00Z | 14.99 | 85 | < 25mph
|  | SKINKLE | 2016-05-29 | 2016 | 22:25 | 36.0091 | -118.9563 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-4566417E | OH-4566417E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-05-29 | 22:25 | Contact From Object |  | Other | Electric Facility | Unknown |  |  |  | 0 | 0 | No data
|  | Saugus-Santa Susana | 2019-08-06 | 2019 | 15:03 | 34.3918 | -118.6596 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | VFD & LACFD | M6-T1 | M6-T1 | Tier 3 | T3 | Y | NA | 66 | Transmission | Other | Overhead | Yes | 2019-08-06 | 12:51 | Contact From Object |  | Animal | Electric Facility | Other | DLVC1 | 2.65 | 2016-04-06T07:55:00Z | 5.99 | 12 | < 25mph
|  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown | SE355 | 7.39 | 2020-12-08T10:30:00Z | 21.19 | 93 | < 25mph
|  | Viento | 2020-06-09 | 2020 | 16:42 | 35.1384 | -118.4809 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4707894E | OH-4707894E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | SE518 | 6.09 | 2020-02-24T16:50:00Z | 12.41 | 90 | < 25mph
|  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather | SE099 | 1.39 | 2019-02-09T09:40:00Z | 14.03 | 55 | < 25mph
|  | JORDAN | 2018-08-29 | 2018 | 17:32 | 35.7358 | -118.7192 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | Jack Ranch Rd/White River Rd, Kernville | OH-4635091E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-08-29 | 19:06 | Contact From Object |  | Vegetation | Electric Facility | Unknown | WOCC1 | 6.68 | 2016-12-04T08:13:00Z | 5.99 | 1 | < 25mph
|  | Kickapoo Trail | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1941931E | OH-1941931E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Unknown | UCBU | 5.62 | 2019-01-14T13:40:00Z | 8.81 | 7 | < 25mph
| OAK |  | 2019-10-28 | 2019 | 8:42 | 34.1489 | -118.6954 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | MBCC1 | 4.51 | 2020-05-28T17:56:00Z | 27 | 267 | 25-40mph
|  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | KNWC1 | 3.86 | 2016-10-06T10:17:00Z | 13 | 24 | < 25mph
|  | Flying D | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County | OH-1761180E | OH-1761180E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown | BKGC1 | 4.48 | 2019-07-26T09:51:00Z | 12.01 | 30 | < 25mph
| MEYERS |  | 2017-12-05 | 2017 | 14:00 | 34.2183 | -117.4062 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | E3127 | 5.41 | 2017-06-08T14:59:00Z | 17 | 10 | < 25mph
| MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | CEEC1 | 3.58 | 2018-05-26T15:38:00Z | 17 | 64 | < 25mph
|  | VALLEY-MAYBERRY-MORENO-VISTA | 2020-05-18 | 2020 | 12:10 | 33.8587 | -117.0203 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire Perris | OH-1979539E | OH-1979539E | T3 | T3 | Y | None | 115 | Transmission | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Other | HSGC1 | 4.08 | 2019-04-07T03:16:00Z | 15.99 | 33 | < 25mph
10005 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | OOSC1 | 5.78 | 2018-02-23T01:45:00Z | 38.5 | 65 | 25-40mph
2 |  | Lopez | 2015-05-23 | 2015 | 11:57 | 34.3006 | -118.3613 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | Pole 1261671E | OH-1261671E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Conductor | Overhead | Yes | 2015-05-23 | 11:05 | Unknown |  |  |  | Unknown | CNIC1 | 4.89 | 2017-12-20T23:55:00Z | 44 | 25 | 40-55mph
|  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other | LPDC1 | 2.12 | 2019-05-02T01:55:00Z | 24 | 54 | < 25mph
|  | TUNA | 2016-09-19 | 2016 | 6:11 | 34.04 | -118.6687 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-1638513E | OH-1638513E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | MBUC1 | 2.01 | 2017-04-26T01:56:00Z | 24.99 | 38 | < 25mph
|  | SODA SPRINGS | 2016-06-21 | 2016 | 21:47 | 36.2515 | -118.7809 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4391218E | OH-4391218E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-21 | 21:47 | Contact From Object |  | Vegetation | Electric Facility | Unknown | TT625 | 4.02 | 2020-05-29T23:49:00Z | 11 | 23 | < 25mph
|  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force | TSHC1 | 6.99 | 2017-01-13T12:04:00Z | 7 | 7 | < 25mph
|  | PATRICIA | 2017-04-16 | 2017 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4495331E | OH-4495331E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown | ROVC1 | 7.28 | 2015-04-27T07:24:00Z | 25.99 | 19 | 25-40mph
|  | GUITAR | 2016-01-16 | 2016 | 15:20 | 34.4096 | -118.6816 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-848266E | OH-848266E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-01-16 | 15:20 | Equipment/Facility Failure | Other |  |  | Unknown | SE086 | 4.16 | 2019-06-24T14:40:00Z | 7.9 | 63 | < 25mph
|  | Soda Springs | 2015-05-14 | 2015 | 22:24 | 36.1318 | -118.7784 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | Soda Springs 12kV out of Boxwood Sub | OH-4464511E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-14 | 22:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown | OORC1 | 5.23 | 2015-03-17T23:12:00Z | 8.01 | 1 | < 25mph
|  | SKINKLE | 2016-05-29 | 2016 | 22:25 | 36.0091 | -118.9563 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-4566417E | OH-4566417E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-05-29 | 22:25 | Contact From Object |  | Other | Electric Facility | Unknown | SE279 | 6.01 | 2020-09-08T03:50:00Z | 8.11 | 49 | < 25mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | AP902 | 7.98 | 2016-03-17T00:01:00Z | 8.99 | 10 | < 25mph
|  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force | SDLEL | 7.62 | 2015-01-10T01:49:00Z | 4.99 | 12 | < 25mph
|  | POPPET FLATS | 2016-02-27 | 2016 | 0:49 | 33.9134 | -116.8003 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1989045E | OH-1989045E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-02-27 | 0:49 | Contact From Object |  | Vehicle | Pole | Unknown | BAZC1 | 1.3 | 2017-06-19T09:14:00Z | 18.99 | 9 | < 25mph
|  | JORDAN | 2018-08-29 | 2018 | 17:32 | 35.7358 | -118.7192 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | Jack Ranch Rd/White River Rd, Kernville | OH-4635091E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-08-29 | 19:06 | Contact From Object |  | Vegetation | Electric Facility | Unknown | WOCC1 | 6.68 | 2017-11-22T01:13:00Z | 5.99 | 1 | < 25mph
|  | GUITAR | 2017-05-11 | 2017 | 12:27 | 34.4127 | -118.6702 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-848255E | OH-848255E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-05-11 | 12:27 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE079 | 7.87 | 2019-10-22T07:10:00Z | 19.95 | 81 | < 25mph
| OAK |  | 2019-10-28 | 2019 | 8:42 | 34.1489 | -118.6954 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | SE291 | 6.52 | 2019-10-10T14:10:00Z | 26.37 | 173 | 25-40mph
|  | BRUMFIELD | 2016-06-04 | 2016 | 10:17 | 33.5947 | -117.1387 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-2206630E | OH-2206630E | Tier 2 | T2 | Y |  | 12 | Distribution | Transformer | Overhead | Yes | 2016-06-04 | 10:17 | Equipment/Facility Failure | Transformer |  |  | Unknown | D7608 | 6.23 | 2016-11-04T01:14:00Z | 11.01 | 24 | < 25mph
|  | MAYBELL | 2017-07-02 | 2017 | 8:24 | 34.0804 | -117.8552 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | OH-144184E | OH-1255315E | T2 200Ft Outer Buffer | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-07-02 | 8:24 | Contact From Object |  | Animal | Electric Facility | Unknown | E9402 | 7.93 | 2018-01-25T20:21:00Z | 14.99 | 82 | < 25mph
|  | Wildomar | 2019-09-19 | 2019 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside County FD | OH-2225310E | OH-2225310E | Tier 3 | T3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other | SDMEA | 4.2 | 2017-12-16T06:49:00Z | 5.99 | 12 | < 25mph
|  | Mettler | 2020-08-10 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | OH-2093506E | OH-2093506E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Unknown | E3266 | 6.59 | 2020-12-12T03:01:00Z | 25 | 150 | 25-40mph
4 |  | ANZAR | 2017-06-04 | 2017 | 13:14 | 33.8373 | -117.4863 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-1757417E | OH-1757417E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2017-06-04 | 13:14 | Wire-Wire Contact |  |  |  | Unknown | AU409 | 5.17 | 2015-10-17T00:29:00Z | 23 | 45 | < 25mph
|  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force | LYQC1 | 1.86 | 2017-06-15T17:18:00Z | 10 | 1 | < 25mph
| RYE |  | 2017-12-05 | 2017 | 15:00 | 34.2676 | -117.844 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | TANC1 | 6.35 | 2019-09-29T11:01:00Z | 4 | 8 | < 25mph
|  | ARCHIE | 2018-11-13 | 2018 | 7:11 | 33.4928 | -117.2796 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | NORTH OF CARANCHO ON VIA CIELO | OH-4149859E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-13 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Unknown | E4050 | 5.17 | 2017-10-13T17:22:00Z | 11.01 | 32 | < 25mph
|  | Pawley | 2015-05-29 | 2015 | 7:29 | 36.387 | -118.9536 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare County Fire | Lemon Cove and Three Rivers Sub. Venida 66kV | OH-4434944E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-05-29 | 7:29 | Contact From Object |  | Animal | Electric Facility | None | D0117 | 5.17 | 2015-07-08T06:30:00Z | 1.01 | 3 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:30 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | None | E3131 | 6.3 | 2016-01-13T14:58:00Z | 18.99 | 31 | < 25mph
| STAR |  | 2019-07-28 | 2019 | 14:00 | 33.9975 | -117.7698 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Chino Valley Fire Department | [13 empty] | Contact From Object |  | Bird |  | Weather | C3917 | 6.16 | 2019-01-22T10:00:00Z | 12.01 | 79 | < 25mph
|  | Elster | 2019-09-21 | 2019 | 10:53 | 36.1026 | -118.8659 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4252581E | OH-4252581E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-21 | 10:53 | Contact From Object |  | Vehicle | Electric Facility | Human Error | SE278 | 7.52 | 2019-06-19T18:00:00Z | 12.48 | 30 | < 25mph
|  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown | LYQC1 | 4.98 | 2017-11-02T09:18:00Z | 18.99 | 1 | < 25mph
| MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | TPGC1 | 4.02 | 2017-02-20T02:57:00Z | 13 | 66 | < 25mph
10004 |  | Peninsula | 2019-03-16 | 2019 | 17:58 | 33.6182 | -117.8025 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1729510E | OH-1729510E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-03-16 | 17:58 | Equipment/Facility Failure | Crossarm |  |  | Unknown | SE024 | 6.43 | 2020-08-29T15:50:00Z | 7.67 | 167 | < 25mph
|  | SHOWDOWN | 2016-06-09 | 2016 | 11:28 | 34.5862 | -118.196 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4267121E | OH-4267121E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-09 | 11:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | LPDC1 | 6.32 | 2015-05-16T08:55:00Z | 24.99 | 16 | < 25mph
|  | Kickapoo Trail | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1941931E | OH-1941931E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Unknown | UCBU | 5.62 | 2016-05-03T20:50:00Z | 15.39 | 19 | < 25mph
| THOMAS |  | 2017-12-04 | 2017 | 18:28 | 34.4152 | -119.0912 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | USFS | [17 empty] | Weather | AT184 | 6.91 | 2017-02-06T17:51:00Z | 24 | 71 | < 25mph
|  | Northpark | 2019-06-20 | 2019 | 14:08 | 34.2298 | -117.4048 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | San Bern. FD | OH-201371S | OH-201371S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Human Error | DVOC1 | 3.48 | 2016-05-13T19:10:00Z | 14.99 | 5 | < 25mph
|  | LEE VINING-LUNDY NO. 1/ET-01774 | 2017-05-01 | 2017 | 5:40 | 38.0209 | -119.1608 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | CAlFIre | OH-1580964E | OH-1580964E | Tier 2 | T2 | Y |  | 55 | Distribution | Conductor | Overhead | No | <Null> |  | Contamination |  |  |  | Unknown | ERYC1 | 7.12 | 2015-11-18T16:00:00Z | 14.99 | 7 | < 25mph
|  | SODA SPRINGS | 2016-06-21 | 2016 | 21:47 | 36.2515 | -118.7809 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4391218E | OH-4391218E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-21 | 21:47 | Contact From Object |  | Vegetation | Electric Facility | Unknown | OORC1 | 6.87 | 2015-11-07T20:12:00Z | 11.01 | 2 | < 25mph
| MEYERS |  | 2017-12-05 | 2017 | 14:00 | 34.2183 | -117.4062 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | DVOC1 | 2.77 | 2015-11-16T00:10:00Z | 17 | 8 | < 25mph
|  | DRISKILL | 2016-10-18 | 2016 | 18:41 | 34.4687 | -119.7722 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Santa Barbara Fire Department | OH-2178476E | OH-2178476E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-18 | 18:41 | Equipment/Facility Failure | Fuse |  |  | Unknown | SE068 | 2.89 | 2020-02-13T20:10:00Z | 13.6 | 220 | < 25mph
|  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | NTBC1 | 7.63 | 2016-06-23T01:06:00Z | 15.99 | 15 | < 25mph
|  | PATRICIA | 2016-09-16 | 2016 | 19:02 | 34.4851 | -119.3001 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ojai City Fire Department | OH-4797071E | OH-4797071E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-09-16 | 19:02 | Contact From Object |  | Vehicle | Pole | Unknown | CSVC1 | 6.69 | 2015-09-27T08:09:00Z | 4.99 | 7 | < 25mph
|  | CARVER | 2016-09-24 | 2016 | 14:20 | 35.7381 | -118.9546 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4784763E | OH-4784763E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-09-24 | 14:20 | Contact From Object |  | Animal | Electric Facility | Unknown | PG165 | 7.77 | 2019-03-02T22:50:00Z | 12.93 | 8 | < 25mph
10005 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error | LPDC1 | 6.51 | 2019-03-01T00:55:00Z | 34 | 32 | 25-40mph
|  | Mettler | 2020-08-10 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | OH-2093506E | OH-2093506E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Unknown | AS826 | 6.28 | 2015-07-04T21:41:00Z | 23 | 29 | < 25mph
|  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | D2363 | 4.48 | 2019-05-11T03:47:00Z | 11.01 | 131 | < 25mph
|  | Pawley | 2015-05-29 | 2015 | 7:29 | 36.387 | -118.9536 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare County Fire | Lemon Cove and Three Rivers Sub. Venida 66kV | OH-4434944E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-05-29 | 7:29 | Contact From Object |  | Animal | Electric Facility | None | D0117 | 5.17 | 2018-09-17T23:09:00Z | 12.01 | 12 | < 25mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | E1966 | 3.22 | 2016-05-03T07:03:00Z | 2.01 | 9 | < 25mph
|  | Maguire | 2015-04-17 | 2015 | 16:41 | 34.0851 | -118.8044 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles County Fire | Maguire 16kV out of Latigo Sub | OH-1199311E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2015-04-17 | 16:41 | Contact From Object |  | Vehicle | Pole | None | OOSC1 | 7.73 | 2017-08-31T03:00:00Z | 8.59 | 23 | < 25mph
|  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error | C1909 | 5.95 | 2016-11-27T07:29:00Z | 10 | 14 | < 25mph
|  | DALBA | 2017-07-11 | 2017 | 18:06 | 34.2054 | -117.1143 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-919465E | OH-919465E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 2.4 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | TR782 | 2.95 | 2019-02-12T21:14:00Z | 18.01 | 57 | < 25mph
| EDISON |  | 2016-05-12 | 2016 | -8 | 34.3135 | -119.1865 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | E8097 | 6.25 | 2018-08-19T10:28:00Z | 7 | 92 | < 25mph
|  | Atlanta | 2015-05-05 | 2015 | 16:00 | 33.711 | -117.7089 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 4229158E | OH-4229158E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.92 | 2016-06-08T03:51:00Z | 15.99 | 91 | < 25mph
4 |  | PYTHON | 2016-12-02 | 2016 | 21:26 | 34.3812 | -118.4132 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | OH-4572770E | OH-4572770E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vegetation | Electric Facility | Unknown | CNIC1 | 1.96 | 2019-02-11T06:55:00Z | 47 | 56 | 40-55mph
| EASY |  | 2019-10-30 | 2019 | 6:00 | 34.2822 | -118.8034 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | WLYC1 | 6.54 | 2015-10-22T03:49:00Z | 17 | 68 | < 25mph
|  | Soda Springs | 2015-05-14 | 2015 | 22:24 | 36.1318 | -118.7784 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | Soda Springs 12kV out of Boxwood Sub | OH-4464511E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-14 | 22:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown | AV342 | 5.2 | 2017-12-15T20:42:00Z | 7 | 16 | < 25mph
|  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown | E3060 | 4.55 | 2016-06-07T07:14:00Z | 17 | 30 | < 25mph
|  | ARCHIE | 2018-11-13 | 2018 | 7:11 | 33.4928 | -117.2796 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | NORTH OF CARANCHO ON VIA CIELO | OH-4149859E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-13 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Unknown | DLZSD | 2.58 | 2020-01-13T10:40:00Z | 8.01 | 51 | < 25mph
|  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other | PPPC1 | 1.78 | 2019-07-30T00:56:00Z | 25.99 | 18 | 25-40mph
| STAR |  | 2019-07-28 | 2019 | 14:00 | 33.9975 | -117.7698 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Chino Valley Fire Department | [13 empty] | Contact From Object |  | Bird |  | Weather | TNRC1 | 4.58 | 2015-07-19T15:57:00Z | 14.99 | 47 | < 25mph
|  | CUDDEBACK | 2017-08-08 | 2017 | 17:52 | 35.1342 | -118.5607 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4179753E | OH-4179753E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-08-08 | 17:52 | Contact From Object |  | Vehicle | Electric Facility | Unknown | KTSP | 6.87 | 2018-01-09T04:35:00Z | 34.52 | 50 | 25-40mph
|  | Kickapoo Trail | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1941931E | OH-1941931E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Unknown | UCCC1 | 6.87 | 2017-09-29T01:56:00Z | 8.99 | 7 | < 25mph
| STAR |  | 2019-07-28 | 2019 | 14:00 | 33.9975 | -117.7698 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Chino Valley Fire Department | [13 empty] | Contact From Object |  | Bird |  | Weather | TNRC1 | 4.58 | 2015-04-04T12:57:00Z | 14.99 | 30 | < 25mph
| TENAJA |  | 2019-09-04 | 2019 | 16:43 | 33.5285 | -117.2732 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | FBOC1 | 7.8 | 2018-03-29T11:00:00Z | 9.1 | 18 | < 25mph
|  | SKINKLE | 2016-05-29 | 2016 | 22:25 | 36.0091 | -118.9563 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-4566417E | OH-4566417E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-05-29 | 22:25 | Contact From Object |  | Other | Electric Facility | Unknown |  |  |  | 0 | 0 | No data
10005 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | E6371 | 5.01 | 2016-01-25T00:41:00Z | 34.99 | 51 | 25-40mph
|  | Elster | 2019-09-21 | 2019 | 10:53 | 36.1026 | -118.8659 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4252581E | OH-4252581E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-21 | 10:53 | Contact From Object |  | Vehicle | Electric Facility | Human Error |  |  |  | 0 | 0 | No data
|  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error | SAUC1 | 7.39 | 2020-04-10T19:57:00Z | 32.99 | 90 | 25-40mph
|  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other | PPPC1 | 1.78 | 2015-05-14T06:56:00Z | 24 | 7 | < 25mph
| ELLIS |  | 2017-10-18 | 2017 | 11:18 | 33.7721 | -117.2173 | Vegetation | Rural | Unknown |  | Unknown | Fire Agency | Cal Fire | [17 empty] | Weather | SDPRR | 3.55 | 2017-12-09T21:49:00Z | 25.99 | 31 | 25-40mph
|  | SODA SPRINGS | 2016-06-21 | 2016 | 21:47 | 36.2515 | -118.7809 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4391218E | OH-4391218E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-21 | 21:47 | Contact From Object |  | Vegetation | Electric Facility | Unknown | MOLC1 | 5.11 | 2015-02-09T23:27:00Z | 10 | 2 | < 25mph
|  | TICO | 2016-04-28 | 2016 | 14:00 | 34.357 | -119.314 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura County FD | OH-1604151E | OH-1604151E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-04-28 | 14:00 | Equipment/Facility Failure | Other |  |  | Unknown | E8097 | 7.74 | 2018-05-25T03:13:00Z | 21 | 34 | < 25mph
|  | Saugus-Santa Susana | 2019-08-06 | 2019 | 15:03 | 34.3918 | -118.6596 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | VFD & LACFD | M6-T1 | M6-T1 | Tier 3 | T3 | Y | NA | 66 | Transmission | Other | Overhead | Yes | 2019-08-06 | 12:51 | Contact From Object |  | Animal | Electric Facility | Other | E3126 | 5.46 | 2016-02-18T02:59:00Z | 34.99 | 9 | 25-40mph
4 |  | ANZAR | 2017-06-04 | 2017 | 13:14 | 33.8373 | -117.4863 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-1757417E | OH-1757417E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2017-06-04 | 13:14 | Wire-Wire Contact |  |  |  | Unknown | MHEC1 | 1.92 | 2018-04-23T08:16:00Z | 7 | 39 | < 25mph
1 |  | Birchim | 2015-02-06 | 2015 | 13:15 | 37.454 | -118.5842 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Various Fire Agencies | Between Poles 1854107E & 1854106E | OH-1854107E | Tier 2 | T2 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-02-06 | 13:15 | Unknown |  |  |  | Unknown | SE102 | 0.67 | 2018-12-28T05:20:00Z | 10.85 | 13 | < 25mph
|  | ARCHIE | 2018-11-13 | 2018 | 7:11 | 33.4928 | -117.2796 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | NORTH OF CARANCHO ON VIA CIELO | OH-4149859E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-13 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Unknown | E4050 | 5.17 | 2019-03-24T09:00:00Z | 7 | 49 | < 25mph
|  | BIG CREEK 1-RECTOR/ET-01082 | 2018-08-04 | 2018 | 0:43 | 37.1895 | -119.2738 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | OH-7021454 | OH-7021454 | Tier 3 | T3 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2018-08-04 | 2:21 | Equipment/Facility Failure | Other |  |  | Unknown | SE370 | 7.02 | 2020-08-25T08:40:00Z | 11.76 | 97 | < 25mph
|  | Mettler | 2020-08-10 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | OH-2093506E | OH-2093506E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Unknown | E3266 | 6.59 | 2017-06-11T11:52:00Z | 28.01 | 32 | 25-40mph
|  | HUCKLEBERRY | 2017-03-17 | 2017 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4493863E | OH-4493863E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown | AU414 | 6.26 | 2015-07-21T08:54:00Z | 2.01 | 4 | < 25mph
| OAK |  | 2019-10-28 | 2019 | 8:42 | 34.1489 | -118.6954 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | MBUC1 | 6.68 | 2015-10-29T05:56:00Z | 32.99 | 40 | 25-40mph
|  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | RSVC1 | 7.14 | 2018-05-11T06:00:00Z | 6.2 | 25 | < 25mph
|  | Conestoga | 2020-06-13 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Other | E3128 | 6.07 | 2015-03-17T13:30:00Z | 8.99 | 26 | < 25mph
10002 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | CEEC1 | 3.51 | 2019-09-25T06:38:00Z | 22.01 | 132 | < 25mph
|  | Viento | 2020-06-09 | 2020 | 16:42 | 35.1384 | -118.4809 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4707894E | OH-4707894E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | KTSP | 2.37 | 2017-11-05T21:15:00Z | 20.71 | 36 | < 25mph
|  | PATRICIA | 2016-09-16 | 2016 | 19:02 | 34.4851 | -119.3001 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ojai City Fire Department | OH-4797071E | OH-4797071E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-09-16 | 19:02 | Contact From Object |  | Vehicle | Pole | Unknown | CSVC1 | 6.69 | 2015-01-31T09:09:00Z | 5.99 | 8 | < 25mph
|  | MIST | 2016-08-24 | 2016 | 16:37 | 34.4665 | -120.0701 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Santa Barbara County Fire Department | Refiugio Canyon, Santa Barbara | OH-4538468E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-24 | 18:50 | Contact From Object |  | Animal | Electric Facility | Unknown | C6499 | 7.68 | 2018-05-28T21:33:00Z | 11.01 | 13 | < 25mph
| EDISON |  | 2016-05-12 | 2016 | -8 | 34.3135 | -119.1865 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | E3136 | 6.83 | 2015-01-01T01:02:00Z | 10.98 | 55 | < 25mph
|  | MAYBELL | 2017-07-02 | 2017 | 8:24 | 34.0804 | -117.8552 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | OH-144184E | OH-1255315E | T2 200Ft Outer Buffer | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-07-02 | 8:24 | Contact From Object |  | Animal | Electric Facility | Unknown | E5045 | 5 | 2017-04-16T06:06:00Z | 3 | 36 | < 25mph
|  | DRISKILL | 2016-10-18 | 2016 | 18:41 | 34.4687 | -119.7722 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Santa Barbara Fire Department | OH-2178476E | OH-2178476E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-18 | 18:41 | Equipment/Facility Failure | Fuse |  |  | Unknown | SBVC1 | 3.89 | 2017-03-07T14:24:00Z | 12.01 | 135 | < 25mph
|  | MIST | 2016-08-24 | 2016 | 16:37 | 34.4665 | -120.0701 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Santa Barbara County Fire Department | Refiugio Canyon, Santa Barbara | OH-4538468E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-24 | 18:50 | Contact From Object |  | Animal | Electric Facility | Unknown | RHWC1 | 3.48 | 2016-10-05T18:06:00Z | 22.01 | 13 | < 25mph
|  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | F0145 | 4.82 | 2018-03-04T17:20:00Z | 10 | 37 | < 25mph
|  | DEACON | 2017-10-18 | 2017 | 13:34 | 33.7702 | -117.2157 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1564666E | OH-1564666E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SDUNC | 4.59 | 2015-08-17T22:49:00Z | 18.99 | 8 | < 25mph
|  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force | TSHC1 | 6.99 | 2016-03-21T20:04:00Z | 13 | 12 | < 25mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | SE171 | 7 | 2019-05-22T00:10:00Z | 21.92 | 37 | < 25mph
|  | POULTRY | 2018-09-21 | 2018 | 8:28 | 34.0728 | -117.0397 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Juniper St. Yucaipa | OH-129241E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SE085 | 4.77 | 2019-10-20T07:40:00Z | 14.03 | 96 | < 25mph
|  | Kickapoo Trail | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1941931E | OH-1941931E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE346 | 7.42 | 2019-09-28T00:20:00Z | 25.14 | 59 | 25-40mph
|  | MIST | 2016-08-24 | 2016 | 16:37 | 34.4665 | -120.0701 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Santa Barbara County Fire Department | Refiugio Canyon, Santa Barbara | OH-4538468E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-24 | 18:50 | Contact From Object |  | Animal | Electric Facility | Unknown | RHWC1 | 3.48 | 2016-06-27T03:06:00Z | 34.99 | 14 | 25-40mph
|  | SANTA CLARA-TAYSHELL/ET-00423 | 2016-04-21 | 2016 | 12:20 | 34.3339 | -119.2748 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4434916E | OH-4434916E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2016-04-21 | 12:20 | Contact From Object |  | Animal | Electric Facility | Unknown | E8097 | 5.68 | 2016-02-13T10:59:00Z | 4.99 | 25 | < 25mph
|  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather | SE678 | 7.28 | 2020-06-22T11:30:00Z | 14.76 | 128 | < 25mph
|  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force | SE087 | 7.75 | 2018-11-13T19:20:00Z | 21.81 | 19 | < 25mph
|  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force | LYQC1 | 1.86 | 2017-12-16T15:18:00Z | 21 | 5 | < 25mph
|  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | D5145 | 4.16 | 2018-08-18T17:01:00Z | 14 | 57 | < 25mph
|  | SHOWDOWN | 2016-06-09 | 2016 | 11:28 | 34.5862 | -118.196 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4267121E | OH-4267121E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-09 | 11:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | LPDC1 | 6.32 | 2015-04-03T18:55:00Z | 21 | 16 | < 25mph
|  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown | FTNC1 | 0.32 | 2017-01-23T01:00:00Z | 14.99 | 1 | < 25mph
|  | PATRICIA | 2016-10-23 | 2016 | 9:40 | 34.4603 | -119.2853 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | 900 Rice Road Ojai | OH-786960E | Tier 3 | T3 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | CSVC1 | 6.08 | 2015-03-18T00:09:00Z | 14 | 10 | < 25mph
| ELLIS |  | 2017-10-18 | 2017 | 11:18 | 33.7721 | -117.2173 | Vegetation | Rural | Unknown |  | Unknown | Fire Agency | Cal Fire | [17 empty] | Weather | SE036 | 5.46 | 2020-01-02T20:00:00Z | 10.38 | 34 | < 25mph
|  | CONCEPCION | 2016-05-02 | 2016 | 7:03 | 34.4736 | -120.2153 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-4041841E | OH-4041841E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-02 | 7:03 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | GVTC1 | 1.55 | 2019-03-25T03:09:00Z | 14 | 1 | < 25mph
|  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown | SE248 | 0.73 | 2020-04-23T04:40:00Z | 8.68 | 63 | < 25mph
| CABIN |  | 2015-08-14 | 2015 | 13:07 | 34.0299 | -118.0726 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | D7923 | 5.49 | 2016-01-27T23:28:00Z | 7 | 64 | < 25mph
|  | Wildomar | 2019-09-19 | 2019 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside County FD | OH-2225310E | OH-2225310E | Tier 3 | T3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other | SDMEA | 4.2 | 2016-11-22T03:49:00Z | 14.99 | 11 | < 25mph
|  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | MBUC1 | 5.12 | 2015-07-03T04:56:00Z | 14.99 | 33 | < 25mph
4 |  | PYTHON | 2016-12-02 | 2016 | 21:26 | 34.3812 | -118.4132 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | OH-4572770E | OH-4572770E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE130 | 5.86 | 2020-12-06T08:40:00Z | 25 | 232 | 25-40mph
|  | Maguire | 2015-04-17 | 2015 | 16:41 | 34.0851 | -118.8044 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles County Fire | Maguire 16kV out of Latigo Sub | OH-1199311E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2015-04-17 | 16:41 | Contact From Object |  | Vehicle | Pole | None | SE204 | 6.52 | 2020-04-23T18:50:00Z | 19.95 | 117 | < 25mph
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | HBDC1 | 6.11 | 2016-09-08T19:00:00Z | 10 | 10 | < 25mph
|  | Saugus-Santa Susana | 2019-08-06 | 2019 | 15:03 | 34.3918 | -118.6596 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | VFD & LACFD | M6-T1 | M6-T1 | Tier 3 | T3 | Y | NA | 66 | Transmission | Other | Overhead | Yes | 2019-08-06 | 12:51 | Contact From Object |  | Animal | Electric Facility | Other | SE034 | 5.95 | 2020-01-15T00:40:00Z | 11.7 | 79 | < 25mph
| SADDLE RIDGE |  | 2019-10-10 | 2019 | 21:09 | 34.3299 | -118.4816 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | SAUC1 | 7.48 | 2015-06-03T02:57:00Z | 24.99 | 48 | < 25mph
|  | Zone | 2015-04-27 | 2015 | 19:10 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 4734128E | OH-4734128E | Tier 3 | T3 | Y |  | 16 | Distribution | Other | Overhead | Yes | 2015-04-27 | 19:10 | Equipment/Facility Failure | Other |  |  | Unknown | WLYC1 | 7.19 | 2016-01-10T00:49:00Z | 12.01 | 57 | < 25mph
|  | Flying D | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County | OH-1761180E | OH-1761180E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown | BKGC1 | 4.48 | 2016-09-03T12:51:00Z | 17 | 2 | < 25mph
|  | Bonanza | 2020-06-05 | 2020 | 17:33 | 35.7635 | -118.4218 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Kern County Fire Department | OH-4451126E | OH-4451126E | T3 | T3 | Y | None | 12 | Distribution | Other | Overhead | Yes | 2020-06-05 | 17:33 | Contact From Object |  | Animal | Electric Facility | Other | KRNC1 | 1.16 | 2017-10-20T22:57:00Z | 42.99 | 6 | 40-55mph
10007 |  | Vicasa | 2020-11-30 | 2020 | 21:02 | 34.0723 | -118.588 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles Fire Department | OH-4535641E | OH-4535641E | T3 | T3 |  | Verizon Wireless, AT&T Mobility, Frontier Communications, Crown Castle NG West, Inc | 16 | Distribution | Other | Overhead | Yes | 2020-11-30 | 21:02 | Contact From Object |  | Vehicle | Electric Facility | Outside Force | SE204 | 5.94 | 2019-06-21T01:10:00Z | 21.25 | 166 | < 25mph
|  | Atlanta | 2015-05-05 | 2015 | 16:00 | 33.711 | -117.7089 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 4229158E | OH-4229158E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.92 | 2016-07-25T02:51:00Z | 20 | 97 | < 25mph
|  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force | LYQC1 | 1.86 | 2016-08-24T21:18:00Z | 28.01 | 1 | 25-40mph
|  | Taiwan | 2015-07-13 | 2015 | 11:15 | 33.7678 | -117.7207 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | Cal Fire | Pole 960439E | OH-960439E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-07-13 | 13:30 | Unknown |  |  |  | Unknown | SE148 | 4.61 | 2020-02-14T07:00:00Z | 9.35 | 137 | < 25mph
|  | POPPET FLATS | 2016-02-27 | 2016 | 0:49 | 33.9134 | -116.8003 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1989045E | OH-1989045E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-02-27 | 0:49 | Contact From Object |  | Vehicle | Pole | Unknown | UP276 | 2.78 | 2016-09-10T15:55:00Z | 11.97 | 8 | < 25mph
4 |  | ANZAR | 2017-06-04 | 2017 | 13:14 | 33.8373 | -117.4863 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-1757417E | OH-1757417E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2017-06-04 | 13:14 | Wire-Wire Contact |  |  |  | Unknown | TSCC1 | 5.76 | 2016-07-20T09:41:00Z | 7 | 60 | < 25mph
| HOLIDAY |  | 2018-07-06 | 2018 | 20:40 | 34.4639 | -119.8314 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Santa Barbara Fire Department | [17 empty] | Weather | AS303 | 6.76 | 2015-03-05T23:25:00Z | 14 | 66 | < 25mph
|  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force | CSWC1 | 5.63 | 2016-01-04T00:35:00Z | 15.99 | 12 | < 25mph
|  | PATRICIA | 2017-04-16 | 2017 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4495331E | OH-4495331E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown | E3136 | 4.9 | 2015-04-29T07:31:00Z | 4.99 | 19 | < 25mph
|  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather | SRXC1 | 7.9 | 2018-12-11T22:56:00Z | 12.01 | 49 | < 25mph
|  | MIST | 2016-08-24 | 2016 | 16:37 | 34.4665 | -120.0701 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Santa Barbara County Fire Department | Refiugio Canyon, Santa Barbara | OH-4538468E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-24 | 18:50 | Contact From Object |  | Animal | Electric Facility | Unknown | RHWC1 | 3.48 | 2016-02-14T12:06:00Z | 32.01 | 13 | 25-40mph
|  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | TPGC1 | 0.38 | 2015-12-04T19:57:00Z | 18.99 | 60 | < 25mph
|  | HUCKLEBERRY | 2017-03-17 | 2017 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4493863E | OH-4493863E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown | E1966 | 2.92 | 2015-06-08T14:11:00Z | 1.01 | 8 | < 25mph
|  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TPGC1 | 1.58 | 2018-10-07T22:57:00Z | 24.99 | 113 | < 25mph
|  | CONCEPCION | 2016-05-02 | 2016 | 7:03 | 34.4736 | -120.2153 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-4041841E | OH-4041841E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-02 | 7:03 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UP481 | 0.66 | 2015-03-25T21:00:00Z | 7.02 | 13 | < 25mph
|  | Pawley | 2015-05-29 | 2015 | 7:29 | 36.387 | -118.9536 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare County Fire | Lemon Cove and Three Rivers Sub. Venida 66kV | OH-4434944E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-05-29 | 7:29 | Contact From Object |  | Animal | Electric Facility | None | D0117 | 5.17 | 2018-04-24T13:35:00Z | 3 | 4 | < 25mph
|  | CACHUMA | 2016-08-18 | 2016 | 14:52 | 34.5356 | -119.8523 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-1413051E | OH-1413051E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-18 | 14:52 | Contact From Object |  | Vegetation | Communication Facility | Unknown | SE068 | 4.85 | 2019-06-09T23:10:00Z | 17.76 | 121 | < 25mph
|  | TUNA | 2016-09-19 | 2016 | 6:11 | 34.04 | -118.6687 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-1638513E | OH-1638513E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | MBUC1 | 2.01 | 2020-02-25T11:56:00Z | 27 | 155 | 25-40mph
|  | BRUMFIELD | 2016-06-04 | 2016 | 10:17 | 33.5947 | -117.1387 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-2206630E | OH-2206630E | Tier 2 | T2 | Y |  | 12 | Distribution | Transformer | Overhead | Yes | 2016-06-04 | 10:17 | Equipment/Facility Failure | Transformer |  |  | Unknown | SDMEA | 6.79 | 2019-05-03T21:49:00Z | 18.99 | 44 | < 25mph
|  | CABANA | 2017-10-16 | 2017 | 6:11 | 34.0217 | -117.5069 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1670014E | OH-1670014E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-10-16 | 6:11 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE822 | 4.35 | 2020-11-25T13:10:00Z | 10.45 | 109 | < 25mph
|  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | SE204 | 5.55 | 2020-12-25T21:30:00Z | 15.93 | 252 | < 25mph
| RYE |  | 2017-12-05 | 2017 | 15:00 | 34.2676 | -117.844 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | TANC1 | 6.35 | 2020-02-27T17:01:00Z | 11.01 | 16 | < 25mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | E1966 | 3.22 | 2015-06-27T21:09:00Z | 30 | 13 | 25-40mph
|  | Plateau | 2019-09-11 | 2019 | 8:08 | 34.0991 | -118.6793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4424792E | OH-4424792E | Tier 3 | T3 | Y | Verizon / AT&T / Crown Castle | 16 | Distribution | Conductor | Overhead | Yes | 2019-09-11 | 8:08 | Equipment/Facility Failure | Conductor |  | Electric Facility | Human Error | MBCC1 | 1.73 | 2020-05-02T22:56:00Z | 28.01 | 202 | 25-40mph
|  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SE336 | 7.18 | 2020-09-03T01:10:00Z | 21.34 | 115 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TNRC1 | 2.34 | 2015-05-23T01:57:00Z | 14 | 65 | < 25mph
|  | LEE VINING-LUNDY NO. 1/ET-01774 | 2017-05-01 | 2017 | 5:40 | 38.0209 | -119.1608 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | CAlFIre | OH-1580964E | OH-1580964E | Tier 2 | T2 | Y |  | 55 | Distribution | Conductor | Overhead | No | <Null> |  | Contamination |  |  |  | Unknown | ERYC1 | 7.12 | 2015-01-27T18:00:00Z | 10.29 | 12 | < 25mph
|  | CACHUMA | 2016-08-18 | 2016 | 14:52 | 34.5356 | -119.8523 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-1413051E | OH-1413051E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-18 | 14:52 | Contact From Object |  | Vegetation | Communication Facility | Unknown | AS303 | 7.85 | 2016-08-07T16:18:00Z | 11.01 | 105 | < 25mph
|  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown | UCSH | 2.26 | 2015-07-29T07:50:00Z | 10.4 | 10 | < 25mph
|  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error | C1909 | 5.95 | 2017-03-01T20:09:00Z | 4.99 | 12 | < 25mph
|  | Conestoga | 2020-06-13 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Other | TSCC1 | 2.56 | 2019-11-26T23:41:00Z | 13 | 83 | < 25mph
|  | OAK GLEN | 2017-03-15 | 2017 | 13:23 | 34.0534 | -116.971 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-2326555E | OH-2326555E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-15 | 13:23 | Contact From Object |  | Animal | Electric Facility | Unknown | C9072 | 4.81 | 2015-11-08T05:27:00Z | 12.01 | 54 | < 25mph
|  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | SE208 | 6.68 | 2020-06-20T14:10:00Z | 6.21 | 232 | < 25mph
|  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | MLCC1 | 7.93 | 2017-06-13T23:53:00Z | 14 | 10 | < 25mph
|  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.54 | 2019-07-21T01:51:00Z | 17 | 136 | < 25mph
|  | Mettler | 2020-08-10 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | OH-2093506E | OH-2093506E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Unknown | E3266 | 6.59 | 2018-08-20T06:34:00Z | 14 | 40 | < 25mph
|  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other | PPPC1 | 1.78 | 2018-07-01T01:56:00Z | 35.99 | 3 | 25-40mph
|  | VALLEY-MAYBERRY-MORENO-VISTA | 2020-05-18 | 2020 | 12:10 | 33.8587 | -117.0203 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire Perris | OH-1979539E | OH-1979539E | T3 | T3 | Y | None | 115 | Transmission | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Other | HSGC1 | 4.08 | 2019-01-23T10:16:00Z | 17 | 20 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | SE122 | 3.24 | 2019-05-28T15:40:00Z | 8.32 | 106 | < 25mph
| LIBERTY |  | 2017-12-07 | 2017 | 13:00 | 33.5926 | -117.1498 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | Murrieta Fire Department | [17 empty] | Weather | SE224 | 0.95 | 2019-11-23T04:30:00Z | 10.29 | 55 | < 25mph
|  | Zone | 2015-04-27 | 2015 | 19:10 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 4734128E | OH-4734128E | Tier 3 | T3 | Y |  | 16 | Distribution | Other | Overhead | Yes | 2015-04-27 | 19:10 | Equipment/Facility Failure | Other |  |  | Unknown | SE107 | 7.41 | 2018-10-25T13:20:00Z | 10.51 | 94 | < 25mph
|  | TUNA | 2016-09-19 | 2016 | 6:11 | 34.04 | -118.6687 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-1638513E | OH-1638513E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | E2805 | 6.33 | 2017-07-28T04:55:00Z | 10 | 35 | < 25mph
|  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather | CEKC1 | 7.88 | 2020-03-22T04:54:00Z | 5.99 | 93 | < 25mph
|  | OAK GLEN | 2017-03-15 | 2017 | 13:23 | 34.0534 | -116.971 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-2326555E | OH-2326555E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-15 | 13:23 | Contact From Object |  | Animal | Electric Facility | Unknown | C9072 | 4.81 | 2017-02-04T03:57:00Z | 14.99 | 54 | < 25mph
|  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other | SE438 | 5.87 | 2020-10-07T06:10:00Z | 26.59 | 36 | 25-40mph
|  | Atlanta | 2015-05-05 | 2015 | 16:00 | 33.711 | -117.7089 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 4229158E | OH-4229158E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vehicle | Electric Facility | None | E3131 | 7.82 | 2016-12-16T02:30:00Z | 24 | 91 | < 25mph
|  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown | FTNC1 | 0.32 | 2015-08-21T01:00:00Z | 15.99 | 1 | < 25mph
|  | POPPET FLATS | 2016-02-27 | 2016 | 0:49 | 33.9134 | -116.8003 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1989045E | OH-1989045E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-02-27 | 0:49 | Contact From Object |  | Vehicle | Pole | Unknown | SE552 | 6.18 | 2020-09-11T15:50:00Z | 15.05 | 113 | < 25mph
10005 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error | LPDC1 | 6.51 | 2018-06-05T14:55:00Z | 31 | 8 | 25-40mph
|  | Hughes Lake | 2019-09-02 | 2019 | 14:02 | 34.7026 | -118.342 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4782978E | OH-4782978E | Tier 2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-02 | 14:02 | Contact From Object |  | Balloons | Electric Facility | Other | PPPC1 | 3.45 | 2019-04-06T03:56:00Z | 21 | 39 | < 25mph
|  | Saugus-Santa Susana | 2019-08-06 | 2019 | 15:03 | 34.3918 | -118.6596 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | VFD & LACFD | M6-T1 | M6-T1 | Tier 3 | T3 | Y | NA | 66 | Transmission | Other | Overhead | Yes | 2019-08-06 | 12:51 | Contact From Object |  | Animal | Electric Facility | Other | DLVC1 | 2.65 | 2015-02-02T13:55:00Z | 8.01 | 7 | < 25mph
|  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error | E3266 | 7.24 | 2018-05-14T22:27:00Z | 21 | 21 | < 25mph
|  | ELSTER | 2016-04-25 | 2016 | 19:15 | 36.1372 | -118.8615 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-X16345E | OH-X16345E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 120/240 V | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 19:15 | Equipment/Facility Failure | Conductor |  |  | Unknown | MOLC1 | 6.51 | 2020-01-10T02:27:00Z | 7 | 28 | < 25mph
|  | GUITAR | 2017-05-11 | 2017 | 12:27 | 34.4127 | -118.6702 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-848255E | OH-848255E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-05-11 | 12:27 | Contact From Object |  | Balloons | Electric Facility | Unknown | E3126 | 6.99 | 2016-11-20T07:29:00Z | 23 | 7 | < 25mph
|  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other | SE178 | 7.71 | 2020-08-03T14:20:00Z | 22.65 | 120 | < 25mph
|  | GUITAR | 2017-05-11 | 2017 | 12:27 | 34.4127 | -118.6702 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-848255E | OH-848255E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-05-11 | 12:27 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE079 | 7.87 | 2019-10-26T10:50:00Z | 14.03 | 81 | < 25mph
|  | GUITAR | 2016-01-16 | 2016 | 15:20 | 34.4096 | -118.6816 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-848266E | OH-848266E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-01-16 | 15:20 | Equipment/Facility Failure | Other |  |  | Unknown | PU | 7.33 | 2015-01-18T12:00:00Z | 9.4 | 10 | < 25mph
10002 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | CEEC1 | 3.51 | 2015-04-17T13:38:00Z | 5.99 | 36 | < 25mph
10006 |  | CONCEPCION | 2016-05-12 | 2016 | 8:55 | 34.4736 | -120.216 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-708452E | OH-708452E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-12 | 8:55 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UP481 | 0.62 | 2015-09-03T14:00:00Z | 21.99 | 10 | < 25mph
|  | WELCH | 2016-04-25 | 2016 | 15:23 | 35.8387 | -118.9147 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1078325E | OH-1078325E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 15:23 | Equipment/Facility Failure | Insulator |  |  | Unknown | FTNC1 | 3.62 | 2015-11-14T16:00:00Z | 5.99 | 1 | < 25mph
| RYE |  | 2017-12-05 | 2017 | 11:31 | 34.4528 | -118.5819 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | SAUC1 | 4.1 | 2017-12-06T21:57:00Z | 32.01 | 15 | 25-40mph
|  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other | LPDC1 | 2.12 | 2016-11-22T17:55:00Z | 8.99 | 10 | < 25mph
|  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force | TSHC1 | 6.99 | 2017-12-01T04:04:00Z | 8.99 | 8 | < 25mph
|  | Zone | 2015-04-27 | 2015 | 19:09 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | 9372 STOCKTON RD PMP MOORPARK | OH-4734128E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-04-27 | 19:09 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | F1963 | 1.81 | 2019-02-21T18:17:00Z | 12.01 | 98 | < 25mph
10006 |  | Capanero | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | T2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Unknown | UHLC1 | 1.17 | 2018-06-20T10:59:00Z | 5.99 | 13 | < 25mph
|  | CABANA | 2017-10-16 | 2017 | 6:11 | 34.0217 | -117.5069 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1670014E | OH-1670014E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-10-16 | 6:11 | Contact From Object |  | Balloons | Electric Facility | Unknown | AU481 | 5 | 2019-02-01T16:45:00Z | 7 | 16 | < 25mph
|  | Soda Springs | 2015-05-14 | 2015 | 22:24 | 36.1318 | -118.7784 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | Soda Springs 12kV out of Boxwood Sub | OH-4464511E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-14 | 22:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown | OORC1 | 5.23 | 2016-04-03T13:12:00Z | 10 | 1 | < 25mph
|  | VIENTO | 2016-06-06 | 2016 | 17:44 | 35.1355 | -118.4771 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1373165E | OH-1373165E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-06 | 17:44 | Contact From Object |  | Other | Pole | Unknown | SE067 | 5.98 | 2019-12-06T11:00:00Z | 32.66 | 85 | 25-40mph
|  | DALBA | 2017-07-11 | 2017 | 18:06 | 34.2054 | -117.1143 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-919465E | OH-919465E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 2.4 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | SE151 | 3.96 | 2019-11-18T21:10:00Z | 12.41 | 160 | < 25mph
|  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | KNWC1 | 3.86 | 2018-09-20T04:17:00Z | 10 | 31 | < 25mph
10005 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | E7577 | 6.74 | 2017-02-01T03:48:00Z | 7 | 46 | < 25mph
|  | Flying D | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County | OH-1761180E | OH-1761180E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown | BKGC1 | 4.48 | 2017-12-23T06:51:00Z | 18.99 | 2 | < 25mph
|  | Zone | 2019-08-10 | 2019 | 13:00 | 34.3089 | -118.9413 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | VFD | OH-4734128E | OH-4734128E | Tier 3 | T3 | Y | AT&T Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | SE044 | 4.3 | 2018-08-21T11:00:00Z | 9.75 | 78 | < 25mph
|  | Python | 2015-06-06 | 2015 | 10:00 | 34.4043 | -118.4234 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | 16450 Alamo Canyon Rd, Canyon Country | OH-4779534E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-06-06 | 10:13 | Contact From Object |  | Animal | Electric Facility | None | CNIC1 | 3.54 | 2018-01-25T03:55:00Z | 14.99 | 35 | < 25mph
|  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error | AU563 | 7.19 | 2018-05-13T07:52:00Z | 35.99 | 21 | 25-40mph
|  | ELSTER | 2016-04-25 | 2016 | 19:15 | 36.1372 | -118.8615 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-X16345E | OH-X16345E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 120/240 V | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 19:15 | Equipment/Facility Failure | Conductor |  |  | Unknown | MOLC1 | 6.51 | 2016-05-25T13:27:00Z | 10 | 1 | < 25mph
|  | HUCKLEBERRY | 2017-03-17 | 2017 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4493863E | OH-4493863E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown | E1966 | 2.92 | 2017-05-27T15:09:00Z | 4 | 10 | < 25mph
| TENAJA |  | 2019-09-04 | 2019 | 16:43 | 33.5285 | -117.2732 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | SRUC1 | 2.64 | 2017-09-16T22:54:00Z | 18.99 | 19 | < 25mph
| CABIN |  | 2015-08-14 | 2015 | 13:07 | 34.0299 | -118.0726 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | WTHC1 | 4.82 | 2019-09-04T01:57:00Z | 13 | 89 | < 25mph
10002 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | CEEC1 | 3.51 | 2017-08-20T16:38:00Z | 8.01 | 68 | < 25mph
|  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other | GMTC1 | 4.77 | 2019-01-02T23:59:00Z | 18.01 | 11 | < 25mph
| TENAJA |  | 2019-09-04 | 2019 | 16:43 | 33.5285 | -117.2732 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | SE452 | 4.75 | 2020-10-01T04:00:00Z | 11.69 | 149 | < 25mph
|  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown | KMMH | 1.38 | 2017-04-20T02:35:00Z | 34.52 | 14 | 25-40mph
|  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather | CEKC1 | 7.88 | 2018-11-01T02:54:00Z | 17 | 56 | < 25mph
10005 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error | ATNC1 | 5.18 | 2017-03-02T15:54:00Z | 18.01 | 12 | < 25mph
10004 |  | HUGHES LAKE | 2016-10-26 | 2016 | 12:19 | 34.7081 | -118.5367 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | ELIZABETH LAKE ROAD AND KINGS CANYON ROAD, LAKE HUGHES | OH-1586523E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-26 | 12:19 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE071 | 5.52 | 2019-12-01T11:00:00Z | 9.57 | 18 | < 25mph
|  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE093 | 0.96 | 2018-10-19T07:10:00Z | 21.25 | 44 | < 25mph
|  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force | SE311 | 4.49 | 2020-01-07T01:00:00Z | 13.87 | 45 | < 25mph
| RYE |  | 2017-12-05 | 2017 | 15:00 | 34.2676 | -117.844 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | TANC1 | 6.35 | 2015-02-24T19:01:00Z | 17 | 1 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TNRC1 | 2.34 | 2015-01-08T22:57:00Z | 17 | 41 | < 25mph
4 |  | ANZAR | 2017-06-04 | 2017 | 13:14 | 33.8373 | -117.4863 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-1757417E | OH-1757417E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2017-06-04 | 13:14 | Wire-Wire Contact |  |  |  | Unknown | TSCC1 | 5.76 | 2019-04-02T21:41:00Z | 30 | 62 | 25-40mph
|  | PATRICIA | 2016-10-23 | 2016 | 9:40 | 34.4603 | -119.2853 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | 900 Rice Road Ojai | OH-786960E | Tier 3 | T3 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | CSVC1 | 6.08 | 2016-06-09T08:09:00Z | 4 | 5 | < 25mph
4 |  | PYTHON | 2016-12-02 | 2016 | 21:26 | 34.3812 | -118.4132 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | OH-4572770E | OH-4572770E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vegetation | Electric Facility | Unknown | NHPC1 | 6.84 | 2015-12-13T17:56:00Z | 20 | 24 | < 25mph
|  | LEE VINING-LUNDY NO. 1/ET-01774 | 2017-05-01 | 2017 | 5:40 | 38.0209 | -119.1608 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | CAlFIre | OH-1580964E | OH-1580964E | Tier 2 | T2 | Y |  | 55 | Distribution | Conductor | Overhead | No | <Null> |  | Contamination |  |  |  | Unknown | ERYC1 | 7.12 | 2017-04-17T04:00:00Z | 31.9 | 6 | 25-40mph
|  | GUITAR | 2016-01-16 | 2016 | 15:20 | 34.4096 | -118.6816 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-848266E | OH-848266E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-01-16 | 15:20 | Equipment/Facility Failure | Other |  |  | Unknown | PU | 7.33 | 2018-07-04T05:00:00Z | 9.4 | 15 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | E4628 | 5.1 | 2015-09-16T17:26:00Z | 10 | 102 | < 25mph
10006 |  | CONCEPCION | 2016-05-12 | 2016 | 8:55 | 34.4736 | -120.216 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-708452E | OH-708452E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-12 | 8:55 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | GVTC1 | 1.52 | 2019-02-06T04:09:00Z | 17 | 4 | < 25mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | ATNC1 | 4.83 | 2015-10-22T09:54:00Z | 11.01 | 3 | < 25mph
|  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown | SE388 | 2.62 | 2020-08-02T00:30:00Z | 26.3 | 84 | 25-40mph
|  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other | SE071 | 4.6 | 2020-09-10T15:20:00Z | 12.13 | 35 | < 25mph
| SADDLE RIDGE |  | 2019-10-10 | 2019 | 21:09 | 34.3299 | -118.4816 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | CNIC1 | 3.94 | 2017-02-04T22:55:00Z | 17 | 70 | < 25mph
|  | Conestoga | 2020-06-13 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Other | MHEC1 | 2.44 | 2017-04-15T20:16:00Z | 18.01 | 29 | < 25mph
10004 |  | HUGHES LAKE | 2016-10-26 | 2016 | 12:19 | 34.7081 | -118.5367 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | ELIZABETH LAKE ROAD AND KINGS CANYON ROAD, LAKE HUGHES | OH-1586523E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-26 | 12:19 | Contact From Object |  | Vegetation | Electric Facility | Unknown | C4614 | 6.71 | 2017-03-02T00:30:00Z | 15.99 | 6 | < 25mph
10005 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | SE424 | 7.23 | 2020-04-02T06:20:00Z | 10.58 | 188 | < 25mph
|  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error | SAUC1 | 7.39 | 2015-09-12T22:57:00Z | 17 | 12 | < 25mph
| MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | CEEC1 | 3.58 | 2020-12-08T19:38:00Z | 32 | 264 | 25-40mph
| TENAJA |  | 2019-09-04 | 2019 | 16:43 | 33.5285 | -117.2732 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | DLZSD | 5.04 | 2019-03-10T21:00:00Z | 14 | 30 | < 25mph
|  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE757 | 3.02 | 2020-07-19T01:20:00Z | 18.85 | 119 | < 25mph
|  | WELCH | 2016-04-25 | 2016 | 15:23 | 35.8387 | -118.9147 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1078325E | OH-1078325E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 15:23 | Equipment/Facility Failure | Insulator |  |  | Unknown | FTNC1 | 3.62 | 2018-08-28T04:00:00Z | 4 | 1 | < 25mph
3 |  | Bidder | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire | OH-2023941E | OH-2023941E | T3 | T3 |  | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force | E6919 | 1.69 | 2015-07-05T13:15:00Z | 5.99 | 27 | < 25mph
|  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None | SE134 | 0.88 | 2020-05-24T17:20:00Z | 10.89 | 188 | < 25mph
|  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | D5145 | 4.16 | 2019-01-22T09:16:00Z | 28.01 | 61 | 25-40mph
|  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error | AU563 | 7.19 | 2016-11-14T10:40:00Z | 20 | 19 | < 25mph
|  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | TNRC1 | 5.88 | 2016-09-18T23:57:00Z | 15.99 | 112 | < 25mph
|  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other | UCCC1 | 5.31 | 2017-07-13T06:56:00Z | 5.99 | 16 | < 25mph
|  | Pawley | 2015-05-29 | 2015 | 7:29 | 36.387 | -118.9536 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare County Fire | Lemon Cove and Three Rivers Sub. Venida 66kV | OH-4434944E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-05-29 | 7:29 | Contact From Object |  | Animal | Electric Facility | None | SE589 | 4.29 | 2020-09-05T00:30:00Z | 9.57 | 54 | < 25mph
|  | Lasker | 2020-07-26 | 2020 | 12:50 | 34.5326 | -118.0541 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4619162E | OH-4619162E | T3 | T3 |  | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | LPDC1 | 2.76 | 2018-04-12T00:55:00Z | 51 | 16 | 40-55mph
|  | Maguire | 2015-04-17 | 2015 | 16:41 | 34.0851 | -118.8044 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles County Fire | Maguire 16kV out of Latigo Sub | OH-1199311E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2015-04-17 | 16:41 | Contact From Object |  | Vehicle | Pole | None | MBCC1 | 5.78 | 2017-07-18T03:56:00Z | 15.99 | 25 | < 25mph
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | BPOC1 | 4.63 | 2016-07-01T02:49:00Z | 24 | 12 | < 25mph
|  | GUITAR | 2017-05-11 | 2017 | 12:27 | 34.4127 | -118.6702 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-848255E | OH-848255E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-05-11 | 12:27 | Contact From Object |  | Balloons | Electric Facility | Unknown | PU | 7.98 | 2018-05-11T03:00:00Z | 11.41 | 8 | < 25mph
|  | CACHUMA | 2016-08-18 | 2016 | 14:52 | 34.5356 | -119.8523 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-1413051E | OH-1413051E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-18 | 14:52 | Contact From Object |  | Vegetation | Communication Facility | Unknown | KSBA | 7.58 | 2017-03-24T23:25:00Z | 25.32 | 123 | 25-40mph
| HOLIDAY |  | 2018-07-06 | 2018 | 20:40 | 34.4639 | -119.8314 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Santa Barbara Fire Department | [17 empty] | Weather | MPWC1 | 2.75 | 2019-02-18T13:06:00Z | 18.99 | 155 | < 25mph
|  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | WTHC1 | 5.52 | 2017-03-22T20:57:00Z | 24.99 | 117 | < 25mph
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | BPOC1 | 4.63 | 2018-04-10T04:49:00Z | 8.99 | 13 | < 25mph
|  | SPRINGVILLE-LINDSAY-VENIDA/ET-07230,SPRINGVILLE-STRATHMORE/ET-07256 | 2015-06-17 | 2015 | 17:29 | 36.1086 | -118.9425 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 722603E | OH-722604E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-06-17 | 17:29 | Contact From Object |  | Animal | Electric Facility | None | SE279 | 3.12 | 2020-01-08T16:20:00Z | 5.55 | 43 | < 25mph
2 |  | Lopez | 2015-05-23 | 2015 | 11:57 | 34.3006 | -118.3613 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | Pole 1261671E | OH-1261671E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Conductor | Overhead | Yes | 2015-05-23 | 11:05 | Unknown |  |  |  | Unknown | CNIC1 | 4.89 | 2020-05-02T00:55:00Z | 14.99 | 113 | < 25mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | ATNC1 | 4.83 | 2017-06-01T08:54:00Z | 4.99 | 1 | < 25mph
|  | WELCH | 2016-04-25 | 2016 | 15:23 | 35.8387 | -118.9147 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1078325E | OH-1078325E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 15:23 | Equipment/Facility Failure | Insulator |  |  | Unknown | FTNC1 | 3.62 | 2018-06-21T23:00:00Z | 14 | 1 | < 25mph
|  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown | WTPC1 | 2.77 | 2020-12-16T04:57:00Z | 26 | 50 | 25-40mph
|  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force | SE113 | 6.61 | 2019-01-18T13:30:00Z | 31.56 | 23 | 25-40mph
|  | HUGHES LAKE/ED-08810 | 2018-07-06 | 2018 | 5:38 | 34.6744 | -118.4517 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | 465140E | OH-1938477E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-07-06 | 5:38 | Contact From Object |  | Vehicle | Pole | Unknown | SE438 | 6.94 | 2019-11-05T05:10:00Z | 12.12 | 39 | < 25mph
|  | TUNA | 2016-09-19 | 2016 | 6:11 | 34.04 | -118.6687 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-1638513E | OH-1638513E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | MBCC1 | 3.63 | 2018-06-18T20:56:00Z | 25.99 | 87 | 25-40mph
10004 |  | HUGHES LAKE | 2016-10-26 | 2016 | 12:19 | 34.7081 | -118.5367 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | ELIZABETH LAKE ROAD AND KINGS CANYON ROAD, LAKE HUGHES | OH-1586523E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-26 | 12:19 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE071 | 5.52 | 2020-07-31T22:00:00Z | 29.23 | 18 | 25-40mph
|  | LEE VINING-LUNDY NO. 1/ET-01774 | 2017-05-01 | 2017 | 5:40 | 38.0209 | -119.1608 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | CAlFIre | OH-1580964E | OH-1580964E | Tier 2 | T2 | Y |  | 55 | Distribution | Conductor | Overhead | No | <Null> |  | Contamination |  |  |  | Unknown | UNDC1 | 1.29 | 2018-03-06T07:23:00Z | 8.01 | 9 | < 25mph
|  | POPPET FLATS | 2016-02-27 | 2016 | 0:49 | 33.9134 | -116.8003 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1989045E | OH-1989045E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-02-27 | 0:49 | Contact From Object |  | Vehicle | Pole | Unknown | POPC1 | 5.22 | 2019-01-23T16:14:00Z | 18.01 | 22 | < 25mph
|  | METTLER | 2017-06-02 | 2017 | 10:50 | 35.1021 | -118.5328 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4416566E | OH-4416566E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | C1020 | 3.62 | 2015-07-15T20:00:00Z | 23 | 46 | < 25mph
|  | SPRINGVILLE-LINDSAY-VENIDA/ET-07230,SPRINGVILLE-STRATHMORE/ET-07256 | 2015-06-17 | 2015 | 17:29 | 36.1086 | -118.9425 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 722603E | OH-722604E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-06-17 | 17:29 | Contact From Object |  | Animal | Electric Facility | None | SE279 | 3.12 | 2020-11-24T06:50:00Z | 9.79 | 59 | < 25mph
|  | MAYBELL | 2017-07-02 | 2017 | 8:24 | 34.0804 | -117.8552 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | OH-144184E | OH-1255315E | T2 200Ft Outer Buffer | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-07-02 | 8:24 | Contact From Object |  | Animal | Electric Facility | Unknown | D6285 | 6.41 | 2019-03-04T13:55:00Z | 5.99 | 90 | < 25mph
|  | Flying D | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County | OH-1761180E | OH-1761180E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown | SE232 | 7.46 | 2020-07-06T23:30:00Z | 32.08 | 26 | 25-40mph
2 |  | Lopez | 2015-05-23 | 2015 | 11:57 | 34.3006 | -118.3613 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | Pole 1261671E | OH-1261671E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Conductor | Overhead | Yes | 2015-05-23 | 11:05 | Unknown |  |  |  | Unknown | CNIC1 | 4.89 | 2018-02-27T01:55:00Z | 28.99 | 49 | 25-40mph
|  | Taiwan | 2015-07-13 | 2015 | 11:15 | 33.7678 | -117.7207 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | Cal Fire | Pole 960439E | OH-960439E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-07-13 | 13:30 | Unknown |  |  |  | Unknown | E3131 | 5.99 | 2016-10-09T10:58:00Z | 4.99 | 94 | < 25mph
|  | Northpark | 2019-06-20 | 2019 | 14:08 | 34.2298 | -117.4048 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | San Bern. FD | OH-201371S | OH-201371S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Human Error | DVOC1 | 3.48 | 2016-11-30T14:10:00Z | 12.01 | 7 | < 25mph
10004 |  | HUGHES LAKE | 2016-10-26 | 2016 | 12:19 | 34.7081 | -118.5367 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | ELIZABETH LAKE ROAD AND KINGS CANYON ROAD, LAKE HUGHES | OH-1586523E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-26 | 12:19 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE071 | 5.52 | 2020-10-16T21:40:00Z | 23.17 | 35 | < 25mph
|  | RHODA | 2016-12-30 | 2016 | 11:42 | 34.1231 | -118.723 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-1927507E | OH-1927507E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-12-30 | 11:42 | Contact From Object |  | Balloons | Electric Facility | Unknown | MBCC1 | 2.93 | 2016-04-13T00:56:00Z | 24.99 | 53 | < 25mph
|  | Zone | 2015-04-27 | 2015 | 19:09 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | 9372 STOCKTON RD PMP MOORPARK | OH-4734128E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-04-27 | 19:09 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | WLYC1 | 7.19 | 2015-01-26T07:49:00Z | 15.99 | 29 | < 25mph
|  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | D2363 | 4.16 | 2017-04-03T10:39:00Z | 13 | 59 | < 25mph
|  | PATRICIA | 2016-10-23 | 2016 | 9:40 | 34.4603 | -119.2853 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | 900 Rice Road Ojai | OH-786960E | Tier 3 | T3 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | CSVC1 | 6.08 | 2016-11-04T20:09:00Z | 14.99 | 4 | < 25mph
|  | MIST | 2016-08-24 | 2016 | 16:37 | 34.4665 | -120.0701 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Santa Barbara County Fire Department | Refiugio Canyon, Santa Barbara | OH-4538468E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-24 | 18:50 | Contact From Object |  | Animal | Electric Facility | Unknown | RHWC1 | 3.48 | 2018-06-30T00:06:00Z | 11.01 | 13 | < 25mph
|  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown | HMMC1 | 3.23 | 2016-08-25T22:14:00Z | 21 | 15 | < 25mph
|  | BRUMFIELD | 2016-06-04 | 2016 | 10:17 | 33.5947 | -117.1387 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-2206630E | OH-2206630E | Tier 2 | T2 | Y |  | 12 | Distribution | Transformer | Overhead | Yes | 2016-06-04 | 10:17 | Equipment/Facility Failure | Transformer |  |  | Unknown | E3052 | 7.64 | 2017-02-24T10:50:00Z | 8.01 | 37 | < 25mph
|  | Sexton | 2015-02-22 | 2015 | 9:52 | 34.2849 | -119.2173 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura Fire Department | Pole 1718768E | OH-1718768E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-02-22 | 10:49 | Unknown |  |  |  | None | AT185 | 8 | 2017-03-31T15:19:00Z | 24.99 | 28 | < 25mph
|  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | LCBC1 | 6.83 | 2020-10-21T00:55:00Z | 17 | 213 | < 25mph
|  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other | UCBU | 3.92 | 2016-02-09T08:20:00Z | 14.41 | 7 | < 25mph
|  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TPGC1 | 1.58 | 2017-06-11T14:57:00Z | 17 | 65 | < 25mph
|  | OAK GLEN | 2017-03-15 | 2017 | 13:23 | 34.0534 | -116.971 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-2326555E | OH-2326555E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-15 | 13:23 | Contact From Object |  | Animal | Electric Facility | Unknown | BNJC1 | 6.47 | 2019-12-08T05:13:00Z | 11.01 | 71 | < 25mph
3 |  | Bidder | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire | OH-2023941E | OH-2023941E | T3 | T3 |  | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force | MPWC1 | 5.77 | 2020-10-19T06:06:00Z | 25 | 216 | 25-40mph
| STAR |  | 2019-07-28 | 2019 | 14:00 | 33.9975 | -117.7698 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Chino Valley Fire Department | [13 empty] | Contact From Object |  | Bird |  | Weather | TNRC1 | 4.58 | 2015-10-25T11:57:00Z | 17 | 81 | < 25mph
|  | Maguire | 2015-04-17 | 2015 | 16:41 | 34.0851 | -118.8044 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles County Fire | Maguire 16kV out of Latigo Sub | OH-1199311E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2015-04-17 | 16:41 | Contact From Object |  | Vehicle | Pole | None | D1664 | 3.65 | 2017-01-08T17:13:00Z | 11.01 | 23 | < 25mph
| MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | D2363 | 5.89 | 2017-10-20T13:33:00Z | 12.01 | 72 | < 25mph
|  | JORDAN | 2018-08-29 | 2018 | 17:32 | 35.7358 | -118.7192 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | Jack Ranch Rd/White River Rd, Kernville | OH-4635091E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-08-29 | 19:06 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE290 | 5.44 | 2020-08-13T05:10:00Z | 13.15 | 28 | < 25mph
|  | PYTHON | 2016-06-05 | 2016 | 15:59 | 34.4208 | -118.4218 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4154960E | OH-4154960E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-06-05 | 15:59 | Unknown |  |  |  | Unknown | CNIC1 | 4.67 | 2017-07-24T07:55:00Z | 8.99 | 28 | < 25mph
|  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | MSJC1 | 4.82 | 2017-04-08T13:53:00Z | 22.01 | 17 | < 25mph
|  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown | LYQC1 | 4.98 | 2018-06-22T02:18:00Z | 28.01 | 1 | 25-40mph
|  | SHOWDOWN | 2016-06-09 | 2016 | 11:28 | 34.5862 | -118.196 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4267121E | OH-4267121E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-09 | 11:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE178 | 3.25 | 2019-10-19T04:10:00Z | 29.53 | 65 | 25-40mph
|  | PICK | 2017-06-19 | 2017 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | 30278 Arrastre Canyon Rd., Acton | OH-699610E | Tier 3 | T3 | Y |  | 33 | Distribution | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown | ATNC1 | 0.34 | 2019-12-02T23:54:00Z | 18.99 | 44 | < 25mph
|  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather | SE177 | 6.99 | 2020-09-20T09:20:00Z | 18.27 | 158 | < 25mph
|  | VALLEY-MAYBERRY-MORENO-VISTA | 2020-05-18 | 2020 | 12:10 | 33.8587 | -117.0203 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire Perris | OH-1979539E | OH-1979539E | T3 | T3 | Y | None | 115 | Transmission | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Other | HSGC1 | 4.08 | 2016-05-02T06:16:00Z | 8.01 | 28 | < 25mph
|  | VALLECITO | 2016-08-18 | 2016 | 19:00 | 34.4214 | -119.5964 | Other | Rural | Structure Only | Structure Only |  | Fire Agency | Santa Barbara County Fire Department | 2400 block of Whitney Avenue in Summerland | OH-1523986E | Tier 2 | T2 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | MTIC1 | 4.08 | 2016-03-09T16:47:00Z | 24.99 | 32 | < 25mph
4 |  | ANZAR | 2017-06-04 | 2017 | 13:14 | 33.8373 | -117.4863 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-1757417E | OH-1757417E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2017-06-04 | 13:14 | Wire-Wire Contact |  |  |  | Unknown | SDRVP | 7.42 | 2017-10-12T15:49:00Z | 5.99 | 58 | < 25mph
|  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error | SAUC1 | 7.39 | 2018-02-08T20:57:00Z | 28.99 | 13 | 25-40mph
|  | Lasker | 2020-07-26 | 2020 | 12:50 | 34.5326 | -118.0541 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4619162E | OH-4619162E | T3 | T3 |  | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | LPDC1 | 2.76 | 2016-09-07T23:55:00Z | 42.01 | 8 | 40-55mph
4 |  | PYTHON | 2016-12-02 | 2016 | 21:26 | 34.3812 | -118.4132 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | OH-4572770E | OH-4572770E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vegetation | Electric Facility | Unknown | CNIC1 | 1.96 | 2019-09-09T22:55:00Z | 24.99 | 104 | < 25mph
10004 |  | HUGHES LAKE | 2016-10-26 | 2016 | 12:19 | 34.7081 | -118.5367 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | ELIZABETH LAKE ROAD AND KINGS CANYON ROAD, LAKE HUGHES | OH-1586523E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-26 | 12:19 | Contact From Object |  | Vegetation | Electric Facility | Unknown | C4614 | 6.71 | 2016-11-01T23:40:00Z | 24.99 | 10 | < 25mph
|  | Morongo | 2020-08-03 | 2020 | 10:33 | 34.0758 | -116.5548 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-2107480E | OH-2107480E | T2 | T2 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-08-03 | 19:15 | Contact From Object |  | Balloons | Electric Facility | Outside Force | SE351 | 6.16 | 2020-07-20T14:30:00Z | 9.79 | 76 | < 25mph
|  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | MLCC1 | 7.93 | 2019-12-21T12:53:00Z | 21 | 45 | < 25mph
| MEYERS |  | 2017-12-05 | 2017 | 14:00 | 34.2183 | -117.4062 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | DVOC1 | 2.77 | 2016-03-13T23:10:00Z | 11.01 | 4 | < 25mph
|  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | AT643 | 4.77 | 2015-05-12T22:48:00Z | 21.99 | 33 | < 25mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | AU715 | 4.25 | 2015-11-16T20:04:00Z | 32.01 | 17 | 25-40mph
|  | BRUMFIELD | 2016-06-04 | 2016 | 10:17 | 33.5947 | -117.1387 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-2206630E | OH-2206630E | Tier 2 | T2 | Y |  | 12 | Distribution | Transformer | Overhead | Yes | 2016-06-04 | 10:17 | Equipment/Facility Failure | Transformer |  |  | Unknown | SRUC1 | 7.42 | 2015-10-27T17:54:00Z | 10 | 26 | < 25mph
|  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UCMO | 4.71 | 2015-04-19T01:30:00Z | 23 | 13 | < 25mph
|  | RHODA | 2016-12-30 | 2016 | 11:42 | 34.1231 | -118.723 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-1927507E | OH-1927507E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-12-30 | 11:42 | Contact From Object |  | Balloons | Electric Facility | Unknown | CEEC1 | 4.39 | 2017-09-28T14:38:00Z | 4.99 | 50 | < 25mph
10003 |  | SHEFFIELD | 2016-02-22 | 2016 | 17:04 | 34.4492 | -119.5845 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Montecito Fire Department | OH-1082380E | OH-1082380E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-02-22 | 17:04 | Equipment/Facility Failure | Conductor |  |  | Unknown | SBVC1 | 6.92 | 2015-12-18T22:24:00Z | 14.99 | 20 | < 25mph
|  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | LPDC1 | 5.12 | 2020-03-13T18:55:00Z | 41 | 44 | 40-55mph
|  | HUGHES LAKE/ED-08810 | 2018-07-06 | 2018 | 5:38 | 34.6744 | -118.4517 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | 465140E | OH-1938477E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-07-06 | 5:38 | Contact From Object |  | Vehicle | Pole | Unknown | PPPC1 | 4.96 | 2018-04-25T02:56:00Z | 31 | 4 | 25-40mph
|  | SANTA CLARA-TAYSHELL/ET-00423 | 2016-04-21 | 2016 | 12:20 | 34.3339 | -119.2748 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4434916E | OH-4434916E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2016-04-21 | 12:20 | Contact From Object |  | Animal | Electric Facility | Unknown | E8097 | 5.68 | 2018-05-01T19:33:00Z | 18.01 | 27 | < 25mph
|  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force | SDMEA | 5.11 | 2016-04-22T11:49:00Z | 4.99 | 11 | < 25mph
|  | Enchanted | 2019-08-25 | 2019 | 8:03 | 34.301 | -118.8308 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4754475E | OH-4754475E | Tier 3 | T3 | Y | NA | 16 | Distribution | Lightning Arrestor | Overhead | Yes | 2019-08-25 | 8:03 | Contact From Object |  | Animal | Electric Facility | Other | WLYC1 | 4.92 | 2015-10-14T12:49:00Z | 14.99 | 59 | < 25mph
|  | Elster | 2019-09-21 | 2019 | 10:53 | 36.1026 | -118.8659 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4252581E | OH-4252581E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-21 | 10:53 | Contact From Object |  | Vehicle | Electric Facility | Human Error | SE282 | 6.36 | 2020-11-22T18:10:00Z | 7.46 | 65 | < 25mph
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | BPOC1 | 4.63 | 2017-11-23T05:49:00Z | 10 | 12 | < 25mph
|  | BIG CREEK 3-RECTOR NO.1/ET-01046 | 2015-09-03 | 2015 | 17:00 | 36.8936 | -119.4571 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | East of Watts Valley Rd and Pittman Hill Rd, East of Clovis | OH-7020930 | Tier 2 | T2 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2015-09-03 | 16:15 | Contact From Object |  | Balloons | Electric Facility | None | FCHC1 | 1.24 | 2018-03-23T17:00:00Z | 8.01 | 1 | < 25mph
10005 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | D5145 | 7.89 | 2019-08-07T12:31:00Z | 13 | 144 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TNRC1 | 2.34 | 2017-03-02T12:57:00Z | 20 | 111 | < 25mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | AU715 | 4.25 | 2015-01-25T23:58:00Z | 15.99 | 14 | < 25mph
|  | VIENTO | 2016-06-06 | 2016 | 17:44 | 35.1355 | -118.4771 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1373165E | OH-1373165E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-06 | 17:44 | Contact From Object |  | Other | Pole | Unknown | SE531 | 3 | 2020-10-07T11:20:00Z | 12.78 | 158 | < 25mph
|  | POULTRY | 2018-09-21 | 2018 | 8:28 | 34.0728 | -117.0397 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Juniper St. Yucaipa | OH-129241E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SE263 | 4.25 | 2019-10-04T10:10:00Z | 10.22 | 82 | < 25mph
|  | Wildomar | 2019-09-19 | 2019 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside County FD | OH-2225310E | OH-2225310E | Tier 3 | T3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other | SRUC1 | 3.86 | 2018-04-28T18:54:00Z | 17 | 11 | < 25mph
|  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown | SE069 | 5.79 | 2019-12-04T12:20:00Z | 16.28 | 58 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:30 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | None | FRCC1 | 7.87 | 2019-03-05T07:51:00Z | 11.01 | 84 | < 25mph
10006 |  | CONCEPCION | 2016-05-12 | 2016 | 8:55 | 34.4736 | -120.216 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-708452E | OH-708452E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-12 | 8:55 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UP481 | 0.62 | 2018-01-16T12:40:00Z | 21.05 | 16 | < 25mph
|  | Zone | 2015-06-23 | 2015 | 17:21 | 34.279 | -118.9072 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura Fire Department | Primary splice box at base of pole 2115918e | OH-2115918E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Subsurface | No | <Null> |  | Equipment/Facility Failure | Other |  |  | Unknown | WLYC1 | 7.44 | 2020-05-07T10:49:00Z | 21 | 211 | < 25mph
|  | Viento | 2020-06-09 | 2020 | 16:42 | 35.1384 | -118.4809 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4707894E | OH-4707894E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | KTSP | 2.37 | 2015-06-15T00:15:00Z | 32.21 | 32 | 25-40mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | E1966 | 3.22 | 2016-09-10T22:26:00Z | 24 | 9 | < 25mph
|  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather | LTJC1 | 4.14 | 2015-08-13T18:54:00Z | 13 | 15 | < 25mph
|  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown | CNSC1 | 7.75 | 2015-11-09T13:16:00Z | 7 | 15 | < 25mph
|  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | MBCC1 | 6.95 | 2019-11-19T21:56:00Z | 21 | 189 | < 25mph
|  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force | TSHC1 | 6.99 | 2016-07-26T05:04:00Z | 8.99 | 15 | < 25mph
|  | Enchanted | 2019-08-25 | 2019 | 8:03 | 34.301 | -118.8308 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4754475E | OH-4754475E | Tier 3 | T3 | Y | NA | 16 | Distribution | Lightning Arrestor | Overhead | Yes | 2019-08-25 | 8:03 | Contact From Object |  | Animal | Electric Facility | Other | SE057 | 7.49 | 2019-04-29T10:00:00Z | 13.38 | 128 | < 25mph
|  | HUCKLEBERRY | 2017-03-17 | 2017 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4493863E | OH-4493863E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE444 | 0.61 | 2019-09-24T12:50:00Z | 28.5 | 54 | 25-40mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | E6472 | 6.33 | 2015-03-12T18:47:00Z | 20 | 53 | < 25mph
|  | WELCH | 2016-04-25 | 2016 | 15:23 | 35.8387 | -118.9147 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1078325E | OH-1078325E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 15:23 | Equipment/Facility Failure | Insulator |  |  | Unknown | FTNC1 | 3.62 | 2015-03-10T14:00:00Z | 5.99 | 1 | < 25mph
|  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | SE033 | 5.08 | 2020-09-10T10:40:00Z | 8.04 | 143 | < 25mph
|  | La Mancha | 2020-07-05 | 2020 | 3:57 | 34.1325 | -118.8532 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1848406E | OH-1848406E | T3 | T3 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-07-05 | 3:57 | Equipment/Facility Failure | Insulator |  |  | Unknown | OOSC1 | 4.63 | 2019-04-13T16:30:00Z | 18.59 | 83 | < 25mph
10005 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | SE141 | 5 | 2019-07-09T19:00:00Z | 14.03 | 142 | < 25mph
|  | OAK GLEN | 2017-03-15 | 2017 | 13:23 | 34.0534 | -116.971 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-2326555E | OH-2326555E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-15 | 13:23 | Contact From Object |  | Animal | Electric Facility | Unknown | MMKC1 | 4.7 | 2020-04-09T01:34:00Z | 14 | 106 | < 25mph
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | SE405 | 5.42 | 2020-02-13T16:50:00Z | 4.54 | 42 | < 25mph
| MEYERS |  | 2017-12-05 | 2017 | 14:00 | 34.2183 | -117.4062 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | SE064 | 2.26 | 2018-10-04T09:10:00Z | 13.6 | 23 | < 25mph
|  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown | E3047 | 1.29 | 2016-04-20T16:41:00Z | 21 | 11 | < 25mph
|  | VALLECITO | 2016-08-18 | 2016 | 19:00 | 34.4214 | -119.5964 | Other | Rural | Structure Only | Structure Only |  | Fire Agency | Santa Barbara County Fire Department | 2400 block of Whitney Avenue in Summerland | OH-1523986E | Tier 2 | T2 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | MOIC1 | 2.34 | 2015-12-05T09:07:00Z | 8.99 | 16 | < 25mph
|  | DALBA | 2017-07-11 | 2017 | 18:06 | 34.2054 | -117.1143 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-919465E | OH-919465E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 2.4 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | E9874 | 7.54 | 2016-10-14T00:23:00Z | 11.01 | 59 | < 25mph
| THOMAS |  | 2017-12-04 | 2017 | 18:28 | 34.4152 | -119.0912 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | USFS | [17 empty] | Weather | AT184 | 6.91 | 2017-01-05T22:49:00Z | 14.99 | 74 | < 25mph
|  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | D3590 | 2.93 | 2018-06-05T05:11:00Z | 10 | 35 | < 25mph
|  | HUCKLEBERRY | 2017-03-17 | 2017 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4493863E | OH-4493863E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown | E1966 | 2.92 | 2017-10-02T19:20:00Z | 8.01 | 8 | < 25mph
|  | Plateau | 2019-09-11 | 2019 | 8:08 | 34.0991 | -118.6793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4424792E | OH-4424792E | Tier 3 | T3 | Y | Verizon / AT&T / Crown Castle | 16 | Distribution | Conductor | Overhead | Yes | 2019-09-11 | 8:08 | Equipment/Facility Failure | Conductor |  | Electric Facility | Human Error | MBUC1 | 3.24 | 2015-03-02T07:56:00Z | 28.01 | 29 | 25-40mph
|  | GUITAR | 2016-01-16 | 2016 | 15:20 | 34.4096 | -118.6816 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-848266E | OH-848266E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-01-16 | 15:20 | Equipment/Facility Failure | Other |  |  | Unknown | SE104 | 5.67 | 2019-10-12T10:20:00Z | 22.37 | 92 | < 25mph
|  | BENCH | 2018-06-26 | 2018 | 20:48 | 34.0158 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Holmes St/Wildwood Canyon Rd, Yucaipa | OH-4367391E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-26 | 20:48 | Contact From Object |  | Vehicle | Pole | Unknown | MMKC1 | 4.65 | 2015-05-12T09:34:00Z | 8.99 | 26 | < 25mph
|  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other | LPDC1 | 2.12 | 2020-08-02T01:55:00Z | 40 | 120 | 40-55mph
|  | Elster | 2019-09-21 | 2019 | 10:53 | 36.1026 | -118.8659 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4252581E | OH-4252581E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-21 | 10:53 | Contact From Object |  | Vehicle | Electric Facility | Human Error |  |  |  | 0 | 0 | No data
|  | Viento | 2020-06-09 | 2020 | 16:42 | 35.1384 | -118.4809 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4707894E | OH-4707894E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | SE060 | 5.8 | 2020-10-12T14:00:00Z | 11.84 | 148 | < 25mph
|  | BIG CREEK 3-RECTOR NO.1/ET-01046 | 2015-09-03 | 2015 | 17:00 | 36.8936 | -119.4571 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | East of Watts Valley Rd and Pittman Hill Rd, East of Clovis | OH-7020930 | Tier 2 | T2 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2015-09-03 | 16:15 | Contact From Object |  | Balloons | Electric Facility | None | FCHC1 | 1.24 | 2017-10-05T23:00:00Z | 10 | 1 | < 25mph
|  | ELSTER | 2016-04-25 | 2016 | 19:15 | 36.1372 | -118.8615 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-X16345E | OH-X16345E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 120/240 V | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 19:15 | Equipment/Facility Failure | Conductor |  |  | Unknown | MOLC1 | 6.51 | 2020-02-22T07:27:00Z | 15.99 | 28 | < 25mph
|  | Wildomar | 2019-09-19 | 2019 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside County FD | OH-2225310E | OH-2225310E | Tier 3 | T3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other | DLZSD | 4.22 | 2015-10-03T10:00:00Z | 10 | 18 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TNRC1 | 2.34 | 2016-10-01T19:57:00Z | 18.99 | 90 | < 25mph
10005 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | D5145 | 7.89 | 2015-04-18T09:23:00Z | 8.01 | 43 | < 25mph
| ERSKINE |  | 2016-06-23 | 2016 | 16:00 | 34.2676 | -117.844 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | BLM | [13 empty] | Contact From Object |  | Vegetation |  |  | TANC1 | 6.35 | 2019-08-09T13:01:00Z | 5.99 | 7 | < 25mph
|  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other | PPPC1 | 1.78 | 2019-03-22T06:56:00Z | 17 | 10 | < 25mph
|  | Pawley | 2015-05-29 | 2015 | 7:29 | 36.387 | -118.9536 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare County Fire | Lemon Cove and Three Rivers Sub. Venida 66kV | OH-4434944E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-05-29 | 7:29 | Contact From Object |  | Animal | Electric Facility | None | D0117 | 5.17 | 2018-06-15T21:54:00Z | 11.01 | 12 | < 25mph
|  | PATRICIA | 2016-10-23 | 2016 | 9:40 | 34.4603 | -119.2853 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | 900 Rice Road Ojai | OH-786960E | Tier 3 | T3 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | SE233 | 6.81 | 2020-08-27T03:30:00Z | 13.44 | 100 | < 25mph
| MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | D2363 | 5.89 | 2018-02-18T05:35:00Z | 14.99 | 74 | < 25mph
|  | Soda Springs | 2015-05-14 | 2015 | 22:24 | 36.1318 | -118.7784 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | Soda Springs 12kV out of Boxwood Sub | OH-4464511E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-14 | 22:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown | AV342 | 5.2 | 2018-02-11T10:11:00Z | 18.01 | 16 | < 25mph
3 |  | Bidder | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire | OH-2023941E | OH-2023941E | T3 | T3 |  | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force | E2046 | 4.64 | 2015-09-16T20:26:00Z | 11.01 | 62 | < 25mph
|  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE444 | 4.44 | 2020-04-11T14:50:00Z | 22.64 | 85 | < 25mph
|  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown | WMSC1 | 6.6 | 2018-04-24T09:53:00Z | 12.01 | 2 | < 25mph
|  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather | CEKC1 | 7.88 | 2018-01-09T22:54:00Z | 34.99 | 15 | 25-40mph
|  | Taggert | 2019-04-23 | 2019 | 21:06 | 34.2147 | -117.0973 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1027559E | OH-1027559E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution |  | Overhead | No |  |  | Unknown |  |  |  | Unknown | HHPC1 | 2.75 | 2017-12-29T07:15:00Z | 8.99 | 53 | < 25mph
|  | Elster | 2019-09-21 | 2019 | 10:53 | 36.1026 | -118.8659 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4252581E | OH-4252581E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-21 | 10:53 | Contact From Object |  | Vehicle | Electric Facility | Human Error |  |  |  | 0 | 0 | No data
|  | Atlanta | 2015-05-05 | 2015 | 16:00 | 33.711 | -117.7089 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 4229158E | OH-4229158E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vehicle | Electric Facility | None | E3131 | 7.82 | 2016-04-19T14:30:00Z | 8.99 | 86 | < 25mph
|  | Wildomar | 2019-09-19 | 2019 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside County FD | OH-2225310E | OH-2225310E | Tier 3 | T3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other | SRUC1 | 3.86 | 2020-05-25T04:54:00Z | 12 | 60 | < 25mph
|  | Soda Springs | 2015-05-14 | 2015 | 22:24 | 36.1318 | -118.7784 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | Soda Springs 12kV out of Boxwood Sub | OH-4464511E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-14 | 22:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE278 | 5.65 | 2020-09-15T23:40:00Z | 11.4 | 49 | < 25mph
|  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown | UCSH | 2.26 | 2015-10-18T10:30:00Z | 5.1 | 11 | < 25mph
|  | Taiwan | 2015-07-13 | 2015 | 11:15 | 33.7678 | -117.7207 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | Cal Fire | Pole 960439E | OH-960439E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-07-13 | 13:30 | Unknown |  |  |  | Unknown | FRCC1 | 3.07 | 2017-06-02T22:51:00Z | 20 | 83 | < 25mph
|  | PATRICIA | 2016-10-23 | 2016 | 9:40 | 34.4603 | -119.2853 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | 900 Rice Road Ojai | OH-786960E | Tier 3 | T3 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | SE046 | 5.81 | 2018-08-23T16:30:00Z | 5.7 | 37 | < 25mph
|  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | NTBC1 | 7.63 | 2015-06-24T14:06:00Z | 8.99 | 15 | < 25mph
| ERSKINE |  | 2016-06-23 | 2016 | 16:00 | 34.2676 | -117.844 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | BLM | [13 empty] | Contact From Object |  | Vegetation |  |  | TANC1 | 6.35 | 2017-09-15T15:01:00Z | 4.99 | 1 | < 25mph
|  | Keller | 2015-06-09 | 2015 | 5:46 | 33.5986 | -117.1311 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 4401960E | OH-2297077E | Tier 2 | T2 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2015-06-09 | 5:46 | Contact From Object |  | Animal | Electric Facility | None | SRUC1 | 7.92 | 2020-11-24T14:54:00Z | 5.99 | 169 | < 25mph
|  | SHOWDOWN | 2016-06-09 | 2016 | 11:28 | 34.5862 | -118.196 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4267121E | OH-4267121E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-09 | 11:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | LPDC1 | 6.32 | 2017-01-04T03:55:00Z | 34.99 | 17 | 25-40mph
|  | DRISKILL | 2016-10-18 | 2016 | 18:41 | 34.4687 | -119.7722 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Santa Barbara Fire Department | OH-2178476E | OH-2178476E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-18 | 18:41 | Equipment/Facility Failure | Fuse |  |  | Unknown | AS303 | 3.63 | 2015-01-12T12:52:00Z | 11.99 | 68 | < 25mph
|  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | CRXC1 | 2.74 | 2017-01-06T15:05:00Z | 13 | 46 | < 25mph
|  | TICO | 2016-04-28 | 2016 | 14:00 | 34.357 | -119.314 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura County FD | OH-1604151E | OH-1604151E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-04-28 | 14:00 | Equipment/Facility Failure | Other |  |  | Unknown | E8097 | 7.74 | 2019-08-06T21:15:00Z | 27 | 98 | 25-40mph
|  | Kickapoo Trail | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1941931E | OH-1941931E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Unknown | UCBU | 5.62 | 2017-01-06T13:10:00Z | 23.91 | 19 | < 25mph
|  | BRUMFIELD | 2016-06-04 | 2016 | 10:17 | 33.5947 | -117.1387 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-2206630E | OH-2206630E | Tier 2 | T2 | Y |  | 12 | Distribution | Transformer | Overhead | Yes | 2016-06-04 | 10:17 | Equipment/Facility Failure | Transformer |  |  | Unknown | F0145 | 7.21 | 2019-05-06T03:00:00Z | 22.01 | 53 | < 25mph
|  | Conestoga | 2020-06-13 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Other | SNPC1 | 6.73 | 2015-04-21T02:20:00Z | 18.39 | 27 | < 25mph
|  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown | SE451 | 7.9 | 2020-07-05T21:30:00Z | 21.7 | 44 | < 25mph
10007 |  | Vicasa | 2020-11-30 | 2020 | 21:02 | 34.0723 | -118.588 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles Fire Department | OH-4535641E | OH-4535641E | T3 | T3 |  | Verizon Wireless, AT&T Mobility, Frontier Communications, Crown Castle NG West, Inc | 16 | Distribution | Other | Overhead | Yes | 2020-11-30 | 21:02 | Contact From Object |  | Vehicle | Electric Facility | Outside Force | MBCC1 | 6.65 | 2016-10-26T17:56:00Z | 21 | 68 | < 25mph
|  | CONCEPCION | 2016-05-02 | 2016 | 7:03 | 34.4736 | -120.2153 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-4041841E | OH-4041841E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-02 | 7:03 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | GVTC1 | 1.55 | 2020-11-02T04:09:00Z | 17 | 13 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TNRC1 | 2.34 | 2015-12-20T03:57:00Z | 20 | 103 | < 25mph
|  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | D3590 | 2.93 | 2016-11-23T12:06:00Z | 0 | 10 | < 25mph
|  | PYTHON | 2016-10-22 | 2016 | 15:17 | 34.3812 | -118.4132 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | RAR 0038 | OH-4860064E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-22 | 15:17 | Contact From Object |  | Balloons | Electric Facility | Unknown | CNIC1 | 1.96 | 2018-08-10T13:55:00Z | 13 | 52 | < 25mph
1 |  | Birchim | 2015-02-06 | 2015 | 13:15 | 37.454 | -118.5842 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Various Fire Agencies | Between Poles 1854107E & 1854106E | OH-1854107E | Tier 2 | T2 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-02-06 | 13:15 | Unknown |  |  |  | Unknown | OVRC1 | 4.68 | 2017-09-14T06:54:00Z | 4 | 1 | < 25mph
|  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other | SE985 | 5.9 | 2020-11-12T03:20:00Z | 16.38 | 36 | < 25mph
10004 |  | Peninsula | 2019-03-16 | 2019 | 17:58 | 33.6182 | -117.8025 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1729510E | OH-1729510E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-03-16 | 17:58 | Equipment/Facility Failure | Crossarm |  |  | Unknown | SE024 | 6.43 | 2018-10-14T20:40:00Z | 16.98 | 101 | < 25mph
|  | RHODA | 2016-12-30 | 2016 | 11:42 | 34.1231 | -118.723 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-1927507E | OH-1927507E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-12-30 | 11:42 | Contact From Object |  | Balloons | Electric Facility | Unknown | CEEC1 | 4.39 | 2017-08-11T05:38:00Z | 8.99 | 63 | < 25mph
|  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | NTBC1 | 7.63 | 2016-09-19T21:36:00Z | 15.99 | 14 | < 25mph
|  | Northpark | 2019-06-20 | 2019 | 14:08 | 34.2298 | -117.4048 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | San Bern. FD | OH-201371S | OH-201371S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Human Error | DVOC1 | 3.48 | 2016-01-09T18:10:00Z | 7 | 10 | < 25mph
|  | CARVER | 2016-09-24 | 2016 | 14:20 | 35.7381 | -118.9546 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4784763E | OH-4784763E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-09-24 | 14:20 | Contact From Object |  | Animal | Electric Facility | Unknown | WOCC1 | 7.2 | 2015-06-13T01:13:00Z | 13 | 1 | < 25mph
|  | BRUMFIELD | 2016-06-04 | 2016 | 10:17 | 33.5947 | -117.1387 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-2206630E | OH-2206630E | Tier 2 | T2 | Y |  | 12 | Distribution | Transformer | Overhead | Yes | 2016-06-04 | 10:17 | Equipment/Facility Failure | Transformer |  |  | Unknown | SRUC1 | 7.42 | 2015-12-17T16:54:00Z | 14 | 26 | < 25mph
|  | HUCKLEBERRY | 2017-03-17 | 2017 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4493863E | OH-4493863E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown | E1966 | 2.92 | 2017-11-06T01:29:00Z | 28.01 | 11 | 25-40mph
|  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other | UCBU | 3.92 | 2016-03-23T07:30:00Z | 30.31 | 19 | 25-40mph
|  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | OJ | 0.4 | 2015-07-30T08:00:00Z | 2.68 | 6 | < 25mph
|  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | TPGC1 | 0.38 | 2015-11-12T22:57:00Z | 41 | 48 | 40-55mph
|  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown | CNSC1 | 7.75 | 2016-09-11T06:16:00Z | 5.99 | 15 | < 25mph
|  | Conestoga | 2020-06-13 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Other | E3128 | 6.07 | 2015-11-20T06:30:00Z | 14 | 26 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:26 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | Unknown | FRCC1 | 7.87 | 2017-12-22T21:51:00Z | 22.01 | 45 | < 25mph
|  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | D3590 | 2.93 | 2016-10-20T02:46:00Z | 4 | 23 | < 25mph
|  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | F0063 | 5.09 | 2019-05-02T00:03:00Z | 18.99 | 118 | < 25mph
|  | Soda Springs | 2015-05-14 | 2015 | 22:24 | 36.1318 | -118.7784 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | Soda Springs 12kV out of Boxwood Sub | OH-4464511E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-14 | 22:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown | OORC1 | 5.23 | 2015-08-03T20:12:00Z | 14.99 | 1 | < 25mph
|  | OAK GLEN | 2017-03-15 | 2017 | 13:23 | 34.0534 | -116.971 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-2326555E | OH-2326555E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-15 | 13:23 | Contact From Object |  | Animal | Electric Facility | Unknown | MMKC1 | 4.7 | 2015-05-27T17:34:00Z | 11.01 | 41 | < 25mph
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | ERYC1 | 5.82 | 2016-10-03T16:00:00Z | 22.39 | 13 | < 25mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | E1966 | 3.22 | 2017-05-11T09:24:00Z | 28.01 | 13 | 25-40mph
|  | DEACON | 2017-10-18 | 2017 | 13:34 | 33.7702 | -117.2157 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1564666E | OH-1564666E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SE036 | 5.46 | 2018-10-28T11:10:00Z | 2.73 | 39 | < 25mph
|  | Hughes Lake | 2019-09-02 | 2019 | 14:02 | 34.7026 | -118.342 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4782978E | OH-4782978E | Tier 2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-02 | 14:02 | Contact From Object |  | Balloons | Electric Facility | Other | PPPC1 | 3.45 | 2020-05-25T02:56:00Z | 25 | 63 | 25-40mph
|  | TUNA | 2016-09-19 | 2016 | 6:11 | 34.04 | -118.6687 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-1638513E | OH-1638513E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | MBCC1 | 3.63 | 2017-05-07T01:56:00Z | 18.01 | 33 | < 25mph
|  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error | AU563 | 7.19 | 2019-08-29T12:05:00Z | 24 | 30 | < 25mph
|  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error | SE273 | 3.85 | 2019-07-29T11:20:00Z | 7.61 | 68 | < 25mph
|  | Elster | 2019-09-21 | 2019 | 10:53 | 36.1026 | -118.8659 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4252581E | OH-4252581E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-21 | 10:53 | Contact From Object |  | Vehicle | Electric Facility | Human Error | SE282 | 6.36 | 2019-07-02T04:40:00Z | 11.41 | 30 | < 25mph
|  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force | TSHC1 | 6.99 | 2015-03-25T09:04:00Z | 8.99 | 11 | < 25mph
|  | LEE VINING-LUNDY NO. 1/ET-01774 | 2017-05-01 | 2017 | 5:40 | 38.0209 | -119.1608 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | CAlFIre | OH-1580964E | OH-1580964E | Tier 2 | T2 | Y |  | 55 | Distribution | Conductor | Overhead | No | <Null> |  | Contamination |  |  |  | Unknown | SE089 | 4.38 | 2019-03-25T22:30:00Z | 52.84 | 16 | 40-55mph
|  | PATRICIA | 2016-09-16 | 2016 | 19:02 | 34.4851 | -119.3001 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ojai City Fire Department | OH-4797071E | OH-4797071E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-09-16 | 19:02 | Contact From Object |  | Vehicle | Pole | Unknown | RSVC1 | 7.44 | 2020-08-19T19:15:00Z | 14.69 | 90 | < 25mph
|  | Hughes Lake | 2019-09-02 | 2019 | 14:02 | 34.7026 | -118.342 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4782978E | OH-4782978E | Tier 2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-02 | 14:02 | Contact From Object |  | Balloons | Electric Facility | Other | PPPC1 | 3.45 | 2015-07-30T22:56:00Z | 15.99 | 19 | < 25mph
|  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other | UCBU | 3.92 | 2016-11-17T06:40:00Z | 29.71 | 21 | 25-40mph
| RYE |  | 2017-12-05 | 2017 | 11:31 | 34.4528 | -118.5819 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | SAUC1 | 4.1 | 2016-09-02T01:57:00Z | 23 | 18 | < 25mph
|  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | SE122 | 6.49 | 2018-11-18T22:40:00Z | 12.39 | 87 | < 25mph
|  | PATRICIA | 2016-09-16 | 2016 | 19:02 | 34.4851 | -119.3001 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ojai City Fire Department | OH-4797071E | OH-4797071E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-09-16 | 19:02 | Contact From Object |  | Vehicle | Pole | Unknown | CSVC1 | 6.69 | 2017-03-26T05:09:00Z | 5.99 | 6 | < 25mph
|  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UCMO | 4.71 | 2018-07-30T08:30:00Z | 11.01 | 44 | < 25mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | ATNC1 | 4.83 | 2018-09-09T01:54:00Z | 17 | 13 | < 25mph
|  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other | PPPC1 | 1.78 | 2017-03-24T23:56:00Z | 28.01 | 4 | 25-40mph
10004 |  | Peninsula | 2019-03-16 | 2019 | 17:58 | 33.6182 | -117.8025 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1729510E | OH-1729510E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-03-16 | 17:58 | Equipment/Facility Failure | Crossarm |  |  | Unknown | E4246 | 5.82 | 2015-03-29T14:24:00Z | 8.01 | 83 | < 25mph
|  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | TO | 5.22 | 2017-01-13T23:00:00Z | 17.67 | 47 | < 25mph
| HOLIDAY |  | 2018-07-06 | 2018 | 20:40 | 34.4639 | -119.8314 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Santa Barbara Fire Department | [17 empty] | Weather | SE510 | 4.8 | 2020-08-11T20:40:00Z | 15.12 | 265 | < 25mph
|  | Flying D | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County | OH-1761180E | OH-1761180E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown | DEMC1 | 6.46 | 2018-08-11T22:25:00Z | 15.99 | 2 | < 25mph
10006 |  | CONCEPCION | 2016-05-12 | 2016 | 8:55 | 34.4736 | -120.216 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-708452E | OH-708452E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-12 | 8:55 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | GVTC1 | 1.52 | 2018-02-15T09:09:00Z | 30 | 13 | 25-40mph
|  | GUITAR | 2016-01-16 | 2016 | 15:20 | 34.4096 | -118.6816 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-848266E | OH-848266E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-01-16 | 15:20 | Equipment/Facility Failure | Other |  |  | Unknown | TCLC1 | 6.37 | 2016-05-06T17:12:00Z | 13 | 5 | < 25mph
|  | Plateau | 2019-09-11 | 2019 | 8:08 | 34.0991 | -118.6793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4424792E | OH-4424792E | Tier 3 | T3 | Y | Verizon / AT&T / Crown Castle | 16 | Distribution | Conductor | Overhead | Yes | 2019-09-11 | 8:08 | Equipment/Facility Failure | Conductor |  | Electric Facility | Human Error | D2363 | 3.42 | 2019-02-21T07:30:00Z | 21 | 95 | < 25mph
|  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown | WTPC1 | 2.77 | 2016-03-04T20:57:00Z | 8.01 | 2 | < 25mph
|  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force | LYQC1 | 1.86 | 2015-01-03T07:18:00Z | 7 | 1 | < 25mph
| CABIN |  | 2015-08-14 | 2015 | 13:07 | 34.0299 | -118.0726 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | D7261 | 5.98 | 2016-08-06T09:14:00Z | 3 | 34 | < 25mph
|  | DEACON | 2017-10-18 | 2017 | 13:34 | 33.7702 | -117.2157 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1564666E | OH-1564666E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SDPRR | 3.64 | 2015-10-26T09:49:00Z | 4.99 | 10 | < 25mph
| EDISON |  | 2016-05-12 | 2016 | -8 | 34.3135 | -119.1865 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | E8097 | 6.25 | 2017-10-31T02:30:00Z | 18.99 | 100 | < 25mph
|  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown | E1966 | 2.94 | 2017-01-04T14:55:00Z | 31 | 14 | 25-40mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | SE785 | 3.4 | 2020-07-28T09:10:00Z | 11.54 | 97 | < 25mph
|  | VALLEY-MAYBERRY-MORENO-VISTA | 2020-05-18 | 2020 | 12:10 | 33.8587 | -117.0203 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire Perris | OH-1979539E | OH-1979539E | T3 | T3 | Y | None | 115 | Transmission | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Other | BNTC1 | 6.4 | 2016-03-08T09:14:00Z | 7 | 32 | < 25mph
|  | SKINKLE | 2016-05-29 | 2016 | 22:25 | 36.0091 | -118.9563 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-4566417E | OH-4566417E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-05-29 | 22:25 | Contact From Object |  | Other | Electric Facility | Unknown | C1000 | 7.9 | 2015-09-18T21:00:00Z | 3 | 13 | < 25mph
|  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force | SDMEA | 5.11 | 2017-07-07T00:49:00Z | 22.01 | 21 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:26 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | Unknown | E3131 | 6.3 | 2015-03-11T01:00:00Z | 14.99 | 35 | < 25mph
|  | Zone | 2015-04-27 | 2015 | 19:10 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 4734128E | OH-4734128E | Tier 3 | T3 | Y |  | 16 | Distribution | Other | Overhead | Yes | 2015-04-27 | 19:10 | Equipment/Facility Failure | Other |  |  | Unknown | AT184 | 5.07 | 2016-01-02T12:13:00Z | 38.99 | 61 | 25-40mph
|  | ARCHIE | 2018-11-13 | 2018 | 7:11 | 33.4928 | -117.2796 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | NORTH OF CARANCHO ON VIA CIELO | OH-4149859E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-13 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Unknown | SRUC1 | 3.4 | 2019-09-14T03:54:00Z | 8.99 | 49 | < 25mph
|  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown | SE332 | 7.21 | 2020-02-14T02:00:00Z | 6.35 | 11 | < 25mph
|  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other | LPDC1 | 2.12 | 2017-12-17T22:55:00Z | 24 | 17 | < 25mph
|  | Viento | 2020-06-09 | 2020 | 16:42 | 35.1384 | -118.4809 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4707894E | OH-4707894E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | E3266 | 4.26 | 2018-06-19T07:51:00Z | 14.99 | 42 | < 25mph
10004 |  | Peninsula | 2019-03-16 | 2019 | 17:58 | 33.6182 | -117.8025 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1729510E | OH-1729510E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-03-16 | 17:58 | Equipment/Facility Failure | Crossarm |  |  | Unknown | F0107 | 5.38 | 2019-04-29T17:05:00Z | 8.99 | 106 | < 25mph
|  | Plateau | 2019-09-11 | 2019 | 8:08 | 34.0991 | -118.6793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4424792E | OH-4424792E | Tier 3 | T3 | Y | Verizon / AT&T / Crown Castle | 16 | Distribution | Conductor | Overhead | Yes | 2019-09-11 | 8:08 | Equipment/Facility Failure | Conductor |  | Electric Facility | Human Error | MBUC1 | 3.24 | 2016-10-19T17:56:00Z | 42.01 | 39 | 40-55mph
|  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | MTIC1 | 4.81 | 2016-10-03T10:47:00Z | 38.01 | 11 | 25-40mph
|  | Viento | 2020-06-09 | 2020 | 16:42 | 35.1384 | -118.4809 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4707894E | OH-4707894E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | KTSP | 2.37 | 2017-04-01T23:15:00Z | 20.71 | 35 | < 25mph
|  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown | CNSC1 | 7.75 | 2020-09-20T09:16:00Z | 9 | 92 | < 25mph
|  | La Mancha | 2020-07-05 | 2020 | 3:57 | 34.1325 | -118.8532 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1848406E | OH-1848406E | T3 | T3 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-07-05 | 3:57 | Equipment/Facility Failure | Insulator |  |  | Unknown | OOSC1 | 4.63 | 2019-02-07T10:30:00Z | 20.69 | 50 | < 25mph
10004 |  | HUGHES LAKE | 2016-10-26 | 2016 | 12:19 | 34.7081 | -118.5367 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | ELIZABETH LAKE ROAD AND KINGS CANYON ROAD, LAKE HUGHES | OH-1586523E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-26 | 12:19 | Contact From Object |  | Vegetation | Electric Facility | Unknown | C4614 | 6.71 | 2017-03-14T20:40:00Z | 8.99 | 7 | < 25mph
|  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown | E3047 | 1.29 | 2016-03-18T06:25:00Z | 11.01 | 26 | < 25mph
|  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown | SE338 | 7.45 | 2019-11-19T19:40:00Z | 35.3 | 73 | 25-40mph
|  | SKINKLE | 2016-05-29 | 2016 | 22:25 | 36.0091 | -118.9563 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-4566417E | OH-4566417E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-05-29 | 22:25 | Contact From Object |  | Other | Electric Facility | Unknown |  |  |  | 0 | 0 | No data
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | SE852 | 5.94 | 2020-12-11T15:00:00Z | 27.77 | 39 | 25-40mph
|  | CUDDEBACK | 2017-08-08 | 2017 | 17:52 | 35.1342 | -118.5607 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4179753E | OH-4179753E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-08-08 | 17:52 | Contact From Object |  | Vehicle | Electric Facility | Unknown | SE067 | 1.99 | 2020-12-03T20:00:00Z | 43.56 | 115 | 40-55mph
| TENAJA |  | 2019-09-04 | 2019 | 16:43 | 33.5285 | -117.2732 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | SRUC1 | 2.64 | 2019-04-20T10:54:00Z | 12.01 | 37 | < 25mph
|  | Kickapoo Trail | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1941931E | OH-1941931E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Unknown | UCBU | 5.62 | 2017-01-04T11:30:00Z | 14.29 | 19 | < 25mph
|  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown | E3047 | 1.29 | 2016-01-17T06:28:00Z | 8.01 | 23 | < 25mph
|  | CUDDEBACK | 2017-08-08 | 2017 | 17:52 | 35.1342 | -118.5607 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4179753E | OH-4179753E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-08-08 | 17:52 | Contact From Object |  | Vehicle | Electric Facility | Unknown | C6906 | 4.44 | 2016-04-10T07:52:00Z | 8.99 | 41 | < 25mph
|  | VALLEY-MAYBERRY-MORENO-VISTA | 2020-05-18 | 2020 | 12:10 | 33.8587 | -117.0203 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire Perris | OH-1979539E | OH-1979539E | T3 | T3 | Y | None | 115 | Transmission | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Other | HSGC1 | 4.08 | 2019-01-02T15:16:00Z | 15.99 | 21 | < 25mph
|  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force | F0145 | 2.93 | 2018-12-09T23:29:00Z | 10 | 26 | < 25mph
|  | VALLEY-MAYBERRY-MORENO-VISTA | 2020-05-18 | 2020 | 12:10 | 33.8587 | -117.0203 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire Perris | OH-1979539E | OH-1979539E | T3 | T3 | Y | None | 115 | Transmission | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Other | SE551 | 5.8 | 2020-03-26T06:30:00Z | 22.86 | 66 | < 25mph
|  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other | AV447 | 7.14 | 2019-01-15T10:30:00Z | 13 | 40 | < 25mph
|  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | MBCC1 | 5.33 | 2016-06-25T23:56:00Z | 40 | 55 | 40-55mph
|  | Morongo | 2020-08-03 | 2020 | 10:33 | 34.0758 | -116.5548 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-2107480E | OH-2107480E | T2 | T2 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-08-03 | 19:15 | Contact From Object |  | Balloons | Electric Facility | Outside Force | UCBU | 7.55 | 2019-03-09T18:30:00Z | 9.31 | 6 | < 25mph
|  | Vicasa | 2020-10-26 | 2020 | 11:56 | 34.0998 | -118.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | OH-795990E | OH-795990E | T3 | T3 |  | Frontier Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Weather | MBCC1 | 6.44 | 2016-07-29T00:56:00Z | 34.99 | 57 | 25-40mph
|  | PICK | 2017-06-19 | 2017 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | 30278 Arrastre Canyon Rd., Acton | OH-699610E | Tier 3 | T3 | Y |  | 33 | Distribution | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown | MLCC1 | 7.72 | 2015-12-04T21:53:00Z | 24 | 2 | < 25mph
3 |  | Bidder | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire | OH-2023941E | OH-2023941E | T3 | T3 |  | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force | MPWC1 | 5.77 | 2018-01-22T06:06:00Z | 18.99 | 109 | < 25mph
|  | SKINKLE | 2016-05-29 | 2016 | 22:25 | 36.0091 | -118.9563 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-4566417E | OH-4566417E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-05-29 | 22:25 | Contact From Object |  | Other | Electric Facility | Unknown | C1000 | 7.9 | 2015-06-05T21:45:00Z | 3 | 13 | < 25mph
|  | Hughes Lake | 2019-09-02 | 2019 | 14:02 | 34.7026 | -118.342 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4782978E | OH-4782978E | Tier 2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-02 | 14:02 | Contact From Object |  | Balloons | Electric Facility | Other | C5551 | 4.01 | 2017-09-26T17:54:00Z | 18.01 | 22 | < 25mph
|  | CARVER | 2016-09-24 | 2016 | 14:20 | 35.7381 | -118.9546 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4784763E | OH-4784763E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-09-24 | 14:20 | Contact From Object |  | Animal | Electric Facility | Unknown | WOCC1 | 7.2 | 2017-04-15T06:13:00Z | 3 | 1 | < 25mph
| ERSKINE |  | 2016-06-23 | 2016 | 16:00 | 34.2676 | -117.844 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | BLM | [13 empty] | Contact From Object |  | Vegetation |  |  | TANC1 | 6.35 | 2019-07-10T10:01:00Z | 4.99 | 1 | < 25mph
|  | Zone | 2019-08-10 | 2019 | 13:00 | 34.3089 | -118.9413 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | VFD | OH-4734128E | OH-4734128E | Tier 3 | T3 | Y | AT&T Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | E1625 | 7.18 | 2018-02-10T18:43:00Z | 10 | 52 | < 25mph
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | ERYC1 | 5.82 | 2016-12-08T20:00:00Z | 35.39 | 9 | 25-40mph
|  | DEACON | 2017-10-18 | 2017 | 13:34 | 33.7702 | -117.2157 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1564666E | OH-1564666E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | UCMO | 3.31 | 2015-08-11T18:10:00Z | 11.01 | 8 | < 25mph
|  | Calgrove | 2020-10-03 | 2020 | 17:45 | 34.357 | -118.5659 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | OH-2101062E | OH-2101062E | T3 | T3 |  | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | SE486 | 3.94 | 2020-07-21T22:20:00Z | 26.38 | 175 | 25-40mph
|  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown | FTNC1 | 0.32 | 2015-04-02T09:00:00Z | 5.99 | 1 | < 25mph
|  | SANTA CLARA-TAYSHELL/ET-00423 | 2016-04-21 | 2016 | 12:20 | 34.3339 | -119.2748 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4434916E | OH-4434916E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2016-04-21 | 12:20 | Contact From Object |  | Animal | Electric Facility | Unknown | E8097 | 5.68 | 2019-07-31T23:01:00Z | 23 | 71 | < 25mph
|  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown | WMSC1 | 6.6 | 2020-03-06T17:53:00Z | 13 | 36 | < 25mph
|  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | MBUC1 | 5.12 | 2016-01-30T02:56:00Z | 75 | 64 | 55mph+
|  | Pawley | 2015-05-29 | 2015 | 7:29 | 36.387 | -118.9536 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare County Fire | Lemon Cove and Three Rivers Sub. Venida 66kV | OH-4434944E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-05-29 | 7:29 | Contact From Object |  | Animal | Electric Facility | None | D0117 | 5.17 | 2016-09-04T05:55:00Z | 0 | 7 | < 25mph
10005 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error | LPDC1 | 6.51 | 2015-04-02T18:55:00Z | 23 | 10 | < 25mph
|  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.54 | 2015-11-03T14:51:00Z | 15.99 | 90 | < 25mph
|  | Flying D | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County | OH-1761180E | OH-1761180E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown | DEMC1 | 6.46 | 2018-07-21T03:25:00Z | 10 | 2 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:26 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | Unknown | HP018 | 6.4 | 2019-01-07T02:46:00Z | 17.67 | 80 | < 25mph
|  | HUGHES LAKE/ED-08810 | 2018-07-06 | 2018 | 5:38 | 34.6744 | -118.4517 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | 465140E | OH-1938477E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-07-06 | 5:38 | Contact From Object |  | Vehicle | Pole | Unknown | PPPC1 | 4.96 | 2015-08-17T10:56:00Z | 17 | 10 | < 25mph
|  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other | GMTC1 | 4.77 | 2015-12-13T21:59:00Z | 41 | 6 | 40-55mph
|  | TICO | 2016-04-28 | 2016 | 14:00 | 34.357 | -119.314 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura County FD | OH-1604151E | OH-1604151E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-04-28 | 14:00 | Equipment/Facility Failure | Other |  |  | Unknown | E8097 | 7.74 | 2018-11-15T19:46:00Z | 18.99 | 49 | < 25mph
|  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | MSJC1 | 4.82 | 2018-03-04T10:53:00Z | 27 | 18 | 25-40mph
| HOLIDAY |  | 2018-07-06 | 2018 | 20:40 | 34.4639 | -119.8314 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Santa Barbara Fire Department | [17 empty] | Weather | MPWC1 | 2.75 | 2016-08-14T07:06:00Z | 25.99 | 124 | 25-40mph
| EDISON |  | 2016-05-12 | 2016 | -8 | 34.3135 | -119.1865 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | SE047 | 6.77 | 2019-07-31T11:40:00Z | 5.03 | 116 | < 25mph
|  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error | UP478 | 6.05 | 2016-12-02T15:50:00Z | 10.02 | 22 | < 25mph
|  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | RSVC1 | 7.14 | 2020-08-06T18:30:00Z | 24.4 | 106 | < 25mph
|  | Zone | 2015-04-27 | 2015 | 19:10 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 4734128E | OH-4734128E | Tier 3 | T3 | Y |  | 16 | Distribution | Other | Overhead | Yes | 2015-04-27 | 19:10 | Equipment/Facility Failure | Other |  |  | Unknown | WLYC1 | 7.19 | 2016-10-27T16:49:00Z | 14 | 55 | < 25mph
|  | JORDAN | 2018-08-29 | 2018 | 17:32 | 35.7358 | -118.7192 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | Jack Ranch Rd/White River Rd, Kernville | OH-4635091E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-08-29 | 19:06 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE290 | 5.44 | 2020-08-30T08:30:00Z | 11.4 | 25 | < 25mph
|  | Python | 2015-06-06 | 2015 | 10:00 | 34.4043 | -118.4234 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | 16450 Alamo Canyon Rd, Canyon Country | OH-4779534E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-06-06 | 10:13 | Contact From Object |  | Animal | Electric Facility | None | CNIC1 | 3.54 | 2018-05-06T22:55:00Z | 21 | 33 | < 25mph
|  | Lasker | 2020-07-26 | 2020 | 12:50 | 34.5326 | -118.0541 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4619162E | OH-4619162E | T3 | T3 |  | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | LPDC1 | 2.76 | 2020-08-13T08:55:00Z | 23 | 95 | < 25mph
|  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | UP650 | 4.81 | 2018-02-13T09:15:00Z | 7.02 | 45 | < 25mph
|  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown | SE032 | 6.85 | 2018-07-11T17:20:00Z | 10.09 | 14 | < 25mph
|  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | LPDC1 | 5.12 | 2019-08-14T12:55:00Z | 15.99 | 46 | < 25mph
|  | WELCH | 2016-04-25 | 2016 | 15:23 | 35.8387 | -118.9147 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1078325E | OH-1078325E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 15:23 | Equipment/Facility Failure | Insulator |  |  | Unknown | FTNC1 | 3.62 | 2015-04-25T20:00:00Z | 5.99 | 1 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TNRC1 | 2.34 | 2019-06-10T15:57:00Z | 14 | 118 | < 25mph
|  | RHODA | 2016-12-30 | 2016 | 11:42 | 34.1231 | -118.723 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-1927507E | OH-1927507E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-12-30 | 11:42 | Contact From Object |  | Balloons | Electric Facility | Unknown | MBCC1 | 2.93 | 2020-09-30T21:56:00Z | 25 | 297 | 25-40mph
|  | VIENTO | 2016-06-06 | 2016 | 17:44 | 35.1355 | -118.4771 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1373165E | OH-1373165E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-06 | 17:44 | Contact From Object |  | Other | Pole | Unknown | UP477 | 4.86 | 2017-03-24T22:50:00Z | 30.04 | 36 | 25-40mph
|  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | CEEC1 | 6.07 | 2016-05-12T13:38:00Z | 8.99 | 56 | < 25mph
|  | Taggert | 2019-04-23 | 2019 | 21:06 | 34.2147 | -117.0973 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1027559E | OH-1027559E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution |  | Overhead | No |  |  | Unknown |  |  |  | Unknown | HHPC1 | 2.75 | 2017-07-25T00:15:00Z | 10 | 39 | < 25mph
|  | Sexton | 2015-02-22 | 2015 | 9:52 | 34.2849 | -119.2173 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura Fire Department | Pole 1718768E | OH-1718768E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-02-22 | 10:49 | Unknown |  |  |  | None | E8097 | 3.63 | 2017-07-27T05:01:00Z | 12.01 | 24 | < 25mph
|  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE444 | 4.44 | 2020-08-29T15:20:00Z | 21.49 | 126 | < 25mph
|  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | D3590 | 2.93 | 2018-10-20T16:15:00Z | 3 | 34 | < 25mph
|  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | D7457 | 6.43 | 2018-04-01T21:46:00Z | 14 | 52 | < 25mph
|  | LEE VINING-LUNDY NO. 1/ET-01774 | 2017-05-01 | 2017 | 5:40 | 38.0209 | -119.1608 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | CAlFIre | OH-1580964E | OH-1580964E | Tier 2 | T2 | Y |  | 55 | Distribution | Conductor | Overhead | No | <Null> |  | Contamination |  |  |  | Unknown | SE089 | 4.38 | 2020-03-29T12:30:00Z | 5.19 | 18 | < 25mph
|  | GUITAR | 2016-01-16 | 2016 | 15:20 | 34.4096 | -118.6816 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-848266E | OH-848266E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-01-16 | 15:20 | Equipment/Facility Failure | Other |  |  | Unknown | SE086 | 4.16 | 2019-02-09T09:20:00Z | 10.29 | 51 | < 25mph
| RYE |  | 2017-12-05 | 2017 | 11:31 | 34.4528 | -118.5819 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | SE032 | 4.63 | 2020-06-09T04:20:00Z | 27.25 | 156 | 25-40mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | SE063 | 3.72 | 2019-06-14T07:50:00Z | 28.92 | 46 | 25-40mph
|  | BIG CREEK 1-RECTOR/ET-01082 | 2018-08-04 | 2018 | 0:43 | 37.1895 | -119.2738 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | OH-7021454 | OH-7021454 | Tier 3 | T3 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2018-08-04 | 2:21 | Equipment/Facility Failure | Other |  |  | Unknown | SHVC1 | 3.7 | 2016-02-04T00:56:00Z | 4 | 1 | < 25mph
|  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE444 | 4.44 | 2020-04-08T06:10:00Z | 37.2 | 86 | 25-40mph
|  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force | TSHC1 | 6.99 | 2019-02-11T06:04:00Z | 13 | 15 | < 25mph
|  | SHOWDOWN | 2016-06-09 | 2016 | 11:28 | 34.5862 | -118.196 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4267121E | OH-4267121E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-09 | 11:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | LPDC1 | 6.32 | 2017-11-11T07:55:00Z | 28.01 | 20 | 25-40mph
|  | PICK | 2017-06-19 | 2017 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | 30278 Arrastre Canyon Rd., Acton | OH-699610E | Tier 3 | T3 | Y |  | 33 | Distribution | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown | MLCC1 | 7.72 | 2016-10-24T19:53:00Z | 23 | 2 | < 25mph
|  | METTLER | 2017-06-02 | 2017 | 10:50 | 35.1021 | -118.5328 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4416566E | OH-4416566E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | E3266 | 6.22 | 2017-02-22T23:02:00Z | 28.01 | 44 | 25-40mph
|  | VALLECITO | 2016-08-18 | 2016 | 19:00 | 34.4214 | -119.5964 | Other | Rural | Structure Only | Structure Only |  | Fire Agency | Santa Barbara County Fire Department | 2400 block of Whitney Avenue in Summerland | OH-1523986E | Tier 2 | T2 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | SBVC1 | 6.67 | 2019-04-02T14:24:00Z | 10 | 33 | < 25mph
|  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other | KPMD | 4.87 | 2015-04-01T07:53:00Z | 33.38 | 9 | 25-40mph
|  | SODA SPRINGS | 2016-06-21 | 2016 | 21:47 | 36.2515 | -118.7809 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4391218E | OH-4391218E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-21 | 21:47 | Contact From Object |  | Vegetation | Electric Facility | Unknown | OORC1 | 6.87 | 2017-09-24T16:12:00Z | 5.99 | 2 | < 25mph
3 |  | Bidder | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire | OH-2023941E | OH-2023941E | T3 | T3 |  | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force | SBZC1 | 3.46 | 2016-02-25T01:00:00Z | 10.04 | 94 | < 25mph
| LIBERTY |  | 2017-12-07 | 2017 | 13:00 | 33.5926 | -117.1498 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | Murrieta Fire Department | [17 empty] | Weather | SDMEA | 6.13 | 2018-09-06T04:49:00Z | 11.01 | 23 | < 25mph
|  | Maguire | 2015-04-17 | 2015 | 16:41 | 34.0851 | -118.8044 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles County Fire | Maguire 16kV out of Latigo Sub | OH-1199311E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2015-04-17 | 16:41 | Contact From Object |  | Vehicle | Pole | None | OOSC1 | 7.73 | 2018-10-18T10:30:00Z | 20.49 | 68 | < 25mph
|  | ELSTER | 2016-04-25 | 2016 | 19:15 | 36.1372 | -118.8615 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-X16345E | OH-X16345E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 120/240 V | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 19:15 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE279 | 4.32 | 2019-08-12T02:00:00Z | 13.73 | 25 | < 25mph
1 |  | Birchim | 2015-02-06 | 2015 | 13:15 | 37.454 | -118.5842 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Various Fire Agencies | Between Poles 1854107E & 1854106E | OH-1854107E | Tier 2 | T2 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-02-06 | 13:15 | Unknown |  |  |  | Unknown | OVRC1 | 4.68 | 2015-12-28T11:54:00Z | 5.99 | 1 | < 25mph
|  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown | LYQC1 | 4.98 | 2015-04-07T09:18:00Z | 18.01 | 1 | < 25mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | SE444 | 2.4 | 2020-11-07T19:00:00Z | 45.23 | 148 | 40-55mph
|  | Penstock | 2019-09-18 | 2019 | 2:52 | 34.3143 | -117.3793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4066969E | OH-4066969E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Human Error | F0490 | 6.19 | 2017-02-15T22:23:00Z | 13 | 24 | < 25mph
|  | Conestoga | 2020-06-13 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Other | MHEC1 | 2.44 | 2017-12-04T17:16:00Z | 30 | 42 | 25-40mph
|  | Penstock | 2019-09-18 | 2019 | 2:52 | 34.3143 | -117.3793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4066969E | OH-4066969E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Human Error | LTLC1 | 8 | 2018-01-01T13:15:00Z | 8.01 | 27 | < 25mph
|  | Zone | 2015-04-27 | 2015 | 19:09 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | 9372 STOCKTON RD PMP MOORPARK | OH-4734128E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-04-27 | 19:09 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | WLYC1 | 7.19 | 2016-07-12T03:49:00Z | 10 | 55 | < 25mph
|  | LEE VINING-LUNDY NO. 1/ET-01774 | 2017-05-01 | 2017 | 5:40 | 38.0209 | -119.1608 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | CAlFIre | OH-1580964E | OH-1580964E | Tier 2 | T2 | Y |  | 55 | Distribution | Conductor | Overhead | No | <Null> |  | Contamination |  |  |  | Unknown | UNDC1 | 1.29 | 2020-04-19T22:23:00Z | 27 | 27 | 25-40mph
|  | ARCHIE | 2018-11-13 | 2018 | 7:11 | 33.4928 | -117.2796 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | NORTH OF CARANCHO ON VIA CIELO | OH-4149859E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-13 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Unknown | FBZC1 | 7.6 | 2020-01-25T20:22:00Z | 12.01 | 55 | < 25mph
|  | PATRICIA | 2016-09-16 | 2016 | 19:02 | 34.4851 | -119.3001 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ojai City Fire Department | OH-4797071E | OH-4797071E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-09-16 | 19:02 | Contact From Object |  | Vehicle | Pole | Unknown | CSVC1 | 6.69 | 2016-09-03T11:09:00Z | 4.99 | 6 | < 25mph
|  | Taiwan | 2015-07-13 | 2015 | 11:15 | 33.7678 | -117.7207 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | Cal Fire | Pole 960439E | OH-960439E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-07-13 | 13:30 | Unknown |  |  |  | Unknown | FRCC1 | 3.07 | 2020-01-30T05:51:00Z | 44 | 149 | 40-55mph
10005 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | OOSC1 | 5.78 | 2018-09-07T12:15:00Z | 12.59 | 67 | < 25mph
|  | Lasker | 2020-07-26 | 2020 | 12:50 | 34.5326 | -118.0541 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4619162E | OH-4619162E | T3 | T3 |  | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | LPDC1 | 2.76 | 2015-06-17T20:55:00Z | 37 | 6 | 25-40mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TNRC1 | 2.34 | 2015-08-26T22:57:00Z | 18.99 | 102 | < 25mph
|  | PYTHON | 2016-06-05 | 2016 | 15:59 | 34.4208 | -118.4218 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4154960E | OH-4154960E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-06-05 | 15:59 | Unknown |  |  |  | Unknown | CNIC1 | 4.67 | 2018-10-30T21:55:00Z | 32.01 | 55 | 25-40mph
|  | JORDAN | 2018-08-29 | 2018 | 17:32 | 35.7358 | -118.7192 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | Jack Ranch Rd/White River Rd, Kernville | OH-4635091E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-08-29 | 19:06 | Contact From Object |  | Vegetation | Electric Facility | Unknown | WOCC1 | 6.68 | 2018-01-22T17:13:00Z | 4.99 | 1 | < 25mph
|  | Morongo | 2020-08-03 | 2020 | 10:33 | 34.0758 | -116.5548 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-2107480E | OH-2107480E | T2 | T2 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-08-03 | 19:15 | Contact From Object |  | Balloons | Electric Facility | Outside Force | UCBU | 7.55 | 2018-11-15T23:10:00Z | 13.09 | 6 | < 25mph
|  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.54 | 2015-08-29T20:51:00Z | 18.99 | 50 | < 25mph
10005 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | D5145 | 7.89 | 2016-03-11T09:16:00Z | 8.01 | 69 | < 25mph
2 |  | Lopez | 2015-05-23 | 2015 | 11:57 | 34.3006 | -118.3613 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | Pole 1261671E | OH-1261671E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Conductor | Overhead | Yes | 2015-05-23 | 11:05 | Unknown |  |  |  | Unknown | CNIC1 | 4.89 | 2020-01-14T16:55:00Z | 28.01 | 98 | 25-40mph
10004 |  | Peninsula | 2019-03-16 | 2019 | 17:58 | 33.6182 | -117.8025 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1729510E | OH-1729510E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-03-16 | 17:58 | Equipment/Facility Failure | Crossarm |  |  | Unknown | SE024 | 6.43 | 2019-05-11T20:50:00Z | 20.4 | 108 | < 25mph
|  | Northpark | 2019-06-20 | 2019 | 14:08 | 34.2298 | -117.4048 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | San Bern. FD | OH-201371S | OH-201371S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Human Error | RLTC1 | 7.03 | 2015-11-13T06:35:00Z | 29.97 | 9 | 25-40mph
1 |  | Birchim | 2015-02-06 | 2015 | 13:15 | 37.454 | -118.5842 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Various Fire Agencies | Between Poles 1854107E & 1854106E | OH-1854107E | Tier 2 | T2 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-02-06 | 13:15 | Unknown |  |  |  | Unknown | OVRC1 | 4.68 | 2018-01-30T07:54:00Z | 11.01 | 1 | < 25mph
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | UNDC1 | 4.3 | 2018-02-09T20:23:00Z | 8.99 | 9 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:26 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | Unknown | FRCC1 | 7.87 | 2017-05-13T19:51:00Z | 18.99 | 49 | < 25mph
|  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | MBCC1 | 6.95 | 2017-08-21T02:56:00Z | 21 | 76 | < 25mph
|  | Wildomar | 2019-09-19 | 2019 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside County FD | OH-2225310E | OH-2225310E | Tier 3 | T3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other | E4050 | 3.1 | 2016-01-26T21:12:00Z | 21 | 11 | < 25mph
|  | Zone | 2019-08-10 | 2019 | 13:00 | 34.3089 | -118.9413 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | VFD | OH-4734128E | OH-4734128E | Tier 3 | T3 | Y | AT&T Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | SE107 | 7.41 | 2019-01-16T14:20:00Z | 13.6 | 93 | < 25mph
|  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SDPNN | 3.59 | 2015-06-18T01:34:00Z | 20.98 | 33 | < 25mph
|  | PATRICIA | 2017-04-16 | 2017 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4495331E | OH-4495331E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown | RSVC1 | 6.98 | 2018-10-29T07:00:00Z | 5.91 | 39 | < 25mph
|  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force | LYQC1 | 1.86 | 2016-11-27T07:18:00Z | 28.01 | 1 | 25-40mph
|  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force | SE228 | 6.47 | 2019-10-19T21:20:00Z | 15.21 | 77 | < 25mph
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | SE089 | 7.37 | 2018-10-06T15:20:00Z | 14.58 | 17 | < 25mph
2 |  | Lopez | 2015-05-23 | 2015 | 11:57 | 34.3006 | -118.3613 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | Pole 1261671E | OH-1261671E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Conductor | Overhead | Yes | 2015-05-23 | 11:05 | Unknown |  |  |  | Unknown | CNIC1 | 4.89 | 2017-06-27T11:55:00Z | 8.99 | 39 | < 25mph
|  | PALOMINO | 2015-10-09 | 2015 | 14:00 | 33.5752 | -117.17 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | BEHIND ADDRESS 28151 CELIA RD / PROPERTY LINE., STR 212903S | OH-212903S | Tier 2 | T2 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | SDMEA | 4.76 | 2016-02-28T05:49:00Z | 7 | 18 | < 25mph
|  | Zone | 2019-08-10 | 2019 | 13:00 | 34.3089 | -118.9413 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | VFD | OH-4734128E | OH-4734128E | Tier 3 | T3 | Y | AT&T Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | WLYC1 | 7.19 | 2019-06-13T08:49:00Z | 11.01 | 151 | < 25mph
|  | SODA SPRINGS | 2016-06-21 | 2016 | 21:47 | 36.2515 | -118.7809 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4391218E | OH-4391218E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-21 | 21:47 | Contact From Object |  | Vegetation | Electric Facility | Unknown | MOLC1 | 5.11 | 2015-06-25T01:27:00Z | 12.01 | 2 | < 25mph
|  | CACHUMA | 2016-08-18 | 2016 | 14:52 | 34.5356 | -119.8523 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-1413051E | OH-1413051E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-18 | 14:52 | Contact From Object |  | Vegetation | Communication Facility | Unknown | AS303 | 7.85 | 2016-07-06T04:46:00Z | 17 | 120 | < 25mph
|  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown | FTNC1 | 0.32 | 2020-01-16T12:00:00Z | 7 | 11 | < 25mph
|  | Saugus-Santa Susana | 2019-08-06 | 2019 | 15:03 | 34.3918 | -118.6596 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | VFD & LACFD | M6-T1 | M6-T1 | Tier 3 | T3 | Y | NA | 66 | Transmission | Other | Overhead | Yes | 2019-08-06 | 12:51 | Contact From Object |  | Animal | Electric Facility | Other | E3126 | 5.46 | 2017-02-10T04:30:00Z | 4.99 | 6 | < 25mph
|  | BIG CREEK 1-RECTOR/ET-01082 | 2018-08-04 | 2018 | 0:43 | 37.1895 | -119.2738 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | OH-7021454 | OH-7021454 | Tier 3 | T3 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2018-08-04 | 2:21 | Equipment/Facility Failure | Other |  |  | Unknown | SHVC1 | 3.7 | 2015-11-21T13:56:00Z | 2.01 | 3 | < 25mph
|  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force | E4050 | 7.03 | 2016-09-17T21:10:00Z | 15.99 | 11 | < 25mph
|  | Keller | 2015-06-09 | 2015 | 5:46 | 33.5986 | -117.1311 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 4401960E | OH-2297077E | Tier 2 | T2 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2015-06-09 | 5:46 | Contact From Object |  | Animal | Electric Facility | None | SDMEA | 7.28 | 2017-07-04T07:49:00Z | 7 | 37 | < 25mph
| RYE |  | 2017-12-05 | 2017 | 15:00 | 34.2676 | -117.844 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | TANC1 | 6.35 | 2017-12-26T14:01:00Z | 4.99 | 1 | < 25mph
|  | Viento | 2020-06-09 | 2020 | 16:42 | 35.1384 | -118.4809 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4707894E | OH-4707894E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | KTSP | 2.37 | 2018-03-01T22:55:00Z | 25.32 | 40 | 25-40mph
|  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | MLCC1 | 7.93 | 2018-09-17T08:53:00Z | 22.01 | 18 | < 25mph
|  | Plateau | 2019-09-11 | 2019 | 8:08 | 34.0991 | -118.6793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4424792E | OH-4424792E | Tier 3 | T3 | Y | Verizon / AT&T / Crown Castle | 16 | Distribution | Conductor | Overhead | Yes | 2019-09-11 | 8:08 | Equipment/Facility Failure | Conductor |  | Electric Facility | Human Error | D2363 | 3.42 | 2020-12-20T04:52:00Z | 34.99 | 227 | 25-40mph
|  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown | LYQC1 | 4.98 | 2016-12-28T09:18:00Z | 8.01 | 1 | < 25mph
10002 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | CEEC1 | 3.51 | 2017-07-20T19:38:00Z | 14 | 63 | < 25mph
| EASY |  | 2019-10-30 | 2019 | 6:00 | 34.2822 | -118.8034 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | E1625 | 7.52 | 2016-11-28T16:23:00Z | 10 | 64 | < 25mph
|  | Northpark | 2019-06-20 | 2019 | 14:08 | 34.2298 | -117.4048 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | San Bern. FD | OH-201371S | OH-201371S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Human Error | E3127 | 5.2 | 2017-05-09T23:00:00Z | 32.01 | 14 | 25-40mph
|  | SHOWDOWN | 2016-06-09 | 2016 | 11:28 | 34.5862 | -118.196 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4267121E | OH-4267121E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-09 | 11:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | KPMD | 7.18 | 2016-07-11T00:53:00Z | 43.73 | 23 | 40-55mph
|  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SE251 | 3.84 | 2020-01-04T06:50:00Z | 15.05 | 76 | < 25mph
10005 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | OOSC1 | 5.78 | 2017-10-17T05:30:00Z | 13.31 | 53 | < 25mph
|  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other | E8870 | 7.27 | 2017-04-11T07:14:00Z | 7 | 17 | < 25mph
|  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error | AU563 | 7.19 | 2016-01-29T21:44:00Z | 42.01 | 17 | 40-55mph
|  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error | SAUC1 | 7.39 | 2016-02-27T19:57:00Z | 11.01 | 8 | < 25mph
10002 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | E1856 | 4.13 | 2017-09-16T23:03:00Z | 17 | 57 | < 25mph
|  | DRISKILL | 2016-10-18 | 2016 | 18:41 | 34.4687 | -119.7722 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Santa Barbara Fire Department | OH-2178476E | OH-2178476E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-18 | 18:41 | Equipment/Facility Failure | Fuse |  |  | Unknown | MPWC1 | 2.09 | 2020-05-16T19:06:00Z | 13 | 244 | < 25mph
10006 |  | CONCEPCION | 2016-05-12 | 2016 | 8:55 | 34.4736 | -120.216 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-708452E | OH-708452E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-12 | 8:55 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UP481 | 0.62 | 2019-06-21T09:30:00Z | 7.02 | 9 | < 25mph
|  | Zone | 2015-04-27 | 2015 | 19:10 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 4734128E | OH-4734128E | Tier 3 | T3 | Y |  | 16 | Distribution | Other | Overhead | Yes | 2015-04-27 | 19:10 | Equipment/Facility Failure | Other |  |  | Unknown | AT184 | 5.07 | 2016-03-13T05:06:00Z | 10 | 52 | < 25mph
|  | TICO | 2016-04-28 | 2016 | 14:00 | 34.357 | -119.314 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura County FD | OH-1604151E | OH-1604151E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-04-28 | 14:00 | Equipment/Facility Failure | Other |  |  | Unknown | E8097 | 7.74 | 2016-08-14T21:54:00Z | 23 | 22 | < 25mph
| EDISON |  | 2016-05-12 | 2016 | -8 | 34.3135 | -119.1865 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | SE047 | 6.77 | 2018-11-20T17:00:00Z | 11.83 | 90 | < 25mph
|  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | MTIC1 | 4.81 | 2017-03-06T00:47:00Z | 40 | 16 | 40-55mph
|  | PYTHON | 2016-06-05 | 2016 | 15:59 | 34.4208 | -118.4218 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4154960E | OH-4154960E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-06-05 | 15:59 | Unknown |  |  |  | Unknown | SE177 | 6.54 | 2020-11-12T08:00:00Z | 15.71 | 294 | < 25mph
|  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other | LPDC1 | 2.12 | 2017-03-31T17:55:00Z | 18.01 | 6 | < 25mph
|  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE113 | 5.34 | 2019-01-11T17:40:00Z | 5.82 | 7 | < 25mph
|  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force | E4050 | 7.03 | 2017-04-08T01:06:00Z | 18.01 | 20 | < 25mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | E1966 | 3.22 | 2015-03-19T13:29:00Z | 5.99 | 18 | < 25mph
|  | Taggert | 2019-04-23 | 2019 | 21:06 | 34.2147 | -117.0973 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1027559E | OH-1027559E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution |  | Overhead | No |  |  | Unknown |  |  |  | Unknown | HHPC1 | 2.75 | 2019-11-20T04:15:00Z | 34 | 125 | 25-40mph
|  | La Mancha | 2020-07-05 | 2020 | 3:57 | 34.1325 | -118.8532 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1848406E | OH-1848406E | T3 | T3 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-07-05 | 3:57 | Equipment/Facility Failure | Insulator |  |  | Unknown | OOSC1 | 4.63 | 2018-08-21T06:30:00Z | 11.79 | 73 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:26 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | Unknown | SNPC1 | 6.52 | 2020-02-03T09:30:00Z | 17.98 | 139 | < 25mph
|  | PYTHON | 2016-10-22 | 2016 | 15:17 | 34.3812 | -118.4132 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | RAR 0038 | OH-4860064E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-22 | 15:17 | Contact From Object |  | Balloons | Electric Facility | Unknown | NHPC1 | 6.84 | 2016-05-08T20:56:00Z | 24 | 38 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:30 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | None | SNPC1 | 6.52 | 2020-03-28T14:00:00Z | 14.99 | 147 | < 25mph
|  | Elster | 2019-09-21 | 2019 | 10:53 | 36.1026 | -118.8659 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4252581E | OH-4252581E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-21 | 10:53 | Contact From Object |  | Vehicle | Electric Facility | Human Error | SE572 | 7.09 | 2020-03-29T22:20:00Z | 9.57 | 47 | < 25mph
|  | CONCEPCION | 2016-05-02 | 2016 | 7:03 | 34.4736 | -120.2153 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-4041841E | OH-4041841E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-02 | 7:03 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | C6499 | 0.63 | 2016-10-28T13:38:00Z | 8.99 | 13 | < 25mph
|  | GUITAR | 2016-01-16 | 2016 | 15:20 | 34.4096 | -118.6816 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-848266E | OH-848266E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-01-16 | 15:20 | Equipment/Facility Failure | Other |  |  | Unknown | E3126 | 7.2 | 2016-10-31T15:00:00Z | 18.99 | 10 | < 25mph
|  | Saugus-Santa Susana | 2019-08-06 | 2019 | 15:03 | 34.3918 | -118.6596 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | VFD & LACFD | M6-T1 | M6-T1 | Tier 3 | T3 | Y | NA | 66 | Transmission | Other | Overhead | Yes | 2019-08-06 | 12:51 | Contact From Object |  | Animal | Electric Facility | Other | E3126 | 5.46 | 2016-10-29T03:59:00Z | 24.99 | 8 | < 25mph
|  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown | FTNC1 | 0.32 | 2019-01-26T17:00:00Z | 4.99 | 1 | < 25mph
|  | POPPET FLATS | 2016-02-27 | 2016 | 0:49 | 33.9134 | -116.8003 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1989045E | OH-1989045E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-02-27 | 0:49 | Contact From Object |  | Vehicle | Pole | Unknown | POPC1 | 5.22 | 2016-02-06T21:14:00Z | 35.99 | 14 | 25-40mph
|  | PATRICIA | 2016-10-23 | 2016 | 9:40 | 34.4603 | -119.2853 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | 900 Rice Road Ojai | OH-786960E | Tier 3 | T3 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | CSVC1 | 6.08 | 2017-10-19T21:09:00Z | 18.99 | 11 | < 25mph
| MEYERS |  | 2017-12-05 | 2017 | 14:00 | 34.2183 | -117.4062 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | DVOC1 | 2.77 | 2015-05-20T18:10:00Z | 13 | 4 | < 25mph
|  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown | E3047 | 1.29 | 2016-09-09T17:06:00Z | 8.01 | 22 | < 25mph
2 |  | Lopez | 2015-05-23 | 2015 | 11:57 | 34.3006 | -118.3613 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | Pole 1261671E | OH-1261671E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Conductor | Overhead | Yes | 2015-05-23 | 11:05 | Unknown |  |  |  | Unknown | CNIC1 | 4.89 | 2017-06-11T14:55:00Z | 22.01 | 34 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:30 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | None | HP018 | 6.4 | 2018-11-19T01:36:00Z | 17.22 | 85 | < 25mph
|  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other | SE286 | 7.46 | 2019-08-26T12:30:00Z | 11.18 | 75 | < 25mph
|  | SODA SPRINGS | 2016-06-21 | 2016 | 21:47 | 36.2515 | -118.7809 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4391218E | OH-4391218E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-21 | 21:47 | Contact From Object |  | Vegetation | Electric Facility | Unknown | OORC1 | 6.87 | 2017-05-22T07:12:00Z | 11.01 | 2 | < 25mph
|  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather | SE270 | 4.16 | 2020-06-30T19:00:00Z | 16.07 | 126 | < 25mph
|  | POULTRY | 2018-09-21 | 2018 | 8:28 | 34.0728 | -117.0397 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Juniper St. Yucaipa | OH-129241E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | MMKC1 | 0.63 | 2015-07-20T09:34:00Z | 23 | 29 | < 25mph
|  | MIST | 2016-08-24 | 2016 | 16:37 | 34.4665 | -120.0701 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Santa Barbara County Fire Department | Refiugio Canyon, Santa Barbara | OH-4538468E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-24 | 18:50 | Contact From Object |  | Animal | Electric Facility | Unknown | RHWC1 | 3.48 | 2017-01-26T20:06:00Z | 10 | 11 | < 25mph
| RYE |  | 2017-12-05 | 2017 | 11:31 | 34.4528 | -118.5819 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | SE437 | 7.77 | 2020-04-27T01:10:00Z | 16.73 | 137 | < 25mph
|  | CABANA | 2017-10-16 | 2017 | 6:11 | 34.0217 | -117.5069 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1670014E | OH-1670014E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-10-16 | 6:11 | Contact From Object |  | Balloons | Electric Facility | Unknown | E7239 | 2.66 | 2016-08-12T16:53:00Z | 7 | 13 | < 25mph
|  | METTLER | 2017-06-02 | 2017 | 10:50 | 35.1021 | -118.5328 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4416566E | OH-4416566E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | E3266 | 6.22 | 2016-12-20T22:06:00Z | 20 | 42 | < 25mph
|  | Soda Springs | 2015-05-14 | 2015 | 22:24 | 36.1318 | -118.7784 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | Soda Springs 12kV out of Boxwood Sub | OH-4464511E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-14 | 22:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown | OORC1 | 5.23 | 2015-07-26T17:12:00Z | 12.01 | 1 | < 25mph
|  | Taggert | 2019-04-23 | 2019 | 21:06 | 34.2147 | -117.0973 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1027559E | OH-1027559E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution |  | Overhead | No |  |  | Unknown |  |  |  | Unknown | HHPC1 | 2.75 | 2016-02-27T13:15:00Z | 20 | 52 | < 25mph
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | SE089 | 7.37 | 2018-12-04T19:50:00Z | 19.19 | 17 | < 25mph
|  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown | KMMH | 1.38 | 2020-03-15T12:37:00Z | 35.68 | 72 | 25-40mph
| LIBERTY |  | 2017-12-07 | 2017 | 13:00 | 33.5926 | -117.1498 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | Murrieta Fire Department | [17 empty] | Weather | SDMEA | 6.13 | 2016-04-14T05:49:00Z | 13 | 19 | < 25mph
|  | POULTRY | 2018-09-21 | 2018 | 8:28 | 34.0728 | -117.0397 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Juniper St. Yucaipa | OH-129241E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | MMKC1 | 0.63 | 2016-01-25T02:34:00Z | 8.99 | 55 | < 25mph
|  | BIG CREEK 1-RECTOR/ET-01082 | 2018-08-04 | 2018 | 0:43 | 37.1895 | -119.2738 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | OH-7021454 | OH-7021454 | Tier 3 | T3 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2018-08-04 | 2:21 | Equipment/Facility Failure | Other |  |  | Unknown | SHVC1 | 3.7 | 2017-05-13T17:56:00Z | 10 | 1 | < 25mph
|  | Morongo | 2020-08-03 | 2020 | 10:33 | 34.0758 | -116.5548 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-2107480E | OH-2107480E | T2 | T2 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-08-03 | 19:15 | Contact From Object |  | Balloons | Electric Facility | Outside Force | UCBU | 7.55 | 2016-05-13T16:10:00Z | 8.9 | 6 | < 25mph
|  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown | E3047 | 1.29 | 2017-10-05T23:18:00Z | 11.01 | 24 | < 25mph
|  | DEACON | 2017-10-18 | 2017 | 13:34 | 33.7702 | -117.2157 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1564666E | OH-1564666E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | UCMO | 3.31 | 2018-10-15T03:40:00Z | 12.3 | 43 | < 25mph
|  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown | E3047 | 1.29 | 2016-02-19T05:41:00Z | 10 | 20 | < 25mph
10005 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | OOSC1 | 5.78 | 2019-03-06T19:45:00Z | 64.09 | 69 | 55mph+
|  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UCMO | 4.71 | 2019-03-14T16:40:00Z | 21.61 | 42 | < 25mph
1 |  | Birchim | 2015-02-06 | 2015 | 13:15 | 37.454 | -118.5842 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Various Fire Agencies | Between Poles 1854107E & 1854106E | OH-1854107E | Tier 2 | T2 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-02-06 | 13:15 | Unknown |  |  |  | Unknown | OVRC1 | 4.68 | 2018-02-28T12:54:00Z | 8.99 | 1 | < 25mph
| ERSKINE |  | 2016-06-23 | 2016 | 16:00 | 34.2676 | -117.844 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | BLM | [13 empty] | Contact From Object |  | Vegetation |  |  | TANC1 | 6.35 | 2017-07-27T04:01:00Z | 4.99 | 1 | < 25mph
|  | DEACON | 2017-10-18 | 2017 | 13:34 | 33.7702 | -117.2157 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1564666E | OH-1564666E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | UCMO | 3.31 | 2018-06-20T06:20:00Z | 5.3 | 31 | < 25mph
|  | JORDAN | 2018-08-29 | 2018 | 17:32 | 35.7358 | -118.7192 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | Jack Ranch Rd/White River Rd, Kernville | OH-4635091E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-08-29 | 19:06 | Contact From Object |  | Vegetation | Electric Facility | Unknown | WOCC1 | 6.68 | 2020-10-26T14:13:00Z | 11 | 29 | < 25mph
|  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other | UCBU | 3.92 | 2015-06-20T00:10:00Z | 18.41 | 35 | < 25mph
|  | La Mancha | 2020-07-05 | 2020 | 3:57 | 34.1325 | -118.8532 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1848406E | OH-1848406E | T3 | T3 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-07-05 | 3:57 | Equipment/Facility Failure | Insulator |  |  | Unknown | SE037 | 7.94 | 2020-01-15T20:30:00Z | 10.58 | 147 | < 25mph
|  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | AT643 | 4.77 | 2015-03-06T03:20:00Z | 10 | 33 | < 25mph
10003 |  | SHEFFIELD | 2016-02-22 | 2016 | 17:04 | 34.4492 | -119.5845 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Montecito Fire Department | OH-1082380E | OH-1082380E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-02-22 | 17:04 | Equipment/Facility Failure | Conductor |  |  | Unknown | NTBC1 | 6.39 | 2015-07-04T08:06:00Z | 16.98 | 16 | < 25mph
|  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error | SAUC1 | 7.39 | 2015-04-14T11:57:00Z | 8.01 | 15 | < 25mph
|  | CARVER | 2016-09-24 | 2016 | 14:20 | 35.7381 | -118.9546 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4784763E | OH-4784763E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-09-24 | 14:20 | Contact From Object |  | Animal | Electric Facility | Unknown | WOCC1 | 7.2 | 2017-05-09T16:13:00Z | 11.01 | 1 | < 25mph
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | S408E | 7.97 | 2019-11-13T18:10:00Z | 6.44 | 54 | < 25mph
|  | WELCH | 2016-04-25 | 2016 | 15:23 | 35.8387 | -118.9147 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1078325E | OH-1078325E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 15:23 | Equipment/Facility Failure | Insulator |  |  | Unknown | SE435 | 2.88 | 2020-09-30T05:00:00Z | 13.52 | 25 | < 25mph
|  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | SDUNC | 4.84 | 2015-01-16T20:49:00Z | 10 | 9 | < 25mph
|  | PICK | 2017-06-19 | 2017 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | 30278 Arrastre Canyon Rd., Acton | OH-699610E | Tier 3 | T3 | Y |  | 33 | Distribution | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown | ATNC1 | 0.34 | 2016-12-29T08:54:00Z | 23 | 2 | < 25mph
|  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | F0145 | 4.82 | 2018-05-19T00:40:00Z | 18.01 | 35 | < 25mph
|  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TPGC1 | 1.58 | 2016-05-03T16:57:00Z | 14 | 49 | < 25mph
|  | Verdugo | 2019-06-25 | 2019 | 14:31 | 34.2903 | -118.2885 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-X314E | OH-X314E | Tier 3 | T3 | Y | LADWP | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-25 | 14:31 | Wire-Wire Contact |  |  |  | Weather | CEKC1 | 7.88 | 2015-10-14T12:54:00Z | 7 | 14 | < 25mph
|  | TUNA | 2016-09-19 | 2016 | 6:11 | 34.04 | -118.6687 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-1638513E | OH-1638513E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | MBCC1 | 3.63 | 2016-05-30T21:56:00Z | 30 | 38 | 25-40mph
|  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | LCBC1 | 6.83 | 2017-06-15T10:55:00Z | 11.01 | 44 | < 25mph
|  | Maguire | 2015-04-17 | 2015 | 16:41 | 34.0851 | -118.8044 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles County Fire | Maguire 16kV out of Latigo Sub | OH-1199311E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2015-04-17 | 16:41 | Contact From Object |  | Vehicle | Pole | None | OOSC1 | 7.73 | 2020-08-18T02:15:00Z | 17.5 | 160 | < 25mph
1 |  | Birchim | 2015-02-06 | 2015 | 13:15 | 37.454 | -118.5842 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Various Fire Agencies | Between Poles 1854107E & 1854106E | OH-1854107E | Tier 2 | T2 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-02-06 | 13:15 | Unknown |  |  |  | Unknown | SE390 | 6.9 | 2020-03-03T05:20:00Z | 25.79 | 24 | 25-40mph
|  | Plateau | 2019-09-11 | 2019 | 8:08 | 34.0991 | -118.6793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4424792E | OH-4424792E | Tier 3 | T3 | Y | Verizon / AT&T / Crown Castle | 16 | Distribution | Conductor | Overhead | Yes | 2019-09-11 | 8:08 | Equipment/Facility Failure | Conductor |  | Electric Facility | Human Error | D2363 | 3.42 | 2017-02-12T07:35:00Z | 5.99 | 43 | < 25mph
|  | CONCEPCION | 2016-05-02 | 2016 | 7:03 | 34.4736 | -120.2153 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-4041841E | OH-4041841E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-02 | 7:03 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UP481 | 0.66 | 2016-01-26T10:00:00Z | 21.99 | 13 | < 25mph
|  | La Mancha | 2020-07-05 | 2020 | 3:57 | 34.1325 | -118.8532 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1848406E | OH-1848406E | T3 | T3 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-07-05 | 3:57 | Equipment/Facility Failure | Insulator |  |  | Unknown | D5145 | 6.42 | 2020-02-21T16:46:00Z | 25.99 | 144 | 25-40mph
4 |  | PYTHON | 2016-12-02 | 2016 | 21:26 | 34.3812 | -118.4132 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | OH-4572770E | OH-4572770E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vegetation | Electric Facility | Unknown | NHPC1 | 6.84 | 2016-06-18T16:56:00Z | 14 | 32 | < 25mph
|  | Zone | 2015-06-23 | 2015 | 17:21 | 34.279 | -118.9072 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura Fire Department | Primary splice box at base of pole 2115918e | OH-2115918E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Subsurface | No | <Null> |  | Equipment/Facility Failure | Other |  |  | Unknown | WLYC1 | 7.44 | 2016-04-18T09:49:00Z | 20 | 61 | < 25mph
|  | METTLER | 2017-06-02 | 2017 | 10:50 | 35.1021 | -118.5328 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4416566E | OH-4416566E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SE237 | 7.68 | 2019-09-04T02:00:00Z | 18.79 | 84 | < 25mph
|  | Taiwan | 2015-07-13 | 2015 | 11:15 | 33.7678 | -117.7207 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | Cal Fire | Pole 960439E | OH-960439E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-07-13 | 13:30 | Unknown |  |  |  | Unknown | SE081 | 1.69 | 2020-03-28T11:30:00Z | 13.6 | 156 | < 25mph
|  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | SE208 | 6.68 | 2019-11-06T14:00:00Z | 10.38 | 183 | < 25mph
|  | GUITAR | 2016-01-16 | 2016 | 15:20 | 34.4096 | -118.6816 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-848266E | OH-848266E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-01-16 | 15:20 | Equipment/Facility Failure | Other |  |  | Unknown | SE436 | 4.97 | 2019-09-15T13:50:00Z | 13.15 | 93 | < 25mph
|  | CONCEPCION | 2016-05-02 | 2016 | 7:03 | 34.4736 | -120.2153 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-4041841E | OH-4041841E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-02 | 7:03 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | C6499 | 0.63 | 2017-01-27T09:33:00Z | 4 | 7 | < 25mph
|  | Python | 2015-06-06 | 2015 | 10:00 | 34.4043 | -118.4234 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | 16450 Alamo Canyon Rd, Canyon Country | OH-4779534E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-06-06 | 10:13 | Contact From Object |  | Animal | Electric Facility | None | SE486 | 6.03 | 2020-08-01T16:00:00Z | 14.69 | 202 | < 25mph
|  | WELCH | 2016-04-25 | 2016 | 15:23 | 35.8387 | -118.9147 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1078325E | OH-1078325E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 15:23 | Equipment/Facility Failure | Insulator |  |  | Unknown | FTNC1 | 3.62 | 2015-08-21T04:00:00Z | 4 | 1 | < 25mph
|  | BIG CREEK 1-RECTOR/ET-01082 | 2018-08-04 | 2018 | 0:43 | 37.1895 | -119.2738 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | OH-7021454 | OH-7021454 | Tier 3 | T3 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2018-08-04 | 2:21 | Equipment/Facility Failure | Other |  |  | Unknown | SE379 | 2.71 | 2020-08-18T06:30:00Z | 13.59 | 91 | < 25mph
| TENAJA |  | 2019-09-04 | 2019 | 16:43 | 33.5285 | -117.2732 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | SE229 | 7.3 | 2020-07-15T15:20:00Z | 10.52 | 82 | < 25mph
|  | BIG CREEK 3-RECTOR NO.1/ET-01046 | 2015-09-03 | 2015 | 17:00 | 36.8936 | -119.4571 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | East of Watts Valley Rd and Pittman Hill Rd, East of Clovis | OH-7020930 | Tier 2 | T2 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2015-09-03 | 16:15 | Contact From Object |  | Balloons | Electric Facility | None | FCHC1 | 1.24 | 2019-07-18T15:00:00Z | 4.99 | 11 | < 25mph
|  | CACHUMA | 2016-08-18 | 2016 | 14:52 | 34.5356 | -119.8523 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-1413051E | OH-1413051E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-18 | 14:52 | Contact From Object |  | Vegetation | Communication Facility | Unknown | MPWC1 | 4.41 | 2017-12-16T16:06:00Z | 30 | 120 | 25-40mph
|  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown | SE077 | 7.59 | 2018-11-30T17:00:00Z | 12.17 | 45 | < 25mph
|  | Maguire | 2015-04-17 | 2015 | 16:41 | 34.0851 | -118.8044 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles County Fire | Maguire 16kV out of Latigo Sub | OH-1199311E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2015-04-17 | 16:41 | Contact From Object |  | Vehicle | Pole | None | MBCC1 | 5.78 | 2015-11-27T20:56:00Z | 21 | 23 | < 25mph
|  | CUDDEBACK | 2017-08-08 | 2017 | 17:52 | 35.1342 | -118.5607 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4179753E | OH-4179753E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-08-08 | 17:52 | Contact From Object |  | Vehicle | Electric Facility | Unknown | C1020 | 3.61 | 2015-12-15T23:06:00Z | 12.01 | 32 | < 25mph
|  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other | LPDC1 | 2.12 | 2020-07-12T23:55:00Z | 36 | 124 | 25-40mph
|  | PYTHON | 2016-10-22 | 2016 | 15:17 | 34.3812 | -118.4132 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | RAR 0038 | OH-4860064E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-22 | 15:17 | Contact From Object |  | Balloons | Electric Facility | Unknown | CNIC1 | 1.96 | 2015-12-28T19:55:00Z | 24 | 23 | < 25mph
|  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error | AU563 | 7.19 | 2018-12-21T06:20:00Z | 22.01 | 27 | < 25mph
|  | Bonanza | 2020-06-05 | 2020 | 17:33 | 35.7635 | -118.4218 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Kern County Fire Department | OH-4451126E | OH-4451126E | T3 | T3 | Y | None | 12 | Distribution | Other | Overhead | Yes | 2020-06-05 | 17:33 | Contact From Object |  | Animal | Electric Facility | Other | KRNC1 | 1.16 | 2015-08-05T06:57:00Z | 17 | 2 | < 25mph
|  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force | D0117 | 2.25 | 2019-12-11T17:39:00Z | 8.01 | 42 | < 25mph
|  | BIG CREEK 1-RECTOR/ET-01082 | 2018-08-04 | 2018 | 0:43 | 37.1895 | -119.2738 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | OH-7021454 | OH-7021454 | Tier 3 | T3 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2018-08-04 | 2:21 | Equipment/Facility Failure | Other |  |  | Unknown | SHVC1 | 3.7 | 2016-07-20T22:56:00Z | 13 | 1 | < 25mph
|  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | SE918 | 4.21 | 2020-12-06T00:30:00Z | 11.62 | 177 | < 25mph
| LIBERTY |  | 2017-12-07 | 2017 | 13:00 | 33.5926 | -117.1498 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | Murrieta Fire Department | [17 empty] | Weather | SRUC1 | 6.88 | 2017-12-07T14:54:00Z | 14 | 27 | < 25mph
|  | Mettler | 2020-08-10 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | OH-2093506E | OH-2093506E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Unknown | C0464 | 3.56 | 2017-12-03T12:03:00Z | 12.01 | 35 | < 25mph
10002 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | SE458 | 4.72 | 2020-05-14T18:10:00Z | 16.22 | 224 | < 25mph
10005 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error | ATNC1 | 5.18 | 2017-07-27T17:54:00Z | 14 | 10 | < 25mph
|  | OAK GLEN | 2017-03-15 | 2017 | 13:23 | 34.0534 | -116.971 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-2326555E | OH-2326555E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-15 | 13:23 | Contact From Object |  | Animal | Electric Facility | Unknown | MMKC1 | 4.7 | 2015-08-21T03:34:00Z | 12.01 | 36 | < 25mph
|  | SANTA CLARA-TAYSHELL/ET-00423 | 2016-04-21 | 2016 | 12:20 | 34.3339 | -119.2748 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4434916E | OH-4434916E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2016-04-21 | 12:20 | Contact From Object |  | Animal | Electric Facility | Unknown | CSVC1 | 7.52 | 2015-05-28T23:09:00Z | 17 | 26 | < 25mph
|  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE258 | 5.3 | 2019-10-17T23:40:00Z | 43.62 | 36 | 40-55mph
|  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown | WMSC1 | 6.6 | 2019-02-06T05:53:00Z | 31 | 26 | 25-40mph
|  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force | LYQC1 | 1.86 | 2017-10-18T10:18:00Z | 5.99 | 5 | < 25mph
| RYE |  | 2017-12-05 | 2017 | 11:31 | 34.4528 | -118.5819 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | DLVC1 | 5.11 | 2015-09-14T01:55:00Z | 21 | 13 | < 25mph
|  | PICK | 2017-06-19 | 2017 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | 30278 Arrastre Canyon Rd., Acton | OH-699610E | Tier 3 | T3 | Y |  | 33 | Distribution | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown | SE063 | 7.19 | 2018-09-15T20:50:00Z | 32.32 | 26 | 25-40mph
|  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown | UCSH | 2.26 | 2018-06-02T05:30:00Z | 6.11 | 10 | < 25mph
|  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown | HMMC1 | 3.23 | 2016-10-01T19:14:00Z | 15.99 | 16 | < 25mph
10006 |  | CONCEPCION | 2016-05-12 | 2016 | 8:55 | 34.4736 | -120.216 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-708452E | OH-708452E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-12 | 8:55 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | C6499 | 0.67 | 2016-08-04T10:59:00Z | 0 | 12 | < 25mph
10005 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error | LPDC1 | 6.51 | 2017-04-07T12:55:00Z | 34.99 | 14 | 25-40mph
|  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | AT643 | 4.77 | 2015-12-14T15:48:00Z | 28.99 | 35 | 25-40mph
|  | PALOMINO | 2015-10-09 | 2015 | 14:00 | 33.5752 | -117.17 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | BEHIND ADDRESS 28151 CELIA RD / PROPERTY LINE., STR 212903S | OH-212903S | Tier 2 | T2 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | SRUC1 | 5.21 | 2018-06-25T17:54:00Z | 11.01 | 27 | < 25mph
|  | HUGHES LAKE/ED-08810 | 2018-07-06 | 2018 | 5:38 | 34.6744 | -118.4517 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | 465140E | OH-1938477E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-07-06 | 5:38 | Contact From Object |  | Vehicle | Pole | Unknown | PPPC1 | 4.96 | 2018-05-13T04:56:00Z | 31 | 5 | 25-40mph
|  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force | SDMEA | 5.11 | 2015-02-11T05:49:00Z | 12.01 | 16 | < 25mph
| STAR |  | 2019-07-28 | 2019 | 14:00 | 33.9975 | -117.7698 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Chino Valley Fire Department | [13 empty] | Contact From Object |  | Bird |  | Weather | TNRC1 | 4.58 | 2015-03-14T03:57:00Z | 8.01 | 32 | < 25mph
10002 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | CEEC1 | 3.51 | 2019-09-02T00:38:00Z | 15.99 | 119 | < 25mph
|  | PATRICIA | 2016-09-16 | 2016 | 19:02 | 34.4851 | -119.3001 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ojai City Fire Department | OH-4797071E | OH-4797071E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-09-16 | 19:02 | Contact From Object |  | Vehicle | Pole | Unknown | SE046 | 6.83 | 2018-11-02T12:30:00Z | 7.45 | 32 | < 25mph
|  | ELSTER | 2016-04-25 | 2016 | 19:15 | 36.1372 | -118.8615 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-X16345E | OH-X16345E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 120/240 V | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 19:15 | Equipment/Facility Failure | Conductor |  |  | Unknown | MOLC1 | 6.51 | 2019-02-16T00:27:00Z | 14.99 | 1 | < 25mph
|  | Conestoga | 2020-06-13 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Other | CNAC1 | 6.47 | 2015-04-25T02:11:00Z | 28.01 | 24 | 25-40mph
|  | Flying D | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County | OH-1761180E | OH-1761180E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown | BKGC1 | 4.48 | 2018-09-04T16:51:00Z | 8.99 | 2 | < 25mph
10002 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | CEEC1 | 3.51 | 2019-04-05T22:38:00Z | 24 | 84 | < 25mph
| HOLIDAY |  | 2018-07-06 | 2018 | 20:40 | 34.4639 | -119.8314 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Santa Barbara Fire Department | [17 empty] | Weather | MPWC1 | 2.75 | 2020-04-05T03:06:00Z | 24.99 | 166 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:30 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | None | E3131 | 6.3 | 2017-02-25T00:59:00Z | 14.99 | 37 | < 25mph
|  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE093 | 0.96 | 2018-12-29T06:10:00Z | 17.54 | 36 | < 25mph
|  | Conestoga | 2020-06-13 | 2020 | 17:26 | 33.782 | -117.47 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Riverside County Fire Department | OH-4709138E | OH-4709138E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-13 | 17:26 | Contact From Object |  | Balloons | Electric Facility | Other | E9117 | 7.33 | 2019-07-12T16:30:00Z | 8.99 | 52 | < 25mph
| HOLIDAY |  | 2018-07-06 | 2018 | 20:40 | 34.4639 | -119.8314 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Santa Barbara Fire Department | [17 empty] | Weather | AS303 | 6.76 | 2015-10-15T09:18:00Z | 12.01 | 81 | < 25mph
|  | Flying D | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County | OH-1761180E | OH-1761180E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown | SE303 | 6.35 | 2020-11-22T11:10:00Z | 10.23 | 38 | < 25mph
|  | PATRICIA | 2016-09-16 | 2016 | 19:02 | 34.4851 | -119.3001 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ojai City Fire Department | OH-4797071E | OH-4797071E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-09-16 | 19:02 | Contact From Object |  | Vehicle | Pole | Unknown | ROVC1 | 7.69 | 2017-05-06T11:24:00Z | 11.01 | 6 | < 25mph
|  | TUNA | 2016-09-19 | 2016 | 6:11 | 34.04 | -118.6687 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-1638513E | OH-1638513E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | MBCC1 | 3.63 | 2019-10-09T00:56:00Z | 24 | 142 | < 25mph
|  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other | PPPC1 | 1.78 | 2020-03-18T11:56:00Z | 14 | 25 | < 25mph
|  | Vicasa | 2020-10-26 | 2020 | 11:56 | 34.0998 | -118.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | OH-795990E | OH-795990E | T3 | T3 |  | Frontier Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Weather | MBCC1 | 6.44 | 2015-07-23T07:56:00Z | 14.99 | 35 | < 25mph
|  | CARVER | 2016-09-24 | 2016 | 14:20 | 35.7381 | -118.9546 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4784763E | OH-4784763E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-09-24 | 14:20 | Contact From Object |  | Animal | Electric Facility | Unknown | PG165 | 7.77 | 2019-10-13T17:40:00Z | 10.58 | 13 | < 25mph
|  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | WTHC1 | 5.52 | 2017-03-25T01:57:00Z | 17 | 115 | < 25mph
|  | BENCH | 2018-06-26 | 2018 | 20:48 | 34.0158 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Holmes St/Wildwood Canyon Rd, Yucaipa | OH-4367391E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-26 | 20:48 | Contact From Object |  | Vehicle | Pole | Unknown | MMKC1 | 4.65 | 2015-02-14T11:34:00Z | 12.01 | 33 | < 25mph
| THOMAS |  | 2017-12-04 | 2017 | 18:28 | 34.4152 | -119.0912 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | USFS | [17 empty] | Weather | AT184 | 6.91 | 2016-09-03T05:48:00Z | 18.01 | 78 | < 25mph
|  | PATRICIA | 2017-04-16 | 2017 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4495331E | OH-4495331E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown | ROVC1 | 7.28 | 2016-02-04T21:24:00Z | 15.99 | 11 | < 25mph
|  | GUITAR | 2017-05-11 | 2017 | 12:27 | 34.4127 | -118.6702 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-848255E | OH-848255E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-05-11 | 12:27 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE079 | 7.87 | 2020-03-02T00:20:00Z | 26.44 | 79 | 25-40mph
|  | CARVER | 2016-09-24 | 2016 | 14:20 | 35.7381 | -118.9546 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4784763E | OH-4784763E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-09-24 | 14:20 | Contact From Object |  | Animal | Electric Facility | Unknown | SE274 | 2.92 | 2020-08-08T11:30:00Z | 7.38 | 31 | < 25mph
|  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE232 | 1.2 | 2020-03-01T19:40:00Z | 26.22 | 34 | 25-40mph
| THOMAS |  | 2017-12-04 | 2017 | 18:28 | 34.4152 | -119.0912 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | USFS | [17 empty] | Weather | D7412 | 1.16 | 2018-03-03T22:40:00Z | 11.01 | 65 | < 25mph
|  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | E6371 | 4.86 | 2016-05-02T00:51:00Z | 17 | 47 | < 25mph
3 |  | Bidder | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire | OH-2023941E | OH-2023941E | T3 | T3 |  | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force | PG718 | 6.62 | 2020-10-13T01:20:00Z | 13.96 | 234 | < 25mph
|  | VIENTO | 2016-06-06 | 2016 | 17:44 | 35.1355 | -118.4771 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1373165E | OH-1373165E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-06 | 17:44 | Contact From Object |  | Other | Pole | Unknown | SE237 | 5.12 | 2020-01-08T09:40:00Z | 29.66 | 79 | 25-40mph
|  | CUDDEBACK | 2017-08-08 | 2017 | 17:52 | 35.1342 | -118.5607 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4179753E | OH-4179753E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-08-08 | 17:52 | Contact From Object |  | Vehicle | Electric Facility | Unknown | SE060 | 2.15 | 2019-01-07T14:50:00Z | 22.24 | 57 | < 25mph
|  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | MBCC1 | 6.95 | 2019-10-05T23:56:00Z | 22.01 | 158 | < 25mph
|  | DEACON | 2017-10-18 | 2017 | 13:34 | 33.7702 | -117.2157 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1564666E | OH-1564666E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | UCMO | 3.31 | 2017-09-18T08:30:00Z | 6.6 | 23 | < 25mph
|  | KINSEY | 2016-07-08 | 2016 | 11:15 | 34.7906 | -118.8256 | Vegetation | Rural | 300 - 999 Acres | 300 - 999 Acres |  | Fire Agency | Kern County Fire Department | 1-5, Gorman | OH-4539401E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown |  |  |  | 0 | 0 | No data
|  | KINSEY | 2016-07-08 | 2016 | 11:15 | 34.7906 | -118.8256 | Vegetation | Rural | 300 - 999 Acres | 300 - 999 Acres |  | Fire Agency | Kern County Fire Department | 1-5, Gorman | OH-4539401E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | KSDB | 6.6 | 2016-06-07T05:48:00Z | 27.63 | 6 | 25-40mph
|  | Zone | 2015-06-23 | 2015 | 17:21 | 34.279 | -118.9072 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura Fire Department | Primary splice box at base of pole 2115918e | OH-2115918E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Subsurface | No | <Null> |  | Equipment/Facility Failure | Other |  |  | Unknown | WLYC1 | 7.44 | 2016-02-22T20:49:00Z | 35.99 | 59 | 25-40mph
|  | PICK | 2017-06-19 | 2017 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | 30278 Arrastre Canyon Rd., Acton | OH-699610E | Tier 3 | T3 | Y |  | 33 | Distribution | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown | MLCC1 | 7.72 | 2015-04-12T23:53:00Z | 23 | 2 | < 25mph
| RYE |  | 2017-12-05 | 2017 | 15:00 | 34.2676 | -117.844 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | TANC1 | 6.35 | 2016-08-27T20:01:00Z | 12.01 | 1 | < 25mph
10006 |  | CONCEPCION | 2016-05-12 | 2016 | 8:55 | 34.4736 | -120.216 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-708452E | OH-708452E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-12 | 8:55 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UP481 | 0.62 | 2016-03-18T07:00:00Z | 14.97 | 13 | < 25mph
|  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown | SE178 | 1.42 | 2020-05-08T05:40:00Z | 21.12 | 91 | < 25mph
|  | Bonanza | 2020-06-05 | 2020 | 17:33 | 35.7635 | -118.4218 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Kern County Fire Department | OH-4451126E | OH-4451126E | T3 | T3 | Y | None | 12 | Distribution | Other | Overhead | Yes | 2020-06-05 | 17:33 | Contact From Object |  | Animal | Electric Facility | Other | KRNC1 | 1.16 | 2018-03-16T00:57:00Z | 28.01 | 6 | 25-40mph
|  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force | SDUNC | 4.84 | 2016-01-28T03:49:00Z | 8.99 | 16 | < 25mph
|  | Python | 2015-06-06 | 2015 | 10:00 | 34.4043 | -118.4234 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | 16450 Alamo Canyon Rd, Canyon Country | OH-4779534E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-06-06 | 10:13 | Contact From Object |  | Animal | Electric Facility | None | CNIC1 | 3.54 | 2019-04-08T18:55:00Z | 18.99 | 111 | < 25mph
|  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | NTBC1 | 7.63 | 2016-11-12T22:12:00Z | 13 | 15 | < 25mph
3 |  | Bidder | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire | OH-2023941E | OH-2023941E | T3 | T3 |  | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force | AT923 | 4.89 | 2015-04-08T12:16:00Z | 17.98 | 59 | < 25mph
10006 |  | Capanero | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | T2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE290 | 4.95 | 2020-02-01T03:30:00Z | 8.68 | 25 | < 25mph
|  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown | UCSH | 2.26 | 2016-04-17T21:00:00Z | 20.49 | 11 | < 25mph
|  | Lasker | 2020-07-26 | 2020 | 12:50 | 34.5326 | -118.0541 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4619162E | OH-4619162E | T3 | T3 |  | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | LPDC1 | 2.76 | 2018-01-04T15:55:00Z | 8.01 | 5 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | SE132 | 6.92 | 2020-05-28T08:40:00Z | 10.01 | 111 | < 25mph
|  | Calgrove | 2020-10-03 | 2020 | 17:45 | 34.357 | -118.5659 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | OH-2101062E | OH-2101062E | T3 | T3 |  | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | SE079 | 2.48 | 2018-09-29T17:10:00Z | 19.51 | 44 | < 25mph
|  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force | D0117 | 2.25 | 2019-03-31T02:49:00Z | 0 | 13 | < 25mph
|  | MAYBELL | 2017-07-02 | 2017 | 8:24 | 34.0804 | -117.8552 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | OH-144184E | OH-1255315E | T2 200Ft Outer Buffer | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-07-02 | 8:24 | Contact From Object |  | Animal | Electric Facility | Unknown | STFC1 | 6.14 | 2019-02-13T18:57:00Z | 7 | 86 | < 25mph
| ERSKINE |  | 2016-06-23 | 2016 | 16:00 | 34.2676 | -117.844 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | BLM | [13 empty] | Contact From Object |  | Vegetation |  |  | TANC1 | 6.35 | 2018-04-04T13:01:00Z | 4 | 1 | < 25mph
|  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | SE122 | 6.49 | 2019-11-01T21:10:00Z | 11.7 | 115 | < 25mph
|  | La Mancha | 2020-07-05 | 2020 | 3:57 | 34.1325 | -118.8532 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1848406E | OH-1848406E | T3 | T3 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-07-05 | 3:57 | Equipment/Facility Failure | Insulator |  |  | Unknown | D9395 | 6.72 | 2016-04-13T20:53:00Z | 17 | 49 | < 25mph
10005 |  | GOLDSMITH | 2016-11-20 | 2016 | 11:15 | 34.1883 | -118.8743 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1473501E | OH-1473501E | Tier 3 | T3 | Y | TIME WARNER CABLE/AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | D5145 | 7.89 | 2017-09-05T23:00:00Z | 22.01 | 47 | < 25mph
|  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | SE211 | 5.09 | 2020-11-03T18:30:00Z | 8.11 | 96 | < 25mph
|  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | NTBC1 | 7.63 | 2019-06-21T21:06:00Z | 14 | 59 | < 25mph
|  | Wildomar | 2019-09-19 | 2019 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside County FD | OH-2225310E | OH-2225310E | Tier 3 | T3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other | BUBSD | 7.99 | 2020-11-08T15:30:00Z | 24.33 | 142 | < 25mph
|  | Medusa | 2020-03-06 | 2020 | 17:05 | 34.0802 | -117.254 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1811355E | OH-1811355E | T2 | T2 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Other | AU239 | 7.19 | 2015-10-04T22:35:00Z | 12.01 | 17 | < 25mph
|  | CUDDEBACK | 2017-08-08 | 2017 | 17:52 | 35.1342 | -118.5607 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4179753E | OH-4179753E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-08-08 | 17:52 | Contact From Object |  | Vehicle | Electric Facility | Unknown | SE467 | 4.55 | 2019-11-14T14:50:00Z | 10.51 | 54 | < 25mph
|  | PICK | 2017-06-19 | 2017 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | 30278 Arrastre Canyon Rd., Acton | OH-699610E | Tier 3 | T3 | Y |  | 33 | Distribution | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown | ATNC1 | 0.34 | 2016-02-11T21:54:00Z | 18.99 | 2 | < 25mph
|  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | KNWC1 | 3.86 | 2018-09-04T16:17:00Z | 24 | 31 | < 25mph
|  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error | AU563 | 7.19 | 2018-05-15T18:18:00Z | 20 | 18 | < 25mph
|  | ELSTER | 2016-04-25 | 2016 | 19:15 | 36.1372 | -118.8615 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-X16345E | OH-X16345E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 120/240 V | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 19:15 | Equipment/Facility Failure | Conductor |  |  | Unknown | MOLC1 | 6.51 | 2018-12-31T19:27:00Z | 11.01 | 1 | < 25mph
|  | Lasker | 2020-07-26 | 2020 | 12:50 | 34.5326 | -118.0541 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4619162E | OH-4619162E | T3 | T3 |  | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | LPDC1 | 2.76 | 2020-07-08T05:55:00Z | 23 | 95 | < 25mph
|  | Hughes Lake | 2019-09-02 | 2019 | 14:02 | 34.7026 | -118.342 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4782978E | OH-4782978E | Tier 2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-02 | 14:02 | Contact From Object |  | Balloons | Electric Facility | Other | SE075 | 7.75 | 2018-12-21T17:30:00Z | 32.77 | 32 | 25-40mph
|  | Soda Springs | 2015-05-14 | 2015 | 22:24 | 36.1318 | -118.7784 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | Soda Springs 12kV out of Boxwood Sub | OH-4464511E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-14 | 22:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE479 | 2.59 | 2019-12-29T19:50:00Z | 6.71 | 22 | < 25mph
|  | Soda Springs | 2015-05-14 | 2015 | 22:24 | 36.1318 | -118.7784 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | Soda Springs 12kV out of Boxwood Sub | OH-4464511E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-14 | 22:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown | OORC1 | 5.23 | 2016-07-04T20:12:00Z | 12.01 | 1 | < 25mph
|  | Elster | 2019-09-21 | 2019 | 10:53 | 36.1026 | -118.8659 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4252581E | OH-4252581E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-21 | 10:53 | Contact From Object |  | Vehicle | Electric Facility | Human Error |  |  |  | 0 | 0 | No data
|  | Northpark | 2019-06-20 | 2019 | 14:08 | 34.2298 | -117.4048 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | San Bern. FD | OH-201371S | OH-201371S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Human Error | E7809 | 7.27 | 2018-02-24T14:33:00Z | 15.99 | 9 | < 25mph
| SADDLE RIDGE |  | 2019-10-10 | 2019 | 21:09 | 34.3299 | -118.4816 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | E3126 | 6.84 | 2015-01-20T22:00:00Z | 14.99 | 55 | < 25mph
|  | PYTHON | 2016-10-22 | 2016 | 15:17 | 34.3812 | -118.4132 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | RAR 0038 | OH-4860064E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-22 | 15:17 | Contact From Object |  | Balloons | Electric Facility | Unknown | CNIC1 | 1.96 | 2018-03-17T03:55:00Z | 28.99 | 32 | 25-40mph
|  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | F0145 | 4.82 | 2017-09-20T05:57:00Z | 11.01 | 27 | < 25mph
|  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE375 | 4.39 | 2019-08-17T20:10:00Z | 17.83 | 68 | < 25mph
|  | PALOMINO | 2015-10-09 | 2015 | 14:00 | 33.5752 | -117.17 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | BEHIND ADDRESS 28151 CELIA RD / PROPERTY LINE., STR 212903S | OH-212903S | Tier 2 | T2 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | SDMEA | 4.76 | 2020-02-06T03:49:00Z | 10 | 56 | < 25mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | SE130 | 4.93 | 2019-03-18T19:30:00Z | 15.77 | 25 | < 25mph
| MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | TPGC1 | 4.02 | 2015-01-16T15:57:00Z | 20 | 35 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TNRC1 | 2.34 | 2015-03-05T03:57:00Z | 10 | 37 | < 25mph
|  | Zone | 2019-08-10 | 2019 | 13:00 | 34.3089 | -118.9413 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | VFD | OH-4734128E | OH-4734128E | Tier 3 | T3 | Y | AT&T Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | AT184 | 5.07 | 2017-02-13T03:56:00Z | 21 | 43 | < 25mph
|  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | SE211 | 5.09 | 2020-08-12T14:10:00Z | 8.04 | 106 | < 25mph
|  | TICO | 2016-04-28 | 2016 | 14:00 | 34.357 | -119.314 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura County FD | OH-1604151E | OH-1604151E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-04-28 | 14:00 | Equipment/Facility Failure | Other |  |  | Unknown | AT185 | 1.35 | 2016-02-28T06:49:00Z | 7 | 20 | < 25mph
|  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error | SAUC1 | 7.39 | 2019-03-05T20:57:00Z | 24.99 | 55 | < 25mph
|  | Lasker | 2020-07-26 | 2020 | 12:50 | 34.5326 | -118.0541 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4619162E | OH-4619162E | T3 | T3 |  | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | LPDC1 | 2.76 | 2018-08-11T01:55:00Z | 49.01 | 13 | 40-55mph
|  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error | AU563 | 7.19 | 2019-04-26T10:40:00Z | 32.99 | 40 | 25-40mph
|  | METTLER | 2017-06-02 | 2017 | 10:50 | 35.1021 | -118.5328 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4416566E | OH-4416566E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | E3266 | 6.22 | 2015-12-15T14:27:00Z | 8.99 | 42 | < 25mph
|  | BIG CREEK 3-RECTOR NO.1/ET-01046 | 2015-09-03 | 2015 | 17:00 | 36.8936 | -119.4571 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | East of Watts Valley Rd and Pittman Hill Rd, East of Clovis | OH-7020930 | Tier 2 | T2 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2015-09-03 | 16:15 | Contact From Object |  | Balloons | Electric Facility | None | FCHC1 | 1.24 | 2017-03-20T12:00:00Z | 7 | 1 | < 25mph
|  | Saugus-Santa Susana | 2019-08-06 | 2019 | 15:03 | 34.3918 | -118.6596 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | VFD & LACFD | M6-T1 | M6-T1 | Tier 3 | T3 | Y | NA | 66 | Transmission | Other | Overhead | Yes | 2019-08-06 | 12:51 | Contact From Object |  | Animal | Electric Facility | Other | DLVC1 | 2.65 | 2017-03-28T09:55:00Z | 27 | 2 | 25-40mph
2 |  | Lopez | 2015-05-23 | 2015 | 11:57 | 34.3006 | -118.3613 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | Pole 1261671E | OH-1261671E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Conductor | Overhead | Yes | 2015-05-23 | 11:05 | Unknown |  |  |  | Unknown | CNIC1 | 4.89 | 2018-04-28T03:55:00Z | 20 | 47 | < 25mph
|  | VIENTO | 2016-06-06 | 2016 | 17:44 | 35.1355 | -118.4771 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1373165E | OH-1373165E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-06 | 17:44 | Contact From Object |  | Other | Pole | Unknown | KTSP | 2.14 | 2017-12-11T16:55:00Z | 19.57 | 33 | < 25mph
| EASY |  | 2019-10-30 | 2019 | 6:00 | 34.2822 | -118.8034 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | WLYC1 | 6.54 | 2017-08-19T17:49:00Z | 12.01 | 64 | < 25mph
| SADDLE RIDGE |  | 2019-10-10 | 2019 | 21:09 | 34.3299 | -118.4816 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | E3126 | 6.84 | 2015-08-28T08:59:00Z | 24 | 55 | < 25mph
|  | BIG CREEK 1-RECTOR/ET-01082 | 2018-08-04 | 2018 | 0:43 | 37.1895 | -119.2738 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | OH-7021454 | OH-7021454 | Tier 3 | T3 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2018-08-04 | 2:21 | Equipment/Facility Failure | Other |  |  | Unknown | SHVC1 | 3.7 | 2015-07-08T18:56:00Z | 10 | 1 | < 25mph
|  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | F0063 | 5.09 | 2019-04-15T14:33:00Z | 4.99 | 98 | < 25mph
|  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SE335 | 3.21 | 2020-08-16T22:40:00Z | 24.85 | 113 | < 25mph
| MEYERS |  | 2017-12-05 | 2017 | 14:00 | 34.2183 | -117.4062 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | E7809 | 6.47 | 2016-10-29T03:11:00Z | 5.99 | 7 | < 25mph
|  | BRUMFIELD | 2016-06-04 | 2016 | 10:17 | 33.5947 | -117.1387 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-2206630E | OH-2206630E | Tier 2 | T2 | Y |  | 12 | Distribution | Transformer | Overhead | Yes | 2016-06-04 | 10:17 | Equipment/Facility Failure | Transformer |  |  | Unknown | SDFRV | 2.92 | 2019-03-18T06:49:00Z | 5.99 | 30 | < 25mph
|  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force | SDMEA | 5.11 | 2018-10-10T19:49:00Z | 14 | 30 | < 25mph
|  | Bonanza | 2020-06-05 | 2020 | 17:33 | 35.7635 | -118.4218 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Kern County Fire Department | OH-4451126E | OH-4451126E | T3 | T3 | Y | None | 12 | Distribution | Other | Overhead | Yes | 2020-06-05 | 17:33 | Contact From Object |  | Animal | Electric Facility | Other | KRNC1 | 1.16 | 2015-04-30T07:57:00Z | 18.01 | 2 | < 25mph
|  | CARVER | 2016-09-24 | 2016 | 14:20 | 35.7381 | -118.9546 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4784763E | OH-4784763E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-09-24 | 14:20 | Contact From Object |  | Animal | Electric Facility | Unknown | WOCC1 | 7.2 | 2017-06-03T15:13:00Z | 4.99 | 1 | < 25mph
|  | Keller | 2015-06-09 | 2015 | 5:46 | 33.5986 | -117.1311 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 4401960E | OH-2297077E | Tier 2 | T2 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2015-06-09 | 5:46 | Contact From Object |  | Animal | Electric Facility | None | SDFRV | 2.48 | 2016-12-01T03:49:00Z | 8.01 | 24 | < 25mph
|  | PYTHON | 2016-06-05 | 2016 | 15:59 | 34.4208 | -118.4218 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4154960E | OH-4154960E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-06-05 | 15:59 | Unknown |  |  |  | Unknown | S183E | 6.94 | 2019-06-22T19:10:00Z | 30.24 | 113 | 25-40mph
|  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.54 | 2017-01-23T08:51:00Z | 48 | 99 | 40-55mph
|  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown | FTNC1 | 0.32 | 2018-05-20T06:00:00Z | 8.01 | 1 | < 25mph
|  | BENCH | 2018-06-26 | 2018 | 20:48 | 34.0158 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Holmes St/Wildwood Canyon Rd, Yucaipa | OH-4367391E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-26 | 20:48 | Contact From Object |  | Vehicle | Pole | Unknown | BNJC1 | 6.9 | 2020-04-20T14:13:00Z | 17 | 115 | < 25mph
|  | PYTHON | 2016-10-22 | 2016 | 15:17 | 34.3812 | -118.4132 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | RAR 0038 | OH-4860064E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-22 | 15:17 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE130 | 5.86 | 2020-11-30T14:40:00Z | 25.5 | 234 | 25-40mph
|  | HUGHES LAKE/ED-08810 | 2018-07-06 | 2018 | 5:38 | 34.6744 | -118.4517 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | 465140E | OH-1938477E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-07-06 | 5:38 | Contact From Object |  | Vehicle | Pole | Unknown | SE985 | 5.12 | 2020-10-20T10:00:00Z | 20.31 | 65 | < 25mph
|  | CARVER | 2016-09-24 | 2016 | 14:20 | 35.7381 | -118.9546 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4784763E | OH-4784763E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-09-24 | 14:20 | Contact From Object |  | Animal | Electric Facility | Unknown | WOCC1 | 7.2 | 2018-09-16T05:13:00Z | 7 | 1 | < 25mph
|  | BENCH | 2018-06-26 | 2018 | 20:48 | 34.0158 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Holmes St/Wildwood Canyon Rd, Yucaipa | OH-4367391E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-26 | 20:48 | Contact From Object |  | Vehicle | Pole | Unknown | MMKC1 | 4.65 | 2016-06-20T08:34:00Z | 11.01 | 50 | < 25mph
|  | DALBA | 2017-07-11 | 2017 | 18:06 | 34.2054 | -117.1143 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-919465E | OH-919465E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 2.4 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | HHPC1 | 2.47 | 2015-10-02T09:15:00Z | 11.01 | 47 | < 25mph
|  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error | SAUC1 | 7.39 | 2017-08-22T18:57:00Z | 8.99 | 11 | < 25mph
| SADDLE RIDGE |  | 2019-10-10 | 2019 | 21:09 | 34.3299 | -118.4816 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | E8724 | 4.33 | 2018-02-17T11:26:00Z | 15.99 | 66 | < 25mph
|  | OAK GLEN | 2017-03-15 | 2017 | 13:23 | 34.0534 | -116.971 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-2326555E | OH-2326555E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-15 | 13:23 | Contact From Object |  | Animal | Electric Facility | Unknown | BNJC1 | 6.47 | 2018-08-03T13:13:00Z | 15.99 | 56 | < 25mph
|  | KEENE | 2015-08-12 | 2015 | 12:00 | 35.1772 | -118.3373 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | Pole 2135290E | OH-2135290E | Tier 2 | T2 | Y |  | 120 V | Distribution | Conductor | Subsurface | Yes | 2015-08-12 | 11:07 | Other |  |  |  | Human Error | AU563 | 7.19 | 2020-12-06T03:45:00Z | 13 | 52 | < 25mph
|  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | D2363 | 4.16 | 2019-03-31T06:36:00Z | 25.99 | 99 | 25-40mph
|  | PATRICIA | 2017-04-16 | 2017 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4495331E | OH-4495331E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown | ROVC1 | 7.28 | 2016-08-28T20:24:00Z | 18.01 | 10 | < 25mph
|  | Kickapoo Trail | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1941931E | OH-1941931E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Unknown | UCCC1 | 6.87 | 2017-09-07T02:56:00Z | 10 | 7 | < 25mph
|  | BRUMFIELD | 2016-06-04 | 2016 | 10:17 | 33.5947 | -117.1387 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-2206630E | OH-2206630E | Tier 2 | T2 | Y |  | 12 | Distribution | Transformer | Overhead | Yes | 2016-06-04 | 10:17 | Equipment/Facility Failure | Transformer |  |  | Unknown | SRUC1 | 7.42 | 2020-10-12T07:54:00Z | 18 | 187 | < 25mph
|  | Saugus-Santa Susana | 2019-08-06 | 2019 | 15:03 | 34.3918 | -118.6596 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | VFD & LACFD | M6-T1 | M6-T1 | Tier 3 | T3 | Y | NA | 66 | Transmission | Other | Overhead | Yes | 2019-08-06 | 12:51 | Contact From Object |  | Animal | Electric Facility | Other | SE519 | 7.81 | 2020-06-18T12:50:00Z | 9.72 | 137 | < 25mph
|  | SODA SPRINGS | 2016-06-21 | 2016 | 21:47 | 36.2515 | -118.7809 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4391218E | OH-4391218E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-21 | 21:47 | Contact From Object |  | Vegetation | Electric Facility | Unknown | MOLC1 | 5.11 | 2017-03-27T11:27:00Z | 10 | 3 | < 25mph
|  | Keller | 2015-06-09 | 2015 | 5:46 | 33.5986 | -117.1311 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 4401960E | OH-2297077E | Tier 2 | T2 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2015-06-09 | 5:46 | Contact From Object |  | Animal | Electric Facility | None | SE078 | 7.61 | 2020-04-17T17:20:00Z | 14.16 | 48 | < 25mph
|  | ELSTER | 2016-04-25 | 2016 | 19:15 | 36.1372 | -118.8615 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-X16345E | OH-X16345E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 120/240 V | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 19:15 | Equipment/Facility Failure | Conductor |  |  | Unknown | MOLC1 | 6.51 | 2018-01-24T22:27:00Z | 8.01 | 1 | < 25mph
|  | PATRICIA | 2017-04-16 | 2017 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4495331E | OH-4495331E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE211 | 3.78 | 2019-10-22T05:20:00Z | 9.51 | 88 | < 25mph
| STAR |  | 2019-07-28 | 2019 | 14:00 | 33.9975 | -117.7698 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Chino Valley Fire Department | [13 empty] | Contact From Object |  | Bird |  | Weather | TNRC1 | 4.58 | 2015-12-06T16:57:00Z | 21 | 76 | < 25mph
|  | BIG CREEK 3-RECTOR NO.1/ET-01046 | 2015-09-03 | 2015 | 17:00 | 36.8936 | -119.4571 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | East of Watts Valley Rd and Pittman Hill Rd, East of Clovis | OH-7020930 | Tier 2 | T2 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2015-09-03 | 16:15 | Contact From Object |  | Balloons | Electric Facility | None | FCHC1 | 1.24 | 2016-12-22T01:00:00Z | 7 | 1 | < 25mph
|  | MAYBELL | 2017-07-02 | 2017 | 8:24 | 34.0804 | -117.8552 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | OH-144184E | OH-1255315E | T2 200Ft Outer Buffer | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-07-02 | 8:24 | Contact From Object |  | Animal | Electric Facility | Unknown | E9402 | 7.93 | 2018-06-21T22:35:00Z | 17 | 73 | < 25mph
10002 | WOOLSEY |  | 2018-11-08 | 2018 | 14:24 | 34.235 | -118.7013 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | CEEC1 | 3.51 | 2018-06-30T02:38:00Z | 13 | 73 | < 25mph
|  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown | FTNC1 | 0.32 | 2017-04-21T21:00:00Z | 14.99 | 1 | < 25mph
|  | Pawley | 2015-05-29 | 2015 | 7:29 | 36.387 | -118.9536 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare County Fire | Lemon Cove and Three Rivers Sub. Venida 66kV | OH-4434944E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-05-29 | 7:29 | Contact From Object |  | Animal | Electric Facility | None | D0117 | 5.17 | 2017-02-19T17:15:00Z | 3 | 9 | < 25mph
|  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | F0145 | 4.82 | 2017-03-20T22:17:00Z | 11.01 | 36 | < 25mph
|  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | SE192 | 6.78 | 2019-07-23T23:40:00Z | 25.21 | 66 | 25-40mph
| LIBERTY |  | 2017-12-07 | 2017 | 13:00 | 33.5926 | -117.1498 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | Murrieta Fire Department | [17 empty] | Weather | SE772 | 7.85 | 2020-12-15T23:10:00Z | 16.44 | 190 | < 25mph
|  | PICK | 2017-06-19 | 2017 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | 30278 Arrastre Canyon Rd., Acton | OH-699610E | Tier 3 | T3 | Y |  | 33 | Distribution | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown | SE015 | 5.04 | 2019-01-28T10:10:00Z | 19.06 | 27 | < 25mph
|  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown | HMMC1 | 3.23 | 2017-06-19T14:14:00Z | 8.01 | 15 | < 25mph
|  | Python | 2015-06-06 | 2015 | 10:00 | 34.4043 | -118.4234 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | 16450 Alamo Canyon Rd, Canyon Country | OH-4779534E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-06-06 | 10:13 | Contact From Object |  | Animal | Electric Facility | None | CNIC1 | 3.54 | 2017-05-05T20:55:00Z | 20 | 36 | < 25mph
|  | Wildomar | 2019-09-19 | 2019 | 15:16 | 33.5195 | -117.2961 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside County FD | OH-2225310E | OH-2225310E | Tier 3 | T3 | Y | None | 33 | Distribution | Conductor | Overhead | Yes | 2019-09-19 | 15:16 | Contact From Object |  | Balloons | Electric Facility | Other | SRUC1 | 3.86 | 2019-01-13T23:54:00Z | 11.01 | 23 | < 25mph
|  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force | LYQC1 | 1.86 | 2020-06-20T05:18:00Z | 31 | 58 | 25-40mph
|  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | AT643 | 4.77 | 2015-12-07T20:48:00Z | 18.01 | 36 | < 25mph
|  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UCMO | 4.71 | 2018-06-14T20:40:00Z | 18.9 | 29 | < 25mph
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | SE405 | 5.42 | 2020-01-29T00:20:00Z | 21.25 | 42 | < 25mph
|  | HUCKLEBERRY | 2017-03-17 | 2017 | 17:14 | 34.5759 | -118.2629 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4493863E | OH-4493863E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-17 | 17:14 | Contact From Object |  | Balloons | Electric Facility | Unknown | AU414 | 6.26 | 2017-11-04T04:46:00Z | 8.99 | 15 | < 25mph
10004 |  | HUGHES LAKE | 2016-10-26 | 2016 | 12:19 | 34.7081 | -118.5367 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | ELIZABETH LAKE ROAD AND KINGS CANYON ROAD, LAKE HUGHES | OH-1586523E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-26 | 12:19 | Contact From Object |  | Vegetation | Electric Facility | Unknown | C4614 | 6.71 | 2015-12-05T04:40:00Z | 28.99 | 11 | 25-40mph
|  | JORDAN | 2018-08-29 | 2018 | 17:32 | 35.7358 | -118.7192 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | Jack Ranch Rd/White River Rd, Kernville | OH-4635091E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-08-29 | 19:06 | Contact From Object |  | Vegetation | Electric Facility | Unknown | WOCC1 | 6.68 | 2018-02-22T05:13:00Z | 4.99 | 1 | < 25mph
|  | BENCH | 2018-06-26 | 2018 | 20:48 | 34.0158 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Holmes St/Wildwood Canyon Rd, Yucaipa | OH-4367391E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-26 | 20:48 | Contact From Object |  | Vehicle | Pole | Unknown | BNJC1 | 6.9 | 2020-05-20T03:13:00Z | 22.01 | 127 | < 25mph
|  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | LCBC1 | 6.83 | 2020-01-28T20:55:00Z | 21 | 159 | < 25mph
|  | PYTHON | 2016-10-22 | 2016 | 15:17 | 34.3812 | -118.4132 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | RAR 0038 | OH-4860064E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-22 | 15:17 | Contact From Object |  | Balloons | Electric Facility | Unknown | SAUC1 | 6.81 | 2016-07-20T00:57:00Z | 24 | 32 | < 25mph
|  | Flying D | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County | OH-1761180E | OH-1761180E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown | BKGC1 | 4.48 | 2016-04-08T04:51:00Z | 23 | 2 | < 25mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | ATNC1 | 4.83 | 2018-11-06T11:54:00Z | 11.01 | 19 | < 25mph
|  | CACHUMA | 2016-08-18 | 2016 | 14:52 | 34.5356 | -119.8523 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-1413051E | OH-1413051E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-18 | 14:52 | Contact From Object |  | Vegetation | Communication Facility | Unknown | SE068 | 4.85 | 2020-01-09T14:50:00Z | 21.92 | 119 | < 25mph
|  | Davenport | 2019-06-06 | 2019 | 9:00 | 34.4734 | -118.3921 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local (Valencia) Fire Department | OH-4419830E | OH-4419830E | Tier 3 | T3 | Y | NA | 16 | Distribution | Conductor | Overhead | Yes | 2019-06-06 | 9:10 | Equipment/Facility Failure | Conductor |  |  | Human Error | SAUC1 | 7.39 | 2016-12-20T12:57:00Z | 12.01 | 13 | < 25mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | E1966 | 3.22 | 2016-04-13T08:15:00Z | 17 | 12 | < 25mph
|  | Zone | 2015-04-27 | 2015 | 19:10 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 4734128E | OH-4734128E | Tier 3 | T3 | Y |  | 16 | Distribution | Other | Overhead | Yes | 2015-04-27 | 19:10 | Equipment/Facility Failure | Other |  |  | Unknown | TO | 7.93 | 2017-02-21T02:00:00Z | 6.93 | 36 | < 25mph
|  | ARCHIE | 2018-11-13 | 2018 | 7:11 | 33.4928 | -117.2796 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | NORTH OF CARANCHO ON VIA CIELO | OH-4149859E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-13 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Unknown | FBZC1 | 7.6 | 2019-10-19T07:22:00Z | 8.01 | 55 | < 25mph
|  | PATRICIA | 2016-10-23 | 2016 | 9:40 | 34.4603 | -119.2853 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | 900 Rice Road Ojai | OH-786960E | Tier 3 | T3 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | SE046 | 5.81 | 2018-09-27T13:40:00Z | 4.61 | 35 | < 25mph
|  | PATRICIA | 2017-04-16 | 2017 | 15:39 | 34.4556 | -119.2557 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4495331E | OH-4495331E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2017-04-16 | 15:39 | Contact From Object |  | Vegetation | Electric Facility | Unknown | ROVC1 | 7.28 | 2016-05-20T14:24:00Z | 8.99 | 13 | < 25mph
|  | Elster | 2019-09-21 | 2019 | 10:53 | 36.1026 | -118.8659 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4252581E | OH-4252581E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-21 | 10:53 | Contact From Object |  | Vehicle | Electric Facility | Human Error |  |  |  | 0 | 0 | No data
|  | GUITAR | 2016-01-16 | 2016 | 15:20 | 34.4096 | -118.6816 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-848266E | OH-848266E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-01-16 | 15:20 | Equipment/Facility Failure | Other |  |  | Unknown | SE437 | 3.94 | 2019-09-28T19:20:00Z | 21.34 | 87 | < 25mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | ATNC1 | 4.83 | 2019-07-27T07:54:00Z | 12.01 | 43 | < 25mph
| CABIN |  | 2015-08-14 | 2015 | 13:07 | 34.0299 | -118.0726 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | WTHC1 | 4.82 | 2018-12-30T00:57:00Z | 8.99 | 70 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TNRC1 | 2.34 | 2016-10-11T08:57:00Z | 11.01 | 1 | < 25mph
|  | PATRICIA | 2016-09-16 | 2016 | 19:02 | 34.4851 | -119.3001 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ojai City Fire Department | OH-4797071E | OH-4797071E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-09-16 | 19:02 | Contact From Object |  | Vehicle | Pole | Unknown | CSVC1 | 6.69 | 2017-01-17T14:09:00Z | 4.99 | 7 | < 25mph
|  | ELSTER | 2016-04-25 | 2016 | 19:15 | 36.1372 | -118.8615 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-X16345E | OH-X16345E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 120/240 V | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 19:15 | Equipment/Facility Failure | Conductor |  |  | Unknown | MOLC1 | 6.51 | 2018-03-04T21:27:00Z | 8.99 | 1 | < 25mph
|  | MESQUITE | 2018-06-15 | 2018 | 17:04 | 34.3702 | -117.3179 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 4769611E | OH-4769611E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-15 | 17:04 | Contact From Object |  | Vehicle | Pole | Unknown | E3047 | 1.29 | 2015-09-14T20:33:00Z | 25.99 | 16 | 25-40mph
10001 | VAN DYKE |  | 2015-02-06 | 2015 | 15:00 | 38.2256 | -119.2274 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | BPOC1 | 4.63 | 2017-08-17T07:49:00Z | 8.01 | 12 | < 25mph
|  | GAMBLER | 2017-06-14 | 2017 | 15:32 | 34.4118 | -117.5925 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Tulare Fire Department | OH-4155776E | OH-4155776E | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | E3130 | 6.26 | 2017-11-17T14:30:00Z | 24.99 | 42 | < 25mph
|  | Flying D | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County | OH-1761180E | OH-1761180E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown | BKGC1 | 4.48 | 2019-11-17T07:51:00Z | 13 | 32 | < 25mph
|  | PICK | 2017-06-19 | 2017 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | 30278 Arrastre Canyon Rd., Acton | OH-699610E | Tier 3 | T3 | Y |  | 33 | Distribution | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown | MLCC1 | 7.72 | 2017-05-25T11:53:00Z | 13 | 2 | < 25mph
|  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other | UCBU | 3.92 | 2015-06-09T13:30:00Z | 17.9 | 36 | < 25mph
|  | Lasker | 2020-07-26 | 2020 | 12:50 | 34.5326 | -118.0541 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4619162E | OH-4619162E | T3 | T3 |  | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | LPDC1 | 2.76 | 2018-04-18T00:55:00Z | 24.99 | 13 | < 25mph
|  | VIENTO | 2016-06-06 | 2016 | 17:44 | 35.1355 | -118.4771 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1373165E | OH-1373165E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-06 | 17:44 | Contact From Object |  | Other | Pole | Unknown | KTSP | 2.14 | 2015-08-12T17:15:00Z | 20.71 | 31 | < 25mph
| TENAJA |  | 2019-09-04 | 2019 | 16:43 | 33.5285 | -117.2732 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | SE772 | 4.46 | 2020-08-20T11:20:00Z | 9.42 | 106 | < 25mph
|  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.54 | 2015-02-15T18:51:00Z | 14 | 50 | < 25mph
4 |  | PYTHON | 2016-12-02 | 2016 | 21:26 | 34.3812 | -118.4132 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | OH-4572770E | OH-4572770E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vegetation | Electric Facility | Unknown | NHPC1 | 6.84 | 2016-05-29T10:56:00Z | 15.99 | 35 | < 25mph
|  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | WTHC1 | 5.52 | 2015-05-12T12:57:00Z | 24 | 58 | < 25mph
|  | Medusa | 2020-03-06 | 2020 | 17:05 | 34.0802 | -117.254 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1811355E | OH-1811355E | T2 | T2 | Y | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Insulator |  |  | Other | UP629 | 3.4 | 2017-01-16T17:05:00Z | 8.05 | 30 | < 25mph
10005 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error | LPDC1 | 6.51 | 2020-11-19T01:55:00Z | 29 | 173 | 25-40mph
|  | BIG CREEK 3-RECTOR NO.1/ET-01046 | 2015-09-03 | 2015 | 17:00 | 36.8936 | -119.4571 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | East of Watts Valley Rd and Pittman Hill Rd, East of Clovis | OH-7020930 | Tier 2 | T2 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2015-09-03 | 16:15 | Contact From Object |  | Balloons | Electric Facility | None | FCHC1 | 1.24 | 2015-12-07T07:00:00Z | 7 | 1 | < 25mph
|  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | LPDC1 | 5.12 | 2015-08-30T17:55:00Z | 32.99 | 4 | 25-40mph
|  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | OOSC1 | 2.03 | 2018-12-11T07:30:00Z | 13.8 | 52 | < 25mph
1 |  | Birchim | 2015-02-06 | 2015 | 13:15 | 37.454 | -118.5842 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Various Fire Agencies | Between Poles 1854107E & 1854106E | OH-1854107E | Tier 2 | T2 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-02-06 | 13:15 | Unknown |  |  |  | Unknown | OVRC1 | 4.68 | 2016-08-03T20:54:00Z | 14.99 | 1 | < 25mph
|  | GUITAR | 2017-05-11 | 2017 | 12:27 | 34.4127 | -118.6702 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-848255E | OH-848255E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-05-11 | 12:27 | Contact From Object |  | Balloons | Electric Facility | Unknown | E3126 | 6.99 | 2015-05-22T12:32:00Z | 11.99 | 7 | < 25mph
|  | Zone | 2019-08-10 | 2019 | 13:00 | 34.3089 | -118.9413 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | VFD | OH-4734128E | OH-4734128E | Tier 3 | T3 | Y | AT&T Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | WLYC1 | 7.19 | 2015-10-17T20:49:00Z | 18.01 | 49 | < 25mph
|  | SPRINGVILLE-LINDSAY-VENIDA/ET-07230,SPRINGVILLE-STRATHMORE/ET-07256 | 2015-06-17 | 2015 | 17:29 | 36.1086 | -118.9425 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 722603E | OH-722604E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-06-17 | 17:29 | Contact From Object |  | Animal | Electric Facility | None | E8094 | 7.51 | 2017-12-08T14:35:00Z | 0 | 12 | < 25mph
| STAR |  | 2019-07-28 | 2019 | 14:00 | 33.9975 | -117.7698 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Chino Valley Fire Department | [13 empty] | Contact From Object |  | Bird |  | Weather | C4803 | 3.37 | 2015-05-04T21:55:00Z | 20.98 | 52 | < 25mph
10007 |  | Vicasa | 2020-11-30 | 2020 | 21:02 | 34.0723 | -118.588 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles Fire Department | OH-4535641E | OH-4535641E | T3 | T3 |  | Verizon Wireless, AT&T Mobility, Frontier Communications, Crown Castle NG West, Inc | 16 | Distribution | Other | Overhead | Yes | 2020-11-30 | 21:02 | Contact From Object |  | Vehicle | Electric Facility | Outside Force | MBCC1 | 6.65 | 2020-07-01T05:56:00Z | 19 | 250 | < 25mph
|  | METTLER | 2017-06-02 | 2017 | 10:50 | 35.1021 | -118.5328 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4416566E | OH-4416566E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | E3266 | 6.22 | 2017-01-08T23:01:00Z | 34.99 | 39 | 25-40mph
|  | GUITAR | 2017-05-11 | 2017 | 12:27 | 34.4127 | -118.6702 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-848255E | OH-848255E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2017-05-11 | 12:27 | Contact From Object |  | Balloons | Electric Facility | Unknown | DLVC1 | 1.19 | 2017-03-05T21:55:00Z | 31 | 7 | 25-40mph
|  | PICK | 2017-06-19 | 2017 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | 30278 Arrastre Canyon Rd., Acton | OH-699610E | Tier 3 | T3 | Y |  | 33 | Distribution | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown | MLCC1 | 7.72 | 2018-03-20T04:53:00Z | 7 | 2 | < 25mph
|  | La Mancha | 2020-07-05 | 2020 | 3:57 | 34.1325 | -118.8532 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1848406E | OH-1848406E | T3 | T3 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-07-05 | 3:57 | Equipment/Facility Failure | Insulator |  |  | Unknown | LCBC1 | 7.67 | 2017-07-06T02:55:00Z | 17 | 46 | < 25mph
| MEYERS |  | 2017-12-05 | 2017 | 14:00 | 34.2183 | -117.4062 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | SE722 | 3.74 | 2020-07-21T19:30:00Z | 21.99 | 285 | < 25mph
|  | POPPET FLATS | 2016-02-27 | 2016 | 0:49 | 33.9134 | -116.8003 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1989045E | OH-1989045E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-02-27 | 0:49 | Contact From Object |  | Vehicle | Pole | Unknown | POPC1 | 5.22 | 2017-03-07T19:14:00Z | 28.99 | 13 | 25-40mph
|  | DEACON | 2017-10-18 | 2017 | 13:34 | 33.7702 | -117.2157 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | OH-1564666E | OH-1564666E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | UCMO | 3.31 | 2015-02-18T16:50:00Z | 4.61 | 9 | < 25mph
|  | CUDDEBACK | 2017-08-08 | 2017 | 17:52 | 35.1342 | -118.5607 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4179753E | OH-4179753E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-08-08 | 17:52 | Contact From Object |  | Vehicle | Electric Facility | Unknown | C8288 | 3.79 | 2019-08-29T11:20:00Z | 8.99 | 69 | < 25mph
4 |  | ANZAR | 2017-06-04 | 2017 | 13:14 | 33.8373 | -117.4863 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-1757417E | OH-1757417E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2017-06-04 | 13:14 | Wire-Wire Contact |  |  |  | Unknown | CNAC1 | 5.17 | 2019-02-07T11:11:00Z | 14.99 | 46 | < 25mph
|  | TUNA | 2016-09-19 | 2016 | 6:11 | 34.04 | -118.6687 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-1638513E | OH-1638513E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | D2363 | 3.41 | 2016-07-31T08:45:00Z | 20 | 37 | < 25mph
|  | Atento | 2015-05-30 | 2015 | 15:26 | 33.7097 | -117.6459 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Pole 2257269E | OH-2257269E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Other | Overhead | Yes | 2015-05-30 | 15:26 | Contact From Object |  | Animal | Electric Facility | Unknown | FRCC1 | 7.87 | 2016-07-17T20:51:00Z | 20 | 38 | < 25mph
10005 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error | LPDC1 | 6.51 | 2016-10-17T19:55:00Z | 28.99 | 12 | 25-40mph
|  | PATRICIA | 2016-10-23 | 2016 | 9:40 | 34.4603 | -119.2853 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | 900 Rice Road Ojai | OH-786960E | Tier 3 | T3 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | CSVC1 | 6.08 | 2017-08-21T23:09:00Z | 17 | 10 | < 25mph
|  | RHODA | 2016-12-30 | 2016 | 11:42 | 34.1231 | -118.723 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-1927507E | OH-1927507E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-12-30 | 11:42 | Contact From Object |  | Balloons | Electric Facility | Unknown | D2363 | 6.42 | 2016-11-07T06:01:00Z | 14.99 | 51 | < 25mph
|  | Penstock | 2019-09-18 | 2019 | 2:52 | 34.3143 | -117.3793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4066969E | OH-4066969E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Human Error | MNCC1 | 7.1 | 2016-07-22T09:16:00Z | 8.99 | 25 | < 25mph
|  | ARCHIE | 2018-11-13 | 2018 | 7:11 | 33.4928 | -117.2796 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | NORTH OF CARANCHO ON VIA CIELO | OH-4149859E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-13 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Unknown | SRUC1 | 3.4 | 2018-09-02T14:54:00Z | 4.99 | 32 | < 25mph
|  | Python | 2015-06-06 | 2015 | 10:00 | 34.4043 | -118.4234 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | 16450 Alamo Canyon Rd, Canyon Country | OH-4779534E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-06-06 | 10:13 | Contact From Object |  | Animal | Electric Facility | None | CNIC1 | 3.54 | 2019-09-02T05:55:00Z | 15.99 | 120 | < 25mph
4 |  | ANZAR | 2017-06-04 | 2017 | 13:14 | 33.8373 | -117.4863 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-1757417E | OH-1757417E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2017-06-04 | 13:14 | Wire-Wire Contact |  |  |  | Unknown | MHEC1 | 1.92 | 2018-06-09T23:16:00Z | 27 | 48 | 25-40mph
|  | DRISKILL | 2016-10-18 | 2016 | 18:41 | 34.4687 | -119.7722 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Santa Barbara Fire Department | OH-2178476E | OH-2178476E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-18 | 18:41 | Equipment/Facility Failure | Fuse |  |  | Unknown | SE068 | 2.89 | 2018-09-29T12:20:00Z | 16.55 | 155 | < 25mph
|  | Taggert | 2019-04-23 | 2019 | 21:06 | 34.2147 | -117.0973 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1027559E | OH-1027559E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution |  | Overhead | No |  |  | Unknown |  |  |  | Unknown | HHPC1 | 2.75 | 2017-03-01T15:15:00Z | 10 | 51 | < 25mph
|  | Flycatcher | 2020-07-25 | 2020 | 13:12 | 35.6345 | -118.3876 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1170270E | OH-1170270E | T3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Animal | Electric Facility | Outside Force | LYQC1 | 1.86 | 2016-12-25T17:18:00Z | 11.01 | 1 | < 25mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | ATNC1 | 4.83 | 2017-04-07T12:54:00Z | 5.99 | 1 | < 25mph
|  | POULTRY | 2018-09-21 | 2018 | 8:28 | 34.0728 | -117.0397 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Juniper St. Yucaipa | OH-129241E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SE095 | 6.98 | 2020-10-27T15:50:00Z | 24.77 | 209 | < 25mph
|  | SODA SPRINGS | 2016-06-21 | 2016 | 21:47 | 36.2515 | -118.7809 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4391218E | OH-4391218E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-21 | 21:47 | Contact From Object |  | Vegetation | Electric Facility | Unknown | AV342 | 7.69 | 2019-09-03T03:04:00Z | 14.99 | 30 | < 25mph
|  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | SE645 | 3.33 | 2020-04-14T08:40:00Z | 13.73 | 60 | < 25mph
|  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | WTHC1 | 5.52 | 2018-03-02T09:57:00Z | 8.01 | 70 | < 25mph
|  | Mettler | 2020-08-10 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | OH-2093506E | OH-2093506E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Unknown | E3266 | 6.59 | 2019-05-04T00:46:00Z | 20 | 56 | < 25mph
|  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown | SE332 | 7.21 | 2019-08-02T13:50:00Z | 9.73 | 7 | < 25mph
|  | Atlanta | 2015-05-05 | 2015 | 16:00 | 33.711 | -117.7089 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire | Pole 4229158E | OH-4229158E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.92 | 2016-01-28T21:51:00Z | 14.99 | 89 | < 25mph
|  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force | SE324 | 5.56 | 2020-03-17T17:40:00Z | 8.61 | 45 | < 25mph
|  | Enchanted | 2019-08-25 | 2019 | 8:03 | 34.301 | -118.8308 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4754475E | OH-4754475E | Tier 3 | T3 | Y | NA | 16 | Distribution | Lightning Arrestor | Overhead | Yes | 2019-08-25 | 8:03 | Contact From Object |  | Animal | Electric Facility | Other | SE146 | 7 | 2019-06-27T16:40:00Z | 12.28 | 129 | < 25mph
10006 |  | CONCEPCION | 2016-05-12 | 2016 | 8:55 | 34.4736 | -120.216 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-708452E | OH-708452E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-12 | 8:55 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UP481 | 0.62 | 2018-01-31T17:40:00Z | 4.94 | 15 | < 25mph
|  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown | SE508 | 3.58 | 2020-09-15T12:20:00Z | 7.96 | 31 | < 25mph
10006 |  | Capanero | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | T2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Unknown | UHLC1 | 1.17 | 2015-07-20T04:59:00Z | 3 | 13 | < 25mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | ATNC1 | 4.83 | 2018-07-05T09:54:00Z | 4.99 | 1 | < 25mph
|  | CUDDEBACK | 2017-08-08 | 2017 | 17:52 | 35.1342 | -118.5607 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4179753E | OH-4179753E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-08-08 | 17:52 | Contact From Object |  | Vehicle | Electric Facility | Unknown | C8288 | 3.79 | 2017-08-21T10:08:00Z | 5.99 | 25 | < 25mph
|  | Hughes Lake | 2019-09-02 | 2019 | 14:02 | 34.7026 | -118.342 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4782978E | OH-4782978E | Tier 2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-02 | 14:02 | Contact From Object |  | Balloons | Electric Facility | Other | E1966 | 7.08 | 2016-06-18T12:34:00Z | 11.01 | 42 | < 25mph
| RYE |  | 2017-12-05 | 2017 | 11:31 | 34.4528 | -118.5819 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | DLVC1 | 5.11 | 2015-01-17T13:55:00Z | 23 | 8 | < 25mph
|  | VIENTO | 2016-06-06 | 2016 | 17:44 | 35.1355 | -118.4771 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1373165E | OH-1373165E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-06 | 17:44 | Contact From Object |  | Other | Pole | Unknown | E3266 | 3.96 | 2016-09-24T01:23:00Z | 15.99 | 29 | < 25mph
| ERSKINE |  | 2016-06-23 | 2016 | 16:00 | 34.2676 | -117.844 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | BLM | [13 empty] | Contact From Object |  | Vegetation |  |  | TANC1 | 6.35 | 2016-08-12T14:01:00Z | 4.99 | 1 | < 25mph
| MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | D2363 | 5.89 | 2019-02-17T13:01:00Z | 27 | 108 | 25-40mph
|  | TUNA | 2016-09-19 | 2016 | 6:11 | 34.04 | -118.6687 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-1638513E | OH-1638513E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | MBCC1 | 3.63 | 2020-06-15T03:56:00Z | 16 | 194 | < 25mph
2 |  | Lopez | 2015-05-23 | 2015 | 11:57 | 34.3006 | -118.3613 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | Pole 1261671E | OH-1261671E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Conductor | Overhead | Yes | 2015-05-23 | 11:05 | Unknown |  |  |  | Unknown | LOMLS | 7.34 | 2015-02-03T22:45:00Z | 13 | 23 | < 25mph
|  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown | WTPC1 | 2.77 | 2017-08-24T11:57:00Z | 18.99 | 2 | < 25mph
|  | POULTRY | 2018-09-21 | 2018 | 8:28 | 34.0728 | -117.0397 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Juniper St. Yucaipa | OH-129241E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | C9072 | 6.74 | 2017-12-25T12:52:00Z | 7 | 58 | < 25mph
|  | MIST | 2016-08-24 | 2016 | 16:37 | 34.4665 | -120.0701 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Santa Barbara County Fire Department | Refiugio Canyon, Santa Barbara | OH-4538468E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-24 | 18:50 | Contact From Object |  | Animal | Electric Facility | Unknown | RHWC1 | 3.48 | 2015-11-12T06:06:00Z | 10 | 13 | < 25mph
|  | SODA SPRINGS | 2016-06-21 | 2016 | 21:47 | 36.2515 | -118.7809 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4391218E | OH-4391218E | Tier 2 | T2 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-21 | 21:47 | Contact From Object |  | Vegetation | Electric Facility | Unknown | AV342 | 7.69 | 2019-06-16T12:59:00Z | 17 | 34 | < 25mph
|  | VIENTO | 2016-06-06 | 2016 | 17:44 | 35.1355 | -118.4771 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-1373165E | OH-1373165E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-06 | 17:44 | Contact From Object |  | Other | Pole | Unknown | KTSP | 2.14 | 2015-09-16T04:55:00Z | 18.41 | 23 | < 25mph
|  | LEE VINING-LUNDY NO. 1/ET-01774 | 2017-05-01 | 2017 | 5:40 | 38.0209 | -119.1608 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | CAlFIre | OH-1580964E | OH-1580964E | Tier 2 | T2 | Y |  | 55 | Distribution | Conductor | Overhead | No | <Null> |  | Contamination |  |  |  | Unknown | C4643 | 1 | 2015-05-11T00:24:00Z | 21.99 | 11 | < 25mph
|  | HUGHES LAKE/ED-08810 | 2018-07-06 | 2018 | 5:38 | 34.6744 | -118.4517 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | 465140E | OH-1938477E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-07-06 | 5:38 | Contact From Object |  | Vehicle | Pole | Unknown | C5551 | 3.76 | 2018-12-23T22:21:00Z | 15.99 | 11 | < 25mph
|  | DALBA | 2017-07-11 | 2017 | 18:06 | 34.2054 | -117.1143 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-919465E | OH-919465E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 2.4 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | HHPC1 | 2.47 | 2018-08-24T20:15:00Z | 24.99 | 63 | < 25mph
|  | KINSEY | 2016-07-08 | 2016 | 11:15 | 34.7906 | -118.8256 | Vegetation | Rural | 300 - 999 Acres | 300 - 999 Acres |  | Fire Agency | Kern County Fire Department | 1-5, Gorman | OH-4539401E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | E5906 | 7.95 | 2017-03-04T06:30:00Z | 10 | 2 | < 25mph
|  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UCMO | 4.71 | 2015-07-16T11:00:00Z | 8.3 | 12 | < 25mph
|  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | ROVC1 | 7.44 | 2018-07-22T22:24:00Z | 17 | 21 | < 25mph
|  | Quinby | 2020-05-01 | 2020 | 21:25 | 34.5654 | -118.1165 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-4339082E | OH-4339082E | T2 | T2 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-05-01 | 21:25 | Contact From Object |  | Vehicle | Electric Facility | Other | LPDC1 | 2.12 | 2017-04-30T15:55:00Z | 11.01 | 6 | < 25mph
| THOMAS |  | 2017-12-04 | 2017 | 18:28 | 34.4152 | -119.0912 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | USFS | [17 empty] | Weather | AT184 | 6.91 | 2016-06-26T04:31:00Z | 7 | 66 | < 25mph
|  | CONCEPCION | 2016-05-02 | 2016 | 7:03 | 34.4736 | -120.2153 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-4041841E | OH-4041841E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-02 | 7:03 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UP481 | 0.66 | 2017-10-16T19:10:00Z | 8.05 | 16 | < 25mph
|  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown | SE161 | 4.34 | 2020-06-05T17:40:00Z | 18.12 | 69 | < 25mph
|  | HUCKLEBERRY | 2017-04-23 | 2017 | 16:24 | 34.5962 | -118.2427 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Palmdale Fire Department | OH-4336106E | OH-4336106E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2017-04-23 | 16:24 | Unknown |  |  |  | Unknown | E1966 | 3.22 | 2015-02-15T16:01:00Z | 1.01 | 18 | < 25mph
|  | OAK GLEN | 2018-11-08 | 2018 | 12:09 | 34.0397 | -116.9362 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 11833 Oak Glen Rd. Yucaipa | OH-4611601E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-08 | 12:09 | Equipment/Facility Failure | Transformer |  |  | Unknown | E5008 | 7.19 | 2018-10-17T11:00:00Z | 32.99 | 72 | 25-40mph
| HOLIDAY |  | 2018-07-06 | 2018 | 20:40 | 34.4639 | -119.8314 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Santa Barbara Fire Department | [17 empty] | Weather | SE052 | 5.26 | 2019-04-12T21:40:00Z | 28.05 | 149 | 25-40mph
|  | Sexton | 2015-02-22 | 2015 | 9:52 | 34.2849 | -119.2173 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Ventura Fire Department | Pole 1718768E | OH-1718768E | Tier 3 | T3 | Y | Phone & Cable | 16 | Distribution | Other | Overhead | Yes | 2015-02-22 | 10:49 | Unknown |  |  |  | None | AT185 | 8 | 2015-10-28T08:34:00Z | 8.01 | 23 | < 25mph
|  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | SE091 | 6.85 | 2020-11-09T22:10:00Z | 14.53 | 94 | < 25mph
|  | POPPET FLATS | 2016-02-27 | 2016 | 0:49 | 33.9134 | -116.8003 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1989045E | OH-1989045E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-02-27 | 0:49 | Contact From Object |  | Vehicle | Pole | Unknown | POPC1 | 5.22 | 2016-02-08T16:14:00Z | 48 | 14 | 40-55mph
|  | PYTHON | 2016-10-22 | 2016 | 15:17 | 34.3812 | -118.4132 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | RAR 0038 | OH-4860064E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-22 | 15:17 | Contact From Object |  | Balloons | Electric Facility | Unknown | SE177 | 3.76 | 2019-11-14T15:10:00Z | 14.38 | 119 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | SE962 | 7.16 | 2020-09-21T16:50:00Z | 9.42 | 187 | < 25mph
|  | METTLER | 2017-06-02 | 2017 | 10:50 | 35.1021 | -118.5328 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4416566E | OH-4416566E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Balloons | Electric Facility | Unknown | SE467 | 2.6 | 2020-11-15T22:30:00Z | 18.92 | 161 | < 25mph
|  | Twister | 2015-03-26 | 2015 | 14:09 | 33.946 | -117.9247 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire | Twister 12kV at La Habra Sub and Whipstock 12kV at Olinda Sub. | OH-1687951E | T2 200Ft Outer Buffer | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-03-26 | 14:09 | Contact From Object |  | Other | Electric Facility | Unknown | TNRC1 | 5.88 | 2016-12-15T12:57:00Z | 4.99 | 103 | < 25mph
| SADDLE RIDGE |  | 2019-10-10 | 2019 | 21:09 | 34.3299 | -118.4816 | Vegetation | Rural | Greater than 5000 Acres |  | Greater than 5000 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | NHPC1 | 2.27 | 2016-04-29T11:56:00Z | 20 | 57 | < 25mph
|  | La Mancha | 2020-07-05 | 2020 | 3:57 | 34.1325 | -118.8532 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Unknown |  | OH-1848406E | OH-1848406E | T3 | T3 | Y | None | 16 | Distribution | Other | Overhead | Yes | 2020-07-05 | 3:57 | Equipment/Facility Failure | Insulator |  |  | Unknown | OOSC1 | 4.63 | 2020-12-06T16:30:00Z | 14.8 | 162 | < 25mph
|  | Calgrove | 2020-10-03 | 2020 | 17:45 | 34.357 | -118.5659 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | OH-2101062E | OH-2101062E | T3 | T3 |  | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | SAUC1 | 6.17 | 2018-02-22T20:57:00Z | 25.99 | 45 | 25-40mph
|  | Enchanted | 2019-08-25 | 2019 | 8:03 | 34.301 | -118.8308 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4754475E | OH-4754475E | Tier 3 | T3 | Y | NA | 16 | Distribution | Lightning Arrestor | Overhead | Yes | 2019-08-25 | 8:03 | Contact From Object |  | Animal | Electric Facility | Other | WLYC1 | 4.92 | 2017-10-26T17:49:00Z | 11.01 | 48 | < 25mph
|  | THACHER | 2016-09-03 | 2016 | 10:24 | 34.4447 | -119.237 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | Bryant Circle, x Saddle Ln., Ojai | OH-3001811E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Animal | Electric Facility | Unknown | SE211 | 5.09 | 2019-09-16T06:10:00Z | 6.58 | 80 | < 25mph
|  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | D3590 | 2.93 | 2018-07-09T07:35:00Z | 3 | 36 | < 25mph
|  | Taggert | 2019-04-23 | 2019 | 21:06 | 34.2147 | -117.0973 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1027559E | OH-1027559E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution |  | Overhead | No |  |  | Unknown |  |  |  | Unknown | HHPC1 | 2.75 | 2017-12-08T05:15:00Z | 49.01 | 52 | 40-55mph
|  | PATRICIA | 2016-10-23 | 2016 | 9:40 | 34.4603 | -119.2853 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County FD | 900 Rice Road Ojai | OH-786960E | Tier 3 | T3 | Y |  | 120/240 V | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Conductor |  |  | Unknown | OJ | 3.19 | 2017-06-07T15:00:00Z | 3.58 | 6 | < 25mph
| MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | D2363 | 5.89 | 2016-06-07T07:32:00Z | 12.01 | 61 | < 25mph
|  | Helenka | 2019-06-23 | 2019 | 14:38 | 33.6416 | -117.242 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4561512E | OH-4561512E | Tier 2 | T2 | Y | NA | 12 | Distribution | Conductor | Overhead | Yes | 2019-06-23 | 14:38 | Contact From Object |  | Balloons | Electric Facility | Outside Force | D7608 | 3.75 | 2015-08-26T07:44:00Z | 3 | 12 | < 25mph
| CABIN |  | 2015-08-14 | 2015 | 13:07 | 34.0299 | -118.0726 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | USFS | [17 empty] | Weather | WTHC1 | 4.82 | 2016-08-16T00:57:00Z | 15.99 | 47 | < 25mph
3 |  | Bidder | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire | OH-2023941E | OH-2023941E | T3 | T3 |  | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force | MPWC1 | 5.77 | 2016-02-15T08:06:00Z | 38.99 | 97 | 25-40mph
|  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | SE234 | 6.46 | 2020-04-24T18:40:00Z | 26.08 | 132 | 25-40mph
|  | Viento | 2020-06-09 | 2020 | 16:42 | 35.1384 | -118.4809 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | OH-4707894E | OH-4707894E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | C1020 | 1.14 | 2018-03-19T23:35:00Z | 22.01 | 41 | < 25mph
4 |  | ANZAR | 2017-06-04 | 2017 | 13:14 | 33.8373 | -117.4863 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-1757417E | OH-1757417E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2017-06-04 | 13:14 | Wire-Wire Contact |  |  |  | Unknown | TSCC1 | 5.76 | 2019-04-17T15:41:00Z | 13 | 56 | < 25mph
|  | JORDAN | 2018-08-29 | 2018 | 17:32 | 35.7358 | -118.7192 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County Fire Department | Jack Ranch Rd/White River Rd, Kernville | OH-4635091E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-08-29 | 19:06 | Contact From Object |  | Vegetation | Electric Facility | Unknown | WOCC1 | 6.68 | 2017-05-14T17:13:00Z | 12.01 | 1 | < 25mph
10004 |  | HUGHES LAKE | 2016-10-26 | 2016 | 12:19 | 34.7081 | -118.5367 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | ELIZABETH LAKE ROAD AND KINGS CANYON ROAD, LAKE HUGHES | OH-1586523E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-26 | 12:19 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE451 | 7.35 | 2019-10-24T08:30:00Z | 16.96 | 21 | < 25mph
|  | Soda Springs | 2015-05-14 | 2015 | 22:24 | 36.1318 | -118.7784 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | Soda Springs 12kV out of Boxwood Sub | OH-4464511E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-14 | 22:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown | OORC1 | 5.23 | 2016-05-18T22:12:00Z | 15.99 | 1 | < 25mph
1 |  | Birchim | 2015-02-06 | 2015 | 13:15 | 37.454 | -118.5842 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Various Fire Agencies | Between Poles 1854107E & 1854106E | OH-1854107E | Tier 2 | T2 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-02-06 | 13:15 | Unknown |  |  |  | Unknown | SE390 | 6.9 | 2020-12-26T03:10:00Z | 12.28 | 29 | < 25mph
|  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.54 | 2017-11-13T02:51:00Z | 8.99 | 89 | < 25mph
|  | Sherwood | 2015-05-26 | 2015 | 14:47 | 34.1412 | -118.9079 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 658179E | OH-658179E | Tier 3 | T3 | Y |  | 4 | Distribution | Other | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | D5145 | 4.16 | 2020-12-06T02:45:00Z | 17 | 174 | < 25mph
10006 |  | CONCEPCION | 2016-05-12 | 2016 | 8:55 | 34.4736 | -120.216 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-708452E | OH-708452E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-12 | 8:55 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | GVTC1 | 1.52 | 2020-12-29T00:09:00Z | 17 | 7 | < 25mph
|  | OAK GLEN | 2017-03-15 | 2017 | 13:23 | 34.0534 | -116.971 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | CalFire | OH-2326555E | OH-2326555E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-03-15 | 13:23 | Contact From Object |  | Animal | Electric Facility | Unknown | MMKC1 | 4.7 | 2016-11-15T00:34:00Z | 10 | 53 | < 25mph
|  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other | UCBU | 3.92 | 2019-01-25T14:50:00Z | 12.8 | 33 | < 25mph
|  | Taggert | 2019-04-23 | 2019 | 21:06 | 34.2147 | -117.0973 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1027559E | OH-1027559E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution |  | Overhead | No |  |  | Unknown |  |  |  | Unknown | E8733 | 7.39 | 2017-04-10T01:42:00Z | 8.01 | 56 | < 25mph
|  | Elster | 2019-09-21 | 2019 | 10:53 | 36.1026 | -118.8659 | Other | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4252581E | OH-4252581E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | Yes | 2019-09-21 | 10:53 | Contact From Object |  | Vehicle | Electric Facility | Human Error |  |  |  | 0 | 0 | No data
|  | PALOMINO | 2015-10-09 | 2015 | 14:00 | 33.5752 | -117.17 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Riverside Fire Department | BEHIND ADDRESS 28151 CELIA RD / PROPERTY LINE., STR 212903S | OH-212903S | Tier 2 | T2 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | SDMEA | 4.76 | 2015-09-07T03:49:00Z | 12.01 | 26 | < 25mph
|  | SANTA CLARA-TAYSHELL/ET-00423 | 2016-04-21 | 2016 | 12:20 | 34.3339 | -119.2748 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Ventura County FD | OH-4434916E | OH-4434916E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2016-04-21 | 12:20 | Contact From Object |  | Animal | Electric Facility | Unknown | VTUC1 | 5.88 | 2018-02-13T14:30:00Z | 11.3 | 24 | < 25mph
10006 |  | Capanero | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | T2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE290 | 4.95 | 2020-12-02T19:10:00Z | 8.33 | 43 | < 25mph
|  | HUGHES LAKE/ED-08810 | 2018-07-06 | 2018 | 5:38 | 34.6744 | -118.4517 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Los Angeles County Fire Department | 465140E | OH-1938477E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-07-06 | 5:38 | Contact From Object |  | Vehicle | Pole | Unknown | PPPC1 | 4.96 | 2016-12-25T18:56:00Z | 14 | 6 | < 25mph
|  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | MBCC1 | 5.33 | 2019-08-16T09:56:00Z | 14.99 | 148 | < 25mph
|  | VALLEY-MAYBERRY-MORENO-VISTA | 2020-05-18 | 2020 | 12:10 | 33.8587 | -117.0203 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire Perris | OH-1979539E | OH-1979539E | T3 | T3 | Y | None | 115 | Transmission | Conductor | Overhead | No |  |  | Contact From Object |  | Other | Electric Facility | Other | HSGC1 | 4.08 | 2019-04-03T20:16:00Z | 14 | 32 | < 25mph
|  | Penstock | 2019-09-18 | 2019 | 2:52 | 34.3143 | -117.3793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4066969E | OH-4066969E | Tier 3 | T3 | Y | NA | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Transformer |  |  | Human Error | E3047 | 4.57 | 2016-10-24T17:14:00Z | 20 | 16 | < 25mph
|  | Plateau | 2019-09-11 | 2019 | 8:08 | 34.0991 | -118.6793 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-4424792E | OH-4424792E | Tier 3 | T3 | Y | Verizon / AT&T / Crown Castle | 16 | Distribution | Conductor | Overhead | Yes | 2019-09-11 | 8:08 | Equipment/Facility Failure | Conductor |  | Electric Facility | Human Error | SE204 | 2.08 | 2019-05-09T11:40:00Z | 7.67 | 113 | < 25mph
|  | LEE VINING-LUNDY NO. 1/ET-01774 | 2017-05-01 | 2017 | 5:40 | 38.0209 | -119.1608 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | CAlFIre | OH-1580964E | OH-1580964E | Tier 2 | T2 | Y |  | 55 | Distribution | Conductor | Overhead | No | <Null> |  | Contamination |  |  |  | Unknown | C4643 | 1 | 2017-12-08T10:30:00Z | 0 | 2 | < 25mph
4 |  | ANZAR | 2017-06-04 | 2017 | 13:14 | 33.8373 | -117.4863 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-1757417E | OH-1757417E | Tier 3 | T3 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2017-06-04 | 13:14 | Wire-Wire Contact |  |  |  | Unknown | MHEC1 | 1.92 | 2016-06-05T04:16:00Z | 13 | 46 | < 25mph
|  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other | PPPC1 | 1.78 | 2017-05-11T10:56:00Z | 27 | 5 | 25-40mph
|  | Keller | 2015-06-09 | 2015 | 5:46 | 33.5986 | -117.1311 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 4401960E | OH-2297077E | Tier 2 | T2 | Y |  | 33 | Distribution | Conductor | Overhead | Yes | 2015-06-09 | 5:46 | Contact From Object |  | Animal | Electric Facility | None | SRUC1 | 7.92 | 2016-08-29T13:54:00Z | 10 | 24 | < 25mph
4 |  | PYTHON | 2016-12-02 | 2016 | 21:26 | 34.3812 | -118.4132 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | OH-4572770E | OH-4572770E | Tier 3 | T3 | Y |  | 66 | Transmission | Conductor | Overhead | No | <Null> |  | Contact From Object |  | Vegetation | Electric Facility | Unknown | CNIC1 | 1.96 | 2015-11-03T12:55:00Z | 14 | 22 | < 25mph
|  | PICK | 2017-06-19 | 2017 | 19:10 | 34.4434 | -118.2016 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | 30278 Arrastre Canyon Rd., Acton | OH-699610E | Tier 3 | T3 | Y |  | 33 | Distribution | Transformer | Overhead | Yes | 2017-06-19 | 20:40 | Equipment/Facility Failure | Transformer |  |  | Unknown | ATNC1 | 0.34 | 2016-06-27T11:54:00Z | 8.01 | 2 | < 25mph
|  | Lasker | 2020-07-26 | 2020 | 12:50 | 34.5326 | -118.0541 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4619162E | OH-4619162E | T3 | T3 |  | None | 12 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Other |  |  | Other | LPDC1 | 2.76 | 2018-08-14T20:55:00Z | 38.99 | 11 | 25-40mph
|  | MIST | 2016-08-24 | 2016 | 16:37 | 34.4665 | -120.0701 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Santa Barbara County Fire Department | Refiugio Canyon, Santa Barbara | OH-4538468E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-24 | 18:50 | Contact From Object |  | Animal | Electric Facility | Unknown | RHWC1 | 3.48 | 2016-11-08T20:06:00Z | 10 | 13 | < 25mph
|  | Flying D | 2020-09-24 | 2020 | 10:35 | 35.489 | -118.5285 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Kern County | OH-1761180E | OH-1761180E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Unknown | SE232 | 7.46 | 2019-12-13T20:50:00Z | 30.69 | 28 | 25-40mph
|  | Zone | 2015-04-27 | 2015 | 19:10 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | Pole 4734128E | OH-4734128E | Tier 3 | T3 | Y |  | 16 | Distribution | Other | Overhead | Yes | 2015-04-27 | 19:10 | Equipment/Facility Failure | Other |  |  | Unknown | WLYC1 | 7.19 | 2016-04-15T11:49:00Z | 30 | 56 | 25-40mph
10006 |  | Capanero | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | T2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Unknown | E6928 | 0.22 | 2017-01-21T02:44:00Z | 0 | 8 | < 25mph
|  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown | WTPC1 | 2.77 | 2015-03-05T04:57:00Z | 28.99 | 4 | 25-40mph
| STAR |  | 2019-07-28 | 2019 | 14:00 | 33.9975 | -117.7698 | Vegetation | Rural | 100 - 299 Acres |  | 100 - 299 Acres | Fire Agency | Chino Valley Fire Department | [13 empty] | Contact From Object |  | Bird |  | Weather | SE218 | 7.69 | 2020-01-27T01:00:00Z | 18.19 | 123 | < 25mph
|  | TUNA | 2016-09-19 | 2016 | 6:11 | 34.04 | -118.6687 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-1638513E | OH-1638513E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | SE003 | 2.61 | 2019-10-10T10:30:00Z | 17.9 | 142 | < 25mph
|  | Enchanted | 2019-08-25 | 2019 | 8:03 | 34.301 | -118.8308 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Local FD | OH-4754475E | OH-4754475E | Tier 3 | T3 | Y | NA | 16 | Distribution | Lightning Arrestor | Overhead | Yes | 2019-08-25 | 8:03 | Contact From Object |  | Animal | Electric Facility | Other | SE227 | 6.74 | 2020-04-25T19:00:00Z | 17.67 | 208 | < 25mph
|  | Bonanza | 2020-06-05 | 2020 | 17:33 | 35.7635 | -118.4218 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Kern County Fire Department | OH-4451126E | OH-4451126E | T3 | T3 | Y | None | 12 | Distribution | Other | Overhead | Yes | 2020-06-05 | 17:33 | Contact From Object |  | Animal | Electric Facility | Other | WFHC1 | 5.2 | 2018-03-26T09:00:00Z | 14.99 | 6 | < 25mph
|  | PYTHON | 2016-06-05 | 2016 | 15:59 | 34.4208 | -118.4218 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | OH-4154960E | OH-4154960E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 16 | Distribution | Conductor | Overhead | Yes | 2016-06-05 | 15:59 | Unknown |  |  |  | Unknown | SE012 | 2.71 | 2018-06-21T19:20:00Z | 15.68 | 38 | < 25mph
10006 |  | Capanero | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | T2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE290 | 4.95 | 2020-12-13T06:30:00Z | 7.74 | 43 | < 25mph
|  | Maguire | 2015-04-17 | 2015 | 16:41 | 34.0851 | -118.8044 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Los Angeles County Fire | Maguire 16kV out of Latigo Sub | OH-1199311E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2015-04-17 | 16:41 | Contact From Object |  | Vehicle | Pole | None | D1664 | 3.65 | 2015-01-14T07:22:00Z | 8.99 | 24 | < 25mph
|  | Zone | 2015-04-27 | 2015 | 19:09 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | 9372 STOCKTON RD PMP MOORPARK | OH-4734128E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-04-27 | 19:09 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | WLYC1 | 7.19 | 2020-03-14T12:49:00Z | 13 | 156 | < 25mph
|  | CONCEPCION | 2016-05-02 | 2016 | 7:03 | 34.4736 | -120.2153 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-4041841E | OH-4041841E | Tier 2 | T2 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-05-02 | 7:03 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | UP481 | 0.66 | 2015-11-29T09:00:00Z | 11.97 | 1 | < 25mph
|  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | KNWC1 | 3.86 | 2019-03-23T06:17:00Z | 7 | 46 | < 25mph
3 |  | Bidder | 2020-11-09 | 2020 | 18:16 | 34.4632 | -119.8917 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Santa Barbara County Fire | OH-2023941E | OH-2023941E | T3 | T3 |  | None | 16 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 20:18 | Contact From Object |  | Animal | Electric Facility | Outside Force | F3082 | 4.6 | 2015-01-18T16:20:00Z | 8.99 | 41 | < 25mph
|  | Kickapoo Trail | 2020-05-26 | 2020 | 22:39 | 34.1034 | -116.4982 | Other | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | OH-2350470E | OH-2350470E | T3 | T3 | Y | None | 12 | Distribution | Conductor | Overhead | No |  |  | Vandalism/Theft |  |  |  | Other | C2900 | 7.95 | 2018-12-21T09:47:00Z | 10 | 31 | < 25mph
|  | Morongo | 2020-08-03 | 2020 | 10:33 | 34.0758 | -116.5548 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-2107480E | OH-2107480E | T2 | T2 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-08-03 | 19:15 | Contact From Object |  | Balloons | Electric Facility | Outside Force | UCBU | 7.55 | 2016-03-31T16:20:00Z | 29.51 | 6 | 25-40mph
|  | Pawley | 2019-06-06 | 2019 | 13:52 | 36.4168 | -118.9102 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1382763E | OH-1382763E | Tier 2 | T2 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vehicle | Electric Facility | Outside Force | TSHC1 | 6.99 | 2019-11-18T02:04:00Z | 7 | 44 | < 25mph
|  | Soda Springs | 2015-05-14 | 2015 | 22:24 | 36.1318 | -118.7784 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Customer |  | Soda Springs 12kV out of Boxwood Sub | OH-4464511E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-14 | 22:24 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE279 | 7.48 | 2019-08-28T16:40:00Z | 8.41 | 34 | < 25mph
10005 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error | LPDC1 | 6.51 | 2015-05-07T11:55:00Z | 38.01 | 16 | 25-40mph
|  | BENCH | 2018-06-26 | 2018 | 20:48 | 34.0158 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | Holmes St/Wildwood Canyon Rd, Yucaipa | OH-4367391E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-26 | 20:48 | Contact From Object |  | Vehicle | Pole | Unknown | MMKC1 | 4.65 | 2015-03-16T05:34:00Z | 11.01 | 38 | < 25mph
|  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | MBCC1 | 6.95 | 2020-08-19T20:56:00Z | 31 | 242 | 25-40mph
|  | WELCH | 2016-04-25 | 2016 | 15:23 | 35.8387 | -118.9147 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1078325E | OH-1078325E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 15:23 | Equipment/Facility Failure | Insulator |  |  | Unknown | SE274 | 6.67 | 2020-12-18T22:50:00Z | 7.74 | 7 | < 25mph
10004 |  | HUGHES LAKE | 2016-10-26 | 2016 | 12:19 | 34.7081 | -118.5367 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | ELIZABETH LAKE ROAD AND KINGS CANYON ROAD, LAKE HUGHES | OH-1586523E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-26 | 12:19 | Contact From Object |  | Vegetation | Electric Facility | Unknown | E5794 | 1.45 | 2018-01-22T21:33:00Z | 10 | 4 | < 25mph
|  | HORNTOAD | 2017-08-28 | 2017 | 17:26 | 34.135 | -118.6336 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-4649701E | OH-4649701E | Tier 3 | T3 | Y | NEXTG NETWORKS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | SE291 | 7.75 | 2020-10-24T17:40:00Z | 11.18 | 267 | < 25mph
| ELLIS |  | 2017-10-18 | 2017 | 11:18 | 33.7721 | -117.2173 | Vegetation | Rural | Unknown |  | Unknown | Fire Agency | Cal Fire | [17 empty] | Weather | UCMO | 3.15 | 2017-11-23T14:20:00Z | 7 | 30 | < 25mph
|  | ERSKINE | 2017-06-10 | 2017 | 12:17 | 35.5966 | -118.4917 | Vegetation | Rural | 100 - 299 Acres | 100 - 299 Acres |  | Fire Agency | CalFire | OH-2261368E | OH-2261368E | Tier 3 | T3 | Y |  | 120/240V | Distribution | Conductor | Overhead | Yes | 2017-06-10 | 12:17 | Equipment/Facility Failure | Conductor |  |  | Unknown | LYQC1 | 4.98 | 2017-09-15T11:18:00Z | 27 | 1 | 25-40mph
|  | WELCH | 2018-06-02 | 2018 | 10:41 | 35.8931 | -118.9207 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Calfire | Avenue 56 and Old Stage Road in Ducor. | OH-730690E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-02 | 11:12 | Contact From Object |  | Animal | Electric Facility | Unknown | FTNC1 | 0.32 | 2017-10-22T10:00:00Z | 4 | 1 | < 25mph
|  | Northpark | 2019-06-20 | 2019 | 14:08 | 34.2298 | -117.4048 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | San Bern. FD | OH-201371S | OH-201371S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Vegetation | Electric Facility | Human Error | F0494 | 5.7 | 2017-04-25T01:47:00Z | 18.01 | 14 | < 25mph
10006 |  | Capanero | 2020-07-05 | 2020 | 12:00 | 35.8708 | -118.6411 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-4541201E | OH-4541201E | T2 | T2 | Y | None | 2.4 | Distribution | Other | Overhead | Yes | 2020-07-05 | 12:00 | Contact From Object |  | Vegetation | Electric Facility | Unknown | UHLC1 | 1.17 | 2016-02-05T23:59:00Z | 4.99 | 13 | < 25mph
|  | Clarinet | 2019-09-12 | 2019 | 22:14 | 34.5758 | -118.6921 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA FD | OH-1937264E | OH-1937264E | Tier 3 | T3 | Y | None | 16 | Distribution | Conductor | Overhead | No |  |  | Contact From Object |  | Unknown | Electric Facility | Unknown | WTPC1 | 2.77 | 2015-06-14T05:57:00Z | 13 | 2 | < 25mph
| EASY |  | 2019-10-30 | 2019 | 6:00 | 34.2822 | -118.8034 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | WLYC1 | 6.54 | 2017-01-01T11:49:00Z | 11.01 | 54 | < 25mph
|  | OAK GLEN | 2018-11-08 | 2018 | 12:09 | 34.0397 | -116.9362 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Calfire | 11833 Oak Glen Rd. Yucaipa | OH-4611601E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-08 | 12:09 | Equipment/Facility Failure | Transformer |  |  | Unknown | BNTC1 | 7.59 | 2018-01-13T01:14:00Z | 15.99 | 62 | < 25mph
|  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown | E1966 | 2.94 | 2019-04-19T08:00:00Z | 11.01 | 32 | < 25mph
| MEYERS |  | 2017-12-05 | 2017 | 14:00 | 34.2183 | -117.4062 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Cal Fire | [17 empty] | Weather | E3127 | 5.41 | 2019-01-09T19:01:00Z | 15.99 | 37 | < 25mph
|  | Zone | 2015-04-27 | 2015 | 19:09 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | 9372 STOCKTON RD PMP MOORPARK | OH-4734128E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-04-27 | 19:09 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | WLYC1 | 7.19 | 2015-12-29T02:49:00Z | 28.01 | 61 | 25-40mph
|  | Corsair | 2015-04-17 | 2015 | 8:41 | 33.6397 | -116.901 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside County Fire | 33425 VALERIO RD hemet ca | OH-2231050E | Tier 3 | T3 | Y |  | 12 | Distribution | Other | Overhead | No | <Null> |  | Other |  |  |  | Unknown | SE074 | 3.24 | 2020-07-18T08:00:00Z | 7.31 | 87 | < 25mph
|  | SPRINGVILLE-LINDSAY-VENIDA/ET-07230,SPRINGVILLE-STRATHMORE/ET-07256 | 2015-06-17 | 2015 | 17:29 | 36.1086 | -118.9425 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | Pole 722603E | OH-722604E | Tier 2 | T2 | Y |  | 66 | Transmission | Conductor | Overhead | Yes | 2015-06-17 | 17:29 | Contact From Object |  | Animal | Electric Facility | None | E8094 | 7.51 | 2018-03-06T16:43:00Z | 8.99 | 12 | < 25mph
|  | DRISKILL | 2016-10-18 | 2016 | 18:41 | 34.4687 | -119.7722 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Santa Barbara Fire Department | OH-2178476E | OH-2178476E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-18 | 18:41 | Equipment/Facility Failure | Fuse |  |  | Unknown | MTIC1 | 7.03 | 2020-03-28T08:47:00Z | 28.99 | 259 | 25-40mph
|  | DRISKILL | 2016-10-18 | 2016 | 18:41 | 34.4687 | -119.7722 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Santa Barbara Fire Department | OH-2178476E | OH-2178476E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-18 | 18:41 | Equipment/Facility Failure | Fuse |  |  | Unknown | MPWC1 | 2.09 | 2018-04-19T11:06:00Z | 24.99 | 166 | < 25mph
|  | LIVERMORE | 2017-05-20 | 2017 | 17:28 | 33.7068 | -117.1388 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Riverside Fire Department | OH-4768465E | OH-4768465E | Tier 2 | No | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2017-05-20 | 17:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | F0145 | 4.82 | 2019-08-24T01:44:00Z | 17 | 56 | < 25mph
|  | Kickapoo Trail | 2020-11-09 | 2020 | 7:49 | 34.0865 | -116.52 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1941931E | OH-1941931E | T3 | T3 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-11-09 | 6:19 | Equipment/Facility Failure | Conductor |  |  | Unknown | UCCC1 | 6.87 | 2015-10-12T23:56:00Z | 14 | 10 | < 25mph
|  | PYTHON | 2016-10-22 | 2016 | 15:17 | 34.3812 | -118.4132 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LACFD | RAR 0038 | OH-4860064E | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | Yes | 2016-10-22 | 15:17 | Contact From Object |  | Balloons | Electric Facility | Unknown | NHPC1 | 6.84 | 2015-02-14T18:56:00Z | 11.01 | 14 | < 25mph
|  | ARCHIE | 2018-11-13 | 2018 | 7:11 | 33.4928 | -117.2796 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | NORTH OF CARANCHO ON VIA CIELO | OH-4149859E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-13 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Unknown | FBOC1 | 6.34 | 2020-02-15T07:00:00Z | 11.03 | 48 | < 25mph
|  | Zone | 2019-08-10 | 2019 | 13:00 | 34.3089 | -118.9413 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | VFD | OH-4734128E | OH-4734128E | Tier 3 | T3 | Y | AT&T Communications | 16 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | E6371 | 7.89 | 2015-11-21T00:48:00Z | 55.99 | 59 | 55mph+
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | C4643 | 3.99 | 2015-07-09T16:03:00Z | 22.01 | 9 | < 25mph
|  | Crowley | 2019-04-24 | 2019 | 16:40 | 37.6391 | -118.8588 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-424080S | OH-424080S | Tier 2 | T2 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Unknown | UCSH | 2.26 | 2015-01-10T01:20:00Z | 11.61 | 10 | < 25mph
|  | VICASA | 2018-06-29 | 2018 | 3:30 | 34.1358 | -118.5994 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | View Ridge Rd/Topanga Canyon Blvd, County of Los Angeles | OH-2045755E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-06-29 | 3:30 | Equipment/Facility Failure | Insulator |  |  | Unknown | SE003 | 5.32 | 2020-05-26T09:20:00Z | 10.3 | 226 | < 25mph
|  | ARCHIE | 2018-11-13 | 2018 | 7:11 | 33.4928 | -117.2796 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | NORTH OF CARANCHO ON VIA CIELO | OH-4149859E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2018-11-13 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Unknown | SDMEA | 5.44 | 2017-10-03T08:49:00Z | 5.99 | 29 | < 25mph
10004 |  | HUGHES LAKE | 2016-10-26 | 2016 | 12:19 | 34.7081 | -118.5367 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | ELIZABETH LAKE ROAD AND KINGS CANYON ROAD, LAKE HUGHES | OH-1586523E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-26 | 12:19 | Contact From Object |  | Vegetation | Electric Facility | Unknown | SE175 | 4.95 | 2020-10-08T10:20:00Z | 12.42 | 30 | < 25mph
|  | WHIP | 2016-10-02 | 2016 | 20:13 | 34.6314 | -118.2556 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | LACFD | OH-4776952E | OH-4776952E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-10-02 | 20:13 | Equipment/Facility Failure | Conductor |  |  | Unknown | E1966 | 2.94 | 2015-05-14T06:26:00Z | 22.97 | 14 | < 25mph
|  | CARVER | 2016-09-24 | 2016 | 14:20 | 35.7381 | -118.9546 | Vegetation | Rural | .26 - 9.99 Acres | .26 - 9.99 Acres |  | Fire Agency | Cal Fire | OH-4784763E | OH-4784763E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-09-24 | 14:20 | Contact From Object |  | Animal | Electric Facility | Unknown | PG165 | 7.77 | 2020-03-08T20:20:00Z | 15.21 | 7 | < 25mph
| MUREAU |  | 2019-10-30 | 2019 | 10:45 | 34.1509 | -118.6741 | Vegetation | Rural | 10 - 99 Acres |  | 10 - 99 Acres | Fire Agency | Los Angeles County Fire Department | [17 empty] | Weather | SE204 | 5.63 | 2020-10-11T20:20:00Z | 22.29 | 296 | < 25mph
|  | CACHUMA | 2016-08-18 | 2016 | 14:52 | 34.5356 | -119.8523 | Vegetation | Rural | Greater than 5000 Acres | Greater than 5000 Acres |  | Fire Agency | Santa Barbara County Fire Department | OH-1413051E | OH-1413051E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | Yes | 2016-08-18 | 14:52 | Contact From Object |  | Vegetation | Communication Facility | Unknown | MPWC1 | 4.41 | 2020-06-11T03:06:00Z | 22 | 185 | < 25mph
|  | Zone | 2015-04-27 | 2015 | 19:09 | 34.3089 | -118.9413 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Ventura County Fire | 9372 STOCKTON RD PMP MOORPARK | OH-4734128E | Tier 3 | T3 | Y | Phone & Cable | 12 | Distribution | Conductor | Overhead | Yes | 2015-04-27 | 19:09 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | WLYC1 | 7.19 | 2016-09-22T00:49:00Z | 25.99 | 50 | 25-40mph
|  | WELCH | 2016-04-25 | 2016 | 15:23 | 35.8387 | -118.9147 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Cal Fire | OH-1078325E | OH-1078325E | Tier 2 | T2 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2016-04-25 | 15:23 | Equipment/Facility Failure | Insulator |  |  | Unknown | FTNC1 | 3.62 | 2015-10-02T15:00:00Z | 5.99 | 1 | < 25mph
|  | Caliber | 2020-01-03 | 2020 | 7:11 | 34.4958 | -118.0276 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | LA County Fire Department | OH-549798E | OH-549798E | T3 | T3 | Y | AT&T Communication | 12 | Distribution | Conductor | Overhead | Yes | 2020-01-03 | 7:11 | Equipment/Facility Failure | Conductor |  |  | Other | LPDC1 | 5.12 | 2016-08-27T23:55:00Z | 35.99 | 7 | 25-40mph
|  | SHEFFIELD | 2017-10-27 | 2017 | 23:45 | 34.457 | -119.5648 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-1675192E | OH-1675192E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Unknown |  |  |  | Unknown | MTIC1 | 4.81 | 2017-05-14T11:47:00Z | 21 | 13 | < 25mph
| EASY |  | 2019-10-30 | 2019 | 6:00 | 34.2822 | -118.8034 | Vegetation | Rural | 1000 - 4999 Acres |  | 1000 - 4999 Acres | Fire Agency | Ventura County Fire Department | [17 empty] | Weather | WLYC1 | 6.54 | 2017-12-31T15:49:00Z | 14 | 55 | < 25mph
|  | Hughes Lake | 2020-06-14 | 2020 | 16:25 | 34.7098 | -118.4159 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4665728E | OH-4665728E | T2 | T2 | Y | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-06-14 | 19:23 | Equipment/Facility Failure | Conductor |  |  | Other | GMTC1 | 4.77 | 2016-02-20T11:59:00Z | 8.01 | 5 | < 25mph
|  | SHOWDOWN | 2016-06-09 | 2016 | 11:28 | 34.5862 | -118.196 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4267121E | OH-4267121E | Tier 3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | Yes | 2016-06-09 | 11:28 | Contact From Object |  | Balloons | Electric Facility | Unknown | LPDC1 | 6.32 | 2020-07-21T08:55:00Z | 20 | 167 | < 25mph
10005 |  | Pick | 2019-06-01 | 2019 | 11:30 | 34.5198 | -118.2148 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-692807E | OH-692807E | Tier 3 | T3 | Y | AT&T Communications | 12 | Distribution | Conductor | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Human Error | LPDC1 | 6.51 | 2015-07-14T11:55:00Z | 24.99 | 11 | < 25mph
10005 | MARINA |  | 2016-06-24 | 2016 | 5:30 | 37.98 | -119.1424 | Vegetation | Rural | 300 - 999 Acres |  | 300 - 999 Acres | Fire Agency | USFS | [17 empty] | Weather | UNDC1 | 4.3 | 2019-05-08T14:23:00Z | 22.01 | 16 | < 25mph
|  | BRAKEMAN | 2017-08-28 | 2017 | 4:10 | 33.957 | -117.8613 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Self Extinguished |  | OH-795917E | OH-788945H | Tier 3 | T3 | Y |  | 16 | Distribution | Conductor | Overhead | No | <Null> |  | Equipment/Facility Failure | Insulator |  |  | Unknown | TNRC1 | 2.34 | 2015-07-14T12:57:00Z | 8.99 | 100 | < 25mph
|  | Mettler | 2020-08-10 | 2020 | 14:35 | 35.1021 | -118.5394 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Utility |  | OH-2093506E | OH-2093506E | T3 | T3 | Y | AT&T CALIFORNIA | 12 | Distribution | Conductor | Overhead | No |  |  | Other |  |  |  | Unknown | E1410 | 5.9 | 2016-02-16T12:33:00Z | 32.01 | 42 | 25-40mph
10005 |  | Sand Canyon | 2020-04-22 | 2020 | 15:20 | 34.44 | -118.2811 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-1090802E | OH-1090802E | T3 | T3 | Y | AT&T Communication | 16 | Distribution | Other | Overhead | No |  |  | Equipment/Facility Failure | Conductor |  |  | Other | ATNC1 | 4.83 | 2020-05-31T14:54:00Z | 7 | 1 | < 25mph
|  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.54 | 2016-12-03T11:51:00Z | 62.01 | 76 | 55mph+
|  | SAUNDERS | 2017-01-13 | 2017 | 11:05 | 33.761 | -116.6948 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-220632S | OH-220632S | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-01-13 | 11:05 | Contact From Object |  | Vegetation | Electric Facility | Unknown | MSJC1 | 4.82 | 2020-01-15T09:53:00Z | 14 | 76 | < 25mph
|  | BIG CREEK 3-RECTOR NO.1/ET-01046 | 2015-09-03 | 2015 | 17:00 | 36.8936 | -119.4571 | Vegetation | Rural | 10 - 99 Acres | 10 - 99 Acres |  | Fire Agency | Cal Fire | East of Watts Valley Rd and Pittman Hill Rd, East of Clovis | OH-7020930 | Tier 2 | T2 | Y |  | 220 | Transmission | Conductor | Overhead | Yes | 2015-09-03 | 16:15 | Contact From Object |  | Balloons | Electric Facility | None | PG658 | 7.14 | 2020-05-01T08:30:00Z | 11.34 | 27 | < 25mph
|  | Atlanta | 2015-05-06 | 2015 | 14:03 | 33.7176 | -117.7254 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Fire Agency | Orange County Fire Authority | Beijing 12kV out of Las Lomas Sub. | OH-4618901E | Tier 3 | T3 | Y |  | 12 | Distribution | Conductor | Overhead | Yes | 2015-05-06 | 14:03 | Contact From Object |  | Vehicle | Electric Facility | None | FRCC1 | 6.54 | 2020-12-16T13:51:00Z | 13 | 170 | < 25mph
|  | SOPHIE | 2017-11-13 | 2017 | 13:49 | 33.7391 | -117.2778 | Vegetation | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-4059962E | OH-4059962E | Tier 3 | T3 | Y | FRONTIER COMMUNICATIONS | 12 | Distribution | Conductor | Overhead | Yes | 2017-11-13 | 13:49 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | SDPRR | 7.34 | 2017-06-20T11:49:00Z | 3 | 23 | < 25mph
|  | Morongo | 2020-08-03 | 2020 | 10:33 | 34.0758 | -116.5548 | Other | Rural | Less Than .25 Acres | Less Than .25 Acres |  | Unknown |  | OH-2107480E | OH-2107480E | T2 | T2 |  | None | 12 | Distribution | Conductor | Overhead | Yes | 2020-08-03 | 19:15 | Contact From Object |  | Balloons | Electric Facility | Outside Force | UCBU | 7.55 | 2016-09-02T13:20:00Z | 7.7 | 7 | < 25mph
Note on D1: Date the event started (Use MM/DD/YY when inputting dates)
Note on F1: The time the event started. This field is only an estimate as in many cases the utility might not know the exact start time. (Use military time when inputing time)
Note on G1: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on H1: Utilities should submit this data as close as it can get to the origin point of the event. Data should be at least given to the thousandths decimal place (i.e. X.00), more accuracy should be used when the utility has that knowledge.
Note on I1: Material involved in the initial fueling of the fire;
Note on J1: Nature of land use in the vicinity of the point of the fire’s origin (i.e., Urban, Rural). Rural and Urban are defined in GO 165.
Note on K1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on L1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on M1: An approximation of the fire's size give in acres. If only a structure was involved in the fire select structure only.
Note on N1: Is who suppressed the fire
Note on O1: If the fire was suppressed by a fire agency or agencies, insert the lead agency when one or more agency was involved
Note on P1: Utility’s description of the pole and/or equipment involved.
Note on U1: Other Companies that were attached to pole in question and known to the utility. If the facilities involved were not overhead leave this field blank. Note this field will be blacked out until "Overhead" is selected in the "Type" Column.
Note on V1: Nominal voltage rating of the utility equipment and/or circuit involved in the fire, use volts. If two or more voltages were involved list the higher voltage.
Note on X1: This field should list the equipment that supplied the heat that ignited the reported fire;
Note on Y1: The equipment involved in the event (overhead, padmounted or subsurface);
Note on Z1: Was there an outage involved in the event? Exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AA1: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AB1: For the purpose of this Data Collection Proposal, list the first outage associated with the event if multiple outages were involved. For the purpose of this Data Collection Proposal, exclude outages that were that were ordered by a governmental agency or were taken by the utility at its discretion.
Note on AC1: The suspected cause of the ignition;
Note on AD1: The specific equipment that malfunctioned that resulted in the “Equipment Involved” to cause the reported fire. (Only to be used if “Equipment/Facility Failure” is selected as Suspected Ignition Cause);
Note on AE1: The first object that contacted the Communication or Electric Facilities (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on AF1: The first facility that was contacted by an outside object (Only to be used if “Contact from Object” is selected as Ignition Cause);
Note on AG1: Factors that contributed to the ignition;

## IgnitionAnalysis
SCE Ignitions 2015-20
Wind Gust | Agent | Equipment | Investigation | Unknown | Vegetation | Total
< 25mph | 46 | 33 | 6 | 10 | 7 | 102
25-40mph | 11 | 11 | 6 | 2 | 1 | 31
40-55mph |  |  | 3 | 1 | 1 | 5
55mph+ |  | 2 | 5 | 1 |  | 8
Total | 57 | 46 | 20 | 14 | 9 | 146
Wind Gust | Random Sample | Fraction | Expected | Excess |  |  | Wind Gust | Expected | Observed
< 25mph | 1253 | 0.83533 | 121.9587 |  |  |  | < 25mph | 121.9587 | 102
25-40mph | 197 | 0.11276 | 16.4637 | 1.8829 | 25-40mph |  | >25 mph | 20.0549 | 44
40-55mph | 32 | 0.020645 | 3.0142 | 1.6588 | 40-55mph
55mph+ | 6 | 0.0039526 | 0.57708 | 13.863 | 55mph+ |  | P>25 chi-squared
No data | 12 | [5 empty] | 1.6603e-08
Grand Total | 1500

## IgnitionAnalysis_fix
SCE Ignitions 2015-20
Wind Gust | Agent | Equipment | Investigation | Unknown | Vegetation | Total
< 25mph | 46 | 33 | 6 | 10 | 7 | 102
25-40mph | 11 | 11 | 6 | 2 | 1 | 31
40-55mph |  |  | 3 | 1 | 1 | 5
55mph+ |  | 2 | 5 | 1 |  | 8
Total | 57 | 46 | 20 | 14 | 9 | 146
Wind Gust | Random Sample | Fraction | Expected | Excess |  |  | Wind Gust | Expected | Observed
< 25mph | 1253 | 0.83533 | 121.9587 |  |  |  | < 25mph | 121.9587 | 102
25-40mph | 197 | 0.13133 | 19.1747 | 1.6167 | 25-40mph |  | >25 mph | 22.8733 | 44
40-55mph | 32 | 0.021333 | 3.1147 | 1.6053 | 40-55mph
55mph+ | 6 | 0.004 | 0.584 | 13.6986 | 55mph+ |  | P>25 chi-squared
No data | 12 | [5 empty] | 1.8168e-06
Grand Total | 1500