## SDGE_Ignitions_2015_2020
OBJECTID | Company | Ignition ID | Month | Day | Year | Quarter | Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Voltage (Volts) | Type | Was There an Outage | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | Tier | District
1 | SDG&E | 20150211IG01 | February | 11 | 2015 | 1 | 2015-02-11 | 15:30 | 32.8941 | -116.9393 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | EA
2 | SDG&E | 20150319IG01 | March | 19 | 2015 | 1 | 2015-03-19 | 23:50 | 33.0565 | -117.0332 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 2 | NE
3 | SDG&E | 20150409IG01 | April | 9 | 2015 | 2 | 2015-04-09 | 17:23 | 32.7233 | -116.8922 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Unknown |  |  |  |  | Tier 3 | EA
4 | SDG&E | 20150412IG01 | April | 12 | 2015 | 2 | 2015-04-12 | 12:31 | 33.0117 | -116.866 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility |  | Tier 2 | RA
5 | SDG&E | 20150412IG02 | April | 12 | 2015 | 2 | 2015-04-12 | 14:30 | 33.2754 | -117.3306 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vehicle | Pole |  | Tier 2 | NC
6 | SDG&E | 20150413IG01 | April | 13 | 2015 | 2 | 2015-04-13 | 10:50 | 32.5859 | -117.0017 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Tier 2 | CM
7 | SDG&E | 20150418IG01 | April | 18 | 2015 | 2 | 2015-04-18 | 12:00 | 32.7764 | -116.9309 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Secondary | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | None | Non- HFTD | EA
8 | SDG&E | 20150428IG01 | April | 28 | 2015 | 2 | 2015-04-28 | 13:30 | 32.8917 | -116.8419 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Tier 3 | EA
9 | SDG&E | 20150429IG01 | April | 29 | 2015 | 2 | 2015-04-29 | 12:00 | 32.6061 | -116.696 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Unknown | Tier 3 | ME
10 | SDG&E | 20150517IG01 | May | 17 | 2015 | 2 | 2015-05-17 | 6:55 | 33.1808 | -117.2064 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility |  | Non- HFTD | NC
11 | SDG&E | 20150528IG01 | May | 28 | 2015 | 2 | 2015-05-28 | 12:45 | 32.7265 | -116.9922 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | EA
12 | SDG&E | 20150707IG01 | July | 7 | 2015 | 3 | 2015-07-07 | 15:00 | 32.7443 | -117.0498 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Non- HFTD | EA
13 | SDG&E | 20150717IG01 | July | 17 | 2015 | 3 | 2015-07-17 | 9:48 | 33.3012 | -117.0222 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Communication Facility | Human Error | Tier 3 | NE
14 | SDG&E | 20150727IG01 | July | 27 | 2015 | 3 | 2015-07-27 | 14:30 | 33.0665 | -116.579 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | None | Tier 3 | RA
15 | SDG&E | 20150808IG01 | August | 8 | 2015 | 3 | 2015-08-08 | 10:00 | 33.1973 | -117.2308 | Vegetation | Urban | Less Than .25 Acres | Customer | 4kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | NC
16 | SDG&E | 20150813IG01 | August | 13 | 2015 | 3 | 2015-08-13 | 20:33 | 33.2457 | -116.6769 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Unknown |  |  |  | Unknown | Tier 2 | RA
17 | SDG&E | 20150815IG01 | August | 15 | 2015 | 3 | 2015-08-15 | 17:30 | 32.7417 | -116.9685 | Other | Urban | Less Than .25 Acres | Customer | 4Kv | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Non- HFTD | EA
18 | SDG&E | 20150823IG01 | August | 23 | 2015 | 3 | 2015-08-23 | 15:00 | 33.2729 | -117.1521 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | NE
19 | SDG&E | 20150901IG01 | September | 1 | 2015 | 3 | 2015-09-01 | 18:01 | 32.7595 | -117.0671 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished | 4kV | Overhead | No | Contact From Object |  | Vehicle | Electric Facility | Human Error | Non- HFTD | CM
20 | SDG&E | 20150901IG02 | September | 1 | 2015 | 3 | 2015-09-01 | 8:50 | 32.669 | -116.286 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | None | Tier 2 | ME
21 | SDG&E | 20150902IG01 | September | 2 | 2015 | 3 | 2015-09-02 | 18:18 | 33.1867 | -117.202 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Non- HFTD | NC
22 | SDG&E | 20150908IG01 | September | 8 | 2015 | 3 | 2015-09-08 | 11:45 | 33.0726 | -116.7436 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | None | Tier 3 | RA
23 | SDG&E | 20150909IG01 | September | 9 | 2015 | 3 | 2015-09-09 | 20:40 | 32.644 | -117.072 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Non- HFTD | CM
24 | SDG&E | 20150917IG01 | September | 17 | 2015 | 3 | 2015-09-17 | 8:09 | 32.6791 | -117.1044 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Transformer |  |  | None | Non- HFTD | CM
25 | SDG&E | 20151002IG01 | October | 2 | 2015 | 4 | 2015-10-02 | 14:30 | 33.1354 | -117.0588 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | NE
26 | SDG&E | 20151009IG01 | October | 9 | 2015 | 4 | 2015-10-09 | 16:00 | 32.7705 | -117.1095 | Other | Urban | Less Than .25 Acres | Fire Agency | Secondary | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | CM
27 | SDG&E | 20151226IG01 | December | 26 | 2015 | 4 | 2015-12-26 | 3:04 | 33.1323 | -117.0695 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | NE
28 | SDG&E | 20160103IG01 | January | 3 | 2016 | 1 | 2016-01-03 | 4:30 | 33.1915 | -117.3655 | Other | Urban | Less Than .25 Acres | Fire Agency | 12kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | Other | Non- HFTD | NC
29 | SDG&E | 20160109IG01 | January | 9 | 2016 | 1 | 2016-01-09 | 4:30 | 33.082 | -117.091 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Non- HFTD | NE
30 | SDG&E | 20160116IG01 | January | 16 | 2016 | 1 | 2016-01-16 | 14:42 | 32.7188 | -116.9745 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | EA
31 | SDG&E | 20160131IG01 | January | 31 | 2016 | 1 | 2016-01-31 | 15:00 | 33.3217 | -117.156 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Weather | Tier 2 | NE
32 | SDG&E | 20160205IG01 | February | 5 | 2016 | 1 | 2016-02-05 | 9:47 | 33.0739 | -117.0862 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | NE
33 | SDG&E | 20160212IG01 | February | 12 | 2016 | 1 | 2016-02-12 | 19:30 | 33.2427 | -116.9664 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Vandalism/Theft |  |  |  | Outside Force | Tier 3 | NE
34 | SDG&E | 20160218IG01 | February | 18 | 2016 | 1 | 2016-02-18 | 0:00 | 32.7063 | -116.397 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | None | Tier 3 | ME
35 | SDG&E | 20160303IG01 | March | 3 | 2016 | 1 | 2016-03-03 | 6:00 | 32.8472 | -116.942 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Non- HFTD | EA
36 | SDG&E | 20160311IG01 | March | 11 | 2016 | 1 | 2016-03-11 | 11:40 | 33.1563 | -117.2152 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Non- HFTD | NC
37 | SDG&E | 20160406IG01 | April | 6 | 2016 | 2 | 2016-04-06 | 10:38 | 33.1865 | -117.1967 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Conductor | Vegetation | Electric Facility | Human Error | Non- HFTD | NC
40 | SDG&E | 20160614IG01 | June | 14 | 2016 | 2 | 2016-06-14 | 6:05 | 32.8801 | -116.9051 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Outside Force | Tier 2 | EA
41 | SDG&E | 20160623IG01 | June | 23 | 2016 | 2 | 2016-06-23 | 15:00 | 32.8058 | -116.961 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | Outside Force | Non- HFTD | EA
42 | SDG&E | 20160627IG01 | June | 27 | 2016 | 2 | 2016-06-27 | 15:30 | 33.2837 | -116.6174 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Human Error | Tier 2 | RA
43 | SDG&E | 20160702IG01 | July | 2 | 2016 | 3 | 2016-07-02 | 7:51 | 32.81 | -116.878 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Capacitor Bank |  |  | None | Tier 2 | EA
44 | SDG&E | 20160711IG01 | July | 11 | 2016 | 3 | 2016-07-11 | 10:27 | 33.4531 | -117.3044 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility |  | Tier 2 | NE
45 | SDG&E | 20160711IG02 | July | 11 | 2016 | 3 | 2016-07-11 | 13:19 | 33.1146 | -116.5843 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  |  | Tier 3 | RA
47 | SDG&E | 20160729IG01 | July | 29 | 2016 | 3 | 2016-07-29 | 10:57 | 33.071 | -116.7424 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  |  | Tier 3 | RA
48 | SDG&E | 20160731IG01 | July | 31 | 2016 | 3 | 2016-07-31 | 13:43 | 33.3663 | -117.2033 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Unknown | Tier 2 | NE
49 | SDG&E | 20160827IG01 | August | 27 | 2016 | 3 | 2016-08-27 | 12:43 | 33.1371 | -117.0761 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Unknown | Non- HFTD | NE
50 | SDG&E | 20160923IG01 | September | 23 | 2016 | 3 | 2016-09-23 | 11:25 | 32.7372 | -116.7343 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Transformer |  |  | None | Tier 3 | EA
51 | SDG&E | 20160927IG01 | September | 27 | 2016 | 3 | 2016-09-27 | 10:18 | 33.2967 | -117.2079 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Animal |  | Unknown | Tier 2 | NE
52 | SDG&E | 20160929IG01 | September | 29 | 2016 | 3 | 2016-09-28 | 14:29 | 32.7418 | -116.9653 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Outside Force | Non- HFTD | EA
53 | SDG&E | 20161021IG01 | October | 21 | 2016 | 4 | 2016-10-21 | 11:20 | 33.0485 | -116.8615 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Transformer |  |  |  | Tier 2 | RA
54 | SDG&E | 20161102IG01 | November | 2 | 2016 | 4 | 2016-11-02 | 10:30 | 32.8373 | -116.7022 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Tier 3 | ME
55 | SDG&E | 20161112IG01 | November | 12 | 2016 | 4 | 2016-11-12 | 20:30 | 32.6227 | -116.9388 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  |  | Tier 2 | CM
56 | SDG&E | 20170120IG01 | January | 20 | 2017 | 1 | 2017-01-20 | 14:00 | 32.6274 | -117.0767 | Building | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Conductor | Vegetation | Pole | Weather | Non- HFTD | CM
57 | SDG&E | 20170608IG01 | June | 8 | 2017 | 2 | 2017-06-08 | 4:12 | 33.0356 | -117.1839 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Tier 2 | NC
58 | SDG&E | 20170612IG01 | June | 12 | 2017 | 2 | 2017-06-12 | 11:20 | 32.843 | -116.7111 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Other | Electric Facility | Weather | Tier 3 | ME
59 | SDG&E | 20170619IG01 | June | 19 | 2017 | 2 | 2017-06-19 | 9:52 | 32.7829 | -117.0488 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility |  | Non- HFTD | EA
60 | SDG&E | 20170626IG01 | June | 26 | 2017 | 2 | 2017-06-26 | 14:30 | 32.7842 | -117.1391 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | BC
61 | SDG&E | 20170629IG01 | June | 29 | 2017 | 2 | 2017-06-29 | 13:07 | 33.1355 | -117.098 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility |  | Non- HFTD | NE
62 | SDG&E | 20170629IG02 | June | 29 | 2017 | 2 | 2017-06-29 | 14:58 | 32.6926 | -116.8564 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Electric Facility | None | Tier 3 | EA
63 | SDG&E | 20170716IG01 | July | 16 | 2017 | 3 | 2017-07-16 | 11:53 | 32.829 | -117.136 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | BC
64 | SDG&E | 20170725IG01 | July | 25 | 2017 | 3 | 2017-07-25 | 15:18 | 33.1343 | -117.1666 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | No | Vandalism/Theft |  |  |  | Other | Non- HFTD | NE
65 | SDG&E | 20170728IG01 | July | 28 | 2017 | 3 | 2017-07-28 | 16:31 | 32.7802 | -116.8722 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Pole /Conductor | Vehicle | Electric Facility | Outside Force | Tier 2 | EA
66 | SDG&E | 20170820IG01 | August | 20 | 2017 | 3 | 2017-08-20 | 22:15 | 32.7522 | -117.1184 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 4kV | Overhead | Yes | Equipment/Facility Failure | Fuse |  |  | None | Non- HFTD | CM
67 | SDG&E | 20170830IG01 | August | 30 | 2017 | 3 | 2017-08-30 | 14:12 | 33.3875 | -117.2459 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Other | Tier 2 | NE
68 | SDG&E | 20170905IG01 | September | 5 | 2017 | 3 | 2017-09-05 | 14:49 | 32.6191 | -116.6949 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Unknown | Tier 3 | ME
69 | SDG&E | 20170927IG01 | September | 27 | 2017 | 3 | 2017-09-27 | 14:28 | 33.2327 | -116.9748 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Unknown |  |  |  | Unknown | Tier 2 | NE
70 | SDG&E | 20170927IG02 | September | 27 | 2017 | 3 | 2017-09-27 | 16:10 | 32.7272 | -116.7788 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | None | Tier 3 | EA
71 | SDG&E | 20171007IG01 | October | 7 | 2017 | 4 | 2017-10-07 | 17:40 | 32.5914 | -116.6216 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Conductor |  |  | Other | Tier 3 | ME
72 | SDG&E | 20171016IG01 | October | 16 | 2017 | 4 | 2017-10-16 | 10:20 | 33.0697 | -116.8813 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | RA
73 | SDG&E | 20171018IG01 | October | 18 | 2017 | 4 | 2017-10-18 | 7:20 | 33.1659 | -117.2053 | Vegetation | Urban | Less Than .25 Acres | Unknown | 12kV | Overhead | No | Contact From Object |  | Vehicle | Pole | Human Error | Non- HFTD | NC
74 | SDG&E | 20171022IG01 | October | 22 | 2017 | 4 | 2017-10-22 | 10:22 | 33.099 | -117.135 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Tier 2 | NE
75 | SDG&E | 20171025IG01 | October | 25 | 2017 | 4 | 2017-10-25 | 13:02 | 33.2857 | -117.0275 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Other |  |  | Weather | Tier 2 | NE
76 | SDG&E | 20171210IG01 | December | 10 | 2017 | 4 | 2017-12-10 | 5:26 | 33.28 | -116.955 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 3 | NE
77 | SDG&E | 20171210IG02 | December | 10 | 2017 | 4 | 2017-12-10 | 2:58 | 33.2739 | -116.9537 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Tier 3 | NE
78 | SDG&E | 20180208IG01 | February | 8 | 2018 | 1 | 2018-02-08 | 10:07 | 33.2071 | -117.2072 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Human Error | Non- HFTD | NC
79 | SDG&E | 20180216IG01 | February | 16 | 2018 | 1 | 2018-02-16 | 16:50 | 32.6276 | -116.9409 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Outside Force | Tier 2 | CM
80 | SDG&E | 20180412IG01 | April | 12 | 2018 | 2 | 2018-04-12 | 19:33 | 32.6965 | -117.0493 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | CM
81 | SDG&E | 20180416IG01 | April | 16 | 2018 | 2 | 2018-04-16 | 14:24 | 33.4176 | -117.6058 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | Weather | Non- HFTD | OC
82 | SDG&E | 20180422IG01 | April | 22 | 2018 | 2 | 2018-04-22 | 14:00 | 32.837 | -117.184 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | BC
83 | SDG&E | 20180522IG01 | May | 22 | 2018 | 2 | 2018-05-22 | 14:23 | 33.362 | -117.032 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | NE
84 | SDG&E | 20180601IG01 | June | 1 | 2018 | 2 | 2018-06-01 | 14:00 | 33.099 | -117.044 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | No | Wire-Wire Contact |  |  |  | Other | Non- HFTD | NE
85 | SDG&E | 20180612IG01 | June | 12 | 2018 | 2 | 2018-06-12 | 9:00 | 32.706 | -116.396 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | ME
86 | SDG&E | 20180612IG02 | June | 12 | 2018 | 2 | 2018-06-12 | 15:14 | 32.864 | -116.747 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact from Object |  | Balloons | Electric Facility | None | Tier 3 | EA
87 | SDG&E | 20180622IG01 | June | 22 | 2018 | 2 | 2018-06-22 | 9:46 | 32.567 | -116.941 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | Unknown | Tier 2 | CM
88 | SDG&E | 20180629IG01 | June | 29 | 2018 | 2 | 2018-06-29 | 13:06 | 32.645 | -117.056 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Unknown | Non- HFTD | CM
89 | SDG&E | 20180706IG01 | July | 6 | 2018 | 3 | 2018-07-06 | 10:26 | 32.6203 | -116.7649 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Transformer |  |  |  | Tier 3 | ME
90 | SDG&E | 20180708IG01 | July | 8 | 2018 | 3 | 2018-07-08 | 16:16 | 32.6349 | -117.103 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Other | Non- HFTD | CM
91 | SDG&E | 20180722IG01 | July | 22 | 2018 | 3 | 2018-07-22 | 23:19 | 33.301 | -116.351 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | None | Non- HFTD | RA
92 | SDG&E | 20180730IG01 | July | 30 | 2018 | 3 | 2018-07-30 | 12:11 | 32.8681 | -117.1902 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | BC
93 | SDG&E | 20180809IG01 | August | 9 | 2018 | 3 | 2018-08-09 | 12:00 | 33.213 | -117.335 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Other |  |  | Other | Non- HFTD | NC
94 | SDG&E | 20180819IG01 | August | 19 | 2018 | 3 | 2018-08-19 | 18:35 | 32.7002 | -116.8639 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | EA
95 | SDG&E | 20180914IG01 | September | 14 | 2018 | 3 | 2018-09-14 | 15:02 | 32.7897 | -117.0809 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure |  |  |  | None | Non- HFTD | EA
96 | SDG&E | 20180914IG02 | September | 14 | 2018 | 3 | 2018-09-14 | 10:00 | 33.3177 | -117.2228 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact Between Third Party Facility on Pole and Supply Lines |  | Vehicle | Communication Facility | Human Error | Tier 2 | NE
97 | SDG&E | 20181015IG01 | October | 15 | 2018 | 4 | 2018-10-15 | 10:21 | 33.3191 | -117.2597 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure |  |  |  | None | Tier 2 | NE
98 | SDG&E | 20181126IG01 | November | 26 | 2018 | 4 | 2018-11-26 | 1:51 | 33.4314 | -117.5952 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility |  | Tier 2 | OC
99 | SDG&E | 20190116IG01 | January | 16 | 2019 | 1 | 2019-01-16 | 16:55 | 33.421 | -117.61 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12 kV | Overhead | No | Equipment/Facility Failure | Crossarm |  |  | Weather | Non- HFTD | OC
100 | SDG&E | 20190415IG01 | April | 15 | 2019 | 2 | 2019-04-15 | 14:05 | 32.7883 | -116.8896 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12 kV | Overhead | Yes | Wire-Wire Contact |  |  |  | Outside Force | Non- HFTD | EA
101 | SDG&E | 20190612IG01 | June | 12 | 2019 | 2 | 2019-06-12 | 22:05 | 33.0484 | -116.8578 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12 kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | None | Tier 2 | RA
102 | SDG&E | 20190703IG01 | July | 3 | 2019 | 3 | 2019-07-03 | 15:15 | 33.0113 | -116.8492 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 3 | RA
103 | SDG&E | 20190705IG01 | July | 5 | 2019 | 3 | 2019-07-05 | 12:32 | 33.1584 | -117.222 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 2 | NC
104 | SDG&E | 20190716IG01 | July | 16 | 2019 | 3 | 2019-07-16 | 19:08 | 33.182 | -117.1126 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Other | Tier 2 | NE
105 | SDG&E | 20190716IG02 | July | 16 | 2019 | 3 | 2019-07-16 | 7:36 | 33.1675 | -117.1462 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Wire-Wire Contact |  |  |  | Other | Tier 2 | NE
106 | SDG&E | 20190805IG01 | August | 5 | 2019 | 3 | 2019-08-05 | 14:14 | 32.7886 | -117.1233 | Vegetation | Urban | Less Than .25 Acres | Utility | 12 kV | Overhead | No | Equipment/Facility Failure | Other |  |  | None | Non- HFTD | BC
107 | SDG&E | 20190910IG01 | September | 10 | 2019 | 3 | 2019-09-10 | 12:59 | 32.5638 | -117.0333 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | None | Tier 2 | CM
108 | SDG&E | 20190911IG01 | September | 11 | 2019 | 3 | 2019-09-11 | 14:17 | 33.226 | -117.085 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 2 | NE
109 | SDG&E | 20190913IG01 | September | 13 | 2019 | 3 | 2019-09-13 | 11:27 | 32.787 | -117.007 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | EA
110 | SDG&E | 20190930IG01 | September | 30 | 2019 | 3 | 2019-09-30 | 2:59 | 33.2618 | -116.3705 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Other | Non- HFTD | RA
111 | SDG&E | 20191017IG01 | October | 17 | 2019 | 4 | 2019-10-17 | 12:15 | 33.2736 | -116.3931 | Vegetation | Urban | Less Than .25 Acres | Utility | 120/240 | Overhead | No | Other |  |  |  | Human Error | Non- HFTD | RA
112 | SDG&E | 20191019IG01 | October | 19 | 2019 | 4 | 2019-10-19 | 13:10 | 33.2317 | -117.2593 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 240V | Overhead | Yes | Other |  |  |  | Human Error | Non- HFTD | NC
113 | SDG&E | 20191024IG01 | October | 24 | 2019 | 4 | 2019-10-24 | 10:16 | 32.8357 | -116.7252 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Fuse |  |  | None | Tier 3 | ME
115 | SDG&E | 20191101IG01 | November | 1 | 2019 | 4 | 2019-11-01 | 5:49 | 33.0924 | -117.0206 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | None | Non- HFTD | NE
116 | SDG&E | 20191104IG01 | November | 4 | 2019 | 4 | 2019-11-04 | 15:30 | 33.1969 | -116.7121 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Other |  |  |  | Tier 3 | RA
117 | SDG&E | 20191112IG01 | November | 12 | 2019 | 4 | 2019-11-12 | 7:51 | 33.1903 | -117.3698 | Other | Urban | Less Than .25 Acres | Fire Agency | 120/240 | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | NC
118 | SDG&E | 20200211IG01 | February | 11 | 2020 | 1 | 2020-02-11 | 1:30 | 32.791 | -116.9194 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Outside Force | Non- HFTD | EA
119 | SDG&E | 20200226IG01 | February | 26 | 2020 | 1 | 2020-02-26 | 0:17 | 32.914 | -116.64 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 3 | ME
120 | SDG&E | 20200517IG01 | May | 17 | 2020 | 2 | 2020-05-17 | 8:52 | 33.2373 | -117.0301 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons |  | Other | Tier 2 | NE
121 | SDG&E | 20200531IG01 | May | 31 | 2020 | 2 | 2020-05-31 | 2:01 | 32.543 | -117.0277 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Outside Force | Non- HFTD | CM
122 | SDG&E | 20200602IG01 | June | 2 | 2020 | 2 | 2020-06-02 | 18:00 | 33.07 | -116.863 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 3 | RA
123 | SDG&E | 20200603IG01 | June | 3 | 2020 | 2 | 2020-06-03 | 11:17 | 33.1234 | -117.025 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | NE
124 | SDG&E | 20200705IG01 | July | 5 | 2020 | 3 | 2020-07-05 | 14:08 | 33.0872 | -116.9856 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 3 | NE
125 | SDG&E | 20200717IG01 | July | 17 | 2020 | 3 | 2020-07-17 | 16:30 | 33.0904 | -116.5798 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | RA
126 | SDG&E | 20200726IG01 | July | 26 | 2020 | 3 | 2020-07-26 | 0:00 | 32.819 | -116.9561 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Fuse |  |  | Unknown | Non- HFTD | EA
127 | SDG&E | 20200729IG01 | July | 29 | 2020 | 3 | 2020-07-29 | 17:14 | 32.737 | -116.875 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Tier 3 | EA
128 | SDG&E | 20200801IG01 | August | 1 | 2020 | 3 | 2020-08-01 | 11:11 | 32.631 | -116.174 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Other |  |  | Unknown | Tier 2 | ME
129 | SDG&E | 20200818IG01 | August | 18 | 2020 | 3 | 2020-08-18 | 13:16 | 32.6248 | -117.096 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | Unknown | Non- HFTD | CM
130 | SDG&E | 20200822IG01 | August | 22 | 2020 | 3 | 2020-08-22 | 13:38 | 33.0744 | -116.5773 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Secondary | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 3 | RA
131 | SDG&E | 20200831IG01 | August | 31 | 2020 | 3 | 2020-08-31 | 14:05 | 33.1128 | -117.0055 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Other | Tier 2 | NE
132 | SDG&E | 20200902IG01 | September | 2 | 2020 | 3 | 2020-09-02 | 19:30 | 33.362 | -117.137 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Tier 3 | NE
133 | SDG&E | 20200904IG01 | September | 4 | 2020 | 3 | 2020-09-04 | 20:30 | 33.0658 | -116.8592 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Other | Tier 2 | RA
134 | SDG&E | 20200905IG01 | September | 5 | 2020 | 3 | 2020-09-05 | 14:30 | 33.066 | -116.859 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 120v | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Outside Force | Non- HFTD | EA
135 | SDG&E | 20200906IG01 | September | 6 | 2020 | 3 | 2020-09-06 | 23:00 | 33.0965 | -117.0237 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Transformer |  |  | None | Tier 2 | NE
138 | SDG&E | 20200917IG01 | September | 17 | 2020 | 3 | 2020-09-17 | 10:00 | 33.1101 | -117.2693 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Other |  |  | None | Non- HFTD | NC
139 | SDG&E | 20200930IG01 | September | 30 | 2020 | 3 | 2020-09-30 | 10:45 | 33.0207 | -116.8783 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Secondary | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | RA
140 | SDG&E | 20201014IG01 | October | 14 | 2020 | 4 | 2020-10-14 | 15:05 | 33.027 | -116.889 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kv | Overhead | No | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 2 | RA
141 | SDG&E | 20201111IG01 | November | 11 | 2020 | 4 | 2020-11-11 | 9:51 | 32.678 | -116.86 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kv | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Unknown | Tier 3 | EA
142 | SDG&E | 20201130IG01 | November | 30 | 2020 | 4 | 2020-11-30 | 9:10 | 33.266 | -117.223 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 2 | NE
143 | SDG&E | 20201203IG01 | December | 3 | 2020 | 4 | 2020-12-03 | 11:56 | 33.176 | -117.1541 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Pole |  |  | Weather | Tier 2 | NE

## SDGE_Ignitions_Analyzed
OBJECTID | Company | Ignition ID | Month | Day | Year | Quarter | Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Voltage (Volts) | Type | Was There an Outage | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | Tier | District | 4 mi / 1 hr |  |  |  |  | 8 mi / 1 hr |  |  |  |  | 4 mi / 2 hr |  |  |  |  | 8 mi / 2 hr |  |  |  |  | Cause | 8 mi / 1 hr
[25 empty] | Station | Dist | Time | MaxGust | Num | Station | Dist | Time | MaxGust | Num | Station | Dist | Time | MaxGust | Num | Station | Dist | Time | MaxGust | Num | Cause | Category | MaxGust | Veg | Equipment | Agent
1 | SDG&E | 20150211IG01 | February | 11 | 2015 | 1 | 2015-02-11 | 15:30 | 32.8941 | -116.9393 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | EA | COCSD | 3.91 | 2015-02-11T23:10:00Z | 18.01 | 21 | E3241 | 6.52 | 2015-02-11T22:38:00Z | 24.99 | 117 | ELMSD | 3.12 | 2015-02-11T23:40:00Z | 18.01 | 39 | E3241 | 6.52 | 2015-02-11T23:43:00Z | 24.99 | 224 | Vegetation | < 25mph | 24.99 | 24.99 | 14.99 | 13
2 | SDG&E | 20150319IG01 | March | 19 | 2015 | 1 | 2015-03-19 | 23:50 | 33.0565 | -117.0332 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 2 | NE | HVWSD | 2.6 | 2015-03-20T06:50:00Z | 11.01 | 13 | HDMSD | 5.96 | 2015-03-20T06:50:00Z | 13 | 134 | HVWSD | 2.6 | 2015-03-20T06:50:00Z | 11.01 | 24 | HDMSD | 5.96 | 2015-03-20T06:50:00Z | 13 | 256 | Agent | < 25mph | 13 | 15.99 | 4.99 | 17.27
3 | SDG&E | 20150409IG01 | April | 9 | 2015 | 2 | 2015-04-09 | 17:23 | 32.7233 | -116.8922 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Unknown |  |  |  |  | Tier 3 | EA | OTYSD | 2.08 | 2015-04-09T23:40:00Z | 17 | 24 | OTYSD | 2.08 | 2015-04-09T23:40:00Z | 17 | 129 | OTYSD | 2.08 | 2015-04-10T00:50:00Z | 17 | 48 | OTYSD | 2.08 | 2015-04-10T00:50:00Z | 17 | 246 | Unknown | < 25mph | 17 | 22.01 | 23 | 11.01
4 | SDG&E | 20150412IG01 | April | 12 | 2015 | 2 | 2015-04-12 | 12:31 | 33.0117 | -116.866 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility |  | Tier 2 | RA | CLMSD | 0.4 | 2015-04-12T19:10:00Z | 14 | 40 | HVYSD | 4.19 | 2015-04-12T18:50:00Z | 14.99 | 131 | CLMSD | 0.4 | 2015-04-12T19:50:00Z | 14 | 81 | CESSD | 4.4 | 2015-04-12T20:10:00Z | 18.01 | 263 | Unknown | < 25mph | 14.99 | 15.21 | 12.01 | 27
5 | SDG&E | 20150412IG02 | April | 12 | 2015 | 2 | 2015-04-12 | 14:30 | 33.2754 | -117.3306 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vehicle | Pole |  | Tier 2 | NC | WIRC1 | 3.5 | 2015-04-12T21:17:00Z | 17 | 1 | KL18 | 7.13 | 2015-04-12T21:15:00Z | 17.27 | 41 | WIRC1 | 3.5 | 2015-04-12T21:17:00Z | 17 | 2 | KL18 | 7.13 | 2015-04-12T21:15:00Z | 17.27 | 78 | Agent | < 25mph | 17.27 | 24.99 | 8.01 | 14
6 | SDG&E | 20150413IG01 | April | 13 | 2015 | 2 | 2015-04-13 | 10:50 | 32.5859 | -117.0017 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Tier 2 | CM | CVXSD | 3.45 | 2015-04-13T17:20:00Z | 10 | 14 | OMBSD | 6.2 | 2015-04-13T17:50:00Z | 11.01 | 39 | CVXSD | 3.45 | 2015-04-13T18:50:00Z | 14 | 26 | MIGSD | 6.94 | 2015-04-13T18:50:00Z | 14.99 | 73 | Agent | < 25mph | 11.01 | 20 | 21 | 17
7 | SDG&E | 20150418IG01 | April | 18 | 2015 | 2 | 2015-04-18 | 12:00 | 32.7764 | -116.9309 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Secondary | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | None | Non- HFTD | EA | OTYSD | 3.89 | 2015-04-18T18:40:00Z | 14 | 35 | E3619 | 6.71 | 2015-04-18T18:58:00Z | 15.99 | 164 | OTYSD | 3.89 | 2015-04-18T20:00:00Z | 17 | 67 | C2462 | 7.32 | 2015-04-18T19:25:00Z | 17.98 | 316 | Vegetation | < 25mph | 15.99 | 24 | 28.99 | 18.01
8 | SDG&E | 20150428IG01 | April | 28 | 2015 | 2 | 2015-04-28 | 13:30 | 32.8917 | -116.8419 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Tier 3 | EA | BNASD | 3.55 | 2015-04-28T20:10:00Z | 18.99 | 21 | WALSD | 4.92 | 2015-04-28T20:20:00Z | 27 | 134 | BNASD | 3.55 | 2015-04-28T21:10:00Z | 18.99 | 39 | MGRSD | 7.58 | 2015-04-28T21:10:00Z | 28.99 | 256 | Agent | 25-40mph | 27 | 17 | 53.02 | 17
9 | SDG&E | 20150429IG01 | April | 29 | 2015 | 2 | 2015-04-29 | 12:00 | 32.6061 | -116.696 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Unknown | Tier 3 | ME | BRJSD | 0.73 | 2015-04-29T18:10:00Z | 21 | 14 | BAJC1 | 4.25 | 2015-04-29T18:50:00Z | 22.01 | 64 | BRJSD | 0.73 | 2015-04-29T18:10:00Z | 21 | 26 | BAJC1 | 4.25 | 2015-04-29T18:50:00Z | 22.01 | 120 | Vegetation | < 25mph | 22.01 | 11.01 | 28.99 | 13
10 | SDG&E | 20150517IG01 | May | 17 | 2015 | 2 | 2015-05-17 | 6:55 | 33.1808 | -117.2064 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility |  | Non- HFTD | NC | C2635 | 3.07 | 2015-05-17T13:46:00Z | 26.98 | 27 | AT125 | 5.28 | 2015-05-17T13:30:00Z | 50.96 | 105 | C2635 | 3.07 | 2015-05-17T14:16:00Z | 40.96 | 52 | AT125 | 5.28 | 2015-05-17T13:30:00Z | 50.96 | 207 | Unknown | 40-55mph | 50.96 | 24.99 | 17.27 | 8.99
11 | SDG&E | 20150528IG01 | May | 28 | 2015 | 2 | 2015-05-28 | 12:45 | 32.7265 | -116.9922 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | EA | D5256 | 3.01 | 2015-05-28T19:28:00Z | 13 | 57 | NATSD | 7.86 | 2015-05-28T19:40:00Z | 14 | 126 | D5256 | 3.01 | 2015-05-28T20:43:00Z | 13 | 115 | NATSD | 7.86 | 2015-05-28T20:40:00Z | 18.01 | 254 | Agent | < 25mph | 14 | 47 | 8.01 | 13
12 | SDG&E | 20150707IG01 | July | 7 | 2015 | 3 | 2015-07-07 | 15:00 | 32.7443 | -117.0498 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Non- HFTD | EA | E3680 | 1.22 | 2015-07-07T21:56:00Z | 15.99 | 43 | OTYSD | 7.28 | 2015-07-07T22:00:00Z | 17 | 124 | E3680 | 1.22 | 2015-07-07T21:56:00Z | 15.99 | 79 | OTYSD | 7.28 | 2015-07-07T22:30:00Z | 21 | 232 | Agent | < 25mph | 17 | 23 | 30 | 9.4
13 | SDG&E | 20150717IG01 | July | 17 | 2015 | 3 | 2015-07-17 | 9:48 | 33.3012 | -117.0222 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Communication Facility | Human Error | Tier 3 | NE | KCKSD | 3.77 | 2015-07-17T16:20:00Z | 5.99 | 48 | HP014 | 6.35 | 2015-07-17T16:17:00Z | 15.21 | 138 | LLCSD | 3.19 | 2015-07-17T17:20:00Z | 10 | 96 | HP014 | 6.35 | 2015-07-17T16:17:00Z | 15.21 | 275 | Vegetation | < 25mph | 15.21 | 77 | 14 | 24
14 | SDG&E | 20150727IG01 | July | 27 | 2015 | 3 | 2015-07-27 | 14:30 | 33.0665 | -116.579 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | None | Tier 3 | RA | VCMSD | 2.52 | 2015-07-27T21:20:00Z | 24.99 | 55 | VCMSD | 2.52 | 2015-07-27T21:20:00Z | 24.99 | 126 | HRPSD | 2.14 | 2015-07-27T22:20:00Z | 25.99 | 105 | HRPSD | 2.14 | 2015-07-27T22:20:00Z | 25.99 | 237 | Vegetation | < 25mph | 24.99 | 12.01 | 13 | 10
15 | SDG&E | 20150808IG01 | August | 8 | 2015 | 3 | 2015-08-08 | 10:00 | 33.1973 | -117.2308 | Vegetation | Urban | Less Than .25 Acres | Customer | 4kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | NC | VISSD | 1.45 | 2015-08-08T16:50:00Z | 8.01 | 32 | E0995 | 7.51 | 2015-08-08T16:56:00Z | 18.01 | 133 | C2635 | 3.35 | 2015-08-08T17:45:00Z | 10 | 62 | E0995 | 7.51 | 2015-08-08T17:46:00Z | 18.01 | 256 | Agent | < 25mph | 18.01 | 28.01 | 22.01 | 8.99
16 | SDG&E | 20150813IG01 | August | 13 | 2015 | 3 | 2015-08-13 | 20:33 | 33.2457 | -116.6769 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Unknown |  |  |  | Unknown | Tier 2 | RA | MGYSD | 2.03 | 2015-08-14T02:40:00Z | 13 | 24 | MGYSD | 2.03 | 2015-08-14T02:40:00Z | 13 | 61 | MGYSD | 2.03 | 2015-08-14T02:40:00Z | 13 | 48 | MGYSD | 2.03 | 2015-08-14T02:40:00Z | 13 | 122 | Unknown | < 25mph | 13 | 33.55 | 14 | 18.01
17 | SDG&E | 20150815IG01 | August | 15 | 2015 | 3 | 2015-08-15 | 17:30 | 32.7417 | -116.9685 | Other | Urban | Less Than .25 Acres | Customer | 4Kv | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Non- HFTD | EA | ECJSD | 3.72 | 2015-08-15T23:40:00Z | 14.99 | 66 | ECJSD | 3.72 | 2015-08-15T23:40:00Z | 14.99 | 120 | ECJSD | 3.72 | 2015-08-15T23:40:00Z | 14.99 | 129 | ECJSD | 3.72 | 2015-08-15T23:40:00Z | 14.99 | 234 | Equipment | < 25mph | 14.99 | 37.41 | 22.01 | 24
18 | SDG&E | 20150823IG01 | August | 23 | 2015 | 3 | 2015-08-23 | 15:00 | 33.2729 | -117.1521 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | NE | CIRSD | 0.95 | 2015-08-23T21:30:00Z | 14 | 17 | PZAC1 | 6.65 | 2015-08-23T21:50:00Z | 20 | 120 | CIRSD | 0.95 | 2015-08-23T21:30:00Z | 14 | 33 | PZAC1 | 6.65 | 2015-08-23T22:50:00Z | 20 | 231 | Vegetation | < 25mph | 20 |  | 8.99 | 18.01
19 | SDG&E | 20150901IG01 | September | 1 | 2015 | 3 | 2015-09-01 | 18:01 | 32.7595 | -117.0671 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished | 4kV | Overhead | No | Contact From Object |  | Vehicle | Electric Facility | Human Error | Non- HFTD | CM | E3680 | 2.6 | 2015-09-02T00:02:00Z | 11.01 | 29 | MTLSD | 5.75 | 2015-09-02T00:30:00Z | 17 | 117 | E3680 | 2.6 | 2015-09-02T00:02:00Z | 11.01 | 54 | MTLSD | 5.75 | 2015-09-02T00:30:00Z | 17 | 234 | Agent | < 25mph | 17 |  | 8.01 | 21.47
20 | SDG&E | 20150901IG02 | September | 1 | 2015 | 3 | 2015-09-01 | 8:50 | 32.669 | -116.286 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | None | Tier 2 | ME | BVDSD | 0.5 | 2015-09-01T15:50:00Z | 4.99 | 14 | LPTSD | 7.51 | 2015-09-01T15:50:00Z | 4.99 | 28 | BVDSD | 0.5 | 2015-09-01T16:40:00Z | 8.99 | 26 | CWDSD | 5.27 | 2015-09-01T16:50:00Z | 10 | 52 | Equipment | < 25mph | 4.99 |  | 24.99 | 8.99
21 | SDG&E | 20150902IG01 | September | 2 | 2015 | 3 | 2015-09-02 | 18:18 | 33.1867 | -117.202 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Non- HFTD | NC | VISSD | 3.27 | 2015-09-03T00:40:00Z | 11.01 | 33 | E6321 | 5.24 | 2015-09-03T00:33:00Z | 13 | 96 | VISSD | 3.27 | 2015-09-03T00:40:00Z | 11.01 | 63 | E6321 | 5.24 | 2015-09-03T00:33:00Z | 13 | 186 | Agent | < 25mph | 13 |  | 20 | 12.01
22 | SDG&E | 20150908IG01 | September | 8 | 2015 | 3 | 2015-09-08 | 11:45 | 33.0726 | -116.7436 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | None | Tier 3 | RA | DYESD | 1.97 | 2015-09-08T18:20:00Z | 20 | 24 | HOSSD | 5.05 | 2015-09-08T18:30:00Z | 23 | 138 | DYESD | 1.97 | 2015-09-08T18:50:00Z | 22.01 | 48 | HOSSD | 5.05 | 2015-09-08T18:30:00Z | 23 | 275 | Equipment | < 25mph | 23 |  | 18.34 | 15.99
23 | SDG&E | 20150909IG01 | September | 9 | 2015 | 3 | 2015-09-09 | 20:40 | 32.644 | -117.072 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Non- HFTD | CM | AT526 | 2.37 | 2015-09-10T03:00:00Z | 8.99 | 23 | MIGC1 | 6.39 | 2015-09-10T02:50:00Z | 12.01 | 73 | NATSD | 1.61 | 2015-09-10T04:10:00Z | 14 | 41 | BFDSD | 7.19 | 2015-09-10T04:00:00Z | 23 | 139 | Equipment | < 25mph | 12.01 |  | 68 | 18.99
24 | SDG&E | 20150917IG01 | September | 17 | 2015 | 3 | 2015-09-17 | 8:09 | 32.6791 | -117.1044 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Transformer |  |  | None | Non- HFTD | CM | NATSD | 1.77 | 2015-09-17T15:00:00Z | 8.01 | 17 | NATSD | 1.77 | 2015-09-17T15:00:00Z | 8.01 | 106 | NATSD | 1.77 | 2015-09-17T16:00:00Z | 8.01 | 34 | NATSD | 1.77 | 2015-09-17T16:00:00Z | 8.01 | 217 | Equipment | < 25mph | 8.01 |  | 21 | 20
25 | SDG&E | 20151002IG01 | October | 2 | 2015 | 4 | 2015-10-02 | 14:30 | 33.1354 | -117.0588 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | NE | D9718 | 1.51 | 2015-10-02T20:57:00Z | 14.99 | 40 | OLVSD | 5.6 | 2015-10-02T21:30:00Z | 21 | 175 | D9718 | 1.51 | 2015-10-02T20:57:00Z | 14.99 | 79 | HDMSD | 7.76 | 2015-10-02T22:20:00Z | 22.01 | 337 | Equipment | < 25mph | 21 |  | 10 | 14.99
26 | SDG&E | 20151009IG01 | October | 9 | 2015 | 4 | 2015-10-09 | 16:00 | 32.7705 | -117.1095 | Other | Urban | Less Than .25 Acres | Fire Agency | Secondary | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | CM | CHOSD | 3.45 | 2015-10-09T23:00:00Z | 15.99 | 31 | MTLSD | 5.84 | 2015-10-09T22:50:00Z | 28.99 | 164 | KMYF | 3.41 | 2015-10-09T23:53:00Z | 20.71 | 62 | MTLSD | 5.84 | 2015-10-09T23:50:00Z | 28.99 | 322 | Equipment | 25-40mph | 28.99 |  | 22.01 | 18.99
27 | SDG&E | 20151226IG01 | December | 26 | 2015 | 4 | 2015-12-26 | 3:04 | 33.1323 | -117.0695 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | NE | ESCSD | 2.91 | 2015-12-26T11:00:00Z | 24 | 40 | OLVSD | 5.01 | 2015-12-26T10:10:00Z | 24 | 163 | ESCSD | 2.91 | 2015-12-26T11:10:00Z | 24.99 | 77 | OLVSD | 5.01 | 2015-12-26T11:20:00Z | 34 | 323 | Vegetation | < 25mph | 24 |  | 38.99 | 21
28 | SDG&E | 20160103IG01 | January | 3 | 2016 | 1 | 2016-01-03 | 4:30 | 33.1915 | -117.3655 | Other | Urban | Less Than .25 Acres | Fire Agency | 12kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | Other | Non- HFTD | NC | E3370 | 0.16 | 2016-01-03T11:45:00Z | 7 | 27 | CBDSD | 4.35 | 2016-01-03T12:30:00Z | 8.99 | 49 | E3370 | 0.16 | 2016-01-03T11:45:00Z | 7 | 52 | CBDSD | 4.35 | 2016-01-03T12:40:00Z | 10 | 94 | Agent | < 25mph | 8.99 |  | 18.41 | 17
29 | SDG&E | 20160109IG01 | January | 9 | 2016 | 1 | 2016-01-09 | 4:30 | 33.082 | -117.091 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Non- HFTD | NE | HDMSD | 3.7 | 2016-01-09T12:00:00Z | 17 | 35 | HDMSD | 3.7 | 2016-01-09T12:00:00Z | 17 | 144 | HDMSD | 3.7 | 2016-01-09T12:00:00Z | 17 | 67 | HDMSD | 3.7 | 2016-01-09T12:00:00Z | 17 | 279 | Vegetation | < 25mph | 17 |  | 21 | 12.01
30 | SDG&E | 20160116IG01 | January | 16 | 2016 | 1 | 2016-01-16 | 14:42 | 32.7188 | -116.9745 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | EA | D7030 | 1.97 | 2016-01-16T22:22:00Z | 13 | 53 | D7030 | 1.97 | 2016-01-16T22:22:00Z | 13 | 107 | OTYSD | 2.72 | 2016-01-16T23:30:00Z | 14 | 106 | OTYSD | 2.72 | 2016-01-16T23:30:00Z | 14 | 212 | Agent | < 25mph | 13 |  | 45.99 | 12.01
31 | SDG&E | 20160131IG01 | January | 31 | 2016 | 1 | 2016-01-31 | 15:00 | 33.3217 | -117.156 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Weather | Tier 2 | NE | FBKSD | 2.37 | 2016-01-31T22:30:00Z | 50 | 20 | AT107 | 6.73 | 2016-01-31T22:57:00Z | 53.02 | 146 | PZAC1 | 3.98 | 2016-01-31T23:50:00Z | 54 | 37 | PZAC1 | 3.98 | 2016-01-31T23:50:00Z | 54 | 278 | Equipment | 40-55mph | 53.02 |  | 18.99 | 13
32 | SDG&E | 20160205IG01 | February | 5 | 2016 | 1 | 2016-02-05 | 9:47 | 33.0739 | -117.0862 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | NE | HDMSD | 3.54 | 2016-02-05T17:40:00Z | 28.01 | 36 | SPVSD | 7.72 | 2016-02-05T17:10:00Z | 28.99 | 158 | HDMSD | 3.54 | 2016-02-05T17:50:00Z | 31 | 76 | HDMSD | 3.54 | 2016-02-05T17:50:00Z | 31 | 319 | Equipment | 25-40mph | 28.99 |  | 18.01 | 24.99
33 | SDG&E | 20160212IG01 | February | 12 | 2016 | 1 | 2016-02-12 | 19:30 | 33.2427 | -116.9664 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Vandalism/Theft |  |  |  | Outside Force | Tier 3 | NE | RINSD | 3.17 | 2016-02-13T02:50:00Z | 7 | 54 | HP014 | 6.9 | 2016-02-13T03:17:00Z | 9.4 | 169 | HHCSD | 2.78 | 2016-02-13T04:30:00Z | 7 | 102 | HP014 | 6.9 | 2016-02-13T04:27:00Z | 9.62 | 319 | Agent | < 25mph | 9.4 |  | 20.13 | 24.99
34 | SDG&E | 20160218IG01 | February | 18 | 2016 | 1 | 2016-02-18 | 0:00 | 32.7063 | -116.397 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | None | Tier 3 | ME | LPTSD | 0.58 | 2016-02-18T07:00:00Z | 14.99 | 14 | BVDSD | 6.99 | 2016-02-18T07:10:00Z | 24 | 64 | LPTSD | 0.58 | 2016-02-18T07:00:00Z | 14.99 | 26 | BVDSD | 6.99 | 2016-02-18T07:10:00Z | 24 | 119 | Agent | < 25mph | 24 |  | 14 | 23
35 | SDG&E | 20160303IG01 | March | 3 | 2016 | 1 | 2016-03-03 | 6:00 | 32.8472 | -116.942 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Non- HFTD | EA | RIOSD | 3.55 | 2016-03-03T14:00:00Z | 3 | 41 | HARSD | 6.79 | 2016-03-03T13:40:00Z | 10 | 213 | RIOSD | 3.55 | 2016-03-03T14:10:00Z | 3 | 77 | HARSD | 6.79 | 2016-03-03T15:00:00Z | 10 | 418 | Agent | < 25mph | 10 |  | 7 | 20
36 | SDG&E | 20160311IG01 | March | 11 | 2016 | 1 | 2016-03-11 | 11:40 | 33.1563 | -117.2152 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Non- HFTD | NC | KCRQ | 3.95 | 2016-03-11T18:53:00Z | 17.27 | 64 | KCRQ | 3.95 | 2016-03-11T18:53:00Z | 17.27 | 140 | KCRQ | 3.95 | 2016-03-11T18:53:00Z | 17.27 | 124 | E0995 | 6.32 | 2016-03-11T20:39:00Z | 22.01 | 275 | Equipment | < 25mph | 17.27 |  | 19.95 | 15.99
37 | SDG&E | 20160406IG01 | April | 6 | 2016 | 2 | 2016-04-06 | 10:38 | 33.1865 | -117.1967 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Conductor | Vegetation | Electric Facility | Human Error | Non- HFTD | NC | SMCSD | 3.98 | 2016-04-06T17:30:00Z | 5.99 | 50 | TLKSD | 7.51 | 2016-04-06T17:30:00Z | 11.01 | 142 | VISSD | 3.55 | 2016-04-06T18:10:00Z | 10 | 100 | TLKSD | 7.51 | 2016-04-06T18:20:00Z | 14 | 283 | Vegetation | < 25mph | 11.01 |  | 21.41 | 18.01
40 | SDG&E | 20160614IG01 | June | 14 | 2016 | 2 | 2016-06-14 | 6:05 | 32.8801 | -116.9051 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Outside Force | Tier 2 | EA | COCSD | 2.09 | 2016-06-14T12:40:00Z | 8.99 | 30 | DEHSD | 7.61 | 2016-06-14T13:00:00Z | 8.99 | 159 | COCSD | 2.09 | 2016-06-14T12:40:00Z | 8.99 | 60 | DEHSD | 7.61 | 2016-06-14T13:00:00Z | 8.99 | 317 | Agent | < 25mph | 8.99 |  | 15.05 | 18.99
41 | SDG&E | 20160623IG01 | June | 23 | 2016 | 2 | 2016-06-23 | 15:00 | 32.8058 | -116.961 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | Outside Force | Non- HFTD | EA | ECJSD | 0.99 | 2016-06-23T21:40:00Z | 14 | 15 | E3070 | 4.62 | 2016-06-23T21:05:00Z | 18.01 | 158 | KSEE | 1.66 | 2016-06-23T22:47:00Z | 16.11 | 30 | E3070 | 4.62 | 2016-06-23T21:05:00Z | 18.01 | 305 | Agent | < 25mph | 18.01 |  | 29.24 | 15.99
42 | SDG&E | 20160627IG01 | June | 27 | 2016 | 2 | 2016-06-27 | 15:30 | 33.2837 | -116.6174 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Human Error | Tier 2 | RA | EWNSD | 3.96 | 2016-06-27T22:00:00Z | 22.01 | 20 | WARSD | 5.24 | 2016-06-27T22:00:00Z | 24 | 61 | EWNSD | 3.96 | 2016-06-27T23:30:00Z | 25.99 | 38 | EWNSD | 3.96 | 2016-06-27T23:30:00Z | 25.99 | 116 | Agent | < 25mph | 24 |  | 53.02 | 8.01
43 | SDG&E | 20160702IG01 | July | 2 | 2016 | 3 | 2016-07-02 | 7:51 | 32.81 | -116.878 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Capacitor Bank |  |  | None | Tier 2 | EA | DEHSD | 2.95 | 2016-07-02T14:30:00Z | 8.01 | 95 | DEHSD | 2.95 | 2016-07-02T14:30:00Z | 8.01 | 191 | DEHSD | 2.95 | 2016-07-02T15:40:00Z | 10 | 190 | WALSD | 4.76 | 2016-07-02T15:30:00Z | 10 | 381 | Equipment | < 25mph | 8.01 |  | 19.46 | 23
44 | SDG&E | 20160711IG01 | July | 11 | 2016 | 3 | 2016-07-11 | 10:27 | 33.4531 | -117.3044 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility |  | Tier 2 | NE |  |  |  | 0 | 0 | CSPC1 | 6.63 | 2016-07-11T17:22:00Z | 13 | 37 |  |  |  | 0 | 0 | FBZCA | 5.03 | 2016-07-11T18:22:00Z | 17 | 74 | Unknown | < 25mph | 13 |  | 5.99 | 8.99
45 | SDG&E | 20160711IG02 | July | 11 | 2016 | 3 | 2016-07-11 | 13:19 | 33.1146 | -116.5843 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  |  | Tier 3 | RA | VCMSD | 0.84 | 2016-07-11T19:40:00Z | 30 | 52 | VCMSD | 0.84 | 2016-07-11T19:40:00Z | 30 | 117 | VCMSD | 0.84 | 2016-07-11T19:40:00Z | 30 | 102 | VCMSD | 0.84 | 2016-07-11T19:40:00Z | 30 | 233 | Equipment | 25-40mph | 30 |  | 7.96 | 17
47 | SDG&E | 20160729IG01 | July | 29 | 2016 | 3 | 2016-07-29 | 10:57 | 33.071 | -116.7424 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  |  | Tier 3 | RA | WCKSD | 0.29 | 2016-07-29T17:50:00Z | 14 | 24 | WCKSD | 0.29 | 2016-07-29T17:50:00Z | 14 | 139 | DYESD | 1.89 | 2016-07-29T18:30:00Z | 14.99 | 48 | IJPSD | 4.74 | 2016-07-29T18:30:00Z | 18.01 | 277 | Equipment | < 25mph | 14 |  | 97.8 | 18.99
48 | SDG&E | 20160731IG01 | July | 31 | 2016 | 3 | 2016-07-31 | 13:43 | 33.3663 | -117.2033 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Unknown | Tier 2 | NE | FBKSD | 2.22 | 2016-07-31T20:40:00Z | 20 | 36 | AT107 | 5.72 | 2016-07-31T20:38:00Z | 24.99 | 92 | FBKSD | 2.22 | 2016-07-31T21:40:00Z | 22.01 | 76 | AT107 | 5.72 | 2016-07-31T20:38:00Z | 24.99 | 187 | Vegetation | < 25mph | 24.99 |  | 24 | 37
49 | SDG&E | 20160827IG01 | August | 27 | 2016 | 3 | 2016-08-27 | 12:43 | 33.1371 | -117.0761 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Unknown | Non- HFTD | NE | ESCSD | 2.77 | 2016-08-27T19:20:00Z | 11.01 | 19 | WRBSD | 7.79 | 2016-08-27T19:40:00Z | 18.01 | 146 | ESCSD | 2.77 | 2016-08-27T20:30:00Z | 13 | 37 | HDMSD | 7.34 | 2016-08-27T20:40:00Z | 18.99 | 293 | Agent | < 25mph | 18.01 |  | 5.19 | 14
50 | SDG&E | 20160923IG01 | September | 23 | 2016 | 3 | 2016-09-23 | 11:25 | 32.7372 | -116.7343 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Transformer |  |  | None | Tier 3 | EA | HP002 | 3.03 | 2016-09-23T17:55:00Z | 12.97 | 31 | SQTSD | 4.93 | 2016-09-23T18:20:00Z | 13 | 101 | DHVSD | 3.83 | 2016-09-23T19:20:00Z | 14 | 61 | DHVSD | 3.83 | 2016-09-23T19:20:00Z | 14 | 201 | Equipment | < 25mph | 13 |  | 16.07 | 21
51 | SDG&E | 20160927IG01 | September | 27 | 2016 | 3 | 2016-09-27 | 10:18 | 33.2967 | -117.2079 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Animal |  | Unknown | Tier 2 | NE | CIRSD | 3.67 | 2016-09-27T17:00:00Z | 8.01 | 10 | HP007 | 7.27 | 2016-09-27T16:46:00Z | 21.47 | 104 | CIRSD | 3.67 | 2016-09-27T17:00:00Z | 8.01 | 20 | HP007 | 7.27 | 2016-09-27T18:06:00Z | 23.71 | 206 | Agent | < 25mph | 21.47 |  | 20.02 | 8.05
52 | SDG&E | 20160929IG01 | September | 29 | 2016 | 3 | 2016-09-28 | 14:29 | 32.7418 | -116.9653 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Outside Force | Non- HFTD | EA | OTYSD | 2.64 | 2016-09-28T20:50:00Z | 22.01 | 61 | OTYSD | 2.64 | 2016-09-28T20:50:00Z | 22.01 | 95 | OTYSD | 2.64 | 2016-09-28T20:50:00Z | 22.01 | 122 | OTYSD | 2.64 | 2016-09-28T20:50:00Z | 22.01 | 191 | Equipment | < 25mph | 22.01 |  | 21.34 | 5.99
53 | SDG&E | 20161021IG01 | October | 21 | 2016 | 4 | 2016-10-21 | 11:20 | 33.0485 | -116.8615 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Transformer |  |  |  | Tier 2 | RA | BLCSD | 3.98 | 2016-10-21T17:40:00Z | 12.01 | 68 | BNASD | 7.93 | 2016-10-21T18:10:00Z | 14 | 179 | CLMSD | 2.33 | 2016-10-21T19:10:00Z | 13 | 129 | ARHSD | 5.69 | 2016-10-21T19:10:00Z | 15.99 | 339 | Equipment | < 25mph | 14 |  | 21.64 | 13
54 | SDG&E | 20161102IG01 | November | 2 | 2016 | 4 | 2016-11-02 | 10:30 | 32.8373 | -116.7022 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Tier 3 | ME | VGDSD | 2.96 | 2016-11-02T17:00:00Z | 18.99 | 43 | WDCSD | 4.27 | 2016-11-02T17:30:00Z | 22.01 | 202 | VGDSD | 2.96 | 2016-11-02T17:00:00Z | 18.99 | 80 | WDCSD | 4.27 | 2016-11-02T17:30:00Z | 22.01 | 386 | Equipment | < 25mph | 22.01 |  | 17.46 | 11.69
55 | SDG&E | 20161112IG01 | November | 12 | 2016 | 4 | 2016-11-12 | 20:30 | 32.6227 | -116.9388 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  |  | Tier 2 | CM | RODB1 | 1.87 | 2016-11-13T04:30:00Z | 5.28 | 7 | OTYC1 | 5.88 | 2016-11-13T04:14:00Z | 8.99 | 64 | RODB1 | 1.87 | 2016-11-13T05:30:00Z | 6.31 | 13 | OTYC1 | 5.88 | 2016-11-13T05:14:00Z | 17 | 125 | Equipment | < 25mph | 8.99 |  | 13.3 | 23.75
56 | SDG&E | 20170120IG01 | January | 20 | 2017 | 1 | 2017-01-20 | 14:00 | 32.6274 | -117.0767 | Building | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Conductor | Vegetation | Pole | Weather | Non- HFTD | CM | NATSD | 2.2 | 2017-01-20T21:30:00Z | 34.99 | 38 | MIGC1 | 7.2 | 2017-01-20T21:50:00Z | 47 | 101 | NATSD | 2.2 | 2017-01-20T23:00:00Z | 51.99 | 70 | BFDSD | 6.01 | 2017-01-20T23:00:00Z | 64 | 203 | Vegetation | 40-55mph | 47 |  | 14.99 | 19.73
57 | SDG&E | 20170608IG01 | June | 8 | 2017 | 2 | 2017-06-08 | 4:12 | 33.0356 | -117.1839 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Tier 2 | NC | WRBSD | 3.58 | 2017-06-08T11:10:00Z | 5.99 | 103 | E9975 | 7.03 | 2017-06-08T10:12:00Z | 8.99 | 223 | HDMSD | 2.89 | 2017-06-08T11:30:00Z | 5.99 | 196 | E9975 | 7.03 | 2017-06-08T10:12:00Z | 8.99 | 430 | Agent | < 25mph | 8.99 |  | 14.17 | 9.17
58 | SDG&E | 20170612IG01 | June | 12 | 2017 | 2 | 2017-06-12 | 11:20 | 32.843 | -116.7111 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Other | Electric Facility | Weather | Tier 3 | ME | EWRSD | 1.71 | 2017-06-12T17:50:00Z | 15.99 | 55 | GTYSD | 7.99 | 2017-06-12T17:30:00Z | 20 | 201 | VJSSD | 0.33 | 2017-06-12T19:00:00Z | 20 | 105 | GTYSD | 7.99 | 2017-06-12T17:30:00Z | 20 | 393 | Unknown | < 25mph | 20 |  | 18.71
59 | SDG&E | 20170619IG01 | June | 19 | 2017 | 2 | 2017-06-19 | 9:52 | 32.7829 | -117.0488 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility |  | Non- HFTD | EA | CHOSD | 3.4 | 2017-06-19T16:50:00Z | 7 | 53 | E3070 | 7.09 | 2017-06-19T16:30:00Z | 12.01 | 154 | CHOSD | 3.4 | 2017-06-19T17:30:00Z | 10 | 111 | MTLSD | 4.13 | 2017-06-19T17:50:00Z | 13 | 313 | Agent | < 25mph | 12.01 |  | 13.65
60 | SDG&E | 20170626IG01 | June | 26 | 2017 | 2 | 2017-06-26 | 14:30 | 32.7842 | -117.1391 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | BC | E8360 | 2 | 2017-06-26T21:14:00Z | 13 | 43 | MTLSD | 6.26 | 2017-06-26T21:10:00Z | 15.99 | 183 | BVDC1 | 0.19 | 2017-06-26T21:50:00Z | 14 | 82 | MTLSD | 6.26 | 2017-06-26T21:40:00Z | 18.01 | 355 | Agent | < 25mph | 15.99 |  | 11
61 | SDG&E | 20170629IG01 | June | 29 | 2017 | 2 | 2017-06-29 | 13:07 | 33.1355 | -117.098 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility |  | Non- HFTD | NE | D9888 | 3.59 | 2017-06-29T19:39:00Z | 12.01 | 42 | HDMSD | 6.74 | 2017-06-29T20:00:00Z | 18.99 | 222 | ESCSD | 3.67 | 2017-06-29T20:50:00Z | 13 | 84 | E9915 | 5.54 | 2017-06-29T21:00:00Z | 20 | 425 | Agent | < 25mph | 18.99 |  | 41.57
62 | SDG&E | 20170629IG02 | June | 29 | 2017 | 2 | 2017-06-29 | 14:58 | 32.6926 | -116.8564 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Electric Facility | None | Tier 3 | EA | LSVSD | 3.56 | 2017-06-29T21:40:00Z | 14 | 12 | DZRSD | 7.85 | 2017-06-29T21:20:00Z | 20 | 90 | LSVSD | 3.56 | 2017-06-29T21:40:00Z | 14 | 24 | DZRSD | 7.85 | 2017-06-29T21:20:00Z | 20 | 180 | Agent | < 25mph | 20
63 | SDG&E | 20170716IG01 | July | 16 | 2017 | 3 | 2017-07-16 | 11:53 | 32.829 | -117.136 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | BC | TCNSD | 3.83 | 2017-07-16T18:30:00Z | 13 | 51 | LJHSD | 6.11 | 2017-07-16T18:30:00Z | 14.99 | 226 | TCNSD | 3.83 | 2017-07-16T19:50:00Z | 14 | 98 | LJAC1 | 7.55 | 2017-07-16T19:42:00Z | 16.98 | 438 | Agent | < 25mph | 14.99
64 | SDG&E | 20170725IG01 | July | 25 | 2017 | 3 | 2017-07-25 | 15:18 | 33.1343 | -117.1666 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | No | Vandalism/Theft |  |  |  | Other | Non- HFTD | NE | E9915 | 3.56 | 2017-07-25T22:09:00Z | 17 | 63 | OLVSD | 4.31 | 2017-07-25T22:10:00Z | 18.99 | 196 | E9915 | 3.56 | 2017-07-25T22:54:00Z | 20 | 130 | E9915 | 3.56 | 2017-07-25T22:54:00Z | 20 | 397 | Agent | < 25mph | 18.99
65 | SDG&E | 20170728IG01 | July | 28 | 2017 | 3 | 2017-07-28 | 16:31 | 32.7802 | -116.8722 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Pole /Conductor | Vehicle | Electric Facility | Outside Force | Tier 2 | EA | DEHSD | 2.19 | 2017-07-28T22:50:00Z | 15.99 | 32 | OTYSD | 5.25 | 2017-07-28T22:50:00Z | 21 | 175 | DEHSD | 2.19 | 2017-07-28T22:50:00Z | 15.99 | 62 | OTYSD | 5.25 | 2017-07-28T22:50:00Z | 21 | 352 | Agent | < 25mph | 21
66 | SDG&E | 20170820IG01 | August | 20 | 2017 | 3 | 2017-08-20 | 22:15 | 32.7522 | -117.1184 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 4kV | Overhead | Yes | Equipment/Facility Failure | Fuse |  |  | None | Non- HFTD | CM | E8360 | 2.44 | 2017-08-21T04:19:00Z | 8.01 | 56 | E8360 | 2.44 | 2017-08-21T04:19:00Z | 8.01 | 177 | E8360 | 2.44 | 2017-08-21T04:19:00Z | 8.01 | 113 | E8360 | 2.44 | 2017-08-21T04:19:00Z | 8.01 | 354 | Equipment | < 25mph | 8.01
67 | SDG&E | 20170830IG01 | August | 30 | 2017 | 3 | 2017-08-30 | 14:12 | 33.3875 | -117.2459 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Other | Tier 2 | NE | FBZCA | 2.35 | 2017-08-30T20:22:00Z | 17 | 30 | FBZCA | 2.35 | 2017-08-30T20:22:00Z | 17 | 63 | FBZCA | 2.35 | 2017-08-30T21:22:00Z | 22.01 | 54 | FBZCA | 2.35 | 2017-08-30T21:22:00Z | 22.01 | 123 | Agent | < 25mph | 17
68 | SDG&E | 20170905IG01 | September | 5 | 2017 | 3 | 2017-09-05 | 14:49 | 32.6191 | -116.6949 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Unknown | Tier 3 | ME | BRJSD | 1.34 | 2017-09-05T21:40:00Z | 23 | 13 | BRJSD | 1.34 | 2017-09-05T21:40:00Z | 23 | 56 | BRJSD | 1.34 | 2017-09-05T22:30:00Z | 24.99 | 26 | SVLSD | 7.04 | 2017-09-05T22:20:00Z | 24.99 | 112 | Vegetation | < 25mph | 23
69 | SDG&E | 20170927IG01 | September | 27 | 2017 | 3 | 2017-09-27 | 14:28 | 33.2327 | -116.9748 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Unknown |  |  |  | Unknown | Tier 2 | NE | RCRSD | 1.66 | 2017-09-27T21:20:00Z | 21 | 58 | RCRSD | 1.66 | 2017-09-27T21:20:00Z | 21 | 170 | RCRSD | 1.66 | 2017-09-27T21:20:00Z | 21 | 116 | RCRSD | 1.66 | 2017-09-27T21:20:00Z | 21 | 340 | Unknown | < 25mph | 21
70 | SDG&E | 20170927IG02 | September | 27 | 2017 | 3 | 2017-09-27 | 16:10 | 32.7272 | -116.7788 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | None | Tier 3 | EA | DHVSD | 2.94 | 2017-09-27T22:50:00Z | 18.99 | 29 | SVLSD | 4.46 | 2017-09-27T22:30:00Z | 24.99 | 191 | DHVSD | 2.94 | 2017-09-27T22:50:00Z | 18.99 | 53 | SVLSD | 4.46 | 2017-09-27T22:30:00Z | 24.99 | 363 | Equipment | < 25mph | 24.99
71 | SDG&E | 20171007IG01 | October | 7 | 2017 | 4 | 2017-10-07 | 17:40 | 32.5914 | -116.6216 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Conductor |  |  | Other | Tier 3 | ME | BRJSD | 3.74 | 2017-10-08T00:30:00Z | 20 | 36 | BRJSD | 3.74 | 2017-10-08T00:30:00Z | 20 | 44 | BRJSD | 3.74 | 2017-10-08T00:30:00Z | 20 | 67 | BRJSD | 3.74 | 2017-10-08T00:30:00Z | 20 | 82 | Equipment | < 25mph | 20
72 | SDG&E | 20171016IG01 | October | 16 | 2017 | 4 | 2017-10-16 | 10:20 | 33.0697 | -116.8813 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | RA | SSOSD | 3.93 | 2017-10-16T16:40:00Z | 10 | 74 | STVSD | 6.92 | 2017-10-16T17:00:00Z | 12.01 | 166 | SSOSD | 3.93 | 2017-10-16T18:00:00Z | 14 | 166 | SSOSD | 3.93 | 2017-10-16T18:00:00Z | 14 | 341 | Agent | < 25mph | 12.01
73 | SDG&E | 20171018IG01 | October | 18 | 2017 | 4 | 2017-10-18 | 7:20 | 33.1659 | -117.2053 | Vegetation | Urban | Less Than .25 Acres | Unknown | 12kV | Overhead | No | Contact From Object |  | Vehicle | Pole | Human Error | Non- HFTD | NC | E9957 | 1.71 | 2017-10-18T14:15:00Z | 8.99 | 51 | OLVSD | 7.37 | 2017-10-18T13:50:00Z | 12.01 | 171 | E9957 | 1.71 | 2017-10-18T14:15:00Z | 8.99 | 102 | OLVSD | 7.37 | 2017-10-18T13:50:00Z | 12.01 | 338 | Agent | < 25mph | 12.01
74 | SDG&E | 20171022IG01 | October | 22 | 2017 | 4 | 2017-10-22 | 10:22 | 33.099 | -117.135 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Tier 2 | NE | HDMSD | 3.87 | 2017-10-22T17:20:00Z | 11.01 | 58 | WRBSD | 4.74 | 2017-10-22T16:30:00Z | 13 | 258 | HDMSD | 3.87 | 2017-10-22T17:20:00Z | 11.01 | 116 | WRBSD | 4.74 | 2017-10-22T16:30:00Z | 13 | 510 | Agent | < 25mph | 13
75 | SDG&E | 20171025IG01 | October | 25 | 2017 | 4 | 2017-10-25 | 13:02 | 33.2857 | -117.0275 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Other |  |  | Weather | Tier 2 | NE | LLCSD | 2.48 | 2017-10-25T19:50:00Z | 14.99 | 62 | HP014 | 7.08 | 2017-10-25T19:57:00Z | 18.34 | 172 | FTVSD | 3.33 | 2017-10-25T20:40:00Z | 18.01 | 123 | HP014 | 7.08 | 2017-10-25T20:47:00Z | 20.36 | 344 | Equipment | < 25mph | 18.34
76 | SDG&E | 20171210IG01 | December | 10 | 2017 | 4 | 2017-12-10 | 5:26 | 33.28 | -116.955 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 3 | NE | HF001 | 3.81 | 2017-12-10T13:15:00Z | 54.67 | 58 | HHCSD | 4.25 | 2017-12-10T13:00:00Z | 77 | 148 | HF001 | 3.81 | 2017-12-10T13:30:00Z | 55.92 | 116 | HHCSD | 4.25 | 2017-12-10T13:00:00Z | 77 | 296 | Vegetation | 55mph+ | 77
77 | SDG&E | 20171210IG02 | December | 10 | 2017 | 4 | 2017-12-10 | 2:58 | 33.2739 | -116.9537 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Tier 3 | NE | HHCSD | 3.84 | 2017-12-10T10:10:00Z | 68 | 54 | HHCSD | 3.84 | 2017-12-10T10:10:00Z | 68 | 142 | HHCSD | 3.84 | 2017-12-10T11:30:00Z | 68.99 | 108 | HHCSD | 3.84 | 2017-12-10T11:30:00Z | 68.99 | 284 | Equipment | 55mph+ | 68
78 | SDG&E | 20180208IG01 | February | 8 | 2018 | 1 | 2018-02-08 | 10:07 | 33.2071 | -117.2072 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Human Error | Non- HFTD | NC | TWOSD | 3.27 | 2018-02-08T17:30:00Z | 11.01 | 30 | CIRSD | 6.48 | 2018-02-08T17:40:00Z | 12.01 | 113 | VISSD | 2.7 | 2018-02-08T18:30:00Z | 12.01 | 60 | VISSD | 2.7 | 2018-02-08T18:30:00Z | 12.01 | 225 | Vegetation | < 25mph | 12.01
79 | SDG&E | 20180216IG01 | February | 16 | 2018 | 1 | 2018-02-16 | 16:50 | 32.6276 | -116.9409 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Outside Force | Tier 2 | CM | RODB1 | 2.12 | 2018-02-17T00:00:00Z | 15.61 | 11 | OTMSD | 6 | 2018-02-17T00:40:00Z | 24.99 | 92 | RODB1 | 2.12 | 2018-02-17T00:00:00Z | 15.61 | 21 | OTMSD | 6 | 2018-02-17T00:40:00Z | 24.99 | 174 | Agent | < 25mph | 24.99
80 | SDG&E | 20180412IG01 | April | 12 | 2018 | 2 | 2018-04-12 | 19:33 | 32.6965 | -117.0493 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | CM | F1077 | 3.65 | 2018-04-13T02:27:00Z | 14.99 | 32 | E8360 | 7.77 | 2018-04-13T01:51:00Z | 24.99 | 160 | F1077 | 3.65 | 2018-04-13T02:27:00Z | 14.99 | 64 | E8360 | 7.77 | 2018-04-13T01:51:00Z | 24.99 | 320 | Agent | < 25mph | 24.99
81 | SDG&E | 20180416IG01 | April | 16 | 2018 | 2 | 2018-04-16 | 14:24 | 33.4176 | -117.6058 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | Weather | Non- HFTD | OC | SCRSD | 1.58 | 2018-04-16T21:20:00Z | 25.99 | 86 | TEOC1 | 4.69 | 2018-04-16T21:22:00Z | 28.01 | 105 | SCRSD | 1.58 | 2018-04-16T22:10:00Z | 30 | 170 | SCRSD | 1.58 | 2018-04-16T22:10:00Z | 30 | 208 | Vegetation | 25-40mph | 28.01
82 | SDG&E | 20180422IG01 | April | 22 | 2018 | 2 | 2018-04-22 | 14:00 | 32.837 | -117.184 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | BC | TCNSD | 3.17 | 2018-04-22T20:10:00Z | 14.99 | 44 | MTLSD | 7.42 | 2018-04-22T20:00:00Z | 23 | 157 | MPESD | 3.91 | 2018-04-22T22:00:00Z | 15.99 | 83 | MTLSD | 7.42 | 2018-04-22T20:00:00Z | 23 | 302 | Agent | < 25mph | 23
83 | SDG&E | 20180522IG01 | May | 22 | 2018 | 2 | 2018-05-22 | 14:23 | 33.362 | -117.032 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | NE | PMASD | 3.8 | 2018-05-22T21:20:00Z | 18.99 | 24 | FBKSD | 7.83 | 2018-05-22T21:20:00Z | 20 | 122 | PMASD | 3.8 | 2018-05-22T21:30:00Z | 18.99 | 48 | PZAC1 | 4.26 | 2018-05-22T21:50:00Z | 23 | 242 | Agent | < 25mph | 20
84 | SDG&E | 20180601IG01 | June | 1 | 2018 | 2 | 2018-06-01 | 14:00 | 33.099 | -117.044 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | No | Wire-Wire Contact |  |  |  | Other | Non- HFTD | NE | PSQC1 | 1.91 | 2018-06-01T20:50:00Z | 15.99 | 32 | HVYSD | 7.93 | 2018-06-01T21:00:00Z | 21 | 144 | HVWSD | 3.82 | 2018-06-01T21:30:00Z | 17 | 63 | HVYSD | 7.93 | 2018-06-01T21:00:00Z | 21 | 278 | Equipment | < 25mph | 21
85 | SDG&E | 20180612IG01 | June | 12 | 2018 | 2 | 2018-06-12 | 9:00 | 32.706 | -116.396 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | ME | CWDSD | 1.65 | 2018-06-12T16:00:00Z | 8.01 | 14 | BVDSD | 6.93 | 2018-06-12T15:50:00Z | 15.99 | 50 | CWDSD | 1.65 | 2018-06-12T17:00:00Z | 11.01 | 26 | BVDSD | 6.93 | 2018-06-12T15:50:00Z | 15.99 | 93 | Agent | < 25mph | 15.99
86 | SDG&E | 20180612IG02 | June | 12 | 2018 | 2 | 2018-06-12 | 15:14 | 32.864 | -116.747 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact from Object |  | Balloons | Electric Facility | None | Tier 3 | EA | VJSSD | 2.69 | 2018-06-12T22:10:00Z | 18.01 | 44 | VJSSD | 2.69 | 2018-06-12T22:10:00Z | 18.01 | 135 | VJSSD | 2.69 | 2018-06-12T22:10:00Z | 18.01 | 88 | VJSSD | 2.69 | 2018-06-12T22:10:00Z | 18.01 | 271 | Agent | < 25mph | 18.01
87 | SDG&E | 20180622IG01 | June | 22 | 2018 | 2 | 2018-06-22 | 9:46 | 32.567 | -116.941 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | Unknown | Tier 2 | CM | OMBSD | 2.44 | 2018-06-22T16:40:00Z | 10 | 12 | CVXSD | 7.22 | 2018-06-22T16:40:00Z | 10 | 36 | OMBSD | 2.44 | 2018-06-22T17:20:00Z | 13 | 24 | OMBSD | 2.44 | 2018-06-22T17:20:00Z | 13 | 71 | Equipment | < 25mph | 10
88 | SDG&E | 20180629IG01 | June | 29 | 2018 | 2 | 2018-06-29 | 13:06 | 32.645 | -117.056 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Unknown | Non- HFTD | CM | E9888 | 0.83 | 2018-06-29T20:04:00Z | 20 | 34 | BFDSD | 7.5 | 2018-06-29T19:50:00Z | 22.01 | 97 | CVXSD | 3 | 2018-06-29T20:50:00Z | 21 | 68 | MIGSD | 5.16 | 2018-06-29T20:10:00Z | 24 | 190 | Equipment | < 25mph | 22.01
89 | SDG&E | 20180706IG01 | July | 6 | 2018 | 3 | 2018-07-06 | 10:26 | 32.6203 | -116.7649 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Transformer |  |  |  | Tier 3 | ME | DZRSD | 0.55 | 2018-07-06T16:40:00Z | 22.01 | 6 | RPOSD | 8 | 2018-07-06T16:40:00Z | 38.99 | 50 | DZRSD | 0.55 | 2018-07-06T18:00:00Z | 24.99 | 12 | RPOSD | 8 | 2018-07-06T17:30:00Z | 41 | 100 | Equipment | 25-40mph | 38.99
90 | SDG&E | 20180708IG01 | July | 8 | 2018 | 3 | 2018-07-08 | 16:16 | 32.6349 | -117.103 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Other | Non- HFTD | CM | E9888 | 2.24 | 2018-07-08T23:05:00Z | 11.01 | 28 | BFDSD | 6.43 | 2018-07-08T22:20:00Z | 13 | 71 | E9888 | 2.24 | 2018-07-08T23:05:00Z | 11.01 | 51 | D7030 | 7.49 | 2018-07-08T23:57:00Z | 14 | 142 | Unknown | < 25mph | 13
91 | SDG&E | 20180722IG01 | July | 22 | 2018 | 3 | 2018-07-22 | 23:19 | 33.301 | -116.351 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | None | Non- HFTD | RA | UCI13 | 1.94 | 2018-07-23T06:00:00Z | 29.37 | 15 | UCI14 | 4.06 | 2018-07-23T06:00:00Z | 33.55 | 23 | UCI13 | 1.94 | 2018-07-23T06:00:00Z | 29.37 | 23 | UCI14 | 4.06 | 2018-07-23T07:00:00Z | 34.4 | 39 | Vegetation | 25-40mph | 33.55
92 | SDG&E | 20180730IG01 | July | 30 | 2018 | 3 | 2018-07-30 | 12:11 | 32.8681 | -117.1902 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | BC | LJHSD | 3.31 | 2018-07-30T19:00:00Z | 18.99 | 43 | LJHSD | 3.31 | 2018-07-30T19:00:00Z | 18.99 | 134 | LJHSD | 3.31 | 2018-07-30T19:40:00Z | 20 | 127 | MTLSD | 7.97 | 2018-07-30T19:20:00Z | 21 | 356 | Agent | < 25mph | 18.99
93 | SDG&E | 20180809IG01 | August | 9 | 2018 | 3 | 2018-08-09 | 12:00 | 33.213 | -117.335 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Other |  |  | Other | Non- HFTD | NC | WIRC1 | 2.46 | 2018-08-09T18:23:00Z | 15.99 | 18 | KNFG | 6.43 | 2018-08-09T18:55:00Z | 18.41 | 51 | WIRC1 | 2.46 | 2018-08-09T19:23:00Z | 17 | 34 | KNFG | 6.43 | 2018-08-09T18:55:00Z | 18.41 | 97 | Equipment | < 25mph | 18.41
94 | SDG&E | 20180819IG01 | August | 19 | 2018 | 3 | 2018-08-19 | 18:35 | 32.7002 | -116.8639 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | EA | OTYSD | 3.97 | 2018-08-20T00:50:00Z | 15.99 | 17 | OTYSD | 3.97 | 2018-08-20T00:50:00Z | 15.99 | 95 | OTYSD | 3.97 | 2018-08-20T00:50:00Z | 15.99 | 33 | OTYSD | 3.97 | 2018-08-20T00:50:00Z | 15.99 | 187 | Agent | < 25mph | 15.99
95 | SDG&E | 20180914IG01 | September | 14 | 2018 | 3 | 2018-09-14 | 15:02 | 32.7897 | -117.0809 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure |  |  |  | None | Non- HFTD | EA | MTLSD | 3.9 | 2018-09-14T21:10:00Z | 21 | 58 | MTLSD | 3.9 | 2018-09-14T21:10:00Z | 21 | 142 | MTLSD | 3.9 | 2018-09-14T22:20:00Z | 21 | 114 | MTLSD | 3.9 | 2018-09-14T22:20:00Z | 21 | 281 | Equipment | < 25mph | 21
96 | SDG&E | 20180914IG02 | September | 14 | 2018 | 3 | 2018-09-14 | 10:00 | 33.3177 | -117.2228 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact Between Third Party Facility on Pole and Supply Lines |  | Vehicle | Communication Facility | Human Error | Tier 2 | NE | E5843 | 3.81 | 2018-09-14T16:30:00Z | 4 | 12 | SE073 | 7.49 | 2018-09-14T17:00:00Z | 8.01 | 88 | E5843 | 3.81 | 2018-09-14T18:00:00Z | 8.01 | 24 | PZAC1 | 7.39 | 2018-09-14T17:50:00Z | 13 | 168 | Agent | < 25mph | 8.01
97 | SDG&E | 20181015IG01 | October | 15 | 2018 | 4 | 2018-10-15 | 10:21 | 33.3191 | -117.2597 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure |  |  |  | None | Tier 2 | NE | KL18 | 2.48 | 2018-10-15T16:55:00Z | 39.12 | 20 | FBZC1 | 4.65 | 2018-10-15T16:22:00Z | 45.99 | 81 | KL18 | 2.48 | 2018-10-15T16:55:00Z | 39.12 | 40 | FBZC1 | 4.65 | 2018-10-15T17:22:00Z | 47 | 163 | Equipment | 40-55mph | 45.99
98 | SDG&E | 20181126IG01 | November | 26 | 2018 | 4 | 2018-11-26 | 1:51 | 33.4314 | -117.5952 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility |  | Tier 2 | OC | SCRSD | 0.45 | 2018-11-26T09:10:00Z | 8.99 | 37 | TLGSD | 7.13 | 2018-11-26T09:40:00Z | 23 | 58 | SCRSD | 0.45 | 2018-11-26T09:10:00Z | 8.99 | 73 | TLGSD | 7.13 | 2018-11-26T09:40:00Z | 23 | 115 | Agent | < 25mph | 23
99 | SDG&E | 20190116IG01 | January | 16 | 2019 | 1 | 2019-01-16 | 16:55 | 33.421 | -117.61 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12 kV | Overhead | No | Equipment/Facility Failure | Crossarm |  |  | Weather | Non- HFTD | OC | F1327 | 0.65 | 2019-01-17T00:00:00Z | 14 | 40 | C2978 | 4.17 | 2019-01-17T00:38:00Z | 18.99 | 59 | F1327 | 0.65 | 2019-01-17T00:00:00Z | 14 | 78 | C2978 | 4.17 | 2019-01-17T00:38:00Z | 18.99 | 116 | Equipment | < 25mph | 18.99
100 | SDG&E | 20190415IG01 | April | 15 | 2019 | 2 | 2019-04-15 | 14:05 | 32.7883 | -116.8896 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12 kV | Overhead | Yes | Wire-Wire Contact |  |  |  | Outside Force | Non- HFTD | EA | DEHSD | 3.16 | 2019-04-15T20:50:00Z | 15.99 | 26 | SQTSD | 6.44 | 2019-04-15T21:00:00Z | 18.01 | 205 | DEHSD | 3.16 | 2019-04-15T21:50:00Z | 18.99 | 52 | SQTSD | 6.44 | 2019-04-15T22:00:00Z | 22.01 | 407 | Equipment | < 25mph | 18.01
101 | SDG&E | 20190612IG01 | June | 12 | 2019 | 2 | 2019-06-12 | 22:05 | 33.0484 | -116.8578 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12 kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | None | Tier 2 | RA | BLCSD | 3.88 | 2019-06-13T04:50:00Z | 4 | 60 | SPVSD | 6.4 | 2019-06-13T04:50:00Z | 8.99 | 138 | AR771 | 2.65 | 2019-06-13T05:24:00Z | 4.99 | 118 | SPVSD | 6.4 | 2019-06-13T04:50:00Z | 8.99 | 274 | Agent | < 25mph | 8.99
102 | SDG&E | 20190703IG01 | July | 3 | 2019 | 3 | 2019-07-03 | 15:15 | 33.0113 | -116.8492 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 3 | RA | SPPSD | 3.6 | 2019-07-03T22:10:00Z | 18.01 | 24 | HP005 | 7.05 | 2019-07-03T22:13:00Z | 20.13 | 112 | SPPSD | 3.6 | 2019-07-03T22:40:00Z | 18.01 | 48 | HP005 | 7.05 | 2019-07-03T22:43:00Z | 22.37 | 215 | Equipment | < 25mph | 20.13
103 | SDG&E | 20190705IG01 | July | 5 | 2019 | 3 | 2019-07-05 | 12:32 | 33.1584 | -117.222 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 2 | NC | E9957 | 2.38 | 2019-07-05T19:25:00Z | 13 | 45 | OLVSD | 7.61 | 2019-07-05T19:10:00Z | 17 | 169 | E9957 | 2.38 | 2019-07-05T20:30:00Z | 13 | 91 | OLVSD | 7.61 | 2019-07-05T20:20:00Z | 18.99 | 335 | Agent | < 25mph | 17
104 | SDG&E | 20190716IG01 | July | 16 | 2019 | 3 | 2019-07-16 | 19:08 | 33.182 | -117.1126 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Other | Tier 2 | NE | ESCSD | 3.61 | 2019-07-17T01:20:00Z | 13 | 42 | SMCSD | 5.88 | 2019-07-17T01:30:00Z | 14 | 176 | ESCSD | 3.61 | 2019-07-17T01:20:00Z | 13 | 82 | SMCSD | 5.88 | 2019-07-17T01:30:00Z | 14 | 350 | Equipment | < 25mph | 14
105 | SDG&E | 20190716IG02 | July | 16 | 2019 | 3 | 2019-07-16 | 7:36 | 33.1675 | -117.1462 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Wire-Wire Contact |  |  |  | Other | Tier 2 | NE | SMCSD | 3.76 | 2019-07-16T14:30:00Z | 3 | 34 | TLKSD | 5.74 | 2019-07-16T14:00:00Z | 7 | 167 | E9957 | 2.37 | 2019-07-16T15:35:00Z | 4.99 | 69 | TLKSD | 5.74 | 2019-07-16T14:00:00Z | 7 | 333 | Equipment | < 25mph | 7
106 | SDG&E | 20190805IG01 | August | 5 | 2019 | 3 | 2019-08-05 | 14:14 | 32.7886 | -117.1233 | Vegetation | Urban | Less Than .25 Acres | Utility | 12 kV | Overhead | No | Equipment/Facility Failure | Other |  |  | None | Non- HFTD | BC | MVNSD | 0.97 | 2019-08-05T21:10:00Z | 15.48 | 42 | LJHSD | 7.78 | 2019-08-05T20:40:00Z | 19.95 | 233 | TCNSD | 3.54 | 2019-08-05T21:20:00Z | 15.99 | 85 | LJHSD | 7.78 | 2019-08-05T20:40:00Z | 19.95 | 465 | Equipment | < 25mph | 19.95
107 | SDG&E | 20190910IG01 | September | 10 | 2019 | 3 | 2019-09-10 | 12:59 | 32.5638 | -117.0333 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | None | Tier 2 | CM | BFDSD | 3.99 | 2019-09-10T19:30:00Z | 21.41 | 13 | BFDSD | 3.99 | 2019-09-10T19:30:00Z | 21.41 | 44 | BFDSD | 3.99 | 2019-09-10T19:30:00Z | 21.41 | 25 | BFDSD | 3.99 | 2019-09-10T19:30:00Z | 21.41 | 87 | Equipment | < 25mph | 21.41
108 | SDG&E | 20190911IG01 | September | 11 | 2019 | 3 | 2019-09-11 | 14:17 | 33.226 | -117.085 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 2 | NE | HMDSD | 0.53 | 2019-09-11T20:50:00Z | 17 | 40 | ESCSD | 4.23 | 2019-09-11T21:00:00Z | 18.99 | 148 | HMDSD | 0.53 | 2019-09-11T20:50:00Z | 17 | 80 | ESCSD | 4.23 | 2019-09-11T22:10:00Z | 22.01 | 295 | Agent | < 25mph | 18.99
109 | SDG&E | 20190913IG01 | September | 13 | 2019 | 3 | 2019-09-13 | 11:27 | 32.787 | -117.007 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | EA | E4521 | 2.22 | 2019-09-13T18:00:00Z | 14 | 51 | MTLSD | 4.78 | 2019-09-13T18:20:00Z | 15.05 | 165 | E4521 | 2.22 | 2019-09-13T19:15:00Z | 14.99 | 102 | OTYSD | 6.52 | 2019-09-13T19:00:00Z | 16.73 | 329 | Equipment | < 25mph | 15.05
110 | SDG&E | 20190930IG01 | September | 30 | 2019 | 3 | 2019-09-30 | 2:59 | 33.2618 | -116.3705 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Other | Non- HFTD | RA | UCI10 | 3.52 | 2019-09-30T09:00:00Z | 26.08 | 27 | UCI11 | 7.36 | 2019-09-30T09:00:00Z | 29.24 | 42 | UCI10 | 3.52 | 2019-09-30T09:00:00Z | 26.08 | 42 | UCI11 | 7.36 | 2019-09-30T09:00:00Z | 29.24 | 71 | Equipment | 25-40mph | 29.24
111 | SDG&E | 20191017IG01 | October | 17 | 2019 | 4 | 2019-10-17 | 12:15 | 33.2736 | -116.3931 | Vegetation | Urban | Less Than .25 Acres | Utility | 120/240 | Overhead | No | Other |  |  |  | Human Error | Non- HFTD | RA | UCAB | 1.39 | 2019-10-17T18:40:00Z | 24.9 | 25 | RCHC1 | 7 | 2019-10-17T19:07:00Z | 37 | 28 | UCI08 | 2.33 | 2019-10-17T20:00:00Z | 28.86 | 50 | UCI11 | 6.85 | 2019-10-17T20:00:00Z | 51.2 | 59 | Agent | 25-40mph | 37
112 | SDG&E | 20191019IG01 | October | 19 | 2019 | 4 | 2019-10-19 | 13:10 | 33.2317 | -117.2593 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 240V | Overhead | Yes | Other |  |  |  | Human Error | Non- HFTD | NC | AT125 | 1.07 | 2019-10-19T20:08:00Z | 14 | 31 | AT125 | 1.07 | 2019-10-19T20:08:00Z | 14 | 103 | AT125 | 1.07 | 2019-10-19T20:08:00Z | 14 | 61 | E9957 | 7.16 | 2019-10-19T21:10:00Z | 14 | 199 | Agent | < 25mph | 14
113 | SDG&E | 20191024IG01 | October | 24 | 2019 | 4 | 2019-10-24 | 10:16 | 32.8357 | -116.7252 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Fuse |  |  | None | Tier 3 | ME | ANEC1 | 3.11 | 2019-10-24T16:52:00Z | 53.02 | 64 | ANEC1 | 3.11 | 2019-10-24T16:52:00Z | 53.02 | 155 | ANEC1 | 3.11 | 2019-10-24T16:52:00Z | 53.02 | 127 | ANEC1 | 3.11 | 2019-10-24T16:52:00Z | 53.02 | 309 | Equipment | 40-55mph | 53.02
115 | SDG&E | 20191101IG01 | November | 1 | 2019 | 4 | 2019-11-01 | 5:49 | 33.0924 | -117.0206 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | None | Non- HFTD | NE | HVWSD | 2.49 | 2019-11-01T12:40:00Z | 7.96 | 33 | HDMSD | 7.44 | 2019-11-01T12:20:00Z | 21 | 177 | HVWSD | 2.49 | 2019-11-01T13:10:00Z | 8.68 | 62 | HDMSD | 7.44 | 2019-11-01T13:40:00Z | 21 | 350 | Agent | < 25mph | 21
116 | SDG&E | 20191104IG01 | November | 4 | 2019 | 4 | 2019-11-04 | 15:30 | 33.1969 | -116.7121 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Other |  |  |  | Tier 3 | RA | MGYSD | 1.96 | 2019-11-04T23:00:00Z | 15.99 | 27 | HP016 | 6.11 | 2019-11-04T22:55:00Z | 19.46 | 88 | MGYSD | 1.96 | 2019-11-04T23:00:00Z | 15.99 | 51 | HP016 | 6.11 | 2019-11-04T22:55:00Z | 19.46 | 166 | Equipment | < 25mph | 19.46
117 | SDG&E | 20191112IG01 | November | 12 | 2019 | 4 | 2019-11-12 | 7:51 | 33.1903 | -117.3698 | Other | Urban | Less Than .25 Acres | Fire Agency | 120/240 | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | NC | WIRC1 | 3.14 | 2019-11-12T15:23:00Z | 5.99 | 15 | WIRC1 | 3.14 | 2019-11-12T15:23:00Z | 5.99 | 45 | WIRC1 | 3.14 | 2019-11-12T15:23:00Z | 5.99 | 31 | WIRC1 | 3.14 | 2019-11-12T15:23:00Z | 5.99 | 91 | Equipment | < 25mph | 5.99
118 | SDG&E | 20200211IG01 | February | 11 | 2020 | 1 | 2020-02-11 | 1:30 | 32.791 | -116.9194 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Outside Force | Non- HFTD | EA | E4521 | 3.76 | 2020-02-11T09:16:00Z | 3 | 32 | COCSD | 4.37 | 2020-02-11T09:10:00Z | 7.96 | 170 | E4858 | 0.85 | 2020-02-11T10:16:00Z | 3 | 61 | EUCSD | 5.87 | 2020-02-11T10:00:00Z | 10.02 | 319 | Equipment | < 25mph | 7.96
119 | SDG&E | 20200226IG01 | February | 26 | 2020 | 1 | 2020-02-26 | 0:17 | 32.914 | -116.64 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 3 | ME | SILSD | 2.77 | 2020-02-26T08:10:00Z | 97.8 | 35 | SILSD | 2.77 | 2020-02-26T08:10:00Z | 97.8 | 95 | SILSD | 2.77 | 2020-02-26T08:50:00Z | 105.49 | 65 | SILSD | 2.77 | 2020-02-26T08:50:00Z | 105.49 | 184 | Equipment | 55mph+ | 97.8
120 | SDG&E | 20200517IG01 | May | 17 | 2020 | 2 | 2020-05-17 | 8:52 | 33.2373 | -117.0301 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons |  | Other | Tier 2 | NE | TLKSD | 2.75 | 2020-05-17T15:50:00Z | 7.96 | 76 | HHCSD | 6.23 | 2020-05-17T15:50:00Z | 8.05 | 195 | TLKSD | 2.75 | 2020-05-17T16:40:00Z | 9.8 | 148 | PCKSD | 6.93 | 2020-05-17T16:50:00Z | 10.58 | 386 | Agent | < 25mph | 8.05
121 | SDG&E | 20200531IG01 | May | 31 | 2020 | 2 | 2020-05-31 | 2:01 | 32.543 | -117.0277 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Outside Force | Non- HFTD | CM |  |  |  | 0 | 0 | AT526 | 6.25 | 2020-05-31T09:00:00Z | 5.99 | 38 |  |  |  | 0 | 0 | AT526 | 6.25 | 2020-05-31T09:00:00Z | 5.99 | 73 | Agent | < 25mph | 5.99
122 | SDG&E | 20200602IG01 | June | 2 | 2020 | 2 | 2020-06-02 | 18:00 | 33.07 | -116.863 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 3 | RA | GOSC1 | 1.28 | 2020-06-03T00:52:00Z | 13 | 61 | GOSC1 | 1.28 | 2020-06-03T00:52:00Z | 13 | 167 | GOSC1 | 1.28 | 2020-06-03T00:52:00Z | 13 | 115 | POVSD | 5.15 | 2020-06-03T01:30:00Z | 13.01 | 315 | Agent | < 25mph | 13
123 | SDG&E | 20200603IG01 | June | 3 | 2020 | 2 | 2020-06-03 | 11:17 | 33.1234 | -117.025 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | NE | ESCSD | 3.66 | 2020-06-03T18:00:00Z | 10.16 | 24 | ARHSD | 6.89 | 2020-06-03T18:10:00Z | 11.69 | 136 | ESCSD | 3.66 | 2020-06-03T19:10:00Z | 16.38 | 49 | ESCSD | 3.66 | 2020-06-03T19:10:00Z | 16.38 | 274 | Agent | < 25mph | 11.69
124 | SDG&E | 20200705IG01 | July | 5 | 2020 | 3 | 2020-07-05 | 14:08 | 33.0872 | -116.9856 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 3 | NE | ROCSD | 3.92 | 2020-07-05T20:10:00Z | 19.58 | 33 | E2652 | 7.21 | 2020-07-05T21:00:00Z | 24 | 165 | ROCSD | 3.92 | 2020-07-05T20:10:00Z | 19.58 | 65 | E2652 | 7.21 | 2020-07-05T21:00:00Z | 24 | 326 | Equipment | < 25mph | 24
125 | SDG&E | 20200717IG01 | July | 17 | 2020 | 3 | 2020-07-17 | 16:30 | 33.0904 | -116.5798 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | RA | HRPSD | 3.68 | 2020-07-17T22:40:00Z | 23.75 | 31 | HRPSD | 3.68 | 2020-07-17T22:40:00Z | 23.75 | 111 | HRPSD | 3.68 | 2020-07-18T00:00:00Z | 23.89 | 58 | HRPSD | 3.68 | 2020-07-18T00:00:00Z | 23.89 | 208 | Agent | < 25mph | 23.75
126 | SDG&E | 20200726IG01 | July | 26 | 2020 | 3 | 2020-07-26 | 0:00 | 32.819 | -116.9561 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Fuse |  |  | Unknown | Non- HFTD | EA | E4858 | 2.05 | 2020-07-26T06:01:00Z | 3 | 21 | SYCSD | 7.86 | 2020-07-26T06:00:00Z | 5.19 | 176 | E3619 | 3.52 | 2020-07-26T07:30:00Z | 4 | 38 | MTLSD | 6.04 | 2020-07-26T07:40:00Z | 7.89 | 334 | Equipment | < 25mph | 5.19
127 | SDG&E | 20200729IG01 | July | 29 | 2020 | 3 | 2020-07-29 | 17:14 | 32.737 | -116.875 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Tier 3 | EA | OTYSD | 3.28 | 2020-07-30T00:10:00Z | 16.07 | 33 | OTYSD | 3.28 | 2020-07-30T00:10:00Z | 16.07 | 189 | OTYSD | 3.28 | 2020-07-30T00:10:00Z | 16.07 | 67 | OTYSD | 3.28 | 2020-07-30T00:10:00Z | 16.07 | 380 | Equipment | < 25mph | 16.07
128 | SDG&E | 20200801IG01 | August | 1 | 2020 | 3 | 2020-08-01 | 11:11 | 32.631 | -116.174 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Other |  |  | Unknown | Tier 2 | ME | IKPSD | 3.26 | 2020-08-01T18:10:00Z | 17.54 | 6 | BVDSD | 7.02 | 2020-08-01T17:50:00Z | 20.02 | 13 | IKPSD | 3.26 | 2020-08-01T18:20:00Z | 20.31 | 12 | IKPSD | 3.26 | 2020-08-01T18:20:00Z | 20.31 | 26 | Equipment | < 25mph | 20.02
129 | SDG&E | 20200818IG01 | August | 18 | 2020 | 3 | 2020-08-18 | 13:16 | 32.6248 | -117.096 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | Unknown | Non- HFTD | CM | E9888 | 2.35 | 2020-08-18T19:40:00Z | 19 | 37 | BFDSD | 5.72 | 2020-08-18T19:20:00Z | 21.34 | 97 | DJZSD | 1.44 | 2020-08-18T20:20:00Z | 19.36 | 63 | F5316 | 7.44 | 2020-08-18T20:30:00Z | 23 | 174 | Equipment | < 25mph | 21.34
130 | SDG&E | 20200822IG01 | August | 22 | 2020 | 3 | 2020-08-22 | 13:38 | 33.0744 | -116.5773 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Secondary | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 3 | RA | VCMSD | 1.98 | 2020-08-22T20:30:00Z | 21.64 | 35 | VCMSD | 1.98 | 2020-08-22T20:30:00Z | 21.64 | 81 | VCMSD | 1.98 | 2020-08-22T20:50:00Z | 25.79 | 69 | VCMSD | 1.98 | 2020-08-22T20:50:00Z | 25.79 | 161 | Equipment | < 25mph | 21.64
131 | SDG&E | 20200831IG01 | August | 31 | 2020 | 3 | 2020-08-31 | 14:05 | 33.1128 | -117.0055 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Other | Tier 2 | NE | ROCSD | 2.95 | 2020-08-31T21:00:00Z | 19.73 | 25 | ROCSD | 2.95 | 2020-08-31T21:00:00Z | 19.73 | 163 | ROCSD | 2.95 | 2020-08-31T21:00:00Z | 19.73 | 49 | OLVSD | 7.53 | 2020-08-31T22:00:00Z | 20.24 | 324 | Agent | < 25mph | 19.73
132 | SDG&E | 20200902IG01 | September | 2 | 2020 | 3 | 2020-09-02 | 19:30 | 33.362 | -117.137 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Tier 3 | NE | PZAC1 | 1.8 | 2020-09-03T01:50:00Z | 14.99 | 46 | SE309 | 7.07 | 2020-09-03T01:50:00Z | 17.46 | 150 | PZAC1 | 1.8 | 2020-09-03T01:50:00Z | 14.99 | 87 | SE309 | 7.07 | 2020-09-03T01:50:00Z | 17.46 | 281 | Equipment | < 25mph | 17.46
133 | SDG&E | 20200904IG01 | September | 4 | 2020 | 3 | 2020-09-04 | 20:30 | 33.0658 | -116.8592 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Other | Tier 2 | RA | GOSC1 | 1.64 | 2020-09-05T02:52:00Z | 5.99 | 76 | HP016 | 7.14 | 2020-09-05T03:25:00Z | 9.17 | 191 | SOSSD | 3.05 | 2020-09-05T04:20:00Z | 6.35 | 143 | HP016 | 7.14 | 2020-09-05T03:25:00Z | 9.17 | 360 | Agent | < 25mph | 9.17
134 | SDG&E | 20200905IG01 | September | 5 | 2020 | 3 | 2020-09-05 | 14:30 | 33.066 | -116.859 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 120v | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Outside Force | Non- HFTD | EA | SOSSD | 3.05 | 2020-09-05T21:10:00Z | 37.41 | 75 | SOSSD | 3.05 | 2020-09-05T21:10:00Z | 37.41 | 190 | SOSSD | 3.05 | 2020-09-05T21:50:00Z | 40.04 | 143 | SOSSD | 3.05 | 2020-09-05T21:50:00Z | 40.04 | 360 | Vegetation | 25-40mph | 37.41
135 | SDG&E | 20200906IG01 | September | 6 | 2020 | 3 | 2020-09-06 | 23:00 | 33.0965 | -117.0237 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Transformer |  |  | None | Tier 2 | NE | MADSD | 3.87 | 2020-09-07T05:50:00Z | 3.07 | 31 | COHSD | 7.6 | 2020-09-07T05:50:00Z | 13.3 | 210 | MADSD | 3.87 | 2020-09-07T06:50:00Z | 4.32 | 58 | COHSD | 7.6 | 2020-09-07T07:00:00Z | 17.32 | 398 | Equipment | < 25mph | 13.3
138 | SDG&E | 20200917IG01 | September | 17 | 2020 | 3 | 2020-09-17 | 10:00 | 33.1101 | -117.2693 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Other |  |  | None | Non- HFTD | NC | D2370 | 3.48 | 2020-09-17T16:30:00Z | 7 | 51 | E8699 | 4.82 | 2020-09-17T16:28:00Z | 14.99 | 189 | CBDSD | 3.84 | 2020-09-17T18:00:00Z | 9.27 | 104 | E8699 | 4.82 | 2020-09-17T17:33:00Z | 17 | 363 | Equipment | < 25mph | 14.99
139 | SDG&E | 20200930IG01 | September | 30 | 2020 | 3 | 2020-09-30 | 10:45 | 33.0207 | -116.8783 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Secondary | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | RA | SOSSD | 3 | 2020-09-30T17:20:00Z | 11.62 | 72 | SSOSD | 5.28 | 2020-09-30T17:40:00Z | 14.17 | 180 | SOSSD | 3 | 2020-09-30T18:40:00Z | 19.87 | 144 | BRMSD | 6.41 | 2020-09-30T18:40:00Z | 22.5 | 359 | Equipment | < 25mph | 14.17
140 | SDG&E | 20201014IG01 | October | 14 | 2020 | 4 | 2020-10-14 | 15:05 | 33.027 | -116.889 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kv | Overhead | No | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 2 | RA | SOSSD | 3.55 | 2020-10-14T21:30:00Z | 18.71 | 72 | SOSSD | 3.55 | 2020-10-14T21:30:00Z | 18.71 | 179 | SOSSD | 3.55 | 2020-10-14T21:30:00Z | 18.71 | 145 | SOSSD | 3.55 | 2020-10-14T21:30:00Z | 18.71 | 359 | Equipment | < 25mph | 18.71
141 | SDG&E | 20201111IG01 | November | 11 | 2020 | 4 | 2020-11-11 | 9:51 | 32.678 | -116.86 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kv | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Unknown | Tier 3 | EA | JAMSD | 2.55 | 2020-11-11T17:50:00Z | 7.81 | 8 | HP002 | 5.78 | 2020-11-11T16:53:00Z | 13.65 | 74 | JAMSD | 2.55 | 2020-11-11T18:10:00Z | 9.64 | 16 | HP002 | 5.78 | 2020-11-11T16:53:00Z | 13.65 | 148 | Equipment | < 25mph | 13.65
142 | SDG&E | 20201130IG01 | November | 30 | 2020 | 4 | 2020-11-30 | 9:10 | 33.266 | -117.223 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 2 | NE | AT125 | 2.22 | 2020-11-30T16:45:00Z | 7 | 19 | E5843 | 7.34 | 2020-11-30T16:55:00Z | 11 | 116 | AT125 | 2.22 | 2020-11-30T16:45:00Z | 7 | 37 | E5843 | 7.34 | 2020-11-30T16:55:00Z | 11 | 223 | Equipment | < 25mph | 11
143 | SDG&E | 20201203IG01 | December | 3 | 2020 | 4 | 2020-12-03 | 11:56 | 33.176 | -117.1541 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Pole |  |  | Weather | Tier 2 | NE | TWOSD | 1.23 | 2020-12-03T19:30:00Z | 28.27 | 50 | ESCSD | 5.94 | 2020-12-03T19:10:00Z | 41.57 | 188 | TWOSD | 1.23 | 2020-12-03T19:30:00Z | 28.27 | 96 | ESCSD | 5.94 | 2020-12-03T19:10:00Z | 41.57 | 367 | Equipment | 40-55mph | 41.57

## SDGE_Ignitions_MC
OBJECTID | Company | Ignition ID | Month | Day | Year | Quarter | Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed by | Voltage (Volts) | Type | Was There an Outage | Suspected Initiating Event | Equipment /Facility Failure | Contact From Object | Facility Contacted | Contributing Factor | Tier | District | 4 mi / 1 hr |  |  |  |  | 8 mi / 1 hr |  |  |  |  | 4 mi / 2 hr |  |  |  |  | 8 mi / 2 hr |  |  |  |  | 8 mi / 1 hr
[25 empty] | Station | Dist | Time | MaxGust | Num | Station | Dist | Time | MaxGust | Num | Station | Dist | Time | MaxGust | Num | Station | Dist | Time | MaxGust | Num | Category
107 | SDG&E | 20190910IG01 | September | 10 | 2019 | 3 | 2019-09-10 | 12:59 | 32.5638 | -117.0333 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | None | Tier 2 | CM | BFDSD | 3.99 | 2020-08-03T02:00:00Z | 13.3 | 14 | OMBSD | 7.75 | 2020-08-03T01:30:00Z | 16.07 | 61 | BFDSD | 3.99 | 2020-08-03T02:00:00Z | 13.3 | 26 | OMBSD | 7.75 | 2020-08-03T01:30:00Z | 16.07 | 115 | < 25mph
117 | SDG&E | 20191112IG01 | November | 12 | 2019 | 4 | 2019-11-12 | 7:51 | 33.1903 | -117.3698 | Other | Urban | Less Than .25 Acres | Fire Agency | 120/240 | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | NC | E3370 | 0.14 | 2018-12-29T13:30:00Z | 15.99 | 28 | E3370 | 0.14 | 2018-12-29T13:30:00Z | 15.99 | 52 | E3370 | 0.14 | 2018-12-29T14:35:00Z | 15.99 | 57 | E3370 | 0.14 | 2018-12-29T14:35:00Z | 15.99 | 105 | < 25mph
33 | SDG&E | 20160212IG01 | February | 12 | 2016 | 1 | 2016-02-12 | 19:30 | 33.2427 | -116.9664 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Vandalism/Theft |  |  |  | Outside Force | Tier 3 | NE | RINSD | 3.17 | 2015-04-10T12:20:00Z | 5.99 | 44 | HP014 | 6.9 | 2015-04-10T11:30:00Z | 11.18 | 138 | RINSD | 3.17 | 2015-04-10T13:20:00Z | 5.99 | 90 | HP014 | 6.9 | 2015-04-10T11:30:00Z | 11.18 | 278 | < 25mph
27 | SDG&E | 20151226IG01 | December | 26 | 2015 | 4 | 2015-12-26 | 3:04 | 33.1323 | -117.0695 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | NE | D9718 | 1.71 | 2015-03-31T00:02:00Z | 8.99 | 32 | OLVSD | 5.01 | 2015-03-31T00:10:00Z | 17 | 148 | D9718 | 1.71 | 2015-03-31T00:02:00Z | 8.99 | 63 | OLVSD | 5.01 | 2015-03-31T00:10:00Z | 17 | 295 | < 25mph
97 | SDG&E | 20181015IG01 | October | 15 | 2018 | 4 | 2018-10-15 | 10:21 | 33.3191 | -117.2597 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure |  |  |  | None | Tier 2 | NE | KL18 | 2.48 | 2018-05-26T21:55:00Z | 20.71 | 19 | FBZCA | 4.6 | 2018-05-26T21:22:00Z | 24.99 | 75 | KL18 | 2.48 | 2018-05-26T21:55:00Z | 20.71 | 39 | FBZCA | 4.6 | 2018-05-26T22:22:00Z | 24.99 | 151 | < 25mph
101 | SDG&E | 20190612IG01 | June | 12 | 2019 | 2 | 2019-06-12 | 22:05 | 33.0484 | -116.8578 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12 kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | None | Tier 2 | RA | SSOSD | 3.13 | 2018-11-19T16:00:00Z | 24 | 62 | STVSD | 5.74 | 2018-11-19T16:00:00Z | 25.99 | 155 | SSOSD | 3.13 | 2018-11-19T16:50:00Z | 25.99 | 122 | STVSD | 5.74 | 2018-11-19T16:50:00Z | 30 | 298 | 25-40mph
105 | SDG&E | 20190716IG02 | July | 16 | 2019 | 3 | 2019-07-16 | 7:36 | 33.1675 | -117.1462 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Wire-Wire Contact |  |  |  | Other | Tier 2 | NE | E6321 | 3.62 | 2016-09-29T21:35:00Z | 13 | 37 | OLVSD | 6.11 | 2016-09-29T22:00:00Z | 17 | 156 | E6321 | 3.62 | 2016-09-29T21:35:00Z | 13 | 72 | OLVSD | 6.11 | 2016-09-29T22:40:00Z | 17 | 313 | < 25mph
118 | SDG&E | 20200211IG01 | February | 11 | 2020 | 1 | 2020-02-11 | 1:30 | 32.791 | -116.9194 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Outside Force | Non- HFTD | EA | ECJSD | 3.11 | 2020-03-28T07:50:00Z | 5.1 | 29 | ELMSD | 5.42 | 2020-03-28T07:50:00Z | 11.34 | 152 | ECJSD | 3.11 | 2020-03-28T07:50:00Z | 5.1 | 57 | ELMSD | 5.42 | 2020-03-28T07:50:00Z | 11.34 | 297 | < 25mph
72 | SDG&E | 20171016IG01 | October | 16 | 2017 | 4 | 2017-10-16 | 10:20 | 33.0697 | -116.8813 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | RA | GOSC1 | 1.04 | 2020-05-03T02:52:00Z | 11.01 | 54 | GOSC1 | 1.04 | 2020-05-03T02:52:00Z | 11.01 | 130 | GOSC1 | 1.04 | 2020-05-03T02:52:00Z | 11.01 | 109 | GOSC1 | 1.04 | 2020-05-03T02:52:00Z | 11.01 | 258 | < 25mph
44 | SDG&E | 20160711IG01 | July | 11 | 2016 | 3 | 2016-07-11 | 10:27 | 33.4531 | -117.3044 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility |  | Tier 2 | NE |  |  |  | 0 | 0 | SRUC1 | 6.25 | 2018-05-01T04:54:00Z | 18.01 | 39 |  |  |  | 0 | 0 | SRUC1 | 6.25 | 2018-05-01T04:54:00Z | 18.01 | 78 | < 25mph
55 | SDG&E | 20161112IG01 | November | 12 | 2016 | 4 | 2016-11-12 | 20:30 | 32.6227 | -116.9388 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  |  | Tier 2 | CM | RODB1 | 1.87 | 2016-07-19T20:50:00Z | 15.99 | 7 | OMBSD | 4.99 | 2016-07-19T20:50:00Z | 18.01 | 60 | RODB1 | 1.87 | 2016-07-19T22:10:00Z | 17.78 | 14 | OMBSD | 4.99 | 2016-07-19T22:00:00Z | 20 | 122 | < 25mph
105 | SDG&E | 20190716IG02 | July | 16 | 2019 | 3 | 2019-07-16 | 7:36 | 33.1675 | -117.1462 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Wire-Wire Contact |  |  |  | Other | Tier 2 | NE | SMCSD | 3.76 | 2015-12-09T04:20:00Z | 4 | 36 | TLKSD | 5.74 | 2015-12-09T04:10:00Z | 8.99 | 152 | TWOSD | 1.86 | 2015-12-09T05:40:00Z | 4.99 | 72 | TLKSD | 5.74 | 2015-12-09T05:40:00Z | 8.99 | 308 | < 25mph
29 | SDG&E | 20160109IG01 | January | 9 | 2016 | 1 | 2016-01-09 | 4:30 | 33.082 | -117.091 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Non- HFTD | NE | OLVSD | 2.24 | 2019-03-28T23:00:00Z | 20 | 38 | ESCSD | 6.6 | 2019-03-28T23:00:00Z | 23 | 163 | OLVSD | 2.24 | 2019-03-28T23:20:00Z | 24 | 76 | E9915 | 4.58 | 2019-03-28T23:45:00Z | 24 | 324 | < 25mph
118 | SDG&E | 20200211IG01 | February | 11 | 2020 | 1 | 2020-02-11 | 1:30 | 32.791 | -116.9194 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Outside Force | Non- HFTD | EA | E4521 | 3.76 | 2018-01-13T08:29:00Z | 5.99 | 37 | LLDSD | 7.68 | 2018-01-13T08:30:00Z | 32.99 | 221 | E4521 | 3.76 | 2018-01-13T10:14:00Z | 5.99 | 73 | LLDSD | 7.68 | 2018-01-13T08:30:00Z | 32.99 | 437 | 25-40mph
59 | SDG&E | 20170619IG01 | June | 19 | 2017 | 2 | 2017-06-19 | 9:52 | 32.7829 | -117.0488 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility |  | Non- HFTD | EA | CHOSD | 3.4 | 2016-09-07T05:20:00Z | 4.99 | 38 | E8360 | 6.59 | 2016-09-07T05:36:00Z | 8.01 | 142 | CHOSD | 3.4 | 2016-09-07T05:20:00Z | 4.99 | 74 | E8360 | 6.59 | 2016-09-07T05:36:00Z | 8.01 | 282 | < 25mph
98 | SDG&E | 20181126IG01 | November | 26 | 2018 | 4 | 2018-11-26 | 1:51 | 33.4314 | -117.5952 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility |  | Tier 2 | OC | CRISD | 3.92 | 2017-09-16T10:20:00Z | 3 | 28 | TEOC1 | 4.21 | 2017-09-16T10:22:00Z | 4 | 41 | CRISD | 3.92 | 2017-09-16T11:10:00Z | 3 | 64 | TEOC1 | 4.21 | 2017-09-16T10:22:00Z | 4 | 91 | < 25mph
1 | SDG&E | 20150211IG01 | February | 11 | 2015 | 1 | 2015-02-11 | 15:30 | 32.8941 | -116.9393 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | EA | BFDSD | 3.99 | 2019-02-02T05:10:00Z | 8.99 | 12 | BFDSD | 3.99 | 2019-02-02T05:10:00Z | 8.99 | 48 | BFDSD | 3.99 | 2019-02-02T06:10:00Z | 11.01 | 24 | BFDSD | 3.99 | 2019-02-02T06:10:00Z | 11.01 | 90 | < 25mph
20 | SDG&E | 20150901IG02 | September | 1 | 2015 | 3 | 2015-09-01 | 8:50 | 32.669 | -116.286 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | None | Tier 2 | ME | BVDSD | 0.5 | 2019-04-13T05:20:00Z | 12.01 | 14 | BVDSD | 0.5 | 2019-04-13T05:20:00Z | 12.01 | 28 | BVDSD | 0.5 | 2019-04-13T05:20:00Z | 12.01 | 26 | BVDSD | 0.5 | 2019-04-13T05:20:00Z | 12.01 | 52 | < 25mph
123 | SDG&E | 20200603IG01 | June | 3 | 2020 | 2 | 2020-06-03 | 11:17 | 33.1234 | -117.025 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | NE | ESCSD | 3.66 | 2015-07-19T18:00:00Z | 8.99 | 35 | ARHSD | 6.89 | 2015-07-19T17:00:00Z | 14 | 116 | ESCSD | 3.66 | 2015-07-19T19:00:00Z | 13 | 71 | OLVSD | 6.75 | 2015-07-19T18:50:00Z | 23 | 224 | < 25mph
93 | SDG&E | 20180809IG01 | August | 9 | 2018 | 3 | 2018-08-09 | 12:00 | 33.213 | -117.335 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Other |  |  | Other | Non- HFTD | NC | WIRC1 | 2.46 | 2018-02-09T10:23:00Z | 7 | 13 | WIRC1 | 2.46 | 2018-02-09T10:23:00Z | 7 | 55 | WIRC1 | 2.46 | 2018-02-09T11:23:00Z | 7 | 26 | CBDSD | 5.25 | 2018-02-09T10:40:00Z | 8.01 | 109 | < 25mph
6 | SDG&E | 20150413IG01 | April | 13 | 2015 | 2 | 2015-04-13 | 10:50 | 32.5859 | -117.0017 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Tier 2 | CM | BLCSD | 3.88 | 2017-08-07T10:20:00Z | 4 | 73 | HP005 | 7.1 | 2017-08-07T10:55:00Z | 9.17 | 168 | BLCSD | 3.88 | 2017-08-07T10:20:00Z | 4 | 126 | HP005 | 7.1 | 2017-08-07T12:05:00Z | 10.07 | 305 | < 25mph
16 | SDG&E | 20150813IG01 | August | 13 | 2015 | 3 | 2015-08-13 | 20:33 | 33.2457 | -116.6769 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Unknown |  |  |  | Unknown | Tier 2 | RA | F1327 | 1.71 | 2018-11-21T04:31:00Z | 8.01 | 38 | F1327 | 1.71 | 2018-11-21T04:31:00Z | 8.01 | 56 | F1327 | 1.71 | 2018-11-21T05:17:00Z | 8.99 | 74 | TEOC1 | 4.21 | 2018-11-21T05:22:00Z | 11.01 | 110 | < 25mph
102 | SDG&E | 20190703IG01 | July | 3 | 2019 | 3 | 2019-07-03 | 15:15 | 33.0113 | -116.8492 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 3 | RA | CESSD | 3.48 | 2016-12-26T09:30:00Z | 8.99 | 62 | WCKSD | 7.72 | 2016-12-26T10:00:00Z | 20 | 141 | CESSD | 3.48 | 2016-12-26T11:10:00Z | 10 | 124 | WCKSD | 7.72 | 2016-12-26T11:00:00Z | 23 | 282 | < 25mph
141 | SDG&E | 20201111IG01 | November | 11 | 2020 | 4 | 2020-11-11 | 9:51 | 32.678 | -116.86 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kv | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Unknown | Tier 3 | EA | JAMSD | 2.55 | 2016-06-30T09:40:00Z | 5.99 | 10 | DZRSD | 7.36 | 2016-06-30T10:00:00Z | 10 | 82 | JAMSD | 2.55 | 2016-06-30T09:40:00Z | 5.99 | 20 | DZRSD | 7.36 | 2016-06-30T10:50:00Z | 11.01 | 165 | < 25mph
33 | SDG&E | 20160212IG01 | February | 12 | 2016 | 1 | 2016-02-12 | 19:30 | 33.2427 | -116.9664 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Vandalism/Theft |  |  |  | Outside Force | Tier 3 | NE | FTVSD | 1.29 | 2018-01-02T16:30:00Z | 7 | 48 | CLNSD | 7.87 | 2018-01-02T16:40:00Z | 24 | 152 | HHCSD | 2.78 | 2018-01-02T17:40:00Z | 17 | 95 | CLNSD | 7.87 | 2018-01-02T16:40:00Z | 24 | 303 | < 25mph
79 | SDG&E | 20180216IG01 | February | 16 | 2018 | 1 | 2018-02-16 | 16:50 | 32.6276 | -116.9409 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Outside Force | Tier 2 | CM | F0551 | 2.19 | 2018-10-08T20:01:00Z | 14 | 10 | OTYSD | 6.44 | 2018-10-08T20:10:00Z | 23 | 91 | RODB1 | 2.12 | 2018-10-08T20:30:00Z | 14.25 | 20 | OTYSD | 6.44 | 2018-10-08T20:20:00Z | 23 | 178 | < 25mph
130 | SDG&E | 20200822IG01 | August | 22 | 2020 | 3 | 2020-08-22 | 13:38 | 33.0744 | -116.5773 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Secondary | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 3 | RA | VCMSD | 1.98 | 2020-11-14T21:10:00Z | 29.89 | 39 | VCMSD | 1.98 | 2020-11-14T21:10:00Z | 29.89 | 100 | VCMSD | 1.98 | 2020-11-14T21:10:00Z | 29.89 | 73 | VCMSD | 1.98 | 2020-11-14T21:10:00Z | 29.89 | 186 | 25-40mph
27 | SDG&E | 20151226IG01 | December | 26 | 2015 | 4 | 2015-12-26 | 3:04 | 33.1323 | -117.0695 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | NE | VCMSD | 1.98 | 2017-10-23T01:50:00Z | 24.99 | 52 | SHCSD | 6.16 | 2017-10-23T02:20:00Z | 34 | 128 | VCMSD | 1.98 | 2017-10-23T01:50:00Z | 24.99 | 96 | SHCSD | 6.16 | 2017-10-23T02:20:00Z | 34 | 240 | 25-40mph
43 | SDG&E | 20160702IG01 | July | 2 | 2016 | 3 | 2016-07-02 | 7:51 | 32.81 | -116.878 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Capacitor Bank |  |  | None | Tier 2 | EA | COCSD | 3.01 | 2015-07-22T00:20:00Z | 18.01 | 70 | OTYSD | 6.85 | 2015-07-22T00:10:00Z | 22.01 | 163 | COCSD | 3.01 | 2015-07-22T00:20:00Z | 18.01 | 146 | OTYSD | 6.85 | 2015-07-22T00:10:00Z | 22.01 | 332 | < 25mph
113 | SDG&E | 20191024IG01 | October | 24 | 2019 | 4 | 2019-10-24 | 10:16 | 32.8357 | -116.7252 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Fuse |  |  | None | Tier 3 | ME | EWRSD | 2.48 | 2020-07-25T19:10:00Z | 14.98 | 63 | SWRSD | 5.63 | 2020-07-25T19:30:00Z | 16.95 | 159 | ANEC1 | 3.11 | 2020-07-25T20:52:00Z | 17 | 126 | SWRSD | 5.63 | 2020-07-25T20:10:00Z | 18.06 | 319 | < 25mph
27 | SDG&E | 20151226IG01 | December | 26 | 2015 | 4 | 2015-12-26 | 3:04 | 33.1323 | -117.0695 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | NE | VCMSD | 1.98 | 2017-06-02T16:20:00Z | 27 | 41 | VCMSD | 1.98 | 2017-06-02T16:20:00Z | 27 | 106 | VCMSD | 1.98 | 2017-06-02T17:10:00Z | 31 | 81 | VCMSD | 1.98 | 2017-06-02T17:10:00Z | 31 | 211 | 25-40mph
17 | SDG&E | 20150815IG01 | August | 15 | 2015 | 3 | 2015-08-15 | 17:30 | 32.7417 | -116.9685 | Other | Urban | Less Than .25 Acres | Customer | 4Kv | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Non- HFTD | EA | SVCSD | 1.46 | 2015-06-08T03:10:00Z | 7 | 18 | ECJSD | 7.09 | 2015-06-08T02:40:00Z | 10 | 111 | SVCSD | 1.46 | 2015-06-08T03:10:00Z | 7 | 36 | ECJSD | 7.09 | 2015-06-08T02:40:00Z | 10 | 221 | < 25mph
115 | SDG&E | 20191101IG01 | November | 1 | 2019 | 4 | 2019-11-01 | 5:49 | 33.0924 | -117.0206 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | None | Non- HFTD | NE | HVWSD | 2.49 | 2018-08-17T14:20:00Z | 3 | 21 | ROCSD | 4.57 | 2018-08-17T14:30:00Z | 4.99 | 136 | SPVSD | 3.81 | 2018-08-17T15:30:00Z | 7 | 42 | WRBSD | 7.25 | 2018-08-17T15:00:00Z | 10 | 269 | < 25mph
7 | SDG&E | 20150418IG01 | April | 18 | 2015 | 2 | 2015-04-18 | 12:00 | 32.7764 | -116.9309 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Secondary | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | None | Non- HFTD | EA | E6321 | 3.62 | 2018-01-01T13:40:00Z | 7 | 47 | E9915 | 6.01 | 2018-01-01T13:12:00Z | 12.01 | 181 | E6321 | 3.62 | 2018-01-01T13:45:00Z | 7 | 93 | E9915 | 6.01 | 2018-01-01T13:12:00Z | 12.01 | 361 | < 25mph
96 | SDG&E | 20180914IG02 | September | 14 | 2018 | 3 | 2018-09-14 | 10:00 | 33.3177 | -117.2228 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact Between Third Party Facility on Pole and Supply Lines |  | Vehicle | Communication Facility | Human Error | Tier 2 | NE | E5843 | 3.81 | 2019-11-13T05:45:00Z | 1.01 | 11 | FBZC1 | 5.78 | 2019-11-13T06:22:00Z | 5.99 | 91 | E5843 | 3.81 | 2019-11-13T05:45:00Z | 1.01 | 22 | FBZC1 | 5.78 | 2019-11-13T06:22:00Z | 5.99 | 182 | < 25mph
97 | SDG&E | 20181015IG01 | October | 15 | 2018 | 4 | 2018-10-15 | 10:21 | 33.3191 | -117.2597 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure |  |  |  | None | Tier 2 | NE | AMOSD | 2.8 | 2018-10-11T06:20:00Z | 3 | 19 | FBZC1 | 4.65 | 2018-10-11T06:22:00Z | 5.99 | 76 | AMOSD | 2.8 | 2018-10-11T06:20:00Z | 3 | 36 | FBZC1 | 4.65 | 2018-10-11T06:22:00Z | 5.99 | 149 | < 25mph
18 | SDG&E | 20150823IG01 | August | 23 | 2015 | 3 | 2015-08-23 | 15:00 | 33.2729 | -117.1521 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | NE | BVDSD | 0.5 | 2020-12-27T03:00:00Z | 10.3 | 18 | BVDSD | 0.5 | 2020-12-27T03:00:00Z | 10.3 | 30 | BVDSD | 0.5 | 2020-12-27T04:40:00Z | 12.06 | 36 | BVDSD | 0.5 | 2020-12-27T04:40:00Z | 12.06 | 60 | < 25mph
56 | SDG&E | 20170120IG01 | January | 20 | 2017 | 1 | 2017-01-20 | 14:00 | 32.6274 | -117.0767 | Building | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Conductor | Vegetation | Pole | Weather | Non- HFTD | CM | CVXSD | 2.09 | 2020-09-09T13:10:00Z | 4.82 | 34 | MIGC1 | 7.2 | 2020-09-09T13:50:00Z | 7 | 80 | CVXSD | 2.09 | 2020-09-09T14:00:00Z | 5.19 | 67 | MIGC1 | 7.2 | 2020-09-09T13:50:00Z | 7 | 158 | < 25mph
36 | SDG&E | 20160311IG01 | March | 11 | 2016 | 1 | 2016-03-11 | 11:40 | 33.1563 | -117.2152 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Non- HFTD | NC | AMOSD | 2.8 | 2016-09-22T03:40:00Z | 5.99 | 14 | FBZCA | 4.6 | 2016-09-22T04:22:00Z | 10 | 75 | AMOSD | 2.8 | 2016-09-22T03:40:00Z | 5.99 | 28 | FBZCA | 4.6 | 2016-09-22T04:22:00Z | 10 | 149 | < 25mph
11 | SDG&E | 20150528IG01 | May | 28 | 2015 | 2 | 2015-05-28 | 12:45 | 32.7265 | -116.9922 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | EA |  |  |  | 0 | 0 | OTMSD | 5.78 | 2015-12-14T09:20:00Z | 41.99 | 54 |  |  |  | 0 | 0 | OTMSD | 5.78 | 2015-12-14T09:20:00Z | 41.99 | 108 | 40-55mph
34 | SDG&E | 20160218IG01 | February | 18 | 2016 | 1 | 2016-02-18 | 0:00 | 32.7063 | -116.397 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | None | Tier 3 | ME | E4521 | 2.78 | 2018-07-16T19:54:00Z | 17 | 42 | E4521 | 2.78 | 2018-07-16T19:54:00Z | 17 | 218 | E4521 | 2.78 | 2018-07-16T19:54:00Z | 17 | 83 | E4521 | 2.78 | 2018-07-16T19:54:00Z | 17 | 438 | < 25mph
111 | SDG&E | 20191017IG01 | October | 17 | 2019 | 4 | 2019-10-17 | 12:15 | 33.2736 | -116.3931 | Vegetation | Urban | Less Than .25 Acres | Utility | 120/240 | Overhead | No | Other |  |  |  | Human Error | Non- HFTD | RA | UCAB | 1.39 | 2017-11-22T14:20:00Z | 6.11 | 26 | RCHC1 | 7 | 2017-11-22T14:07:00Z | 18.01 | 32 | UCAB | 1.39 | 2017-11-22T14:50:00Z | 6.2 | 51 | RCHC1 | 7 | 2017-11-22T14:07:00Z | 18.01 | 63 | < 25mph
17 | SDG&E | 20150815IG01 | August | 15 | 2015 | 3 | 2015-08-15 | 17:30 | 32.7417 | -116.9685 | Other | Urban | Less Than .25 Acres | Customer | 4Kv | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Non- HFTD | EA | ELMSD | 3.12 | 2016-06-22T21:30:00Z | 18.01 | 18 | MTLSD | 7.68 | 2016-06-22T21:40:00Z | 23 | 112 | ELMSD | 3.12 | 2016-06-22T21:30:00Z | 18.01 | 36 | MTLSD | 7.68 | 2016-06-22T21:50:00Z | 23 | 220 | < 25mph
23 | SDG&E | 20150909IG01 | September | 9 | 2015 | 3 | 2015-09-09 | 20:40 | 32.644 | -117.072 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Non- HFTD | CM | SPPSD | 3.6 | 2017-05-06T03:40:00Z | 8.01 | 50 | HP005 | 7.05 | 2017-05-06T03:45:00Z | 16.33 | 125 | SPPSD | 3.6 | 2017-05-06T03:40:00Z | 8.01 | 88 | HP005 | 7.05 | 2017-05-06T03:45:00Z | 16.33 | 242 | < 25mph
115 | SDG&E | 20191101IG01 | November | 1 | 2019 | 4 | 2019-11-01 | 5:49 | 33.0924 | -117.0206 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | None | Non- HFTD | NE | SPVSD | 3.81 | 2020-12-20T05:30:00Z | 11.91 | 26 | HP005 | 6.46 | 2020-12-20T05:23:00Z | 22.14 | 205 | SPVSD | 3.81 | 2020-12-20T05:30:00Z | 11.91 | 51 | HP005 | 6.46 | 2020-12-20T06:23:00Z | 23.94 | 406 | < 25mph
3 | SDG&E | 20150409IG01 | April | 9 | 2015 | 2 | 2015-04-09 | 17:23 | 32.7233 | -116.8922 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Unknown |  |  |  |  | Tier 3 | EA | LHCSD | 1.6 | 2020-06-07T07:40:00Z | 11.69 | 61 | HP014 | 6.9 | 2020-06-07T08:25:00Z | 25.72 | 187 | LHCSD | 1.6 | 2020-06-07T07:40:00Z | 11.69 | 114 | HP014 | 6.9 | 2020-06-07T08:25:00Z | 25.72 | 366 | 25-40mph
72 | SDG&E | 20171016IG01 | October | 16 | 2017 | 4 | 2017-10-16 | 10:20 | 33.0697 | -116.8813 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | RA | RAMSD | 1.37 | 2016-05-21T19:40:00Z | 22.01 | 63 | RAMSD | 1.37 | 2016-05-21T19:40:00Z | 22.01 | 144 | RAMSD | 1.37 | 2016-05-21T19:40:00Z | 22.01 | 126 | RAMSD | 1.37 | 2016-05-21T19:40:00Z | 22.01 | 288 | < 25mph
26 | SDG&E | 20151009IG01 | October | 9 | 2015 | 4 | 2015-10-09 | 16:00 | 32.7705 | -117.1095 | Other | Urban | Less Than .25 Acres | Fire Agency | Secondary | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | CM | RODB1 | 2.12 | 2017-12-05T23:40:00Z | 26.73 | 6 | OTMSD | 6 | 2017-12-05T23:40:00Z | 28.99 | 83 | RODB1 | 2.12 | 2017-12-06T01:10:00Z | 26.73 | 12 | OTMSD | 6 | 2017-12-05T23:40:00Z | 28.99 | 165 | 25-40mph
73 | SDG&E | 20171018IG01 | October | 18 | 2017 | 4 | 2017-10-18 | 7:20 | 33.1659 | -117.2053 | Vegetation | Urban | Less Than .25 Acres | Unknown | 12kV | Overhead | No | Contact From Object |  | Vehicle | Pole | Human Error | Non- HFTD | NC | SMCSD | 2.66 | 2016-05-13T23:30:00Z | 12.01 | 44 | OLVSD | 7.37 | 2016-05-13T23:30:00Z | 18.99 | 143 | SMCSD | 2.66 | 2016-05-13T23:30:00Z | 12.01 | 88 | OLVSD | 7.37 | 2016-05-13T23:30:00Z | 18.99 | 287 | < 25mph
9 | SDG&E | 20150429IG01 | April | 29 | 2015 | 2 | 2015-04-29 | 12:00 | 32.6061 | -116.696 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Unknown | Tier 3 | ME | SSOSD | 3.93 | 2020-12-09T11:10:00Z | 8.33 | 62 | HP016 | 7.54 | 2020-12-09T11:15:00Z | 25.72 | 175 | SSOSD | 3.93 | 2020-12-09T11:10:00Z | 8.33 | 124 | HP016 | 7.54 | 2020-12-09T11:15:00Z | 25.72 | 350 | 25-40mph
31 | SDG&E | 20160131IG01 | January | 31 | 2016 | 1 | 2016-01-31 | 15:00 | 33.3217 | -117.156 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Weather | Tier 2 | NE | ESCSD | 2.91 | 2020-10-04T01:00:00Z | 7.16 | 26 | ROCSD | 5.88 | 2020-10-04T01:00:00Z | 9.57 | 242 | ESCSD | 2.91 | 2020-10-04T01:00:00Z | 7.16 | 52 | ROCSD | 5.88 | 2020-10-04T01:00:00Z | 9.57 | 481 | < 25mph
59 | SDG&E | 20170619IG01 | June | 19 | 2017 | 2 | 2017-06-19 | 9:52 | 32.7829 | -117.0488 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility |  | Non- HFTD | EA | E3680 | 3.25 | 2016-06-07T22:19:00Z | 15.99 | 55 | MTLSD | 4.13 | 2016-06-07T22:20:00Z | 18.99 | 161 | E3680 | 3.25 | 2016-06-07T22:19:00Z | 15.99 | 107 | MTLSD | 4.13 | 2016-06-07T22:20:00Z | 18.99 | 318 | < 25mph
118 | SDG&E | 20200211IG01 | February | 11 | 2020 | 1 | 2020-02-11 | 1:30 | 32.791 | -116.9194 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Outside Force | Non- HFTD | EA | AV271 | 0.4 | 2017-04-12T12:35:00Z | 4 | 29 | BVYSD | 6.91 | 2017-04-12T12:50:00Z | 12.01 | 188 | AV271 | 0.4 | 2017-04-12T12:35:00Z | 4 | 62 | BVYSD | 6.91 | 2017-04-12T12:50:00Z | 12.01 | 385 | < 25mph
67 | SDG&E | 20170830IG01 | August | 30 | 2017 | 3 | 2017-08-30 | 14:12 | 33.3875 | -117.2459 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Other | Tier 2 | NE | FBZCA | 2.35 | 2017-04-17T12:22:00Z | 7 | 27 | RNBSD | 6.26 | 2017-04-17T12:30:00Z | 10 | 68 | FBZCA | 2.35 | 2017-04-17T13:22:00Z | 7 | 50 | HP012 | 6.5 | 2017-04-17T12:46:00Z | 11.18 | 133 | < 25mph
106 | SDG&E | 20190805IG01 | August | 5 | 2019 | 3 | 2019-08-05 | 14:14 | 32.7886 | -117.1233 | Vegetation | Urban | Less Than .25 Acres | Utility | 12 kV | Overhead | No | Equipment/Facility Failure | Other |  |  | None | Non- HFTD | BC | TCNSD | 3.54 | 2015-06-24T06:40:00Z | 4 | 46 | F0495 | 6.22 | 2015-06-24T06:00:00Z | 13 | 176 | MVNSD | 0.97 | 2015-06-24T07:40:00Z | 4.99 | 90 | F0495 | 6.22 | 2015-06-24T06:00:00Z | 13 | 342 | < 25mph
2 | SDG&E | 20150319IG01 | March | 19 | 2015 | 1 | 2015-03-19 | 23:50 | 33.0565 | -117.0332 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 2 | NE | WIRC1 | 3.14 | 2016-04-15T04:23:00Z | 4.99 | 30 | C2635 | 7.73 | 2016-04-15T04:50:00Z | 55.99 | 59 | WIRC1 | 3.14 | 2016-04-15T05:23:00Z | 5.99 | 61 | C2635 | 7.73 | 2016-04-15T05:20:00Z | 55.99 | 116 | 55mph+
57 | SDG&E | 20170608IG01 | June | 8 | 2017 | 2 | 2017-06-08 | 4:12 | 33.0356 | -117.1839 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Tier 2 | NC | FBZCA | 2.35 | 2018-07-04T21:22:00Z | 22.01 | 36 | AT107 | 7.33 | 2018-07-04T21:38:00Z | 23 | 76 | FBZCA | 2.35 | 2018-07-04T22:22:00Z | 22.01 | 72 | AT107 | 7.33 | 2018-07-04T21:38:00Z | 23 | 151 | < 25mph
140 | SDG&E | 20201014IG01 | October | 14 | 2020 | 4 | 2020-10-14 | 15:05 | 33.027 | -116.889 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kv | Overhead | No | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 2 | RA | HVYSD | 2.68 | 2018-12-16T03:20:00Z | 4 | 58 | BLCSD | 6.09 | 2018-12-16T03:40:00Z | 8.99 | 135 | MGRSD | 3.02 | 2018-12-16T05:00:00Z | 4.99 | 118 | BLCSD | 6.09 | 2018-12-16T05:10:00Z | 12.01 | 272 | < 25mph
102 | SDG&E | 20190703IG01 | July | 3 | 2019 | 3 | 2019-07-03 | 15:15 | 33.0113 | -116.8492 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 3 | RA | SPPSD | 3.6 | 2020-05-10T23:40:00Z | 18.99 | 46 | HF005 | 6.67 | 2020-05-11T00:30:00Z | 19.22 | 135 | SPPSD | 3.6 | 2020-05-10T23:40:00Z | 18.99 | 91 | GOSC1 | 5.3 | 2020-05-11T00:52:00Z | 20 | 269 | < 25mph
113 | SDG&E | 20191024IG01 | October | 24 | 2019 | 4 | 2019-10-24 | 10:16 | 32.8357 | -116.7252 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Fuse |  |  | None | Tier 3 | ME | CRVSD | 3.61 | 2020-08-10T22:40:00Z | 16.73 | 64 | NDCSD | 5.6 | 2020-08-10T23:10:00Z | 17.98 | 190 | CRVSD | 3.61 | 2020-08-10T22:40:00Z | 16.73 | 127 | NDCSD | 5.6 | 2020-08-10T23:10:00Z | 17.98 | 377 | < 25mph
141 | SDG&E | 20201111IG01 | November | 11 | 2020 | 4 | 2020-11-11 | 9:51 | 32.678 | -116.86 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kv | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Unknown | Tier 3 | EA | JAMSD | 2.55 | 2019-05-15T14:40:00Z | 5.99 | 6 | DHVSD | 5.72 | 2019-05-15T14:20:00Z | 10 | 76 | JAMSD | 2.55 | 2019-05-15T16:10:00Z | 5.99 | 12 | DHVSD | 5.72 | 2019-05-15T14:20:00Z | 10 | 152 | < 25mph
67 | SDG&E | 20170830IG01 | August | 30 | 2017 | 3 | 2017-08-30 | 14:12 | 33.3875 | -117.2459 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Other | Tier 2 | NE | FBZCA | 2.35 | 2017-01-27T22:22:00Z | 27 | 21 | FBZCA | 2.35 | 2017-01-27T22:22:00Z | 27 | 51 | FBZCA | 2.35 | 2017-01-27T22:22:00Z | 27 | 45 | FBZCA | 2.35 | 2017-01-27T22:22:00Z | 27 | 105 | 25-40mph
85 | SDG&E | 20180612IG01 | June | 12 | 2018 | 2 | 2018-06-12 | 9:00 | 32.706 | -116.396 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | ME | CWDSD | 1.65 | 2015-04-06T12:50:00Z | 24.99 | 12 | BVDSD | 6.93 | 2015-04-06T12:50:00Z | 31.99 | 49 | CWDSD | 1.65 | 2015-04-06T13:20:00Z | 25.99 | 24 | BVDSD | 6.93 | 2015-04-06T13:00:00Z | 34 | 98 | 25-40mph
16 | SDG&E | 20150813IG01 | August | 13 | 2015 | 3 | 2015-08-13 | 20:33 | 33.2457 | -116.6769 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Unknown |  |  |  | Unknown | Tier 2 | RA | SDSCP | 1.53 | 2015-11-27T11:55:00Z | 15.99 | 23 | TEOC1 | 4.21 | 2015-11-27T12:22:00Z | 17 | 55 | SDSCP | 1.53 | 2015-11-27T12:55:00Z | 21 | 48 | TEOC1 | 4.21 | 2015-11-27T13:22:00Z | 24 | 108 | < 25mph
107 | SDG&E | 20190910IG01 | September | 10 | 2019 | 3 | 2019-09-10 | 12:59 | 32.5638 | -117.0333 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | None | Tier 2 | CM | CVXSD | 2.98 | 2016-01-30T21:50:00Z | 14 | 12 | CVXSD | 2.98 | 2016-01-30T21:50:00Z | 14 | 35 | CVXSD | 2.98 | 2016-01-30T22:50:00Z | 14 | 24 | OMBSD | 7.75 | 2016-01-30T23:00:00Z | 14.99 | 70 | < 25mph
14 | SDG&E | 20150727IG01 | July | 27 | 2015 | 3 | 2015-07-27 | 14:30 | 33.0665 | -116.579 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | None | Tier 3 | RA | E3070 | 3.52 | 2016-09-07T02:45:00Z | 12.01 | 29 | E3070 | 3.52 | 2016-09-07T02:45:00Z | 12.01 | 140 | E3070 | 3.52 | 2016-09-07T02:45:00Z | 12.01 | 59 | E3070 | 3.52 | 2016-09-07T02:45:00Z | 12.01 | 281 | < 25mph
96 | SDG&E | 20180914IG02 | September | 14 | 2018 | 3 | 2018-09-14 | 10:00 | 33.3177 | -117.2228 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact Between Third Party Facility on Pole and Supply Lines |  | Vehicle | Communication Facility | Human Error | Tier 2 | NE | SDFBK | 1.45 | 2015-12-25T02:49:00Z | 8.99 | 5 | FBZCA | 5.75 | 2015-12-25T02:22:00Z | 11.01 | 56 | SDFBK | 1.45 | 2015-12-25T02:49:00Z | 8.99 | 10 | FBZCA | 5.75 | 2015-12-25T03:22:00Z | 13 | 111 | < 25mph
118 | SDG&E | 20200211IG01 | February | 11 | 2020 | 1 | 2020-02-11 | 1:30 | 32.791 | -116.9194 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Outside Force | Non- HFTD | EA | ECJSD | 3.11 | 2018-03-23T09:50:00Z | 3 | 30 | LLDSD | 7.68 | 2018-03-23T10:20:00Z | 7 | 226 | ECJSD | 3.11 | 2018-03-23T09:50:00Z | 3 | 60 | LLDSD | 7.68 | 2018-03-23T10:20:00Z | 7 | 448 | < 25mph
63 | SDG&E | 20170716IG01 | July | 16 | 2017 | 3 | 2017-07-16 | 11:53 | 32.829 | -117.136 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | BC | EWRSD | 2.48 | 2017-05-27T00:00:00Z | 18.01 | 56 | LLDSD | 4.15 | 2017-05-27T00:30:00Z | 18.99 | 208 | EWRSD | 2.48 | 2017-05-27T00:00:00Z | 18.01 | 107 | LLDSD | 4.15 | 2017-05-27T00:30:00Z | 18.99 | 399 | < 25mph
57 | SDG&E | 20170608IG01 | June | 8 | 2017 | 2 | 2017-06-08 | 4:12 | 33.0356 | -117.1839 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Tier 2 | NC | FBZC1 | 2.31 | 2020-07-23T05:22:00Z | 8 | 36 | SE772 | 7.43 | 2020-07-23T04:30:00Z | 10.01 | 99 | FBZC1 | 2.31 | 2020-07-23T05:22:00Z | 8 | 72 | SE772 | 7.43 | 2020-07-23T04:30:00Z | 10.01 | 198 | < 25mph
53 | SDG&E | 20161021IG01 | October | 21 | 2016 | 4 | 2016-10-21 | 11:20 | 33.0485 | -116.8615 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Transformer |  |  |  | Tier 2 | RA | BRJSD | 0.73 | 2017-01-31T07:00:00Z | 14 | 12 | BRJSD | 0.73 | 2017-01-31T07:00:00Z | 14 | 44 | BRJSD | 0.73 | 2017-01-31T08:00:00Z | 17 | 24 | BRJSD | 0.73 | 2017-01-31T08:00:00Z | 17 | 88 | < 25mph
44 | SDG&E | 20160711IG01 | July | 11 | 2016 | 3 | 2016-07-11 | 10:27 | 33.4531 | -117.3044 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility |  | Tier 2 | NE | UCI09 | 3 | 2019-11-30T02:00:00Z | 13.8 | 26 | RCHC1 | 7 | 2019-11-30T02:07:00Z | 32.99 | 30 | UCI09 | 3 | 2019-11-30T02:00:00Z | 13.8 | 52 | RCHC1 | 7 | 2019-11-30T02:07:00Z | 32.99 | 60 | 25-40mph
134 | SDG&E | 20200905IG01 | September | 5 | 2020 | 3 | 2020-09-05 | 14:30 | 33.066 | -116.859 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 120v | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Outside Force | Non- HFTD | EA | CLMSD | 3.54 | 2017-08-08T17:40:00Z | 10 | 62 | WCKSD | 7.03 | 2017-08-08T17:40:00Z | 15.99 | 152 | SSOSD | 2.69 | 2017-08-08T18:40:00Z | 12.01 | 123 | HP016 | 7.13 | 2017-08-08T18:27:00Z | 20.58 | 303 | < 25mph
138 | SDG&E | 20200917IG01 | September | 17 | 2020 | 3 | 2020-09-17 | 10:00 | 33.1101 | -117.2693 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Other |  |  | None | Non- HFTD | NC | E0995 | 2.37 | 2017-03-27T18:55:00Z | 20 | 51 | E0995 | 2.37 | 2017-03-27T18:55:00Z | 20 | 174 | E0995 | 2.37 | 2017-03-27T18:55:00Z | 20 | 102 | E0995 | 2.37 | 2017-03-27T18:55:00Z | 20 | 349 | < 25mph
140 | SDG&E | 20201014IG01 | October | 14 | 2020 | 4 | 2020-10-14 | 15:05 | 33.027 | -116.889 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kv | Overhead | No | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 2 | RA | HVYSD | 2.68 | 2020-04-14T06:00:00Z | 5.55 | 60 | SSOSD | 5.46 | 2020-04-14T06:50:00Z | 6.87 | 155 | HVYSD | 2.68 | 2020-04-14T06:00:00Z | 5.55 | 119 | SPPSD | 6.13 | 2020-04-14T07:50:00Z | 8.01 | 309 | < 25mph
51 | SDG&E | 20160927IG01 | September | 27 | 2016 | 3 | 2016-09-27 | 10:18 | 33.2967 | -117.2079 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Animal |  | Unknown | Tier 2 | NE | F1077 | 3.32 | 2018-06-25T14:55:00Z | 8.01 | 60 | E1589 | 6.55 | 2018-06-25T14:56:00Z | 10 | 150 | E8360 | 2.96 | 2018-06-25T15:51:00Z | 13 | 115 | E8360 | 2.96 | 2018-06-25T15:51:00Z | 13 | 288 | < 25mph
30 | SDG&E | 20160116IG01 | January | 16 | 2016 | 1 | 2016-01-16 | 14:42 | 32.7188 | -116.9745 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | EA | EWRSD | 2.48 | 2019-12-02T13:30:00Z | 7.61 | 53 | SQTSD | 4.1 | 2019-12-02T13:50:00Z | 10.51 | 151 | AVYSD | 2.4 | 2019-12-02T14:30:00Z | 8.61 | 106 | VGDSD | 4.14 | 2019-12-02T15:00:00Z | 11.83 | 301 | < 25mph
15 | SDG&E | 20150808IG01 | August | 8 | 2015 | 3 | 2015-08-08 | 10:00 | 33.1973 | -117.2308 | Vegetation | Urban | Less Than .25 Acres | Customer | 4kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | NC | CHOSD | 3.4 | 2016-12-23T12:40:00Z | 5.99 | 59 | MIGSD | 7.84 | 2016-12-23T12:00:00Z | 14.99 | 151 | CHOSD | 3.4 | 2016-12-23T13:30:00Z | 8.01 | 116 | MIGSD | 7.84 | 2016-12-23T12:00:00Z | 14.99 | 300 | < 25mph
2 | SDG&E | 20150319IG01 | March | 19 | 2015 | 1 | 2015-03-19 | 23:50 | 33.0565 | -117.0332 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 2 | NE | WIRC1 | 3.14 | 2020-04-07T05:23:00Z | 5.99 | 30 | WIRC1 | 3.14 | 2020-04-07T05:23:00Z | 5.99 | 60 | WIRC1 | 3.14 | 2020-04-07T05:23:00Z | 5.99 | 60 | WIRC1 | 3.14 | 2020-04-07T05:23:00Z | 5.99 | 120 | < 25mph
2 | SDG&E | 20150319IG01 | March | 19 | 2015 | 1 | 2015-03-19 | 23:50 | 33.0565 | -117.0332 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 2 | NE | WIRC1 | 3.14 | 2020-03-10T20:23:00Z | 14.99 | 29 | WIRC1 | 3.14 | 2020-03-10T20:23:00Z | 14.99 | 77 | KOKB | 2.19 | 2020-03-10T21:20:00Z | 21.85 | 60 | KOKB | 2.19 | 2020-03-10T21:20:00Z | 21.85 | 158 | < 25mph
26 | SDG&E | 20151009IG01 | October | 9 | 2015 | 4 | 2015-10-09 | 16:00 | 32.7705 | -117.1095 | Other | Urban | Less Than .25 Acres | Fire Agency | Secondary | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | CM | RODB1 | 2.12 | 2017-06-17T03:40:00Z | 6.02 | 1 | OMBSD | 5.34 | 2017-06-17T02:50:00Z | 12.01 | 69 | RODB1 | 2.12 | 2017-06-17T03:50:00Z | 6.02 | 7 | OMBSD | 5.34 | 2017-06-17T02:50:00Z | 12.01 | 151 | < 25mph
49 | SDG&E | 20160827IG01 | August | 27 | 2016 | 3 | 2016-08-27 | 12:43 | 33.1371 | -117.0761 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Unknown | Non- HFTD | NE | JAMSD | 1.45 | 2017-06-01T14:20:00Z | 4.99 | 25 | LSVSD | 4.09 | 2017-06-01T13:30:00Z | 5.99 | 160 | JAMSD | 1.45 | 2017-06-01T15:20:00Z | 5.99 | 53 | DHVSD | 7.96 | 2017-06-01T14:30:00Z | 7 | 334 | < 25mph
134 | SDG&E | 20200905IG01 | September | 5 | 2020 | 3 | 2020-09-05 | 14:30 | 33.066 | -116.859 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 120v | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Outside Force | Non- HFTD | EA | GOSC1 | 1.64 | 2018-08-14T23:52:00Z | 21 | 48 | GOSC1 | 1.64 | 2018-08-14T23:52:00Z | 21 | 126 | GOSC1 | 1.64 | 2018-08-14T23:52:00Z | 21 | 98 | GOSC1 | 1.64 | 2018-08-14T23:52:00Z | 21 | 254 | < 25mph
70 | SDG&E | 20170927IG02 | September | 27 | 2017 | 3 | 2017-09-27 | 16:10 | 32.7272 | -116.7788 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | None | Tier 3 | EA | E5843 | 3.81 | 2019-12-12T06:10:00Z | 5.99 | 11 | HP007 | 6.04 | 2019-12-12T06:04:00Z | 13.65 | 80 | E5843 | 3.81 | 2019-12-12T06:50:00Z | 5.99 | 22 | HP007 | 6.04 | 2019-12-12T06:04:00Z | 13.65 | 159 | < 25mph
118 | SDG&E | 20200211IG01 | February | 11 | 2020 | 1 | 2020-02-11 | 1:30 | 32.791 | -116.9194 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Outside Force | Non- HFTD | EA | ECJSD | 3.11 | 2018-11-30T04:20:00Z | 5.99 | 31 | OTYSD | 4.92 | 2018-11-30T04:20:00Z | 18.99 | 159 | ECJSD | 3.11 | 2018-11-30T04:40:00Z | 11.01 | 60 | WALSD | 7.47 | 2018-11-30T05:00:00Z | 24 | 303 | < 25mph
71 | SDG&E | 20171007IG01 | October | 7 | 2017 | 4 | 2017-10-07 | 17:40 | 32.5914 | -116.6216 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Conductor |  |  | Other | Tier 3 | ME | E4858 | 0.85 | 2016-06-13T18:29:00Z | 13 | 31 | BVYSD | 6.91 | 2016-06-13T18:30:00Z | 14.99 | 210 | E4858 | 0.85 | 2016-06-13T18:29:00Z | 13 | 59 | DEHSD | 4.89 | 2016-06-13T19:00:00Z | 15.99 | 415 | < 25mph
24 | SDG&E | 20150917IG01 | September | 17 | 2015 | 3 | 2015-09-17 | 8:09 | 32.6791 | -117.1044 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Transformer |  |  | None | Non- HFTD | CM | JAMSD | 2.55 | 2020-08-28T06:10:00Z | 2.55 | 6 | HP025 | 5.82 | 2020-08-28T06:26:00Z | 22.82 | 84 | JAMSD | 2.55 | 2020-08-28T08:00:00Z | 2.92 | 12 | HP025 | 5.82 | 2020-08-28T06:26:00Z | 22.82 | 168 | < 25mph
79 | SDG&E | 20180216IG01 | February | 16 | 2018 | 1 | 2018-02-16 | 16:50 | 32.6276 | -116.9409 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Outside Force | Tier 2 | CM | CIRSD | 3.67 | 2019-06-16T02:50:00Z | 8.99 | 11 | FBZC1 | 7.45 | 2019-06-16T03:22:00Z | 18 | 107 | CIRSD | 3.67 | 2019-06-16T02:50:00Z | 8.99 | 22 | FBZC1 | 7.45 | 2019-06-16T03:22:00Z | 18 | 209 | < 25mph
62 | SDG&E | 20170629IG02 | June | 29 | 2017 | 2 | 2017-06-29 | 14:58 | 32.6926 | -116.8564 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Electric Facility | None | Tier 3 | EA | SPPSD | 3.6 | 2017-08-04T00:00:00Z | 18.99 | 58 | GOSC1 | 5.3 | 2017-08-03T23:52:00Z | 22.01 | 147 | SPPSD | 3.6 | 2017-08-04T00:00:00Z | 18.99 | 111 | GOSC1 | 5.3 | 2017-08-03T23:52:00Z | 22.01 | 279 | < 25mph
85 | SDG&E | 20180612IG01 | June | 12 | 2018 | 2 | 2018-06-12 | 9:00 | 32.706 | -116.396 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | ME | ESCSD | 2.77 | 2018-03-21T00:20:00Z | 8.01 | 28 | WRBSD | 7.79 | 2018-03-21T00:40:00Z | 17 | 208 | D9718 | 1.5 | 2018-03-21T01:42:00Z | 8.99 | 56 | WRBSD | 7.79 | 2018-03-21T00:40:00Z | 17 | 416 | < 25mph
89 | SDG&E | 20180706IG01 | July | 6 | 2018 | 3 | 2018-07-06 | 10:26 | 32.6203 | -116.7649 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Transformer |  |  |  | Tier 3 | ME | POTSD | 2.8 | 2017-10-21T05:20:00Z | 11.01 | 31 | CPOSD | 7.51 | 2017-10-21T05:20:00Z | 11.01 | 38 | POTSD | 2.8 | 2017-10-21T05:20:00Z | 11.01 | 62 | CPOSD | 7.51 | 2017-10-21T05:20:00Z | 11.01 | 76 | < 25mph
10 | SDG&E | 20150517IG01 | May | 17 | 2015 | 2 | 2015-05-17 | 6:55 | 33.1808 | -117.2064 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility |  | Non- HFTD | NC | DLZSD | 0.55 | 2015-07-27T01:10:00Z | 14 | 6 | SRUC1 | 6.25 | 2015-07-27T01:54:00Z | 17 | 42 | DLZSD | 0.55 | 2015-07-27T01:10:00Z | 14 | 12 | SRUC1 | 6.25 | 2015-07-27T01:54:00Z | 17 | 84 | < 25mph
110 | SDG&E | 20190930IG01 | September | 30 | 2019 | 3 | 2019-09-30 | 2:59 | 33.2618 | -116.3705 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Other | Non- HFTD | RA | UCI09 | 1.48 | 2017-12-09T23:00:00Z | 9.86 | 26 | RCHC1 | 7.83 | 2017-12-09T23:07:00Z | 17 | 35 | UCI09 | 1.48 | 2017-12-09T23:00:00Z | 9.86 | 52 | RCHC1 | 7.83 | 2017-12-09T23:07:00Z | 17 | 70 | < 25mph
104 | SDG&E | 20190716IG01 | July | 16 | 2019 | 3 | 2019-07-16 | 19:08 | 33.182 | -117.1126 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Other | Tier 2 | NE | TLKSD | 3.72 | 2020-10-23T15:50:00Z | 6.87 | 72 | F0381 | 5.11 | 2020-10-23T15:15:00Z | 9 | 251 | ESCSD | 3.61 | 2020-10-23T16:50:00Z | 7.16 | 136 | OLVSD | 7.1 | 2020-10-23T16:20:00Z | 9.5 | 483 | < 25mph
1 | SDG&E | 20150211IG01 | February | 11 | 2015 | 1 | 2015-02-11 | 15:30 | 32.8941 | -116.9393 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | EA | CVXSD | 2.98 | 2017-12-15T18:00:00Z | 8.01 | 12 | OMBSD | 7.75 | 2017-12-15T18:20:00Z | 20 | 50 | CVXSD | 2.98 | 2017-12-15T18:00:00Z | 8.01 | 24 | OMBSD | 7.75 | 2017-12-15T18:40:00Z | 20 | 100 | < 25mph
135 | SDG&E | 20200906IG01 | September | 6 | 2020 | 3 | 2020-09-06 | 23:00 | 33.0965 | -117.0237 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Transformer |  |  | None | Tier 2 | NE | HVWSD | 2.81 | 2020-10-29T15:10:00Z | 4.97 | 27 | ROCSD | 4.49 | 2020-10-29T15:20:00Z | 21.12 | 193 | HVWSD | 2.81 | 2020-10-29T15:10:00Z | 4.97 | 54 | ROCSD | 4.49 | 2020-10-29T15:20:00Z | 21.12 | 386 | < 25mph
37 | SDG&E | 20160406IG01 | April | 6 | 2016 | 2 | 2016-04-06 | 10:38 | 33.1865 | -117.1967 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Conductor | Vegetation | Electric Facility | Human Error | Non- HFTD | NC | AU709 | 3.95 | 2016-11-02T13:00:00Z | 8.01 | 18 | PZAC1 | 6.65 | 2016-11-02T12:50:00Z | 12.01 | 125 | AU709 | 3.95 | 2016-11-02T13:50:00Z | 8.01 | 36 | PZAC1 | 6.65 | 2016-11-02T12:50:00Z | 12.01 | 249 | < 25mph
105 | SDG&E | 20190716IG02 | July | 16 | 2019 | 3 | 2019-07-16 | 7:36 | 33.1675 | -117.1462 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Wire-Wire Contact |  |  |  | Other | Tier 2 | NE | SMCSD | 3.76 | 2019-05-31T13:40:00Z | 5.99 | 40 | E9915 | 6.01 | 2019-05-31T14:00:00Z | 7 | 189 | SMCSD | 3.76 | 2019-05-31T13:40:00Z | 5.99 | 75 | ESCSD | 5.49 | 2019-05-31T14:30:00Z | 8.01 | 366 | < 25mph
142 | SDG&E | 20201130IG01 | November | 30 | 2020 | 4 | 2020-11-30 | 9:10 | 33.266 | -117.223 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 2 | NE | AT125 | 2.22 | 2017-11-15T20:04:00Z | 7 | 18 | FBKSD | 6.92 | 2017-11-15T21:00:00Z | 8.99 | 71 | AT125 | 2.22 | 2017-11-15T20:04:00Z | 7 | 36 | FBKSD | 6.92 | 2017-11-15T21:00:00Z | 8.99 | 142 | < 25mph
115 | SDG&E | 20191101IG01 | November | 1 | 2019 | 4 | 2019-11-01 | 5:49 | 33.0924 | -117.0206 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | None | Non- HFTD | NE | E8894 | 1.45 | 2018-11-04T00:15:00Z | 7 | 21 | F2603 | 7.14 | 2018-11-04T00:15:00Z | 11.01 | 131 | E8894 | 1.45 | 2018-11-04T00:15:00Z | 7 | 42 | F2603 | 7.14 | 2018-11-04T00:15:00Z | 11.01 | 262 | < 25mph
118 | SDG&E | 20200211IG01 | February | 11 | 2020 | 1 | 2020-02-11 | 1:30 | 32.791 | -116.9194 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Outside Force | Non- HFTD | EA | E3070 | 3.52 | 2016-01-06T14:30:00Z | 4.99 | 26 | WALSD | 7.47 | 2016-01-06T15:10:00Z | 10 | 190 | E3070 | 3.52 | 2016-01-06T14:30:00Z | 4.99 | 52 | WALSD | 7.47 | 2016-01-06T15:20:00Z | 10 | 380 | < 25mph
91 | SDG&E | 20180722IG01 | July | 22 | 2018 | 3 | 2018-07-22 | 23:19 | 33.301 | -116.351 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | None | Non- HFTD | RA | RODB1 | 2.12 | 2020-01-31T13:20:00Z | 6.69 | 10 | CVXSD | 7.05 | 2020-01-31T13:30:00Z | 9.51 | 92 | RODB1 | 2.12 | 2020-01-31T13:20:00Z | 6.69 | 20 | CVXSD | 7.05 | 2020-01-31T14:10:00Z | 13.31 | 184 | < 25mph
47 | SDG&E | 20160729IG01 | July | 29 | 2016 | 3 | 2016-07-29 | 10:57 | 33.071 | -116.7424 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  |  | Tier 3 | RA | CVXSD | 3.04 | 2015-03-29T03:40:00Z | 8.01 | 13 | IIWC1 | 7.71 | 2015-03-29T03:54:00Z | 8.99 | 59 | CVXSD | 3.04 | 2015-03-29T03:40:00Z | 8.01 | 26 | IIWC1 | 7.71 | 2015-03-29T03:54:00Z | 8.99 | 118 | < 25mph
82 | SDG&E | 20180422IG01 | April | 22 | 2018 | 2 | 2018-04-22 | 14:00 | 32.837 | -117.184 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | BC | E2652 | 3.73 | 2015-09-29T03:24:00Z | 4 | 17 | RPQSD | 7.62 | 2015-09-29T03:20:00Z | 8.01 | 142 | E2652 | 3.73 | 2015-09-29T03:24:00Z | 4 | 34 | RPQSD | 7.62 | 2015-09-29T03:20:00Z | 8.01 | 286 | < 25mph
42 | SDG&E | 20160627IG01 | June | 27 | 2016 | 2 | 2016-06-27 | 15:30 | 33.2837 | -116.6174 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Human Error | Tier 2 | RA | OTYSD | 3.77 | 2018-02-16T20:40:00Z | 14 | 106 | E9888 | 6.92 | 2018-02-16T20:40:00Z | 17 | 186 | MIGSD | 2.96 | 2018-02-16T21:40:00Z | 18.01 | 211 | MIGSD | 2.96 | 2018-02-16T21:40:00Z | 18.01 | 371 | < 25mph
107 | SDG&E | 20190910IG01 | September | 10 | 2019 | 3 | 2019-09-10 | 12:59 | 32.5638 | -117.0333 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | None | Tier 2 | CM | LJHSD | 3.27 | 2017-12-28T14:40:00Z | 5.99 | 52 | E9870 | 5.59 | 2017-12-28T14:22:00Z | 8.99 | 202 | LJHSD | 3.27 | 2017-12-28T15:00:00Z | 8.01 | 104 | E9870 | 5.59 | 2017-12-28T14:22:00Z | 8.99 | 399 | < 25mph
16 | SDG&E | 20150813IG01 | August | 13 | 2015 | 3 | 2015-08-13 | 20:33 | 33.2457 | -116.6769 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Unknown |  |  |  | Unknown | Tier 2 | RA | SCRSD | 0.45 | 2016-08-27T17:20:00Z | 8.01 | 35 | TEOC1 | 4.21 | 2016-08-27T17:22:00Z | 8.99 | 56 | SCRSD | 0.45 | 2016-08-27T18:30:00Z | 8.99 | 73 | TEOC1 | 4.21 | 2016-08-27T18:22:00Z | 13 | 122 | < 25mph
134 | SDG&E | 20200905IG01 | September | 5 | 2020 | 3 | 2020-09-05 | 14:30 | 33.066 | -116.859 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 120v | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Outside Force | Non- HFTD | EA | GOSC1 | 1.64 | 2017-11-08T11:52:00Z | 7 | 61 | CESSD | 4.62 | 2017-11-08T12:00:00Z | 13 | 145 | SSOSD | 2.69 | 2017-11-08T13:30:00Z | 10 | 123 | CESSD | 4.62 | 2017-11-08T12:00:00Z | 13 | 291 | < 25mph
48 | SDG&E | 20160731IG01 | July | 31 | 2016 | 3 | 2016-07-31 | 13:43 | 33.3663 | -117.2033 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Unknown | Tier 2 | NE | SPVSD | 3.81 | 2016-12-11T16:30:00Z | 8.01 | 22 | SPVSD | 3.81 | 2016-12-11T16:30:00Z | 8.01 | 133 | E8894 | 1.45 | 2016-12-11T18:11:00Z | 8.99 | 42 | HDMSD | 7.44 | 2016-12-11T18:00:00Z | 11.01 | 259 | < 25mph
141 | SDG&E | 20201111IG01 | November | 11 | 2020 | 4 | 2020-11-11 | 9:51 | 32.678 | -116.86 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kv | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Unknown | Tier 3 | EA | JAMSD | 2.55 | 2015-01-02T10:20:00Z | 4.99 | 6 | OTYSD | 4.91 | 2015-01-02T10:10:00Z | 13 | 73 | JAMSD | 2.55 | 2015-01-02T10:20:00Z | 4.99 | 12 | HP002 | 5.78 | 2015-01-02T12:05:00Z | 16.33 | 146 | < 25mph
104 | SDG&E | 20190716IG01 | July | 16 | 2019 | 3 | 2019-07-16 | 19:08 | 33.182 | -117.1126 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Other | Tier 2 | NE | E4521 | 3.76 | 2015-11-13T09:12:00Z | 4 | 30 | HARSD | 5.68 | 2015-11-13T09:10:00Z | 13 | 214 | E4521 | 3.76 | 2015-11-13T09:12:00Z | 4 | 60 | HARSD | 5.68 | 2015-11-13T10:10:00Z | 13 | 426 | < 25mph
110 | SDG&E | 20190930IG01 | September | 30 | 2019 | 3 | 2019-09-30 | 2:59 | 33.2618 | -116.3705 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Other | Non- HFTD | RA | WARSD | 1.19 | 2019-04-14T06:40:00Z | 8.99 | 24 | WARSD | 1.19 | 2019-04-14T06:40:00Z | 8.99 | 60 | WARSD | 1.19 | 2019-04-14T06:40:00Z | 8.99 | 48 | WARSD | 1.19 | 2019-04-14T06:40:00Z | 8.99 | 120 | < 25mph
78 | SDG&E | 20180208IG01 | February | 8 | 2018 | 1 | 2018-02-08 | 10:07 | 33.2071 | -117.2072 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Human Error | Non- HFTD | NC | HVYSD | 2.68 | 2018-06-07T12:20:00Z | 8.99 | 42 | HP005 | 4.91 | 2018-06-07T12:13:00Z | 12.97 | 119 | HVYSD | 2.68 | 2018-06-07T12:20:00Z | 8.99 | 84 | HP005 | 4.91 | 2018-06-07T12:13:00Z | 12.97 | 238 | < 25mph
93 | SDG&E | 20180809IG01 | August | 9 | 2018 | 3 | 2018-08-09 | 12:00 | 33.213 | -117.335 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Other |  |  | Other | Non- HFTD | NC | CWDSD | 1.65 | 2019-01-18T06:00:00Z | 31 | 12 | BVDSD | 6.93 | 2019-01-18T06:20:00Z | 38.01 | 49 | CWDSD | 1.65 | 2019-01-18T06:00:00Z | 31 | 24 | BVDSD | 6.93 | 2019-01-18T06:20:00Z | 38.01 | 98 | 25-40mph
27 | SDG&E | 20151226IG01 | December | 26 | 2015 | 4 | 2015-12-26 | 3:04 | 33.1323 | -117.0695 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | NE | HRPSD | 2.59 | 2020-02-23T03:40:00Z | 48.43 | 36 | HRPSD | 2.59 | 2020-02-23T03:40:00Z | 48.43 | 102 | HRPSD | 2.59 | 2020-02-23T03:40:00Z | 48.43 | 72 | HRPSD | 2.59 | 2020-02-23T03:40:00Z | 48.43 | 205 | 40-55mph
133 | SDG&E | 20200904IG01 | September | 4 | 2020 | 3 | 2020-09-04 | 20:30 | 33.0658 | -116.8592 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Other | Tier 2 | RA | SSOSD | 2.7 | 2020-07-31T09:20:00Z | 4.38 | 57 | HP005 | 7.58 | 2020-07-31T09:53:00Z | 12.08 | 141 | SSOSD | 2.7 | 2020-07-31T09:20:00Z | 4.38 | 112 | HP005 | 7.58 | 2020-07-31T11:03:00Z | 14.32 | 280 | < 25mph
116 | SDG&E | 20191104IG01 | November | 4 | 2019 | 4 | 2019-11-04 | 15:30 | 33.1969 | -116.7121 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Other |  |  |  | Tier 3 | RA | UCI10 | 3.52 | 2017-07-05T09:00:00Z | 7.25 | 27 | UCI14 | 5.71 | 2017-07-05T09:00:00Z | 26.96 | 36 | UCI10 | 3.52 | 2017-07-05T09:00:00Z | 7.25 | 54 | UCI14 | 5.71 | 2017-07-05T10:00:00Z | 30.24 | 72 | 25-40mph
25 | SDG&E | 20151002IG01 | October | 2 | 2015 | 4 | 2015-10-02 | 14:30 | 33.1354 | -117.0588 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | NE | VLCC1 | 2.47 | 2016-03-26T19:14:00Z | 10 | 48 | CLNSD | 7.87 | 2016-03-26T18:50:00Z | 14 | 132 | HHCSD | 2.78 | 2016-03-26T19:40:00Z | 11.01 | 95 | CLNSD | 7.87 | 2016-03-26T18:50:00Z | 14 | 263 | < 25mph
36 | SDG&E | 20160311IG01 | March | 11 | 2016 | 1 | 2016-03-11 | 11:40 | 33.1563 | -117.2152 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Non- HFTD | NC | AMOSD | 2.8 | 2018-08-28T05:40:00Z | 2.01 | 17 | FBZCA | 4.6 | 2018-08-28T05:22:00Z | 5.99 | 79 | AMOSD | 2.8 | 2018-08-28T06:30:00Z | 3 | 34 | FBZCA | 4.6 | 2018-08-28T06:22:00Z | 5.99 | 158 | < 25mph
56 | SDG&E | 20170120IG01 | January | 20 | 2017 | 1 | 2017-01-20 | 14:00 | 32.6274 | -117.0767 | Building | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Conductor | Vegetation | Pole | Weather | Non- HFTD | CM | ECJSD | 3.11 | 2017-09-24T01:30:00Z | 8.01 | 30 | WALSD | 7.47 | 2017-09-24T01:10:00Z | 11.01 | 204 | ECJSD | 3.11 | 2017-09-24T02:20:00Z | 8.01 | 60 | WALSD | 7.47 | 2017-09-24T01:10:00Z | 11.01 | 407 | < 25mph
74 | SDG&E | 20171022IG01 | October | 22 | 2017 | 4 | 2017-10-22 | 10:22 | 33.099 | -117.135 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Tier 2 | NE | SSOSD | 3.3 | 2015-02-01T05:20:00Z | 7 | 55 | CESSD | 4.21 | 2015-02-01T04:40:00Z | 10 | 145 | BLCSD | 3.98 | 2015-02-01T06:20:00Z | 7 | 110 | HP005 | 6.91 | 2015-02-01T06:25:00Z | 10.29 | 290 | < 25mph
25 | SDG&E | 20151002IG01 | October | 2 | 2015 | 4 | 2015-10-02 | 14:30 | 33.1354 | -117.0588 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | NE | F6209 | 2.68 | 2019-11-25T05:30:00Z | 8.99 | 66 | HF001 | 6.43 | 2019-11-25T06:00:00Z | 10.58 | 191 | F6209 | 2.68 | 2019-11-25T05:30:00Z | 8.99 | 131 | HP014 | 6.9 | 2019-11-25T07:05:00Z | 12.53 | 382 | < 25mph
13 | SDG&E | 20150717IG01 | July | 17 | 2015 | 3 | 2015-07-17 | 9:48 | 33.3012 | -117.0222 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Communication Facility | Human Error | Tier 3 | NE | HDMSD | 3.7 | 2017-12-19T14:20:00Z | 17 | 35 | HDMSD | 3.7 | 2017-12-19T14:20:00Z | 17 | 174 | HDMSD | 3.7 | 2017-12-19T14:20:00Z | 17 | 71 | HDMSD | 3.7 | 2017-12-19T14:20:00Z | 17 | 354 | < 25mph
115 | SDG&E | 20191101IG01 | November | 1 | 2019 | 4 | 2019-11-01 | 5:49 | 33.0924 | -117.0206 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | None | Non- HFTD | NE | TWOSD | 2.48 | 2015-02-04T19:00:00Z | 10 | 56 | E6321 | 5.39 | 2015-02-04T19:28:00Z | 10 | 146 | HMDSD | 3.26 | 2015-02-04T20:10:00Z | 10 | 112 | OLVSD | 7.1 | 2015-02-04T20:20:00Z | 11.01 | 293 | < 25mph
101 | SDG&E | 20190612IG01 | June | 12 | 2019 | 2 | 2019-06-12 | 22:05 | 33.0484 | -116.8578 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12 kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | None | Tier 2 | RA | COHSD | 3.7 | 2020-11-14T10:10:00Z | 9.57 | 69 | CDVSD | 7.98 | 2020-11-14T10:10:00Z | 9.86 | 203 | COHSD | 3.7 | 2020-11-14T10:10:00Z | 9.57 | 135 | E9915 | 6.01 | 2020-11-14T11:16:00Z | 10 | 402 | < 25mph
91 | SDG&E | 20180722IG01 | July | 22 | 2018 | 3 | 2018-07-22 | 23:19 | 33.301 | -116.351 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | None | Non- HFTD | RA | RODB1 | 2.12 | 2020-02-24T14:40:00Z | 10.29 | 10 | MIGC1 | 4.4 | 2020-02-24T14:50:00Z | 11.01 | 92 | RODB1 | 2.12 | 2020-02-24T14:40:00Z | 10.29 | 20 | MIGC1 | 4.4 | 2020-02-24T15:50:00Z | 11.01 | 183 | < 25mph
94 | SDG&E | 20180819IG01 | August | 19 | 2018 | 3 | 2018-08-19 | 18:35 | 32.7002 | -116.8639 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | EA | DZRSD | 0.55 | 2019-01-18T18:20:00Z | 8.01 | 6 | OTYC1 | 4.63 | 2019-01-18T18:14:00Z | 14 | 44 | DZRSD | 0.55 | 2019-01-18T20:00:00Z | 12.01 | 12 | SVLSD | 7.84 | 2019-01-18T20:00:00Z | 15.99 | 88 | < 25mph
31 | SDG&E | 20160131IG01 | January | 31 | 2016 | 1 | 2016-01-31 | 15:00 | 33.3217 | -117.156 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Weather | Tier 2 | NE | D9718 | 1.71 | 2017-10-27T23:42:00Z | 8.99 | 32 | WRBSD | 7.63 | 2017-10-28T00:10:00Z | 13 | 199 | D9718 | 1.71 | 2017-10-27T23:42:00Z | 8.99 | 61 | WRBSD | 7.63 | 2017-10-28T00:40:00Z | 13 | 392 | < 25mph
101 | SDG&E | 20190612IG01 | June | 12 | 2019 | 2 | 2019-06-12 | 22:05 | 33.0484 | -116.8578 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12 kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | None | Tier 2 | RA | E6321 | 3.62 | 2015-03-27T16:02:00Z | 5.99 | 26 | C2635 | 5.84 | 2015-03-27T16:36:00Z | 18.99 | 136 | E6321 | 3.62 | 2015-03-27T16:02:00Z | 5.99 | 52 | C2635 | 5.84 | 2015-03-27T16:36:00Z | 18.99 | 272 | < 25mph
7 | SDG&E | 20150418IG01 | April | 18 | 2015 | 2 | 2015-04-18 | 12:00 | 32.7764 | -116.9309 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Secondary | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | None | Non- HFTD | EA | SMCSD | 3.76 | 2017-06-08T10:40:00Z | 3 | 43 | OLVSD | 6.11 | 2017-06-08T10:40:00Z | 7 | 167 | SMCSD | 3.76 | 2017-06-08T11:30:00Z | 4 | 85 | OLVSD | 6.11 | 2017-06-08T10:40:00Z | 7 | 338 | < 25mph
78 | SDG&E | 20180208IG01 | February | 8 | 2018 | 1 | 2018-02-08 | 10:07 | 33.2071 | -117.2072 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Human Error | Non- HFTD | NC | MGRSD | 3.02 | 2015-03-25T06:50:00Z | 4.99 | 63 | STVSD | 7.92 | 2015-03-25T07:00:00Z | 8.01 | 136 | MGRSD | 3.02 | 2015-03-25T08:10:00Z | 4.99 | 128 | STVSD | 7.92 | 2015-03-25T07:00:00Z | 8.01 | 274 | < 25mph
120 | SDG&E | 20200517IG01 | May | 17 | 2020 | 2 | 2020-05-17 | 8:52 | 33.2373 | -117.0301 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons |  | Other | Tier 2 | NE | BLCSD | 2.91 | 2016-12-30T13:40:00Z | 20 | 62 | BLCSD | 2.91 | 2016-12-30T13:40:00Z | 20 | 152 | BLCSD | 2.91 | 2016-12-30T13:40:00Z | 20 | 123 | BLCSD | 2.91 | 2016-12-30T13:40:00Z | 20 | 303 | < 25mph
93 | SDG&E | 20180809IG01 | August | 9 | 2018 | 3 | 2018-08-09 | 12:00 | 33.213 | -117.335 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Other |  |  | Other | Non- HFTD | NC | CWDSD | 1.65 | 2019-02-03T13:50:00Z | 34 | 12 | CWDSD | 1.65 | 2019-02-03T13:50:00Z | 34 | 49 | CWDSD | 1.65 | 2019-02-03T13:50:00Z | 34 | 24 | CWDSD | 1.65 | 2019-02-03T13:50:00Z | 34 | 97 | 25-40mph
101 | SDG&E | 20190612IG01 | June | 12 | 2019 | 2 | 2019-06-12 | 22:05 | 33.0484 | -116.8578 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12 kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | None | Tier 2 | RA | COHSD | 3.7 | 2019-09-16T05:00:00Z | 3.13 | 47 | TLKSD | 5.74 | 2019-09-16T04:00:00Z | 8.01 | 200 | COHSD | 3.7 | 2019-09-16T06:00:00Z | 8.19 | 90 | COHSD | 3.7 | 2019-09-16T06:00:00Z | 8.19 | 382 | < 25mph
94 | SDG&E | 20180819IG01 | August | 19 | 2018 | 3 | 2018-08-19 | 18:35 | 32.7002 | -116.8639 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | EA | DZRSD | 0.55 | 2019-02-17T01:00:00Z | 17 | 6 | OTYC1 | 4.63 | 2019-02-17T01:14:00Z | 31 | 44 | DZRSD | 0.55 | 2019-02-17T01:00:00Z | 17 | 12 | OTYC1 | 4.63 | 2019-02-17T01:14:00Z | 31 | 88 | 25-40mph
54 | SDG&E | 20161102IG01 | November | 2 | 2016 | 4 | 2016-11-02 | 10:30 | 32.8373 | -116.7022 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Tier 3 | ME | PZAC1 | 3.98 | 2019-07-10T14:50:00Z | 7 | 20 | PTMSD | 7.98 | 2019-07-10T14:20:00Z | 7 | 156 | PZAC1 | 3.98 | 2019-07-10T15:50:00Z | 10 | 38 | PZAC1 | 3.98 | 2019-07-10T15:50:00Z | 10 | 297 | < 25mph
134 | SDG&E | 20200905IG01 | September | 5 | 2020 | 3 | 2020-09-05 | 14:30 | 33.066 | -116.859 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 120v | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Outside Force | Non- HFTD | EA | OTYSD | 3.89 | 2018-12-20T16:20:00Z | 11.01 | 36 | OTYSD | 3.89 | 2018-12-20T16:20:00Z | 11.01 | 150 | OTYSD | 3.89 | 2018-12-20T16:20:00Z | 11.01 | 72 | OTYSD | 3.89 | 2018-12-20T16:20:00Z | 11.01 | 296 | < 25mph
37 | SDG&E | 20160406IG01 | April | 6 | 2016 | 2 | 2016-04-06 | 10:38 | 33.1865 | -117.1967 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Conductor | Vegetation | Electric Facility | Human Error | Non- HFTD | NC | CIRSD | 0.95 | 2019-10-10T09:20:00Z | 3 | 17 | HMDSD | 4.64 | 2019-10-10T09:00:00Z | 8.84 | 123 | CIRSD | 0.95 | 2019-10-10T09:20:00Z | 3 | 35 | HMDSD | 4.64 | 2019-10-10T09:00:00Z | 8.84 | 247 | < 25mph
7 | SDG&E | 20150418IG01 | April | 18 | 2015 | 2 | 2015-04-18 | 12:00 | 32.7764 | -116.9309 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Secondary | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | None | Non- HFTD | EA | E9957 | 2.37 | 2019-04-28T20:35:00Z | 20 | 37 | OLVSD | 6.11 | 2019-04-28T20:30:00Z | 31 | 164 | E9957 | 2.37 | 2019-04-28T20:56:00Z | 20 | 75 | OLVSD | 6.11 | 2019-04-28T20:50:00Z | 32.01 | 332 | 25-40mph
104 | SDG&E | 20190716IG01 | July | 16 | 2019 | 3 | 2019-07-16 | 19:08 | 33.182 | -117.1126 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Other | Tier 2 | NE | E4858 | 0.85 | 2015-11-06T23:56:00Z | 13 | 30 | MIGC1 | 7.97 | 2015-11-06T23:50:00Z | 14.99 | 213 | E4858 | 0.85 | 2015-11-06T23:56:00Z | 13 | 60 | MIGC1 | 7.97 | 2015-11-06T23:50:00Z | 14.99 | 427 | < 25mph
122 | SDG&E | 20200602IG01 | June | 2 | 2020 | 2 | 2020-06-02 | 18:00 | 33.07 | -116.863 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 3 | RA | ESCSD | 2.53 | 2019-03-21T11:50:00Z | 12.01 | 18 | ROCSD | 5.24 | 2019-03-21T11:20:00Z | 15.99 | 186 | ESCSD | 2.53 | 2019-03-21T11:50:00Z | 12.01 | 36 | ROCSD | 5.24 | 2019-03-21T12:10:00Z | 15.99 | 371 | < 25mph
117 | SDG&E | 20191112IG01 | November | 12 | 2019 | 4 | 2019-11-12 | 7:51 | 33.1903 | -117.3698 | Other | Urban | Less Than .25 Acres | Fire Agency | 120/240 | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | NC | AT125 | 3.8 | 2019-12-21T13:35:00Z | 4.99 | 32 | COHSD | 7.13 | 2019-12-21T13:10:00Z | 11.03 | 144 | AT125 | 3.8 | 2019-12-21T14:15:00Z | 5.99 | 62 | COHSD | 7.13 | 2019-12-21T14:00:00Z | 12.12 | 276 | < 25mph
97 | SDG&E | 20181015IG01 | October | 15 | 2018 | 4 | 2018-10-15 | 10:21 | 33.3191 | -117.2597 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure |  |  |  | None | Tier 2 | NE | TWOSD | 2.48 | 2015-07-01T15:50:00Z | 8.01 | 63 | OLVSD | 7.1 | 2015-07-01T15:50:00Z | 8.99 | 161 | HMDSD | 3.26 | 2015-07-01T17:10:00Z | 8.01 | 126 | OLVSD | 7.1 | 2015-07-01T15:50:00Z | 8.99 | 323 | < 25mph
76 | SDG&E | 20171210IG01 | December | 10 | 2017 | 4 | 2017-12-10 | 5:26 | 33.28 | -116.955 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 3 | NE | GOSC1 | 1.64 | 2018-06-02T03:52:00Z | 4.99 | 41 | POVSD | 5.39 | 2018-06-02T04:40:00Z | 8.99 | 125 | GOSC1 | 1.64 | 2018-06-02T03:52:00Z | 4.99 | 78 | POVSD | 5.39 | 2018-06-02T04:40:00Z | 8.99 | 246 | < 25mph
80 | SDG&E | 20180412IG01 | April | 12 | 2018 | 2 | 2018-04-12 | 19:33 | 32.6965 | -117.0493 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | CM | OTYSD | 2.72 | 2019-03-08T20:00:00Z | 25.99 | 45 | OTYSD | 2.72 | 2019-03-08T20:00:00Z | 25.99 | 128 | OTYSD | 2.72 | 2019-03-08T20:00:00Z | 25.99 | 90 | OTYSD | 2.72 | 2019-03-08T20:00:00Z | 25.99 | 254 | 25-40mph
122 | SDG&E | 20200602IG01 | June | 2 | 2020 | 2 | 2020-06-02 | 18:00 | 33.07 | -116.863 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 3 | RA | ESCSD | 2.53 | 2016-12-04T02:10:00Z | 7 | 32 | HDMSD | 7.76 | 2016-12-04T01:30:00Z | 15.99 | 175 | ESCSD | 2.53 | 2016-12-04T03:10:00Z | 8.99 | 61 | HDMSD | 7.76 | 2016-12-04T01:30:00Z | 15.99 | 340 | < 25mph
42 | SDG&E | 20160627IG01 | June | 27 | 2016 | 2 | 2016-06-27 | 15:30 | 33.2837 | -116.6174 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Human Error | Tier 2 | RA | OTYSD | 3.77 | 2016-11-19T18:00:00Z | 7 | 45 | OTYSD | 3.77 | 2016-11-19T18:00:00Z | 7 | 109 | MIGSD | 2.96 | 2016-11-19T19:20:00Z | 8.01 | 99 | NATSD | 7.86 | 2016-11-19T19:10:00Z | 10 | 240 | < 25mph
2 | SDG&E | 20150319IG01 | March | 19 | 2015 | 1 | 2015-03-19 | 23:50 | 33.0565 | -117.0332 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 2 | NE | WIRC1 | 3.14 | 2017-07-16T13:23:00Z | 4.99 | 5 | CBDSD | 4.41 | 2017-07-16T12:50:00Z | 5.99 | 27 | WIRC1 | 3.14 | 2017-07-16T14:23:00Z | 4.99 | 10 | CBDSD | 4.41 | 2017-07-16T14:20:00Z | 7 | 55 | < 25mph
117 | SDG&E | 20191112IG01 | November | 12 | 2019 | 4 | 2019-11-12 | 7:51 | 33.1903 | -117.3698 | Other | Urban | Less Than .25 Acres | Fire Agency | 120/240 | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | NC | VISSD | 2.7 | 2020-04-07T00:30:00Z | 17.38 | 30 | TLKSD | 7.71 | 2020-04-07T00:40:00Z | 25.99 | 147 | VISSD | 2.7 | 2020-04-07T00:30:00Z | 17.38 | 60 | TLKSD | 7.71 | 2020-04-07T00:40:00Z | 25.99 | 288 | 25-40mph
1 | SDG&E | 20150211IG01 | February | 11 | 2015 | 1 | 2015-02-11 | 15:30 | 32.8941 | -116.9393 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | EA | BFDSD | 3.99 | 2018-12-28T18:10:00Z | 8.01 | 12 | OMBSD | 7.75 | 2018-12-28T17:40:00Z | 13 | 54 | BFDSD | 3.99 | 2018-12-28T19:30:00Z | 8.99 | 24 | OMBSD | 7.75 | 2018-12-28T17:40:00Z | 13 | 108 | < 25mph
134 | SDG&E | 20200905IG01 | September | 5 | 2020 | 3 | 2020-09-05 | 14:30 | 33.066 | -116.859 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 120v | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Outside Force | Non- HFTD | EA | AV271 | 0.83 | 2019-08-18T12:30:00Z | 8.01 | 42 | RIOSD | 5.45 | 2019-08-18T12:00:00Z | 8.84 | 224 | AV271 | 0.83 | 2019-08-18T13:20:00Z | 8.01 | 83 | RIOSD | 5.45 | 2019-08-18T12:00:00Z | 8.84 | 443 | < 25mph
12 | SDG&E | 20150707IG01 | July | 7 | 2015 | 3 | 2015-07-07 | 15:00 | 32.7443 | -117.0498 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Non- HFTD | EA | E6321 | 3.62 | 2019-01-28T16:03:00Z | 7 | 39 | E9915 | 6.01 | 2019-01-28T16:31:00Z | 11.01 | 171 | SMCSD | 3.76 | 2019-01-28T17:50:00Z | 10 | 75 | E9915 | 6.01 | 2019-01-28T17:45:00Z | 14.99 | 340 | < 25mph
59 | SDG&E | 20170619IG01 | June | 19 | 2017 | 2 | 2017-06-19 | 9:52 | 32.7829 | -117.0488 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility |  | Non- HFTD | EA | HVWSD | 2.6 | 2015-12-08T06:10:00Z | 10 | 17 | HDMSD | 5.96 | 2015-12-08T06:00:00Z | 18.01 | 151 | HVWSD | 2.6 | 2015-12-08T07:00:00Z | 13 | 34 | HDMSD | 5.96 | 2015-12-08T06:00:00Z | 18.01 | 297 | < 25mph
41 | SDG&E | 20160623IG01 | June | 23 | 2016 | 2 | 2016-06-23 | 15:00 | 32.8058 | -116.961 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | Outside Force | Non- HFTD | EA | E8699 | 3.84 | 2020-10-18T15:18:00Z | 13 | 60 | E8699 | 3.84 | 2020-10-18T15:18:00Z | 13 | 188 | E8699 | 3.84 | 2020-10-18T15:18:00Z | 13 | 122 | E8699 | 3.84 | 2020-10-18T15:18:00Z | 13 | 377 | < 25mph
85 | SDG&E | 20180612IG01 | June | 12 | 2018 | 2 | 2018-06-12 | 9:00 | 32.706 | -116.396 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | ME | ESCSD | 2.77 | 2020-06-15T12:10:00Z | 4.38 | 26 | OLVSD | 5.01 | 2020-06-15T11:20:00Z | 8.99 | 217 | ESCSD | 2.77 | 2020-06-15T13:00:00Z | 4.75 | 50 | OLVSD | 5.01 | 2020-06-15T11:20:00Z | 8.99 | 431 | < 25mph
80 | SDG&E | 20180412IG01 | April | 12 | 2018 | 2 | 2018-04-12 | 19:33 | 32.6965 | -117.0493 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | CM | E4521 | 3.33 | 2018-08-14T21:04:00Z | 18.01 | 29 | KSEE | 7.51 | 2018-08-14T20:47:00Z | 20.71 | 88 | E4521 | 3.33 | 2018-08-14T22:03:00Z | 22.01 | 57 | E4521 | 3.33 | 2018-08-14T22:03:00Z | 22.01 | 173 | < 25mph
66 | SDG&E | 20170820IG01 | August | 20 | 2017 | 3 | 2017-08-20 | 22:15 | 32.7522 | -117.1184 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 4kV | Overhead | Yes | Equipment/Facility Failure | Fuse |  |  | None | Non- HFTD | CM | CWDSD | 1.65 | 2020-12-19T13:20:00Z | 39.24 | 12 | CWDSD | 1.65 | 2020-12-19T13:20:00Z | 39.24 | 59 | CWDSD | 1.65 | 2020-12-19T13:20:00Z | 39.24 | 24 | CWDSD | 1.65 | 2020-12-19T13:20:00Z | 39.24 | 118 | 25-40mph
29 | SDG&E | 20160109IG01 | January | 9 | 2016 | 1 | 2016-01-09 | 4:30 | 33.082 | -117.091 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Non- HFTD | NE | COCSD | 3.01 | 2015-10-20T05:40:00Z | 5.99 | 95 | SQTSD | 5.8 | 2015-10-20T06:10:00Z | 8.01 | 205 | CSTSD | 1.38 | 2015-10-20T07:30:00Z | 7 | 189 | SQTSD | 5.8 | 2015-10-20T07:30:00Z | 8.99 | 408 | < 25mph
89 | SDG&E | 20180706IG01 | July | 6 | 2018 | 3 | 2018-07-06 | 10:26 | 32.6203 | -116.7649 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Transformer |  |  |  | Tier 3 | ME | BRJSD | 3.74 | 2018-07-21T20:00:00Z | 23 | 31 | BRJSD | 3.74 | 2018-07-21T20:00:00Z | 23 | 38 | BRJSD | 3.74 | 2018-07-21T21:20:00Z | 24.99 | 62 | BRJSD | 3.74 | 2018-07-21T21:20:00Z | 24.99 | 76 | < 25mph
122 | SDG&E | 20200602IG01 | June | 2 | 2020 | 2 | 2020-06-02 | 18:00 | 33.07 | -116.863 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 3 | RA | E1089 | 3.42 | 2018-10-17T11:15:00Z | 1.01 | 12 | ROCSD | 5.24 | 2018-10-17T10:20:00Z | 21 | 175 | D9888 | 1.5 | 2018-10-17T12:16:00Z | 2.01 | 24 | ROCSD | 5.24 | 2018-10-17T11:40:00Z | 22.01 | 335 | < 25mph
66 | SDG&E | 20170820IG01 | August | 20 | 2017 | 3 | 2017-08-20 | 22:15 | 32.7522 | -117.1184 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 4kV | Overhead | Yes | Equipment/Facility Failure | Fuse |  |  | None | Non- HFTD | CM | CWDSD | 1.65 | 2015-05-12T18:40:00Z | 25.99 | 12 | BVDSD | 6.93 | 2015-05-12T18:30:00Z | 28.99 | 55 | CWDSD | 1.65 | 2015-05-12T18:40:00Z | 25.99 | 24 | BVDSD | 6.93 | 2015-05-12T18:30:00Z | 28.99 | 110 | 25-40mph
57 | SDG&E | 20170608IG01 | June | 8 | 2017 | 2 | 2017-06-08 | 4:12 | 33.0356 | -117.1839 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Tier 2 | NC | FBZC1 | 2.31 | 2020-04-21T09:22:00Z | 10 | 24 | AT107 | 7.33 | 2020-04-21T08:53:00Z | 13 | 63 | FBZC1 | 2.31 | 2020-04-21T09:22:00Z | 10 | 48 | AT107 | 7.33 | 2020-04-21T08:53:00Z | 13 | 126 | < 25mph
141 | SDG&E | 20201111IG01 | November | 11 | 2020 | 4 | 2020-11-11 | 9:51 | 32.678 | -116.86 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kv | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Unknown | Tier 3 | EA | JAMSD | 1.01 | 2019-07-15T05:10:00Z | 5.99 | 16 | HP002 | 5.77 | 2019-07-15T05:43:00Z | 17.9 | 83 | JAMSD | 1.01 | 2019-07-15T05:10:00Z | 5.99 | 32 | HP002 | 5.77 | 2019-07-15T05:43:00Z | 17.9 | 165 | < 25mph
90 | SDG&E | 20180708IG01 | July | 8 | 2018 | 3 | 2018-07-08 | 16:16 | 32.6349 | -117.103 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Other | Non- HFTD | CM | SDCHU | 2.86 | 2015-01-16T22:50:00Z | 5.99 | 11 | SDL13 | 7.83 | 2015-01-16T22:42:00Z | 18.01 | 92 | SDCHU | 2.86 | 2015-01-16T23:50:00Z | 7 | 23 | SDL13 | 7.83 | 2015-01-16T22:42:00Z | 18.01 | 183 | < 25mph
111 | SDG&E | 20191017IG01 | October | 17 | 2019 | 4 | 2019-10-17 | 12:15 | 33.2736 | -116.3931 | Vegetation | Urban | Less Than .25 Acres | Utility | 120/240 | Overhead | No | Other |  |  |  | Human Error | Non- HFTD | RA | GOSC1 | 1.64 | 2017-03-27T02:52:00Z | 11.01 | 68 | GOSC1 | 1.64 | 2017-03-27T02:52:00Z | 11.01 | 180 | GOSC1 | 1.64 | 2017-03-27T02:52:00Z | 11.01 | 130 | GOSC1 | 1.64 | 2017-03-27T02:52:00Z | 11.01 | 344 | < 25mph
26 | SDG&E | 20151009IG01 | October | 9 | 2015 | 4 | 2015-10-09 | 16:00 | 32.7705 | -117.1095 | Other | Urban | Less Than .25 Acres | Fire Agency | Secondary | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | CM | RODB1 | 2.12 | 2015-09-08T12:10:00Z | 0 | 6 | OTYC1 | 6.1 | 2015-09-08T12:14:00Z | 8.01 | 62 | RODB1 | 2.12 | 2015-09-08T13:10:00Z | 0 | 12 | OTYC1 | 6.1 | 2015-09-08T13:14:00Z | 8.01 | 123 | < 25mph
88 | SDG&E | 20180629IG01 | June | 29 | 2018 | 2 | 2018-06-29 | 13:06 | 32.645 | -117.056 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Unknown | Non- HFTD | CM | E4521 | 3.76 | 2017-05-17T04:50:00Z | 8.99 | 30 | OTYSD | 4.92 | 2017-05-17T04:30:00Z | 11.01 | 198 | E4521 | 3.76 | 2017-05-17T05:51:00Z | 8.99 | 56 | OTYSD | 4.92 | 2017-05-17T04:30:00Z | 11.01 | 382 | < 25mph
60 | SDG&E | 20170626IG01 | June | 26 | 2017 | 2 | 2017-06-26 | 14:30 | 32.7842 | -117.1391 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | BC | E9915 | 3.36 | 2017-09-25T05:11:00Z | 8.01 | 114 | RPQSD | 5.87 | 2017-09-25T05:10:00Z | 10 | 258 | HDMSD | 2.89 | 2017-09-25T06:10:00Z | 15.99 | 227 | HDMSD | 2.89 | 2017-09-25T06:10:00Z | 15.99 | 518 | < 25mph
73 | SDG&E | 20171018IG01 | October | 18 | 2017 | 4 | 2017-10-18 | 7:20 | 33.1659 | -117.2053 | Vegetation | Urban | Less Than .25 Acres | Unknown | 12kV | Overhead | No | Contact From Object |  | Vehicle | Pole | Human Error | Non- HFTD | NC | WRBSD | 3.58 | 2015-10-13T19:00:00Z | 20 | 94 | WRBSD | 3.58 | 2015-10-13T19:00:00Z | 20 | 181 | WRBSD | 3.58 | 2015-10-13T20:40:00Z | 20 | 187 | OLVSD | 4.4 | 2015-10-13T20:40:00Z | 20 | 361 | < 25mph
103 | SDG&E | 20190705IG01 | July | 5 | 2019 | 3 | 2019-07-05 | 12:32 | 33.1584 | -117.222 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 2 | NC | HVWSD | 2.49 | 2018-08-21T06:10:00Z | 3 | 21 | HP005 | 6.46 | 2018-08-21T05:53:00Z | 11.41 | 138 | SPVSD | 3.81 | 2018-08-21T07:30:00Z | 3 | 42 | HP005 | 6.46 | 2018-08-21T07:33:00Z | 11.63 | 275 | < 25mph
28 | SDG&E | 20160103IG01 | January | 3 | 2016 | 1 | 2016-01-03 | 4:30 | 33.1915 | -117.3655 | Other | Urban | Less Than .25 Acres | Fire Agency | 12kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | Other | Non- HFTD | NC | ESCSD | 2.91 | 2020-08-10T06:20:00Z | 4.32 | 26 | HDMSD | 7.24 | 2020-08-10T05:50:00Z | 7.16 | 202 | ESCSD | 2.91 | 2020-08-10T07:40:00Z | 7.53 | 52 | ESCSD | 2.91 | 2020-08-10T07:40:00Z | 7.53 | 403 | < 25mph
24 | SDG&E | 20150917IG01 | September | 17 | 2015 | 3 | 2015-09-17 | 8:09 | 32.6791 | -117.1044 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Transformer |  |  | None | Non- HFTD | CM | JAMSD | 2.55 | 2017-09-03T01:00:00Z | 25.99 | 6 | OTMSD | 5.53 | 2017-09-03T01:10:00Z | 40.98 | 77 | JAMSD | 2.55 | 2017-09-03T01:00:00Z | 25.99 | 12 | OTMSD | 5.53 | 2017-09-03T02:10:00Z | 44 | 156 | 40-55mph
112 | SDG&E | 20191019IG01 | October | 19 | 2019 | 4 | 2019-10-19 | 13:10 | 33.2317 | -117.2593 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 240V | Overhead | Yes | Other |  |  |  | Human Error | Non- HFTD | NC | SE073 | 3.95 | 2020-05-23T16:40:00Z | 10.45 | 45 | RBHSD | 5.34 | 2020-05-23T16:30:00Z | 11.02 | 110 | AVOSD | 3.47 | 2020-05-23T18:00:00Z | 14.69 | 85 | AVOSD | 3.47 | 2020-05-23T18:00:00Z | 14.69 | 205 | < 25mph
120 | SDG&E | 20200517IG01 | May | 17 | 2020 | 2 | 2020-05-17 | 8:52 | 33.2373 | -117.0301 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons |  | Other | Tier 2 | NE | SSOSD | 2.7 | 2017-01-26T17:30:00Z | 15.99 | 61 | WCKSD | 7.04 | 2017-01-26T17:30:00Z | 22.01 | 148 | SSOSD | 2.7 | 2017-01-26T18:30:00Z | 17 | 122 | WCKSD | 7.04 | 2017-01-26T18:00:00Z | 22.01 | 285 | < 25mph
64 | SDG&E | 20170725IG01 | July | 25 | 2017 | 3 | 2017-07-25 | 15:18 | 33.1343 | -117.1666 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | No | Vandalism/Theft |  |  |  | Other | Non- HFTD | NE | JAMSD | 2.55 | 2018-07-17T13:30:00Z | 2.01 | 6 | HP002 | 5.78 | 2018-07-17T12:43:00Z | 8.72 | 87 | JAMSD | 2.55 | 2018-07-17T14:30:00Z | 5.99 | 12 | DZRSD | 7.36 | 2018-07-17T14:20:00Z | 10 | 174 | < 25mph
42 | SDG&E | 20160627IG01 | June | 27 | 2016 | 2 | 2016-06-27 | 15:30 | 33.2837 | -116.6174 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Human Error | Tier 2 | RA | C7369 | 3.12 | 2017-04-01T15:27:00Z | 8.01 | 55 | C7369 | 3.12 | 2017-04-01T15:27:00Z | 8.01 | 117 | C7369 | 3.12 | 2017-04-01T15:27:00Z | 8.01 | 111 | C7369 | 3.12 | 2017-04-01T15:27:00Z | 8.01 | 240 | < 25mph
74 | SDG&E | 20171022IG01 | October | 22 | 2017 | 4 | 2017-10-22 | 10:22 | 33.099 | -117.135 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Tier 2 | NE | BLCSD | 3.98 | 2017-02-15T06:30:00Z | 14 | 63 | BLCSD | 3.98 | 2017-02-15T06:30:00Z | 14 | 153 | BLCSD | 3.98 | 2017-02-15T06:30:00Z | 14 | 128 | CESSD | 4.21 | 2017-02-15T08:00:00Z | 14.99 | 308 | < 25mph
4 | SDG&E | 20150412IG01 | April | 12 | 2015 | 2 | 2015-04-12 | 12:31 | 33.0117 | -116.866 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility |  | Tier 2 | RA | AU219 | 1.08 | 2018-10-13T13:15:00Z | 1.01 | 11 | OLVSD | 5.01 | 2018-10-13T13:50:00Z | 8.01 | 185 | D9888 | 1.95 | 2018-10-13T14:30:00Z | 2.01 | 23 | ROCSD | 5.88 | 2018-10-13T14:50:00Z | 10 | 370 | < 25mph
60 | SDG&E | 20170626IG01 | June | 26 | 2017 | 2 | 2017-06-26 | 14:30 | 32.7842 | -117.1391 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | BC | HDMSD | 2.89 | 2015-12-06T19:50:00Z | 14 | 91 | HDMSD | 2.89 | 2015-12-06T19:50:00Z | 14 | 191 | WRBSD | 3.58 | 2015-12-06T20:50:00Z | 20 | 184 | E2652 | 5.94 | 2015-12-06T20:44:00Z | 20 | 383 | < 25mph
19 | SDG&E | 20150901IG01 | September | 1 | 2015 | 3 | 2015-09-01 | 18:01 | 32.7595 | -117.0671 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished | 4kV | Overhead | No | Contact From Object |  | Vehicle | Electric Facility | Human Error | Non- HFTD | CM | ESCSD | 3.66 | 2018-04-16T06:00:00Z | 4.99 | 31 | OLVSD | 6.75 | 2018-04-16T05:40:00Z | 8.01 | 101 | ESCSD | 3.66 | 2018-04-16T06:50:00Z | 8.01 | 60 | F2603 | 8 | 2018-04-16T06:21:00Z | 10 | 200 | < 25mph
73 | SDG&E | 20171018IG01 | October | 18 | 2017 | 4 | 2017-10-18 | 7:20 | 33.1659 | -117.2053 | Vegetation | Urban | Less Than .25 Acres | Unknown | 12kV | Overhead | No | Contact From Object |  | Vehicle | Pole | Human Error | Non- HFTD | NC | HDMSD | 2.89 | 2016-05-02T10:20:00Z | 10 | 102 | HDMSD | 2.89 | 2016-05-02T10:20:00Z | 10 | 219 | HDMSD | 2.89 | 2016-05-02T10:20:00Z | 10 | 190 | OLVSD | 4.4 | 2016-05-02T10:40:00Z | 10 | 415 | < 25mph
40 | SDG&E | 20160614IG01 | June | 14 | 2016 | 2 | 2016-06-14 | 6:05 | 32.8801 | -116.9051 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Outside Force | Tier 2 | EA | CVXSD | 2.09 | 2016-03-17T21:00:00Z | 14 | 18 | BFDSD | 6.01 | 2016-03-17T21:20:00Z | 17 | 73 | CVXSD | 2.09 | 2016-03-17T22:10:00Z | 14.99 | 36 | BFDSD | 6.01 | 2016-03-17T21:40:00Z | 18.01 | 140 | < 25mph
40 | SDG&E | 20160614IG01 | June | 14 | 2016 | 2 | 2016-06-14 | 6:05 | 32.8801 | -116.9051 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Outside Force | Tier 2 | EA | CVXSD | 2.09 | 2016-07-26T00:50:00Z | 12.01 | 18 | CVXSD | 2.09 | 2016-07-26T00:50:00Z | 12.01 | 64 | CVXSD | 2.09 | 2016-07-26T00:50:00Z | 12.01 | 38 | CVXSD | 2.09 | 2016-07-26T00:50:00Z | 12.01 | 130 | < 25mph
76 | SDG&E | 20171210IG01 | December | 10 | 2017 | 4 | 2017-12-10 | 5:26 | 33.28 | -116.955 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 3 | NE | GOSC1 | 1.64 | 2015-12-14T05:52:00Z | 21 | 63 | ARHSD | 6.07 | 2015-12-14T06:00:00Z | 35.99 | 164 | GOSC1 | 1.64 | 2015-12-14T06:52:00Z | 40 | 131 | GOSC1 | 1.64 | 2015-12-14T06:52:00Z | 40 | 331 | 25-40mph
106 | SDG&E | 20190805IG01 | August | 5 | 2019 | 3 | 2019-08-05 | 14:14 | 32.7886 | -117.1233 | Vegetation | Urban | Less Than .25 Acres | Utility | 12 kV | Overhead | No | Equipment/Facility Failure | Other |  |  | None | Non- HFTD | BC | DYESD | 1.89 | 2018-07-09T15:50:00Z | 8.99 | 24 | HOSSD | 5 | 2018-07-09T16:20:00Z | 11.01 | 132 | DYESD | 1.89 | 2018-07-09T17:20:00Z | 12.01 | 48 | BRMSD | 6.81 | 2018-07-09T17:20:00Z | 14 | 264 | < 25mph
17 | SDG&E | 20150815IG01 | August | 15 | 2015 | 3 | 2015-08-15 | 17:30 | 32.7417 | -116.9685 | Other | Urban | Less Than .25 Acres | Customer | 4Kv | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Non- HFTD | EA | ELMSD | 3.12 | 2018-05-09T00:40:00Z | 13 | 18 | MTLSD | 7.68 | 2018-05-09T00:40:00Z | 18.99 | 102 | ELMSD | 3.12 | 2018-05-09T00:40:00Z | 13 | 36 | MTLSD | 7.68 | 2018-05-09T00:40:00Z | 18.99 | 207 | < 25mph
88 | SDG&E | 20180629IG01 | June | 29 | 2018 | 2 | 2018-06-29 | 13:06 | 32.645 | -117.056 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Unknown | Non- HFTD | CM | AV271 | 0.4 | 2017-04-16T22:35:00Z | 14.99 | 30 | OTYSD | 4.92 | 2017-04-16T23:00:00Z | 20 | 203 | AV271 | 0.4 | 2017-04-16T22:35:00Z | 14.99 | 64 | OTYSD | 4.92 | 2017-04-16T23:00:00Z | 20 | 423 | < 25mph
37 | SDG&E | 20160406IG01 | April | 6 | 2016 | 2 | 2016-04-06 | 10:38 | 33.1865 | -117.1967 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Conductor | Vegetation | Electric Facility | Human Error | Non- HFTD | NC | CIRSD | 0.95 | 2018-05-29T17:20:00Z | 11.01 | 18 | PAUSD | 7.99 | 2018-05-29T17:20:00Z | 12.01 | 124 | CIRSD | 0.95 | 2018-05-29T18:20:00Z | 13 | 36 | PZAC1 | 6.65 | 2018-05-29T18:50:00Z | 14.99 | 248 | < 25mph
23 | SDG&E | 20150909IG01 | September | 9 | 2015 | 3 | 2015-09-09 | 20:40 | 32.644 | -117.072 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Non- HFTD | CM | CESSD | 3.48 | 2016-06-18T01:40:00Z | 13 | 47 | GOSC1 | 5.3 | 2016-06-18T01:52:00Z | 18.99 | 115 | CESSD | 3.48 | 2016-06-18T01:40:00Z | 13 | 94 | GOSC1 | 5.3 | 2016-06-18T01:52:00Z | 18.99 | 226 | < 25mph
98 | SDG&E | 20181126IG01 | November | 26 | 2018 | 4 | 2018-11-26 | 1:51 | 33.4314 | -117.5952 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility |  | Tier 2 | OC | ELMSD | 3.12 | 2016-01-27T08:50:00Z | 12.01 | 18 | ELMSD | 3.12 | 2016-01-27T08:50:00Z | 12.01 | 111 | ELMSD | 3.12 | 2016-01-27T08:50:00Z | 12.01 | 36 | ELMSD | 3.12 | 2016-01-27T08:50:00Z | 12.01 | 226 | < 25mph
87 | SDG&E | 20180622IG01 | June | 22 | 2018 | 2 | 2018-06-22 | 9:46 | 32.567 | -116.941 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | Unknown | Tier 2 | CM | HP002 | 1.96 | 2020-11-09T23:43:00Z | 15.66 | 30 | HP002 | 1.96 | 2020-11-09T23:43:00Z | 15.66 | 191 | HP002 | 1.96 | 2020-11-09T23:43:00Z | 15.66 | 60 | SVLSD | 4.46 | 2020-11-10T01:10:00Z | 17.98 | 374 | < 25mph
3 | SDG&E | 20150409IG01 | April | 9 | 2015 | 2 | 2015-04-09 | 17:23 | 32.7233 | -116.8922 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Unknown |  |  |  |  | Tier 3 | EA | RCRSD | 0.81 | 2016-07-05T05:40:00Z | 7 | 48 | HP014 | 6.9 | 2016-07-05T06:17:00Z | 15.21 | 132 | RCRSD | 0.81 | 2016-07-05T05:40:00Z | 7 | 96 | HP014 | 6.9 | 2016-07-05T06:37:00Z | 16.11 | 264 | < 25mph
6 | SDG&E | 20150413IG01 | April | 13 | 2015 | 2 | 2015-04-13 | 10:50 | 32.5859 | -117.0017 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Tier 2 | CM | GOSC1 | 2.72 | 2018-09-03T03:52:00Z | 8.99 | 47 | POVSD | 6.59 | 2018-09-03T03:20:00Z | 10 | 125 | GOSC1 | 2.72 | 2018-09-03T03:52:00Z | 8.99 | 93 | POVSD | 6.59 | 2018-09-03T03:20:00Z | 10 | 249 | < 25mph
69 | SDG&E | 20170927IG01 | September | 27 | 2017 | 3 | 2017-09-27 | 14:28 | 33.2327 | -116.9748 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Unknown |  |  |  | Unknown | Tier 2 | NE | HRPSD | 2.14 | 2019-04-29T13:20:00Z | 47 | 42 | HRPSD | 2.14 | 2019-04-29T13:20:00Z | 47 | 108 | HRPSD | 2.14 | 2019-04-29T13:20:00Z | 47 | 83 | HRPSD | 2.14 | 2019-04-29T13:20:00Z | 47 | 217 | 40-55mph
86 | SDG&E | 20180612IG02 | June | 12 | 2018 | 2 | 2018-06-12 | 15:14 | 32.864 | -116.747 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact from Object |  | Balloons | Electric Facility | None | Tier 3 | EA | GOSC1 | 1.64 | 2017-10-11T22:52:00Z | 20 | 63 | GOSC1 | 1.64 | 2017-10-11T22:52:00Z | 20 | 153 | GOSC1 | 1.64 | 2017-10-11T22:52:00Z | 20 | 125 | GOSC1 | 1.64 | 2017-10-11T22:52:00Z | 20 | 305 | < 25mph
65 | SDG&E | 20170728IG01 | July | 28 | 2017 | 3 | 2017-07-28 | 16:31 | 32.7802 | -116.8722 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Pole /Conductor | Vehicle | Electric Facility | Outside Force | Tier 2 | EA | HP007 | 3.33 | 2015-07-18T10:46:00Z | 3.8 | 22 | DLZSD | 5.72 | 2015-07-18T10:50:00Z | 7 | 72 | E5843 | 1.23 | 2015-07-18T11:51:00Z | 4.99 | 43 | HP012 | 6.5 | 2015-07-18T11:56:00Z | 8.72 | 143 | < 25mph
44 | SDG&E | 20160711IG01 | July | 11 | 2016 | 3 | 2016-07-11 | 10:27 | 33.4531 | -117.3044 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility |  | Tier 2 | NE | BRGSD | 2.71 | 2019-05-01T09:20:00Z | 7 | 28 | UCI11 | 6.85 | 2019-05-01T09:00:00Z | 50.64 | 34 | BRGSD | 2.71 | 2019-05-01T10:00:00Z | 8.99 | 54 | UCI11 | 6.85 | 2019-05-01T09:00:00Z | 50.64 | 66 | 40-55mph
12 | SDG&E | 20150707IG01 | July | 7 | 2015 | 3 | 2015-07-07 | 15:00 | 32.7443 | -117.0498 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Non- HFTD | EA | SMCSD | 3.76 | 2016-03-20T13:00:00Z | 3 | 32 | OLVSD | 6.11 | 2016-03-20T13:10:00Z | 7 | 149 | SMCSD | 3.76 | 2016-03-20T14:50:00Z | 5.99 | 64 | ESCSD | 5.49 | 2016-03-20T14:20:00Z | 8.99 | 290 | < 25mph
7 | SDG&E | 20150418IG01 | April | 18 | 2015 | 2 | 2015-04-18 | 12:00 | 32.7764 | -116.9309 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Secondary | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | None | Non- HFTD | EA | E6321 | 3.62 | 2015-11-01T01:16:00Z | 4.99 | 36 | OLVSD | 6.11 | 2015-11-01T01:20:00Z | 7 | 153 | E6321 | 3.62 | 2015-11-01T01:16:00Z | 4.99 | 71 | OLVSD | 6.11 | 2015-11-01T01:20:00Z | 7 | 284 | < 25mph
51 | SDG&E | 20160927IG01 | September | 27 | 2016 | 3 | 2016-09-27 | 10:18 | 33.2967 | -117.2079 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Animal |  | Unknown | Tier 2 | NE | F5316 | 2.72 | 2020-04-06T04:50:00Z | 12.01 | 69 | E9951 | 7.77 | 2020-04-06T04:16:00Z | 14 | 159 | KMYF | 3.41 | 2020-04-06T05:53:00Z | 16.11 | 139 | E9951 | 7.77 | 2020-04-06T05:30:00Z | 18.99 | 323 | < 25mph
138 | SDG&E | 20200917IG01 | September | 17 | 2020 | 3 | 2020-09-17 | 10:00 | 33.1101 | -117.2693 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Other |  |  | None | Non- HFTD | NC | FTVSD | 3.07 | 2018-12-05T00:30:00Z | 23 | 65 | RCESD | 5.38 | 2018-12-05T00:30:00Z | 32.01 | 175 | FTVSD | 3.07 | 2018-12-05T01:30:00Z | 24.99 | 130 | RCESD | 5.38 | 2018-12-05T00:30:00Z | 32.01 | 349 | 25-40mph
63 | SDG&E | 20170716IG01 | July | 16 | 2017 | 3 | 2017-07-16 | 11:53 | 32.829 | -117.136 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | BC | VJSSD | 1.29 | 2016-07-03T23:30:00Z | 18.01 | 45 | VJSSD | 1.29 | 2016-07-03T23:30:00Z | 18.01 | 192 | VJSSD | 1.29 | 2016-07-03T23:30:00Z | 18.01 | 90 | VJSSD | 1.29 | 2016-07-03T23:30:00Z | 18.01 | 382 | < 25mph
73 | SDG&E | 20171018IG01 | October | 18 | 2017 | 4 | 2017-10-18 | 7:20 | 33.1659 | -117.2053 | Vegetation | Urban | Less Than .25 Acres | Unknown | 12kV | Overhead | No | Contact From Object |  | Vehicle | Pole | Human Error | Non- HFTD | NC | WRBSD | 3.58 | 2017-08-23T12:10:00Z | 5.99 | 100 | OLVSD | 4.4 | 2017-08-23T12:10:00Z | 7 | 221 | WRBSD | 3.58 | 2017-08-23T12:10:00Z | 5.99 | 195 | OLVSD | 4.4 | 2017-08-23T12:10:00Z | 7 | 430 | < 25mph
117 | SDG&E | 20191112IG01 | November | 12 | 2019 | 4 | 2019-11-12 | 7:51 | 33.1903 | -117.3698 | Other | Urban | Less Than .25 Acres | Fire Agency | 120/240 | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | NC | VISSD | 2.7 | 2017-08-29T05:40:00Z | 5.99 | 30 | AV241 | 5.81 | 2017-08-29T04:54:00Z | 8.99 | 124 | VISSD | 2.7 | 2017-08-29T05:40:00Z | 5.99 | 60 | AV241 | 5.81 | 2017-08-29T04:54:00Z | 8.99 | 252 | < 25mph
117 | SDG&E | 20191112IG01 | November | 12 | 2019 | 4 | 2019-11-12 | 7:51 | 33.1903 | -117.3698 | Other | Urban | Less Than .25 Acres | Fire Agency | 120/240 | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | NC | AT125 | 3.8 | 2017-07-12T20:15:00Z | 15.99 | 28 | E9957 | 4.15 | 2017-07-12T20:55:00Z | 18.01 | 115 | AT125 | 3.8 | 2017-07-12T20:15:00Z | 15.99 | 56 | E9957 | 4.15 | 2017-07-12T20:55:00Z | 18.01 | 227 | < 25mph
42 | SDG&E | 20160627IG01 | June | 27 | 2016 | 2 | 2016-06-27 | 15:30 | 33.2837 | -116.6174 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Human Error | Tier 2 | RA | C7369 | 3.12 | 2017-08-18T09:32:00Z | 4 | 55 | F1077 | 4.16 | 2017-08-18T09:31:00Z | 4.99 | 134 | C7369 | 3.12 | 2017-08-18T09:47:00Z | 4.99 | 108 | CHOSD | 4.37 | 2017-08-18T09:40:00Z | 7 | 266 | < 25mph
11 | SDG&E | 20150528IG01 | May | 28 | 2015 | 2 | 2015-05-28 | 12:45 | 32.7265 | -116.9922 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | EA | RODB1 | 1.87 | 2018-07-01T03:50:00Z | 8.05 | 10 | OMBSD | 4.99 | 2018-07-01T03:20:00Z | 10 | 74 | RODB1 | 1.87 | 2018-07-01T03:50:00Z | 8.05 | 20 | OMBSD | 4.99 | 2018-07-01T03:20:00Z | 10 | 148 | < 25mph
125 | SDG&E | 20200717IG01 | July | 17 | 2020 | 3 | 2020-07-17 | 16:30 | 33.0904 | -116.5798 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | RA | HDMSD | 3.87 | 2017-11-13T18:20:00Z | 8.01 | 58 | HDMSD | 3.87 | 2017-11-13T18:20:00Z | 8.01 | 241 | E9915 | 2.32 | 2017-11-13T19:13:00Z | 11.01 | 115 | E9915 | 2.32 | 2017-11-13T19:13:00Z | 11.01 | 479 | < 25mph
25 | SDG&E | 20151002IG01 | October | 2 | 2015 | 4 | 2015-10-02 | 14:30 | 33.1354 | -117.0588 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | NE | RINSD | 3.17 | 2017-05-14T06:40:00Z | 5.99 | 42 | HP014 | 6.9 | 2017-05-14T05:57:00Z | 10.29 | 142 | RINSD | 3.17 | 2017-05-14T07:00:00Z | 5.99 | 82 | HP014 | 6.9 | 2017-05-14T05:57:00Z | 10.29 | 284 | < 25mph
11 | SDG&E | 20150528IG01 | May | 28 | 2015 | 2 | 2015-05-28 | 12:45 | 32.7265 | -116.9922 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | EA | RODB1 | 1.87 | 2020-02-16T05:00:00Z | 6.26 | 10 | OTYC1 | 5.88 | 2020-02-16T04:14:00Z | 7 | 82 | RODB1 | 1.87 | 2020-02-16T05:00:00Z | 6.26 | 20 | CVXSD | 7.09 | 2020-02-16T05:40:00Z | 7 | 160 | < 25mph
97 | SDG&E | 20181015IG01 | October | 15 | 2018 | 4 | 2018-10-15 | 10:21 | 33.3191 | -117.2597 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure |  |  |  | None | Tier 2 | NE | ESCSD | 3.61 | 2020-06-27T15:00:00Z | 7.46 | 54 | ESCSD | 3.61 | 2020-06-27T15:00:00Z | 7.46 | 186 | ESCSD | 3.61 | 2020-06-27T16:20:00Z | 7.96 | 108 | F5340 | 6.64 | 2020-06-27T16:40:00Z | 8 | 383 | < 25mph
20 | SDG&E | 20150901IG02 | September | 1 | 2015 | 3 | 2015-09-01 | 8:50 | 32.669 | -116.286 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | None | Tier 2 | ME | WIRC1 | 2.46 | 2015-03-24T07:17:00Z | 5.99 | 17 | AT125 | 5.25 | 2015-03-24T07:35:00Z | 7 | 65 | WIRC1 | 2.46 | 2015-03-24T08:17:00Z | 7 | 34 | WIRC1 | 2.46 | 2015-03-24T08:17:00Z | 7 | 130 | < 25mph
96 | SDG&E | 20180914IG02 | September | 14 | 2018 | 3 | 2018-09-14 | 10:00 | 33.3177 | -117.2228 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact Between Third Party Facility on Pole and Supply Lines |  | Vehicle | Communication Facility | Human Error | Tier 2 | NE | UCAB | 2 | 2017-01-09T06:50:00Z | 7.7 | 8 | RCHC1 | 7.83 | 2017-01-09T06:07:00Z | 17 | 14 | UCI10 | 3.52 | 2017-01-09T08:00:00Z | 11.63 | 16 | RCHC1 | 7.83 | 2017-01-09T07:07:00Z | 18.01 | 28 | < 25mph
54 | SDG&E | 20161102IG01 | November | 2 | 2016 | 4 | 2016-11-02 | 10:30 | 32.8373 | -116.7022 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Tier 3 | ME | WINSD | 3.21 | 2020-09-08T21:10:00Z | 10.38 | 24 | AT107 | 6.73 | 2020-09-08T21:13:00Z | 13 | 167 | PZAC1 | 3.98 | 2020-09-08T21:50:00Z | 12 | 48 | AT107 | 6.73 | 2020-09-08T21:13:00Z | 13 | 333 | < 25mph
9 | SDG&E | 20150429IG01 | April | 29 | 2015 | 2 | 2015-04-29 | 12:00 | 32.6061 | -116.696 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Unknown | Tier 3 | ME | GOSC1 | 1.04 | 2016-10-03T03:52:00Z | 12.01 | 61 | HP005 | 6.69 | 2016-10-03T04:45:00Z | 14.99 | 148 | GOSC1 | 1.04 | 2016-10-03T03:52:00Z | 12.01 | 123 | HP016 | 7.54 | 2016-10-03T05:47:00Z | 18.34 | 299 | < 25mph
87 | SDG&E | 20180622IG01 | June | 22 | 2018 | 2 | 2018-06-22 | 9:46 | 32.567 | -116.941 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | Unknown | Tier 2 | CM | HP002 | 1.96 | 2017-11-10T21:55:00Z | 16.55 | 34 | SVLSD | 4.46 | 2017-11-10T22:20:00Z | 18.01 | 196 | HP002 | 1.96 | 2017-11-10T21:55:00Z | 16.55 | 64 | SVLSD | 4.46 | 2017-11-10T23:10:00Z | 20 | 372 | < 25mph
59 | SDG&E | 20170619IG01 | June | 19 | 2017 | 2 | 2017-06-19 | 9:52 | 32.7829 | -117.0488 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility |  | Non- HFTD | EA | E8894 | 3.31 | 2019-05-21T21:16:00Z | 20 | 34 | ROCSD | 7.01 | 2019-05-21T21:20:00Z | 28.99 | 179 | E8894 | 3.31 | 2019-05-21T21:16:00Z | 20 | 67 | ROCSD | 7.01 | 2019-05-21T22:00:00Z | 28.99 | 352 | 25-40mph
21 | SDG&E | 20150902IG01 | September | 2 | 2015 | 3 | 2015-09-02 | 18:18 | 33.1867 | -117.202 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Non- HFTD | NC | CVXSD | 3.45 | 2018-06-18T05:50:00Z | 8.01 | 16 | BFDSD | 6.31 | 2018-06-18T05:50:00Z | 8.01 | 67 | CVXSD | 3.45 | 2018-06-18T05:50:00Z | 8.01 | 32 | BFDSD | 6.31 | 2018-06-18T05:50:00Z | 8.01 | 132 | < 25mph
120 | SDG&E | 20200517IG01 | May | 17 | 2020 | 2 | 2020-05-17 | 8:52 | 33.2373 | -117.0301 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons |  | Other | Tier 2 | NE | BLCSD | 2.91 | 2016-09-24T04:40:00Z | 4.99 | 62 | HP016 | 7.14 | 2016-09-24T04:17:00Z | 13.65 | 156 | BLCSD | 2.91 | 2016-09-24T05:40:00Z | 11.01 | 123 | HP016 | 7.14 | 2016-09-24T04:47:00Z | 22.82 | 312 | < 25mph
107 | SDG&E | 20190910IG01 | September | 10 | 2019 | 3 | 2019-09-10 | 12:59 | 32.5638 | -117.0333 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | None | Tier 2 | CM | MPESD | 3.91 | 2019-03-14T22:30:00Z | 20 | 35 | MTLSD | 7.42 | 2019-03-14T22:00:00Z | 28.99 | 206 | LJHSD | 3.27 | 2019-03-14T23:00:00Z | 21 | 69 | MTLSD | 7.42 | 2019-03-14T22:00:00Z | 28.99 | 411 | 25-40mph
47 | SDG&E | 20160729IG01 | July | 29 | 2016 | 3 | 2016-07-29 | 10:57 | 33.071 | -116.7424 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  |  | Tier 3 | RA | CVXSD | 3.04 | 2020-01-17T15:30:00Z | 9.06 | 34 | MIGC1 | 6.39 | 2020-01-17T15:50:00Z | 14.99 | 109 | NATSD | 1.61 | 2020-01-17T16:30:00Z | 9.86 | 68 | MIGC1 | 6.39 | 2020-01-17T16:50:00Z | 15.99 | 217 | < 25mph
122 | SDG&E | 20200602IG01 | June | 2 | 2020 | 2 | 2020-06-02 | 18:00 | 33.07 | -116.863 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 3 | RA | ESCSD | 2.53 | 2019-03-25T23:10:00Z | 17 | 18 | HDMSD | 7.76 | 2019-03-25T23:30:00Z | 18.01 | 186 | ESCSD | 2.53 | 2019-03-25T23:10:00Z | 17 | 36 | HDMSD | 7.76 | 2019-03-25T23:30:00Z | 18.01 | 372 | < 25mph
61 | SDG&E | 20170629IG01 | June | 29 | 2017 | 2 | 2017-06-29 | 13:07 | 33.1355 | -117.098 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility |  | Non- HFTD | NE | MGRSD | 3.02 | 2017-02-13T19:40:00Z | 10 | 73 | HP005 | 4.91 | 2017-02-13T19:45:00Z | 18.57 | 150 | MGRSD | 3.02 | 2017-02-13T20:00:00Z | 11.01 | 142 | HP005 | 4.91 | 2017-02-13T19:45:00Z | 18.57 | 296 | < 25mph
86 | SDG&E | 20180612IG02 | June | 12 | 2018 | 2 | 2018-06-12 | 15:14 | 32.864 | -116.747 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact from Object |  | Balloons | Electric Facility | None | Tier 3 | EA | SSOSD | 2.69 | 2018-05-07T12:10:00Z | 4.99 | 41 | STVSD | 5.63 | 2018-05-07T12:20:00Z | 8.99 | 125 | SSOSD | 2.69 | 2018-05-07T13:20:00Z | 4.99 | 91 | STVSD | 5.63 | 2018-05-07T12:20:00Z | 8.99 | 259 | < 25mph
81 | SDG&E | 20180416IG01 | April | 16 | 2018 | 2 | 2018-04-16 | 14:24 | 33.4176 | -117.6058 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | Weather | Non- HFTD | OC | AT125 | 3.63 | 2017-09-11T11:20:00Z | 4.99 | 25 | CBDSD | 6.94 | 2017-09-11T11:50:00Z | 10 | 147 | AT125 | 3.63 | 2017-09-11T12:40:00Z | 4.99 | 48 | CBDSD | 6.94 | 2017-09-11T11:50:00Z | 10 | 295 | < 25mph
74 | SDG&E | 20171022IG01 | October | 22 | 2017 | 4 | 2017-10-22 | 10:22 | 33.099 | -117.135 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Tier 2 | NE | BLCSD | 3.98 | 2019-04-02T03:00:00Z | 5.99 | 50 | CESSD | 4.21 | 2019-04-02T03:10:00Z | 8.99 | 140 | BLCSD | 3.98 | 2019-04-02T03:20:00Z | 5.99 | 98 | CESSD | 4.21 | 2019-04-02T03:20:00Z | 8.99 | 278 | < 25mph
41 | SDG&E | 20160623IG01 | June | 23 | 2016 | 2 | 2016-06-23 | 15:00 | 32.8058 | -116.961 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | Outside Force | Non- HFTD | EA | E6321 | 3.95 | 2017-12-04T01:08:00Z | 5.99 | 70 | E9915 | 5.71 | 2017-12-04T01:30:00Z | 7 | 193 | E6321 | 3.95 | 2017-12-04T01:08:00Z | 5.99 | 137 | E9915 | 5.71 | 2017-12-04T01:30:00Z | 7 | 371 | < 25mph
84 | SDG&E | 20180601IG01 | June | 1 | 2018 | 2 | 2018-06-01 | 14:00 | 33.099 | -117.044 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | No | Wire-Wire Contact |  |  |  | Other | Non- HFTD | NE | E8360 | 2.96 | 2018-03-26T23:36:00Z | 20 | 60 | E9951 | 7.77 | 2018-03-26T22:49:00Z | 21 | 170 | E8360 | 2.96 | 2018-03-27T00:26:00Z | 20 | 120 | E9951 | 7.77 | 2018-03-26T22:49:00Z | 21 | 355 | < 25mph
66 | SDG&E | 20170820IG01 | August | 20 | 2017 | 3 | 2017-08-20 | 22:15 | 32.7522 | -117.1184 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 4kV | Overhead | Yes | Equipment/Facility Failure | Fuse |  |  | None | Non- HFTD | CM | CWDSD | 1.65 | 2018-07-15T05:40:00Z | 8.99 | 12 | BVDSD | 6.93 | 2018-07-15T05:50:00Z | 14.99 | 41 | CWDSD | 1.65 | 2018-07-15T05:40:00Z | 8.99 | 24 | BVDSD | 6.93 | 2018-07-15T05:50:00Z | 14.99 | 84 | < 25mph
108 | SDG&E | 20190911IG01 | September | 11 | 2019 | 3 | 2019-09-11 | 14:17 | 33.226 | -117.085 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 2 | NE | HP013 | 1.71 | 2015-01-19T08:07:00Z | 5.14 | 18 | HP010 | 6.57 | 2015-01-19T07:56:00Z | 8.72 | 55 | HP013 | 1.71 | 2015-01-19T08:07:00Z | 5.14 | 36 | HP010 | 6.57 | 2015-01-19T09:26:00Z | 9.17 | 110 | < 25mph
1 | SDG&E | 20150211IG01 | February | 11 | 2015 | 1 | 2015-02-11 | 15:30 | 32.8941 | -116.9393 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | EA | BFDSD | 3.99 | 2015-11-18T21:00:00Z | 14.99 | 12 | BFDSD | 3.99 | 2015-11-18T21:00:00Z | 14.99 | 36 | BFDSD | 3.99 | 2015-11-18T21:00:00Z | 14.99 | 24 | BFDSD | 3.99 | 2015-11-18T21:00:00Z | 14.99 | 72 | < 25mph
51 | SDG&E | 20160927IG01 | September | 27 | 2016 | 3 | 2016-09-27 | 10:18 | 33.2967 | -117.2079 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Animal |  | Unknown | Tier 2 | NE | BVDC1 | 1.77 | 2017-04-23T10:50:00Z | 12.01 | 38 | BVDC1 | 1.77 | 2017-04-23T10:50:00Z | 12.01 | 130 | BVDC1 | 1.77 | 2017-04-23T10:50:00Z | 12.01 | 77 | BVDC1 | 1.77 | 2017-04-23T10:50:00Z | 12.01 | 271 | < 25mph
45 | SDG&E | 20160711IG02 | July | 11 | 2016 | 3 | 2016-07-11 | 13:19 | 33.1146 | -116.5843 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  |  | Tier 3 | RA | OTYSD | 2.79 | 2016-01-03T19:00:00Z | 11.01 | 69 | CHOSD | 5.71 | 2016-01-03T19:00:00Z | 11.01 | 116 | E4521 | 1.81 | 2016-01-03T19:55:00Z | 22.01 | 140 | E4521 | 1.81 | 2016-01-03T19:55:00Z | 22.01 | 232 | < 25mph
90 | SDG&E | 20180708IG01 | July | 8 | 2018 | 3 | 2018-07-08 | 16:16 | 32.6349 | -117.103 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Other | Non- HFTD | CM | NATSD | 1.77 | 2016-05-30T16:40:00Z | 7 | 11 | NATSD | 1.77 | 2016-05-30T16:40:00Z | 7 | 114 | NATSD | 1.77 | 2016-05-30T17:40:00Z | 8.99 | 22 | NATSD | 1.77 | 2016-05-30T17:40:00Z | 8.99 | 226 | < 25mph
28 | SDG&E | 20160103IG01 | January | 3 | 2016 | 1 | 2016-01-03 | 4:30 | 33.1915 | -117.3655 | Other | Urban | Less Than .25 Acres | Fire Agency | 12kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | Other | Non- HFTD | NC | ESCSD | 2.91 | 2018-01-30T16:20:00Z | 8.99 | 30 | HDMSD | 7.24 | 2018-01-30T16:10:00Z | 20 | 210 | ESCSD | 2.91 | 2018-01-30T16:20:00Z | 8.99 | 59 | HDMSD | 7.24 | 2018-01-30T16:10:00Z | 20 | 417 | < 25mph
72 | SDG&E | 20171016IG01 | October | 16 | 2017 | 4 | 2017-10-16 | 10:20 | 33.0697 | -116.8813 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | RA | C2735 | 3.55 | 2015-03-05T06:44:00Z | 11.99 | 25 | C2735 | 3.55 | 2015-03-05T06:44:00Z | 11.99 | 126 | C2735 | 3.55 | 2015-03-05T06:49:00Z | 11.99 | 50 | C2735 | 3.55 | 2015-03-05T06:49:00Z | 11.99 | 250 | < 25mph
62 | SDG&E | 20170629IG02 | June | 29 | 2017 | 2 | 2017-06-29 | 14:58 | 32.6926 | -116.8564 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Electric Facility | None | Tier 3 | EA | SPPSD | 3.6 | 2016-05-29T00:30:00Z | 17 | 62 | GOSC1 | 5.3 | 2016-05-29T00:52:00Z | 22.01 | 140 | SPPSD | 3.6 | 2016-05-29T00:30:00Z | 17 | 122 | GOSC1 | 5.3 | 2016-05-29T00:52:00Z | 22.01 | 279 | < 25mph
52 | SDG&E | 20160929IG01 | September | 29 | 2016 | 3 | 2016-09-28 | 14:29 | 32.7418 | -116.9653 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Outside Force | Non- HFTD | EA | E9957 | 1.71 | 2018-05-25T20:25:00Z | 21 | 53 | E9915 | 6.09 | 2018-05-25T20:17:00Z | 24.99 | 168 | E9957 | 1.71 | 2018-05-25T21:25:00Z | 22.01 | 107 | E9915 | 6.09 | 2018-05-25T20:17:00Z | 24.99 | 339 | < 25mph
72 | SDG&E | 20171016IG01 | October | 16 | 2017 | 4 | 2017-10-16 | 10:20 | 33.0697 | -116.8813 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | RA | MPESD | 1.88 | 2019-10-05T02:20:00Z | 7.74 | 29 | E8360 | 4.9 | 2019-10-05T02:41:00Z | 13 | 193 | MPESD | 1.88 | 2019-10-05T02:20:00Z | 7.74 | 58 | E8360 | 4.9 | 2019-10-05T02:41:00Z | 13 | 382 | < 25mph
53 | SDG&E | 20161021IG01 | October | 21 | 2016 | 4 | 2016-10-21 | 11:20 | 33.0485 | -116.8615 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Transformer |  |  |  | Tier 2 | RA | DZRSD | 3.66 | 2015-12-08T20:40:00Z | 13 | 12 | POTSD | 6.93 | 2015-12-08T19:50:00Z | 15.99 | 56 | BRJSD | 0.73 | 2015-12-08T21:10:00Z | 14.99 | 24 | SVLSD | 7.93 | 2015-12-08T20:50:00Z | 21 | 112 | < 25mph
104 | SDG&E | 20190716IG01 | July | 16 | 2019 | 3 | 2019-07-16 | 19:08 | 33.182 | -117.1126 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Other | Tier 2 | NE | E3070 | 3.52 | 2016-01-16T19:20:00Z | 11.01 | 26 | LLDSD | 7.68 | 2016-01-16T19:20:00Z | 12.01 | 214 | ECJSD | 3.11 | 2016-01-16T20:20:00Z | 12.01 | 56 | CSTSD | 4.04 | 2016-01-16T20:20:00Z | 14.99 | 429 | < 25mph
118 | SDG&E | 20200211IG01 | February | 11 | 2020 | 1 | 2020-02-11 | 1:30 | 32.791 | -116.9194 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Outside Force | Non- HFTD | EA | WIRC1 | 2.46 | 2020-01-27T05:23:00Z | 3 | 39 | F6626 | 5.55 | 2020-01-27T05:25:00Z | 3 | 94 | WIRC1 | 2.46 | 2020-01-27T06:23:00Z | 4 | 77 | WIRC1 | 2.46 | 2020-01-27T06:23:00Z | 4 | 186 | < 25mph
73 | SDG&E | 20171018IG01 | October | 18 | 2017 | 4 | 2017-10-18 | 7:20 | 33.1659 | -117.2053 | Vegetation | Urban | Less Than .25 Acres | Unknown | 12kV | Overhead | No | Contact From Object |  | Vehicle | Pole | Human Error | Non- HFTD | NC | HDMSD | 2.89 | 2020-10-16T08:10:00Z | 13.59 | 76 | HF004 | 5.39 | 2020-10-16T08:45:00Z | 18.07 | 251 | HDMSD | 2.89 | 2020-10-16T08:10:00Z | 13.59 | 152 | HF004 | 5.39 | 2020-10-16T08:45:00Z | 18.07 | 499 | < 25mph
18 | SDG&E | 20150823IG01 | August | 23 | 2015 | 3 | 2015-08-23 | 15:00 | 33.2729 | -117.1521 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | NE | TDSSD | 3.89 | 2015-12-18T19:40:00Z | 24 | 14 | CWDSD | 5.27 | 2015-12-18T19:10:00Z | 25.99 | 28 | TDSSD | 3.89 | 2015-12-18T19:40:00Z | 24 | 26 | CWDSD | 5.27 | 2015-12-18T19:10:00Z | 25.99 | 52 | 25-40mph
106 | SDG&E | 20190805IG01 | August | 5 | 2019 | 3 | 2019-08-05 | 14:14 | 32.7886 | -117.1233 | Vegetation | Urban | Less Than .25 Acres | Utility | 12 kV | Overhead | No | Equipment/Facility Failure | Other |  |  | None | Non- HFTD | BC | STVSD | 1.13 | 2015-03-31T22:40:00Z | 21 | 24 | GOSC1 | 7.84 | 2015-03-31T22:52:00Z | 24.99 | 138 | STVSD | 1.13 | 2015-03-31T22:40:00Z | 21 | 48 | GOSC1 | 7.84 | 2015-03-31T22:52:00Z | 24.99 | 276 | < 25mph
135 | SDG&E | 20200906IG01 | September | 6 | 2020 | 3 | 2020-09-06 | 23:00 | 33.0965 | -117.0237 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Transformer |  |  | None | Tier 2 | NE | TWOSD | 3.27 | 2019-03-13T11:10:00Z | 8.01 | 30 | TLKSD | 7.71 | 2019-03-13T11:20:00Z | 14 | 109 | TWOSD | 3.27 | 2019-03-13T11:50:00Z | 8.99 | 60 | TLKSD | 7.71 | 2019-03-13T11:20:00Z | 14 | 222 | < 25mph
13 | SDG&E | 20150717IG01 | July | 17 | 2015 | 3 | 2015-07-17 | 9:48 | 33.3012 | -117.0222 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Communication Facility | Human Error | Tier 3 | NE | OLVSD | 2.24 | 2017-01-01T06:10:00Z | 12.01 | 16 | E9915 | 4.58 | 2017-01-01T06:16:00Z | 12.01 | 163 | OLVSD | 2.24 | 2017-01-01T06:10:00Z | 12.01 | 30 | E9915 | 4.58 | 2017-01-01T06:16:00Z | 12.01 | 313 | < 25mph
71 | SDG&E | 20171007IG01 | October | 7 | 2017 | 4 | 2017-10-07 | 17:40 | 32.5914 | -116.6216 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Conductor |  |  | Other | Tier 3 | ME | E4521 | 3.76 | 2020-06-15T01:46:00Z | 13 | 30 | EUCSD | 5.87 | 2020-06-15T01:10:00Z | 15.78 | 213 | E4521 | 3.76 | 2020-06-15T01:46:00Z | 13 | 61 | EUCSD | 5.87 | 2020-06-15T01:10:00Z | 15.78 | 433 | < 25mph
6 | SDG&E | 20150413IG01 | April | 13 | 2015 | 2 | 2015-04-13 | 10:50 | 32.5859 | -117.0017 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Tier 2 | CM | BLCSD | 3.88 | 2017-01-04T03:30:00Z | 4.99 | 75 | BRMSD | 6.64 | 2017-01-04T02:40:00Z | 5.99 | 159 | BLCSD | 3.88 | 2017-01-04T03:30:00Z | 4.99 | 153 | BRMSD | 6.64 | 2017-01-04T02:40:00Z | 5.99 | 321 | < 25mph
96 | SDG&E | 20180914IG02 | September | 14 | 2018 | 3 | 2018-09-14 | 10:00 | 33.3177 | -117.2228 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact Between Third Party Facility on Pole and Supply Lines |  | Vehicle | Communication Facility | Human Error | Tier 2 | NE | UCAB | 2 | 2017-12-02T10:30:00Z | 7.29 | 26 | UCI11 | 7.36 | 2017-12-02T10:00:00Z | 8.99 | 34 | UCAB | 2 | 2017-12-02T10:30:00Z | 7.29 | 52 | UCI11 | 7.36 | 2017-12-02T11:00:00Z | 13.15 | 69 | < 25mph
75 | SDG&E | 20171025IG01 | October | 25 | 2017 | 4 | 2017-10-25 | 13:02 | 33.2857 | -117.0275 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Other |  |  | Weather | Tier 2 | NE | SE452 | 3.79 | 2020-06-03T18:00:00Z | 9.06 | 12 | SE078 | 7.42 | 2020-06-03T18:00:00Z | 10.67 | 77 | SE452 | 3.79 | 2020-06-03T19:10:00Z | 12.13 | 24 | E4050 | 7.49 | 2020-06-03T18:45:00Z | 20 | 153 | < 25mph
28 | SDG&E | 20160103IG01 | January | 3 | 2016 | 1 | 2016-01-03 | 4:30 | 33.1915 | -117.3655 | Other | Urban | Less Than .25 Acres | Fire Agency | 12kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | Other | Non- HFTD | NC | ESCSD | 2.91 | 2019-06-01T01:10:00Z | 13 | 17 | ROCSD | 5.88 | 2019-06-01T01:00:00Z | 14.99 | 193 | ESCSD | 2.91 | 2019-06-01T01:10:00Z | 13 | 35 | ROCSD | 5.88 | 2019-06-01T01:00:00Z | 14.99 | 390 | < 25mph
53 | SDG&E | 20161021IG01 | October | 21 | 2016 | 4 | 2016-10-21 | 11:20 | 33.0485 | -116.8615 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Transformer |  |  |  | Tier 2 | RA | BRJSD | 0.73 | 2015-12-19T06:20:00Z | 15.99 | 12 | BRJSD | 0.73 | 2015-12-19T06:20:00Z | 15.99 | 56 | BRJSD | 0.73 | 2015-12-19T07:10:00Z | 17 | 24 | BRJSD | 0.73 | 2015-12-19T07:10:00Z | 17 | 112 | < 25mph
52 | SDG&E | 20160929IG01 | September | 29 | 2016 | 3 | 2016-09-28 | 14:29 | 32.7418 | -116.9653 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Outside Force | Non- HFTD | EA | F5340 | 2.1 | 2020-05-11T05:45:00Z | 7 | 57 | OLVSD | 7.37 | 2020-05-11T05:30:00Z | 10.58 | 185 | F5340 | 2.1 | 2020-05-11T07:00:00Z | 7 | 111 | OLVSD | 7.37 | 2020-05-11T07:20:00Z | 11.1 | 358 | < 25mph
71 | SDG&E | 20171007IG01 | October | 7 | 2017 | 4 | 2017-10-07 | 17:40 | 32.5914 | -116.6216 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Conductor |  |  | Other | Tier 3 | ME | E4521 | 3.76 | 2017-02-27T05:25:00Z | 5.99 | 31 | CSTSD | 4.04 | 2017-02-27T05:10:00Z | 8.01 | 156 | E4521 | 3.76 | 2017-02-27T05:25:00Z | 5.99 | 60 | MIGC1 | 7.97 | 2017-02-27T06:50:00Z | 8.99 | 307 | < 25mph
102 | SDG&E | 20190703IG01 | July | 3 | 2019 | 3 | 2019-07-03 | 15:15 | 33.0113 | -116.8492 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 3 | RA | AT125 | 2.22 | 2015-02-28T18:03:00Z | 14 | 19 | FBKSD | 6.92 | 2015-02-28T18:10:00Z | 21 | 69 | AT125 | 2.22 | 2015-02-28T19:23:00Z | 18.99 | 37 | FBKSD | 6.92 | 2015-02-28T18:40:00Z | 21 | 135 | < 25mph
34 | SDG&E | 20160218IG01 | February | 18 | 2016 | 1 | 2016-02-18 | 0:00 | 32.7063 | -116.397 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | None | Tier 3 | ME | OTYSD | 3.89 | 2019-02-16T04:40:00Z | 14 | 36 | OTYSD | 3.89 | 2019-02-16T04:40:00Z | 14 | 164 | OTYSD | 3.89 | 2019-02-16T05:50:00Z | 22.01 | 72 | OTYSD | 3.89 | 2019-02-16T05:50:00Z | 22.01 | 323 | < 25mph
106 | SDG&E | 20190805IG01 | August | 5 | 2019 | 3 | 2019-08-05 | 14:14 | 32.7886 | -117.1233 | Vegetation | Urban | Less Than .25 Acres | Utility | 12 kV | Overhead | No | Equipment/Facility Failure | Other |  |  | None | Non- HFTD | BC | WCKSD | 0.29 | 2020-09-09T16:40:00Z | 24.85 | 24 | HOSSD | 5 | 2020-09-09T17:10:00Z | 27.91 | 132 | WCKSD | 0.29 | 2020-09-09T16:40:00Z | 24.85 | 48 | HOSSD | 5 | 2020-09-09T17:10:00Z | 27.91 | 264 | 25-40mph
48 | SDG&E | 20160731IG01 | July | 31 | 2016 | 3 | 2016-07-31 | 13:43 | 33.3663 | -117.2033 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Unknown | Tier 2 | NE | HVWSD | 2.49 | 2020-01-29T06:30:00Z | 9.06 | 32 | HDMSD | 7.44 | 2020-01-29T07:00:00Z | 17 | 172 | SPVSD | 3.81 | 2020-01-29T07:50:00Z | 10 | 65 | HDMSD | 7.44 | 2020-01-29T07:40:00Z | 18.01 | 345 | < 25mph
98 | SDG&E | 20181126IG01 | November | 26 | 2018 | 4 | 2018-11-26 | 1:51 | 33.4314 | -117.5952 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility |  | Tier 2 | OC | COCSD | 3.91 | 2018-11-10T12:30:00Z | 10 | 18 | MTLSD | 7.68 | 2018-11-10T13:00:00Z | 10 | 113 | COCSD | 3.91 | 2018-11-10T12:30:00Z | 10 | 36 | MTLSD | 7.68 | 2018-11-10T13:00:00Z | 10 | 225 | < 25mph
75 | SDG&E | 20171025IG01 | October | 25 | 2017 | 4 | 2017-10-25 | 13:02 | 33.2857 | -117.0275 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Other |  |  | Weather | Tier 2 | NE |  |  |  | 0 | 0 | FBZCA | 5.03 | 2017-07-28T05:22:00Z | 7 | 32 |  |  |  | 0 | 0 | FBZCA | 5.03 | 2017-07-28T05:22:00Z | 7 | 64 | < 25mph
125 | SDG&E | 20200717IG01 | July | 17 | 2020 | 3 | 2020-07-17 | 16:30 | 33.0904 | -116.5798 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | RA | SDEFF | 3.05 | 2015-09-16T14:54:00Z | 7 | 45 | SDEFF | 3.05 | 2015-09-16T14:54:00Z | 7 | 213 | HDMSD | 3.87 | 2015-09-16T15:50:00Z | 8.01 | 80 | WRBSD | 4.74 | 2015-09-16T16:10:00Z | 8.99 | 414 | < 25mph
118 | SDG&E | 20200211IG01 | February | 11 | 2020 | 1 | 2020-02-11 | 1:30 | 32.791 | -116.9194 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Outside Force | Non- HFTD | EA | WIRC1 | 2.46 | 2020-03-17T05:23:00Z | 28.99 | 42 | WIRC1 | 2.46 | 2020-03-17T05:23:00Z | 28.99 | 98 | WIRC1 | 2.46 | 2020-03-17T05:23:00Z | 28.99 | 79 | WIRC1 | 2.46 | 2020-03-17T05:23:00Z | 28.99 | 191 | 25-40mph
135 | SDG&E | 20200906IG01 | September | 6 | 2020 | 3 | 2020-09-06 | 23:00 | 33.0965 | -117.0237 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Transformer |  |  | None | Tier 2 | NE | AT125 | 3.8 | 2016-04-30T23:57:00Z | 14 | 30 | TLKSD | 7.71 | 2016-05-01T00:00:00Z | 14.99 | 112 | AT125 | 3.8 | 2016-05-01T00:47:00Z | 14.99 | 60 | TLKSD | 7.71 | 2016-05-01T00:00:00Z | 14.99 | 225 | < 25mph
42 | SDG&E | 20160627IG01 | June | 27 | 2016 | 2 | 2016-06-27 | 15:30 | 33.2837 | -116.6174 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Human Error | Tier 2 | RA | MIGSD | 2.96 | 2016-07-11T08:50:00Z | 11.01 | 45 | MIGSD | 2.96 | 2016-07-11T08:50:00Z | 11.01 | 113 | MIGSD | 2.96 | 2016-07-11T08:50:00Z | 11.01 | 90 | NATSD | 7.86 | 2016-07-11T10:00:00Z | 11.01 | 227 | < 25mph
97 | SDG&E | 20181015IG01 | October | 15 | 2018 | 4 | 2018-10-15 | 10:21 | 33.3191 | -117.2597 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure |  |  |  | None | Tier 2 | NE | TWOSD | 2.48 | 2019-08-08T06:50:00Z | 3 | 42 | OLVSD | 7.1 | 2019-08-08T07:10:00Z | 4.99 | 172 | ESCSD | 3.61 | 2019-08-08T08:40:00Z | 4.99 | 84 | LKWSD | 6.77 | 2019-08-08T08:40:00Z | 5.99 | 353 | < 25mph
98 | SDG&E | 20181126IG01 | November | 26 | 2018 | 4 | 2018-11-26 | 1:51 | 33.4314 | -117.5952 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility |  | Tier 2 | OC | SVCSD | 1.46 | 2016-12-15T03:30:00Z | 4.99 | 18 | MTLSD | 7.68 | 2016-12-15T04:10:00Z | 8.99 | 96 | SVCSD | 1.46 | 2016-12-15T03:30:00Z | 4.99 | 36 | MTLSD | 7.68 | 2016-12-15T04:50:00Z | 13 | 196 | < 25mph
112 | SDG&E | 20191019IG01 | October | 19 | 2019 | 4 | 2019-10-19 | 13:10 | 33.2317 | -117.2593 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 240V | Overhead | Yes | Other |  |  |  | Human Error | Non- HFTD | NC | AVOSD | 3.47 | 2020-10-10T12:10:00Z | 2.49 | 46 | 063SE | 6.21 | 2020-10-10T12:10:00Z | 5.19 | 130 | FBKSD | 2.22 | 2020-10-10T12:50:00Z | 4.38 | 92 | RNBSD | 4.99 | 2020-10-10T12:40:00Z | 7.09 | 260 | < 25mph
128 | SDG&E | 20200801IG01 | August | 1 | 2020 | 3 | 2020-08-01 | 11:11 | 32.631 | -116.174 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Other |  |  | Unknown | Tier 2 | ME | MADSD | 3.61 | 2019-11-03T02:30:00Z | 5.19 | 33 | BLUSD | 5.42 | 2019-11-03T02:40:00Z | 8.19 | 177 | SPVSD | 3.81 | 2019-11-03T03:30:00Z | 8.99 | 66 | HDMSD | 7.44 | 2019-11-03T03:30:00Z | 14 | 354 | < 25mph
104 | SDG&E | 20190716IG01 | July | 16 | 2019 | 3 | 2019-07-16 | 19:08 | 33.182 | -117.1126 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Other | Tier 2 | NE | ECJSD | 3.11 | 2017-06-07T13:10:00Z | 5.99 | 31 | ECJSD | 3.11 | 2017-06-07T13:10:00Z | 5.99 | 195 | ECJSD | 3.11 | 2017-06-07T14:10:00Z | 5.99 | 66 | ECJSD | 3.11 | 2017-06-07T14:10:00Z | 5.99 | 403 | < 25mph
16 | SDG&E | 20150813IG01 | August | 13 | 2015 | 3 | 2015-08-13 | 20:33 | 33.2457 | -116.6769 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Unknown |  |  |  | Unknown | Tier 2 | RA | F1327 | 1.71 | 2018-12-01T06:30:00Z | 12.01 | 44 | TEOC1 | 4.21 | 2018-12-01T06:22:00Z | 14 | 66 | F1327 | 1.71 | 2018-12-01T07:15:00Z | 14.99 | 88 | F1327 | 1.71 | 2018-12-01T07:15:00Z | 14.99 | 130 | < 25mph
113 | SDG&E | 20191024IG01 | October | 24 | 2019 | 4 | 2019-10-24 | 10:16 | 32.8357 | -116.7252 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Fuse |  |  | None | Tier 3 | ME | JAMSD | 2.55 | 2018-03-17T19:50:00Z | 12.01 | 6 | OTMSD | 5.53 | 2018-03-17T20:10:00Z | 17 | 84 | JAMSD | 2.55 | 2018-03-17T21:10:00Z | 13 | 12 | OTYC1 | 5.44 | 2018-03-17T21:14:00Z | 23 | 168 | < 25mph
86 | SDG&E | 20180612IG02 | June | 12 | 2018 | 2 | 2018-06-12 | 15:14 | 32.864 | -116.747 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact from Object |  | Balloons | Electric Facility | None | Tier 3 | EA | GOSC1 | 1.64 | 2020-03-20T04:52:00Z | 7 | 61 | HP005 | 7.6 | 2020-03-20T04:53:00Z | 14.54 | 162 | GOSC1 | 1.64 | 2020-03-20T04:52:00Z | 7 | 116 | HP005 | 7.6 | 2020-03-20T06:33:00Z | 14.76 | 307 | < 25mph
75 | SDG&E | 20171025IG01 | October | 25 | 2017 | 4 | 2017-10-25 | 13:02 | 33.2857 | -117.0275 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Other |  |  | Weather | Tier 2 | NE |  |  |  | 0 | 0 | FBOC1 | 6.65 | 2016-04-12T14:00:00Z | 9.24 | 42 |  |  |  | 0 | 0 | FBOC1 | 6.65 | 2016-04-12T14:00:00Z | 9.24 | 83 | < 25mph
107 | SDG&E | 20190910IG01 | September | 10 | 2019 | 3 | 2019-09-10 | 12:59 | 32.5638 | -117.0333 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | None | Tier 2 | CM | TCNSD | 3.17 | 2016-12-15T16:50:00Z | 8.01 | 31 | MTLSD | 7.42 | 2016-12-15T17:10:00Z | 8.99 | 172 | MPESD | 3.91 | 2016-12-15T17:40:00Z | 8.99 | 65 | E3170 | 4.53 | 2016-12-15T17:32:00Z | 10 | 340 | < 25mph
115 | SDG&E | 20191101IG01 | November | 1 | 2019 | 4 | 2019-11-01 | 5:49 | 33.0924 | -117.0206 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | None | Non- HFTD | NE | HMDSD | 3.26 | 2018-09-01T19:10:00Z | 15.99 | 36 | OLVSD | 7.1 | 2018-09-01T19:50:00Z | 21 | 151 | HMDSD | 3.26 | 2018-09-01T19:10:00Z | 15.99 | 72 | OLVSD | 7.1 | 2018-09-01T20:20:00Z | 21 | 305 | < 25mph
57 | SDG&E | 20170608IG01 | June | 8 | 2017 | 2 | 2017-06-08 | 4:12 | 33.0356 | -117.1839 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Tier 2 | NC | HP007 | 3.33 | 2016-02-27T04:16:00Z | 9.4 | 34 | AT107 | 7.33 | 2016-02-27T03:37:00Z | 12.01 | 73 | HP007 | 3.33 | 2016-02-27T04:16:00Z | 9.4 | 68 | AT107 | 7.33 | 2016-02-27T03:37:00Z | 12.01 | 145 | < 25mph
72 | SDG&E | 20171016IG01 | October | 16 | 2017 | 4 | 2017-10-16 | 10:20 | 33.0697 | -116.8813 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | RA | KMYF | 1.01 | 2016-01-31T16:46:00Z | 31.07 | 42 | MTLSD | 4.71 | 2016-01-31T16:50:00Z | 42.99 | 219 | KMYF | 1.01 | 2016-01-31T16:46:00Z | 31.07 | 83 | MTLSD | 4.71 | 2016-01-31T16:50:00Z | 42.99 | 437 | 40-55mph
87 | SDG&E | 20180622IG01 | June | 22 | 2018 | 2 | 2018-06-22 | 9:46 | 32.567 | -116.941 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | Unknown | Tier 2 | CM | WCVSD | 1.06 | 2017-10-08T13:20:00Z | 15.99 | 30 | WCVSD | 1.06 | 2017-10-08T13:20:00Z | 15.99 | 177 | WCVSD | 1.06 | 2017-10-08T13:20:00Z | 15.99 | 60 | SQTSD | 4.87 | 2017-10-08T14:20:00Z | 15.99 | 350 | < 25mph
43 | SDG&E | 20160702IG01 | July | 2 | 2016 | 3 | 2016-07-02 | 7:51 | 32.81 | -116.878 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Capacitor Bank |  |  | None | Tier 2 | EA | CWDSD | 1.71 | 2020-06-13T13:40:00Z | 12.28 | 12 | HF003 | 6.71 | 2020-06-13T13:45:00Z | 26.7 | 59 | CWDSD | 1.71 | 2020-06-13T13:40:00Z | 12.28 | 24 | HF003 | 6.71 | 2020-06-13T13:45:00Z | 26.7 | 118 | 25-40mph
71 | SDG&E | 20171007IG01 | October | 7 | 2017 | 4 | 2017-10-07 | 17:40 | 32.5914 | -116.6216 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Conductor |  |  | Other | Tier 3 | ME | E4858 | 0.85 | 2015-10-23T02:53:00Z | 4.99 | 30 | DEHSD | 4.89 | 2015-10-23T02:50:00Z | 8.01 | 224 | E4858 | 0.85 | 2015-10-23T02:53:00Z | 4.99 | 60 | DEHSD | 4.89 | 2015-10-23T02:50:00Z | 8.01 | 447 | < 25mph
124 | SDG&E | 20200705IG01 | July | 5 | 2020 | 3 | 2020-07-05 | 14:08 | 33.0872 | -116.9856 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 3 | NE | CVXSD | 2.09 | 2015-07-10T23:40:00Z | 18.01 | 19 | MIGSD | 6.84 | 2015-07-10T23:30:00Z | 18.99 | 51 | CVXSD | 2.09 | 2015-07-11T01:00:00Z | 18.01 | 38 | MIGSD | 6.84 | 2015-07-11T00:20:00Z | 18.99 | 102 | < 25mph
76 | SDG&E | 20171210IG01 | December | 10 | 2017 | 4 | 2017-12-10 | 5:26 | 33.28 | -116.955 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 3 | NE | BLCSD | 2.89 | 2020-02-07T03:20:00Z | 7.09 | 50 | CESSD | 4.62 | 2020-02-07T03:30:00Z | 10 | 141 | BLCSD | 2.89 | 2020-02-07T03:20:00Z | 7.09 | 99 | CESSD | 4.62 | 2020-02-07T03:30:00Z | 10 | 280 | < 25mph
10 | SDG&E | 20150517IG01 | May | 17 | 2015 | 2 | 2015-05-17 | 6:55 | 33.1808 | -117.2064 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility |  | Non- HFTD | NC | DLZSD | 0.55 | 2020-02-21T21:00:00Z | 14 | 11 | SRUC1 | 6.25 | 2020-02-21T21:54:00Z | 21 | 68 | DLZSD | 0.55 | 2020-02-21T22:10:00Z | 15.99 | 22 | SE228 | 7.04 | 2020-02-21T22:00:00Z | 21.12 | 135 | < 25mph
65 | SDG&E | 20170728IG01 | July | 28 | 2017 | 3 | 2017-07-28 | 16:31 | 32.7802 | -116.8722 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Pole /Conductor | Vehicle | Electric Facility | Outside Force | Tier 2 | EA | HP007 | 3.33 | 2019-10-02T15:04:00Z | 12.3 | 30 | RNBSD | 6.26 | 2019-10-02T15:00:00Z | 18.99 | 75 | FBZC1 | 2.31 | 2019-10-02T15:22:00Z | 13 | 60 | RNBSD | 6.26 | 2019-10-02T15:00:00Z | 18.99 | 150 | < 25mph
142 | SDG&E | 20201130IG01 | November | 30 | 2020 | 4 | 2020-11-30 | 9:10 | 33.266 | -117.223 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 2 | NE | AVYSD | 3.27 | 2016-07-20T08:00:00Z | 8.99 | 37 | AVYSD | 3.27 | 2016-07-20T08:00:00Z | 8.99 | 191 | AVYSD | 3.27 | 2016-07-20T08:10:00Z | 8.99 | 74 | SWRSD | 4.3 | 2016-07-20T08:30:00Z | 14.99 | 381 | < 25mph
55 | SDG&E | 20161112IG01 | November | 12 | 2016 | 4 | 2016-11-12 | 20:30 | 32.6227 | -116.9388 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  |  | Tier 2 | CM | AT057 | 1.8 | 2015-08-18T03:00:00Z | 8.01 | 50 | MTLSD | 4.13 | 2015-08-18T03:00:00Z | 12.01 | 156 | AT057 | 1.8 | 2015-08-18T03:00:00Z | 8.01 | 96 | MTLSD | 4.13 | 2015-08-18T03:00:00Z | 12.01 | 299 | < 25mph
50 | SDG&E | 20160923IG01 | September | 23 | 2016 | 3 | 2016-09-23 | 11:25 | 32.7372 | -116.7343 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Transformer |  |  | None | Tier 3 | EA | SSOSD | 3.93 | 2020-08-19T08:30:00Z | 5.91 | 56 | SPPSD | 7.31 | 2020-08-19T08:30:00Z | 7.53 | 152 | GOSC1 | 1.04 | 2020-08-19T08:52:00Z | 5.99 | 112 | HVWSD | 6.3 | 2020-08-19T09:10:00Z | 8.77 | 303 | < 25mph
121 | SDG&E | 20200531IG01 | May | 31 | 2020 | 2 | 2020-05-31 | 2:01 | 32.543 | -117.0277 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Outside Force | Non- HFTD | CM | MGYSD | 1.96 | 2019-08-31T04:10:00Z | 7 | 20 | HP016 | 6.11 | 2019-08-31T05:05:00Z | 14.54 | 86 | MGYSD | 1.96 | 2019-08-31T04:10:00Z | 7 | 38 | HP016 | 6.11 | 2019-08-31T06:05:00Z | 16.11 | 164 | < 25mph
33 | SDG&E | 20160212IG01 | February | 12 | 2016 | 1 | 2016-02-12 | 19:30 | 33.2427 | -116.9664 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Vandalism/Theft |  |  |  | Outside Force | Tier 3 | NE | E8894 | 1.45 | 2016-08-19T04:17:00Z | 8.01 | 32 | WRBSD | 7.25 | 2016-08-19T04:10:00Z | 10 | 155 | E8894 | 1.45 | 2016-08-19T04:17:00Z | 8.01 | 53 | WRBSD | 7.25 | 2016-08-19T04:10:00Z | 10 | 270 | < 25mph
107 | SDG&E | 20190910IG01 | September | 10 | 2019 | 3 | 2019-09-10 | 12:59 | 32.5638 | -117.0333 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | None | Tier 2 | CM | MPESD | 3.91 | 2017-02-20T14:30:00Z | 5.99 | 47 | UCEL | 6.53 | 2017-02-20T14:20:00Z | 7.4 | 220 | LJHSD | 3.27 | 2017-02-20T15:40:00Z | 5.99 | 91 | C2735 | 6.33 | 2017-02-20T15:57:00Z | 8.99 | 425 | < 25mph
115 | SDG&E | 20191101IG01 | November | 1 | 2019 | 4 | 2019-11-01 | 5:49 | 33.0924 | -117.0206 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | None | Non- HFTD | NE | TLKSD | 3.72 | 2020-11-27T23:40:00Z | 15.49 | 66 | CDVSD | 5.79 | 2020-11-27T23:40:00Z | 18.19 | 244 | TLKSD | 3.72 | 2020-11-27T23:40:00Z | 15.49 | 130 | CDVSD | 5.79 | 2020-11-27T23:40:00Z | 18.19 | 487 | < 25mph
40 | SDG&E | 20160614IG01 | June | 14 | 2016 | 2 | 2016-06-14 | 6:05 | 32.8801 | -116.9051 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Outside Force | Tier 2 | EA | E9888 | 1.63 | 2017-10-16T19:35:00Z | 11.01 | 34 | E9888 | 1.63 | 2017-10-16T19:35:00Z | 11.01 | 71 | E9888 | 1.63 | 2017-10-16T20:30:00Z | 11.01 | 68 | KSDM | 6.05 | 2017-10-16T19:55:00Z | 21.85 | 139 | < 25mph
13 | SDG&E | 20150717IG01 | July | 17 | 2015 | 3 | 2015-07-17 | 9:48 | 33.3012 | -117.0222 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Communication Facility | Human Error | Tier 3 | NE | WRBSD | 3.95 | 2018-06-04T06:10:00Z | 7 | 37 | WRBSD | 3.95 | 2018-06-04T06:10:00Z | 7 | 173 | OLVSD | 2.24 | 2018-06-04T07:50:00Z | 7 | 75 | AV241 | 7.25 | 2018-06-04T07:38:00Z | 7 | 351 | < 25mph
116 | SDG&E | 20191104IG01 | November | 4 | 2019 | 4 | 2019-11-04 | 15:30 | 33.1969 | -116.7121 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Other |  |  |  | Tier 3 | RA | UCI10 | 3.52 | 2018-01-07T09:00:00Z | 20.83 | 26 | UCI14 | 5.71 | 2018-01-07T09:00:00Z | 28.5 | 31 | UCI10 | 3.52 | 2018-01-07T09:00:00Z | 20.83 | 52 | UCI14 | 5.71 | 2018-01-07T09:00:00Z | 28.5 | 62 | 25-40mph
25 | SDG&E | 20151002IG01 | October | 2 | 2015 | 4 | 2015-10-02 | 14:30 | 33.1354 | -117.0588 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | NE | FTVSD | 1.29 | 2018-01-17T00:30:00Z | 5.99 | 47 | HP014 | 6.9 | 2018-01-17T01:07:00Z | 12.3 | 158 | FTVSD | 1.29 | 2018-01-17T00:30:00Z | 5.99 | 92 | HP014 | 6.9 | 2018-01-17T01:07:00Z | 12.3 | 313 | < 25mph
35 | SDG&E | 20160303IG01 | March | 3 | 2016 | 1 | 2016-03-03 | 6:00 | 32.8472 | -116.942 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Non- HFTD | EA | KL18 | 3 | 2018-08-20T19:55:00Z | 19.57 | 15 | PZAC1 | 7.39 | 2018-08-20T19:50:00Z | 20 | 90 | KL18 | 3 | 2018-08-20T19:55:00Z | 19.57 | 27 | FBZCA | 5.75 | 2018-08-20T20:22:00Z | 22.01 | 177 | < 25mph
97 | SDG&E | 20181015IG01 | October | 15 | 2018 | 4 | 2018-10-15 | 10:21 | 33.3191 | -117.2597 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure |  |  |  | None | Tier 2 | NE | TLKSD | 3.72 | 2020-11-02T14:00:00Z | 5.19 | 65 | E8699 | 6.74 | 2020-11-02T14:26:00Z | 23 | 245 | HMDSD | 3.26 | 2020-11-02T15:20:00Z | 6.5 | 129 | E8699 | 6.74 | 2020-11-02T14:36:00Z | 23 | 486 | < 25mph
124 | SDG&E | 20200705IG01 | July | 5 | 2020 | 3 | 2020-07-05 | 14:08 | 33.0872 | -116.9856 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 3 | NE | NATSD | 2.2 | 2020-06-25T04:10:00Z | 6.87 | 45 | NATSD | 2.2 | 2020-06-25T04:10:00Z | 6.87 | 107 | NATSD | 2.2 | 2020-06-25T04:10:00Z | 6.87 | 90 | NATSD | 2.2 | 2020-06-25T04:10:00Z | 6.87 | 214 | < 25mph
20 | SDG&E | 20150901IG02 | September | 1 | 2015 | 3 | 2015-09-01 | 8:50 | 32.669 | -116.286 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | None | Tier 2 | ME | WIRC1 | 2.46 | 2020-07-18T12:23:00Z | 5 | 38 | CBDSD | 5.25 | 2020-07-18T12:50:00Z | 5.34 | 87 | WIRC1 | 2.46 | 2020-07-18T13:23:00Z | 5 | 77 | CBDSD | 5.25 | 2020-07-18T12:50:00Z | 5.34 | 174 | < 25mph
50 | SDG&E | 20160923IG01 | September | 23 | 2016 | 3 | 2016-09-23 | 11:25 | 32.7372 | -116.7343 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Transformer |  |  | None | Tier 3 | EA | CLMSD | 3.78 | 2016-09-22T17:00:00Z | 14 | 62 | HP005 | 6.69 | 2016-09-22T17:05:00Z | 34 | 145 | CLMSD | 3.78 | 2016-09-22T18:00:00Z | 15.99 | 124 | HP005 | 6.69 | 2016-09-22T17:15:00Z | 34.9 | 290 | 25-40mph
108 | SDG&E | 20190911IG01 | September | 11 | 2019 | 3 | 2019-09-11 | 14:17 | 33.226 | -117.085 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 2 | NE | EWNSD | 3.96 | 2020-12-07T21:10:00Z | 32 | 12 | WARSD | 5.24 | 2020-12-07T21:50:00Z | 41.78 | 48 | EWNSD | 3.96 | 2020-12-07T21:10:00Z | 32 | 24 | WARSD | 5.24 | 2020-12-07T21:50:00Z | 41.78 | 96 | 40-55mph
94 | SDG&E | 20180819IG01 | August | 19 | 2018 | 3 | 2018-08-19 | 18:35 | 32.7002 | -116.8639 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | EA | DZRSD | 0.55 | 2020-09-10T23:30:00Z | 17.68 | 6 | SVLSD | 7.84 | 2020-09-10T23:30:00Z | 22.07 | 56 | DZRSD | 0.55 | 2020-09-10T23:30:00Z | 17.68 | 12 | SVLSD | 7.84 | 2020-09-10T23:30:00Z | 22.07 | 112 | < 25mph
7 | SDG&E | 20150418IG01 | April | 18 | 2015 | 2 | 2015-04-18 | 12:00 | 32.7764 | -116.9309 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Secondary | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | None | Non- HFTD | EA | SMCSD | 3.76 | 2017-11-09T12:50:00Z | 4.99 | 47 | E9915 | 6.01 | 2017-11-09T12:49:00Z | 8.01 | 183 | SMCSD | 3.76 | 2017-11-09T12:50:00Z | 4.99 | 96 | E9915 | 6.01 | 2017-11-09T13:05:00Z | 8.01 | 365 | < 25mph
102 | SDG&E | 20190703IG01 | July | 3 | 2019 | 3 | 2019-07-03 | 15:15 | 33.0113 | -116.8492 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 3 | RA | E3055 | 2.18 | 2020-03-30T21:40:00Z | 7 | 12 | FBKSD | 6.92 | 2020-03-30T21:40:00Z | 20.09 | 78 | E3055 | 2.18 | 2020-03-30T22:30:00Z | 10 | 24 | FBKSD | 6.92 | 2020-03-30T21:40:00Z | 20.09 | 156 | < 25mph
73 | SDG&E | 20171018IG01 | October | 18 | 2017 | 4 | 2017-10-18 | 7:20 | 33.1659 | -117.2053 | Vegetation | Urban | Less Than .25 Acres | Unknown | 12kV | Overhead | No | Contact From Object |  | Vehicle | Pole | Human Error | Non- HFTD | NC | WRBSD | 3.58 | 2015-11-03T01:20:00Z | 18.01 | 95 | OLVSD | 4.4 | 2015-11-03T01:30:00Z | 18.99 | 175 | WRBSD | 3.58 | 2015-11-03T03:10:00Z | 20 | 188 | DMHSD | 5.44 | 2015-11-03T02:50:00Z | 21 | 357 | < 25mph
52 | SDG&E | 20160929IG01 | September | 29 | 2016 | 3 | 2016-09-28 | 14:29 | 32.7418 | -116.9653 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Outside Force | Non- HFTD | EA | D5683 | 3.27 | 2015-10-04T15:48:00Z | 14.99 | 52 | E0995 | 7.15 | 2015-10-04T16:05:00Z | 22.01 | 146 | D5683 | 3.27 | 2015-10-04T15:48:00Z | 14.99 | 99 | E0995 | 7.15 | 2015-10-04T16:45:00Z | 24 | 281 | < 25mph
107 | SDG&E | 20190910IG01 | September | 10 | 2019 | 3 | 2019-09-10 | 12:59 | 32.5638 | -117.0333 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | None | Tier 2 | CM | MSDSD | 3.66 | 2018-12-29T13:30:00Z | 10 | 40 | MTLSD | 7.42 | 2018-12-29T13:10:00Z | 11.01 | 128 | MSDSD | 3.66 | 2018-12-29T13:30:00Z | 10 | 79 | MTLSD | 7.42 | 2018-12-29T13:10:00Z | 11.01 | 256 | < 25mph
118 | SDG&E | 20200211IG01 | February | 11 | 2020 | 1 | 2020-02-11 | 1:30 | 32.791 | -116.9194 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Outside Force | Non- HFTD | EA | WIRC1 | 2.46 | 2015-09-13T11:23:00Z | 7 | 13 | WIRC1 | 2.46 | 2015-09-13T11:23:00Z | 7 | 57 | WIRC1 | 2.46 | 2015-09-13T12:23:00Z | 7 | 26 | WIRC1 | 2.46 | 2015-09-13T12:23:00Z | 7 | 114 | < 25mph
5 | SDG&E | 20150412IG02 | April | 12 | 2015 | 2 | 2015-04-12 | 14:30 | 33.2754 | -117.3306 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vehicle | Pole |  | Tier 2 | NC | KL18 | 2.48 | 2017-07-17T23:35:00Z | 16.11 | 12 | FBZCA | 4.6 | 2017-07-18T00:22:00Z | 21 | 70 | KL18 | 2.48 | 2017-07-17T23:35:00Z | 16.11 | 23 | FBZCA | 4.6 | 2017-07-18T00:22:00Z | 21 | 140 | < 25mph
73 | SDG&E | 20171018IG01 | October | 18 | 2017 | 4 | 2017-10-18 | 7:20 | 33.1659 | -117.2053 | Vegetation | Urban | Less Than .25 Acres | Unknown | 12kV | Overhead | No | Contact From Object |  | Vehicle | Pole | Human Error | Non- HFTD | NC | HDMSD | 2.89 | 2016-01-19T08:00:00Z | 4.99 | 106 | HDMSD | 2.89 | 2016-01-19T08:00:00Z | 4.99 | 215 | HDMSD | 2.89 | 2016-01-19T09:20:00Z | 8.01 | 208 | RPQSD | 5.87 | 2016-01-19T09:30:00Z | 13 | 419 | < 25mph
25 | SDG&E | 20151002IG01 | October | 2 | 2015 | 4 | 2015-10-02 | 14:30 | 33.1354 | -117.0588 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | NE | RCESD | 2.26 | 2019-09-18T02:40:00Z | 7 | 53 | ROCSD | 6.95 | 2019-09-18T02:00:00Z | 8.25 | 180 | RCRSD | 0.81 | 2019-09-18T03:20:00Z | 8.99 | 106 | RCRSD | 0.81 | 2019-09-18T03:20:00Z | 8.99 | 359 | < 25mph
12 | SDG&E | 20150707IG01 | July | 7 | 2015 | 3 | 2015-07-07 | 15:00 | 32.7443 | -117.0498 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Non- HFTD | EA | TWOSD | 1.86 | 2016-05-24T11:00:00Z | 8.01 | 34 | HMDSD | 5.07 | 2016-05-24T11:10:00Z | 11.01 | 141 | SMCSD | 3.76 | 2016-05-24T11:30:00Z | 8.01 | 69 | HMDSD | 5.07 | 2016-05-24T11:30:00Z | 11.01 | 284 | < 25mph
50 | SDG&E | 20160923IG01 | September | 23 | 2016 | 3 | 2016-09-23 | 11:25 | 32.7372 | -116.7343 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Transformer |  |  | None | Tier 3 | EA | GOSC1 | 1.04 | 2018-04-06T09:52:00Z | 8.99 | 48 | HVYSD | 4.19 | 2018-04-06T09:20:00Z | 8.99 | 125 | GOSC1 | 1.04 | 2018-04-06T09:52:00Z | 8.99 | 101 | HVYSD | 4.19 | 2018-04-06T09:20:00Z | 8.99 | 255 | < 25mph
2 | SDG&E | 20150319IG01 | March | 19 | 2015 | 1 | 2015-03-19 | 23:50 | 33.0565 | -117.0332 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 2 | NE | WIRC1 | 3.14 | 2015-04-16T22:17:00Z | 22.01 | 13 | C2635 | 7.73 | 2015-04-16T22:36:00Z | 38.97 | 51 | WIRC1 | 3.14 | 2015-04-16T23:17:00Z | 22.01 | 21 | C2635 | 7.73 | 2015-04-16T22:36:00Z | 38.97 | 96 | 25-40mph
94 | SDG&E | 20180819IG01 | August | 19 | 2018 | 3 | 2018-08-19 | 18:35 | 32.7002 | -116.8639 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | EA | DZRSD | 0.55 | 2019-02-11T15:30:00Z | 10 | 6 | BRJSD | 4.85 | 2019-02-11T15:20:00Z | 15.99 | 44 | DZRSD | 0.55 | 2019-02-11T16:20:00Z | 14 | 12 | BRJSD | 4.85 | 2019-02-11T15:20:00Z | 15.99 | 88 | < 25mph
82 | SDG&E | 20180422IG01 | April | 22 | 2018 | 2 | 2018-04-22 | 14:00 | 32.837 | -117.184 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | BC | HVWSD | 2.6 | 2015-10-08T11:10:00Z | 8.99 | 14 | HDMSD | 5.96 | 2015-10-08T11:10:00Z | 12.01 | 131 | HVWSD | 2.6 | 2015-10-08T11:10:00Z | 8.99 | 30 | HDMSD | 5.96 | 2015-10-08T13:00:00Z | 13 | 263 | < 25mph
29 | SDG&E | 20160109IG01 | January | 9 | 2016 | 1 | 2016-01-09 | 4:30 | 33.082 | -117.091 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Non- HFTD | NE | CSTSD | 1.38 | 2018-03-24T21:00:00Z | 20 | 91 | SQTSD | 5.8 | 2018-03-24T21:40:00Z | 24 | 186 | COCSD | 3.01 | 2018-03-24T21:50:00Z | 21 | 180 | SQTSD | 5.8 | 2018-03-24T21:40:00Z | 24 | 369 | < 25mph
86 | SDG&E | 20180612IG02 | June | 12 | 2018 | 2 | 2018-06-12 | 15:14 | 32.864 | -116.747 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact from Object |  | Balloons | Electric Facility | None | Tier 3 | EA | BLCSD | 2.89 | 2018-03-27T08:20:00Z | 7 | 56 | SPVSD | 5.85 | 2018-03-27T08:20:00Z | 8.99 | 140 | BLCSD | 2.89 | 2018-03-27T08:20:00Z | 7 | 112 | SPVSD | 5.85 | 2018-03-27T09:30:00Z | 10 | 280 | < 25mph
14 | SDG&E | 20150727IG01 | July | 27 | 2015 | 3 | 2015-07-27 | 14:30 | 33.0665 | -116.579 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | None | Tier 3 | RA | ECJSD | 3.11 | 2019-04-25T04:30:00Z | 7 | 31 | E3619 | 6.4 | 2019-04-25T04:19:00Z | 8.01 | 213 | ECJSD | 3.11 | 2019-04-25T04:30:00Z | 7 | 60 | E3619 | 6.4 | 2019-04-25T04:19:00Z | 8.01 | 417 | < 25mph
100 | SDG&E | 20190415IG01 | April | 15 | 2019 | 2 | 2019-04-15 | 14:05 | 32.7883 | -116.8896 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12 kV | Overhead | Yes | Wire-Wire Contact |  |  |  | Outside Force | Non- HFTD | EA | E9957 | 2.61 | 2017-01-04T17:41:00Z | 4.99 | 47 | E9915 | 7.33 | 2017-01-04T18:09:00Z | 8.01 | 138 | E9957 | 2.61 | 2017-01-04T19:00:00Z | 8.99 | 93 | E9915 | 7.33 | 2017-01-04T19:09:00Z | 11.01 | 275 | < 25mph
64 | SDG&E | 20170725IG01 | July | 25 | 2017 | 3 | 2017-07-25 | 15:18 | 33.1343 | -117.1666 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | No | Vandalism/Theft |  |  |  | Other | Non- HFTD | NE | JAMSD | 2.55 | 2018-11-26T05:00:00Z | 4.99 | 6 | WCVSD | 6.85 | 2018-11-26T04:40:00Z | 10 | 82 | JAMSD | 2.55 | 2018-11-26T05:00:00Z | 4.99 | 12 | WCVSD | 6.85 | 2018-11-26T04:40:00Z | 10 | 164 | < 25mph
99 | SDG&E | 20190116IG01 | January | 16 | 2019 | 1 | 2019-01-16 | 16:55 | 33.421 | -117.61 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12 kV | Overhead | No | Equipment/Facility Failure | Crossarm |  |  | Weather | Non- HFTD | OC | PSQC1 | 0.75 | 2020-11-12T01:50:00Z | 4 | 26 | OLVSD | 6.23 | 2020-11-12T01:20:00Z | 10.81 | 192 | PSQC1 | 0.75 | 2020-11-12T02:50:00Z | 4 | 52 | OLVSD | 6.23 | 2020-11-12T01:20:00Z | 10.81 | 384 | < 25mph
119 | SDG&E | 20200226IG01 | February | 26 | 2020 | 1 | 2020-02-26 | 0:17 | 32.914 | -116.64 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 3 | ME | ESCSD | 2.91 | 2020-12-26T13:00:00Z | 4.32 | 26 | E8699 | 6.99 | 2020-12-26T13:38:00Z | 20 | 263 | ESCSD | 2.91 | 2020-12-26T14:20:00Z | 6.79 | 52 | E8699 | 6.99 | 2020-12-26T13:38:00Z | 20 | 523 | < 25mph
106 | SDG&E | 20190805IG01 | August | 5 | 2019 | 3 | 2019-08-05 | 14:14 | 32.7886 | -117.1233 | Vegetation | Urban | Less Than .25 Acres | Utility | 12 kV | Overhead | No | Equipment/Facility Failure | Other |  |  | None | Non- HFTD | BC | DYESD | 1.89 | 2017-09-29T07:50:00Z | 10 | 24 | SHCSD | 7.8 | 2017-09-29T07:50:00Z | 12.01 | 132 | DYESD | 1.89 | 2017-09-29T08:50:00Z | 10 | 48 | IJPSD | 4.74 | 2017-09-29T08:10:00Z | 14 | 264 | < 25mph
56 | SDG&E | 20170120IG01 | January | 20 | 2017 | 1 | 2017-01-20 | 14:00 | 32.6274 | -117.0767 | Building | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Conductor | Vegetation | Pole | Weather | Non- HFTD | CM | AV271 | 0.4 | 2017-06-28T01:25:00Z | 12.01 | 36 | DEHSD | 4.89 | 2017-06-28T01:50:00Z | 14.99 | 210 | E3070 | 3.52 | 2017-06-28T02:35:00Z | 14 | 72 | DEHSD | 4.89 | 2017-06-28T01:50:00Z | 14.99 | 420 | < 25mph
60 | SDG&E | 20170626IG01 | June | 26 | 2017 | 2 | 2017-06-26 | 14:30 | 32.7842 | -117.1391 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | BC | HDMSD | 2.89 | 2019-01-02T12:10:00Z | 15.99 | 62 | HDMSD | 2.89 | 2019-01-02T12:10:00Z | 15.99 | 191 | HDMSD | 2.89 | 2019-01-02T12:10:00Z | 15.99 | 117 | HDMSD | 2.89 | 2019-01-02T12:10:00Z | 15.99 | 375 | < 25mph
4 | SDG&E | 20150412IG01 | April | 12 | 2015 | 2 | 2015-04-12 | 12:31 | 33.0117 | -116.866 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility |  | Tier 2 | RA | ESCSD | 2.91 | 2016-02-13T12:00:00Z | 4 | 46 | HDMSD | 7.24 | 2016-02-13T11:20:00Z | 17 | 169 | ESCSD | 2.91 | 2016-02-13T12:50:00Z | 5.99 | 89 | HDMSD | 7.24 | 2016-02-13T12:30:00Z | 17 | 336 | < 25mph
64 | SDG&E | 20170725IG01 | July | 25 | 2017 | 3 | 2017-07-25 | 15:18 | 33.1343 | -117.1666 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | No | Vandalism/Theft |  |  |  | Other | Non- HFTD | NE | JAMSD | 2.55 | 2015-10-08T10:10:00Z | 4.99 | 10 | HP002 | 5.78 | 2015-10-08T10:25:00Z | 20.13 | 91 | JAMSD | 2.55 | 2015-10-08T10:10:00Z | 4.99 | 20 | HP002 | 5.78 | 2015-10-08T11:05:00Z | 21.03 | 174 | < 25mph
125 | SDG&E | 20200717IG01 | July | 17 | 2020 | 3 | 2020-07-17 | 16:30 | 33.0904 | -116.5798 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | RA | SMCSD | 3.91 | 2015-07-10T12:20:00Z | 4 | 27 | WRBSD | 4.74 | 2015-07-10T12:10:00Z | 5.99 | 181 | SMCSD | 3.91 | 2015-07-10T12:20:00Z | 4 | 55 | WRBSD | 4.74 | 2015-07-10T12:10:00Z | 5.99 | 358 | < 25mph
138 | SDG&E | 20200917IG01 | September | 17 | 2020 | 3 | 2020-09-17 | 10:00 | 33.1101 | -117.2693 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Other |  |  | None | Non- HFTD | NC | FTVSD | 3.07 | 2020-12-18T14:30:00Z | 8.33 | 114 | ESCSD | 4.71 | 2020-12-18T15:20:00Z | 9.34 | 235 | FTVSD | 3.07 | 2020-12-18T14:30:00Z | 8.33 | 227 | ROCSD | 7.48 | 2020-12-18T16:10:00Z | 15.49 | 469 | < 25mph
43 | SDG&E | 20160702IG01 | July | 2 | 2016 | 3 | 2016-07-02 | 7:51 | 32.81 | -116.878 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Capacitor Bank |  |  | None | Tier 2 | EA | LPTSD | 0.58 | 2019-12-18T17:20:00Z | 24.7 | 12 | LPTSD | 0.58 | 2019-12-18T17:20:00Z | 24.7 | 56 | LPTSD | 0.58 | 2019-12-18T17:20:00Z | 24.7 | 24 | LPTSD | 0.58 | 2019-12-18T17:20:00Z | 24.7 | 111 | < 25mph
140 | SDG&E | 20201014IG01 | October | 14 | 2020 | 4 | 2020-10-14 | 15:05 | 33.027 | -116.889 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kv | Overhead | No | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 2 | RA | GOSC1 | 2.72 | 2017-07-08T15:52:00Z | 7 | 53 | HP005 | 7.1 | 2017-07-08T15:45:00Z | 12.75 | 135 | CESSD | 4 | 2017-07-08T17:10:00Z | 11.01 | 106 | BNASD | 7.95 | 2017-07-08T17:10:00Z | 14 | 272 | < 25mph
102 | SDG&E | 20190703IG01 | July | 3 | 2019 | 3 | 2019-07-03 | 15:15 | 33.0113 | -116.8492 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 3 | RA | AT125 | 2.22 | 2019-11-02T11:22:00Z | 2.01 | 18 | E5843 | 7.34 | 2019-11-02T10:45:00Z | 12.01 | 83 | AT125 | 2.22 | 2019-11-02T11:52:00Z | 4.99 | 36 | E5843 | 7.34 | 2019-11-02T10:45:00Z | 12.01 | 165 | < 25mph
77 | SDG&E | 20171210IG02 | December | 10 | 2017 | 4 | 2017-12-10 | 2:58 | 33.2739 | -116.9537 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Tier 3 | NE | E0995 | 2.37 | 2016-04-21T18:49:00Z | 22.01 | 33 | E0995 | 2.37 | 2016-04-21T18:49:00Z | 22.01 | 111 | E0995 | 2.37 | 2016-04-21T19:30:00Z | 22.01 | 66 | E0995 | 2.37 | 2016-04-21T19:30:00Z | 22.01 | 221 | < 25mph
142 | SDG&E | 20201130IG01 | November | 30 | 2020 | 4 | 2020-11-30 | 9:10 | 33.266 | -117.223 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 2 | NE | AVYSD | 3.27 | 2017-08-22T04:00:00Z | 10 | 37 | AVYSD | 3.27 | 2017-08-22T04:00:00Z | 10 | 186 | VGDSD | 2.96 | 2017-08-22T04:50:00Z | 12.01 | 74 | VGDSD | 2.96 | 2017-08-22T04:50:00Z | 12.01 | 367 | < 25mph
32 | SDG&E | 20160205IG01 | February | 5 | 2016 | 1 | 2016-02-05 | 9:47 | 33.0739 | -117.0862 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | NE | E3070 | 1.85 | 2015-02-04T22:40:00Z | 11.99 | 54 | E3619 | 7.98 | 2015-02-04T22:38:00Z | 13 | 106 | E3070 | 1.85 | 2015-02-04T22:40:00Z | 11.99 | 109 | E3619 | 7.98 | 2015-02-04T22:38:00Z | 13 | 214 | < 25mph
85 | SDG&E | 20180612IG01 | June | 12 | 2018 | 2 | 2018-06-12 | 9:00 | 32.706 | -116.396 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | ME | ESCSD | 2.77 | 2017-02-02T06:30:00Z | 7 | 28 | HDMSD | 7.34 | 2017-02-02T06:50:00Z | 13 | 187 | ESCSD | 2.77 | 2017-02-02T07:50:00Z | 8.01 | 58 | HDMSD | 7.34 | 2017-02-02T07:20:00Z | 15.99 | 379 | < 25mph
122 | SDG&E | 20200602IG01 | June | 2 | 2020 | 2 | 2020-06-02 | 18:00 | 33.07 | -116.863 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 3 | RA | ESCSD | 2.53 | 2020-12-26T05:00:00Z | 3.88 | 14 | E8699 | 7.64 | 2020-12-26T04:23:00Z | 25 | 251 | ESCSD | 2.53 | 2020-12-26T06:00:00Z | 7.74 | 28 | E8699 | 7.64 | 2020-12-26T04:23:00Z | 25 | 495 | 25-40mph
64 | SDG&E | 20170725IG01 | July | 25 | 2017 | 3 | 2017-07-25 | 15:18 | 33.1343 | -117.1666 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | No | Vandalism/Theft |  |  |  | Other | Non- HFTD | NE | JAMSD | 2.55 | 2020-08-23T18:30:00Z | 12.49 | 6 | MIGC1 | 6.63 | 2020-08-23T18:50:00Z | 17 | 87 | JAMSD | 2.55 | 2020-08-23T19:30:00Z | 13.81 | 12 | HP002 | 5.78 | 2020-08-23T19:53:00Z | 19.91 | 174 | < 25mph
79 | SDG&E | 20180216IG01 | February | 16 | 2018 | 1 | 2018-02-16 | 16:50 | 32.6276 | -116.9409 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Outside Force | Tier 2 | CM | CIRSD | 3.67 | 2020-06-14T09:50:00Z | 2.7 | 11 | VISSD | 6.84 | 2020-06-14T09:20:00Z | 7.46 | 87 | CIRSD | 3.67 | 2020-06-14T10:30:00Z | 6.57 | 22 | TWOSD | 7.79 | 2020-06-14T10:30:00Z | 8.48 | 171 | < 25mph
66 | SDG&E | 20170820IG01 | August | 20 | 2017 | 3 | 2017-08-20 | 22:15 | 32.7522 | -117.1184 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 4kV | Overhead | Yes | Equipment/Facility Failure | Fuse |  |  | None | Non- HFTD | CM | LPTSD | 0.64 | 2015-01-04T04:40:00Z | 3 | 12 | STTSD | 5.23 | 2015-01-04T04:40:00Z | 12.01 | 49 | CWDSD | 1.65 | 2015-01-04T05:40:00Z | 5.99 | 24 | STTSD | 5.23 | 2015-01-04T04:40:00Z | 12.01 | 98 | < 25mph
12 | SDG&E | 20150707IG01 | July | 7 | 2015 | 3 | 2015-07-07 | 15:00 | 32.7443 | -117.0498 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Non- HFTD | EA | E6321 | 3.62 | 2016-04-16T00:53:00Z | 14 | 36 | C2635 | 5.84 | 2016-04-16T00:50:00Z | 55.99 | 158 | E6321 | 3.62 | 2016-04-16T00:58:00Z | 14 | 70 | C2635 | 5.84 | 2016-04-16T01:50:00Z | 55.99 | 316 | 55mph+
17 | SDG&E | 20150815IG01 | August | 15 | 2015 | 3 | 2015-08-15 | 17:30 | 32.7417 | -116.9685 | Other | Urban | Less Than .25 Acres | Customer | 4Kv | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Non- HFTD | EA | SVCSD | 1.46 | 2019-03-22T05:20:00Z | 4 | 18 | CSTSD | 7.54 | 2019-03-22T05:50:00Z | 10 | 144 | ELMSD | 3.12 | 2019-03-22T07:10:00Z | 5.99 | 36 | CSTSD | 7.54 | 2019-03-22T05:50:00Z | 10 | 287 | < 25mph
110 | SDG&E | 20190930IG01 | September | 30 | 2019 | 3 | 2019-09-30 | 2:59 | 33.2618 | -116.3705 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Other | Non- HFTD | RA | EWNSD | 3.51 | 2018-05-15T20:00:00Z | 27 | 24 | EWNSD | 3.51 | 2018-05-15T20:00:00Z | 27 | 61 | EWNSD | 3.51 | 2018-05-15T20:00:00Z | 27 | 48 | EWNSD | 3.51 | 2018-05-15T20:00:00Z | 27 | 127 | 25-40mph
49 | SDG&E | 20160827IG01 | August | 27 | 2016 | 3 | 2016-08-27 | 12:43 | 33.1371 | -117.0761 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Unknown | Non- HFTD | NE | JAMSD | 1.45 | 2018-06-14T07:40:00Z | 3 | 28 | HP002 | 7.57 | 2018-06-14T07:23:00Z | 8.72 | 116 | JAMSD | 1.45 | 2018-06-14T08:30:00Z | 7 | 56 | HP002 | 7.57 | 2018-06-14T08:43:00Z | 10.96 | 235 | < 25mph
4 | SDG&E | 20150412IG01 | April | 12 | 2015 | 2 | 2015-04-12 | 12:31 | 33.0117 | -116.866 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility |  | Tier 2 | RA | ESCSD | 2.91 | 2015-11-19T03:40:00Z | 5.99 | 45 | HDMSD | 7.24 | 2015-11-19T04:10:00Z | 12.01 | 169 | ESCSD | 2.91 | 2015-11-19T05:10:00Z | 8.01 | 90 | HDMSD | 7.24 | 2015-11-19T04:50:00Z | 15.99 | 334 | < 25mph
53 | SDG&E | 20161021IG01 | October | 21 | 2016 | 4 | 2016-10-21 | 11:20 | 33.0485 | -116.8615 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Transformer |  |  |  | Tier 2 | RA | BRJSD | 0.73 | 2020-08-25T11:20:00Z | 11.62 | 12 | HP002 | 7.71 | 2020-08-25T11:03:00Z | 14.32 | 57 | BRJSD | 0.73 | 2020-08-25T11:20:00Z | 11.62 | 24 | HP002 | 7.71 | 2020-08-25T11:03:00Z | 14.32 | 113 | < 25mph
74 | SDG&E | 20171022IG01 | October | 22 | 2017 | 4 | 2017-10-22 | 10:22 | 33.099 | -117.135 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Tier 2 | NE | SSOSD | 3.3 | 2015-11-21T07:30:00Z | 34 | 56 | SSOSD | 3.3 | 2015-11-21T07:30:00Z | 34 | 144 | SSOSD | 3.3 | 2015-11-21T07:30:00Z | 34 | 119 | SSOSD | 3.3 | 2015-11-21T07:30:00Z | 34 | 300 | 25-40mph
35 | SDG&E | 20160303IG01 | March | 3 | 2016 | 1 | 2016-03-03 | 6:00 | 32.8472 | -116.942 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Non- HFTD | EA | E5843 | 3.81 | 2019-07-30T13:25:00Z | 4 | 11 | SE073 | 7.49 | 2019-07-30T13:30:00Z | 7 | 91 | E5843 | 3.81 | 2019-07-30T13:25:00Z | 4 | 22 | PZAC1 | 7.39 | 2019-07-30T13:50:00Z | 11.01 | 182 | < 25mph
41 | SDG&E | 20160623IG01 | June | 23 | 2016 | 2 | 2016-06-23 | 15:00 | 32.8058 | -116.961 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | Outside Force | Non- HFTD | EA | SMCSD | 2.3 | 2018-11-07T06:50:00Z | 4.99 | 41 | OLVSD | 7.23 | 2018-11-07T06:40:00Z | 5.99 | 153 | SMCSD | 2.3 | 2018-11-07T06:50:00Z | 4.99 | 80 | OLVSD | 7.23 | 2018-11-07T07:20:00Z | 7 | 303 | < 25mph
82 | SDG&E | 20180422IG01 | April | 22 | 2018 | 2 | 2018-04-22 | 14:00 | 32.837 | -117.184 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | BC | HVWSD | 2.6 | 2015-01-15T13:20:00Z | 11.01 | 12 | HP005 | 4.89 | 2015-01-15T13:25:00Z | 22.15 | 118 | HVWSD | 2.6 | 2015-01-15T13:50:00Z | 14 | 24 | HP005 | 4.89 | 2015-01-15T14:15:00Z | 28.19 | 235 | < 25mph
37 | SDG&E | 20160406IG01 | April | 6 | 2016 | 2 | 2016-04-06 | 10:38 | 33.1865 | -117.1967 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Conductor | Vegetation | Electric Facility | Human Error | Non- HFTD | NC | AU709 | 3.95 | 2016-03-26T04:45:00Z | 4.99 | 18 | TWOSD | 5.47 | 2016-03-26T04:50:00Z | 7 | 114 | AU709 | 3.95 | 2016-03-26T04:45:00Z | 4.99 | 36 | VISSD | 7.51 | 2016-03-26T05:20:00Z | 7 | 228 | < 25mph
127 | SDG&E | 20200729IG01 | July | 29 | 2020 | 3 | 2020-07-29 | 17:14 | 32.737 | -116.875 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Tier 3 | EA | LLCSD | 3.19 | 2017-11-04T11:30:00Z | 8.01 | 60 | RHSSD | 7.86 | 2017-11-04T11:10:00Z | 14.99 | 158 | LLCSD | 3.19 | 2017-11-04T11:30:00Z | 8.01 | 120 | HP014 | 6.35 | 2017-11-04T12:27:00Z | 15.21 | 314 | < 25mph
9 | SDG&E | 20150429IG01 | April | 29 | 2015 | 2 | 2015-04-29 | 12:00 | 32.6061 | -116.696 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Unknown | Tier 3 | ME | SSOSD | 3.93 | 2019-04-28T08:50:00Z | 6.44 | 63 | ROCSD | 7.12 | 2019-04-28T09:10:00Z | 11.01 | 152 | SSOSD | 3.93 | 2019-04-28T08:50:00Z | 6.44 | 118 | ROCSD | 7.12 | 2019-04-28T09:20:00Z | 12.01 | 296 | < 25mph
2 | SDG&E | 20150319IG01 | March | 19 | 2015 | 1 | 2015-03-19 | 23:50 | 33.0565 | -117.0332 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 2 | NE | WIRC1 | 3.14 | 2020-10-14T23:23:00Z | 9 | 32 | WIRC1 | 3.14 | 2020-10-14T23:23:00Z | 9 | 74 | WIRC1 | 3.14 | 2020-10-14T23:23:00Z | 9 | 65 | WIRC1 | 3.14 | 2020-10-14T23:23:00Z | 9 | 149 | < 25mph
119 | SDG&E | 20200226IG01 | February | 26 | 2020 | 1 | 2020-02-26 | 0:17 | 32.914 | -116.64 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 3 | ME | ESCSD | 2.91 | 2015-04-19T18:20:00Z | 8.99 | 41 | E2652 | 7.66 | 2015-04-19T18:20:00Z | 14 | 162 | ESCSD | 2.91 | 2015-04-19T19:10:00Z | 11.01 | 82 | OLVSD | 5.01 | 2015-04-19T19:10:00Z | 18.99 | 321 | < 25mph
35 | SDG&E | 20160303IG01 | March | 3 | 2016 | 1 | 2016-03-03 | 6:00 | 32.8472 | -116.942 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Non- HFTD | EA | SDFBK | 1.45 | 2016-04-11T21:49:00Z | 14 | 9 | PZAC1 | 7.39 | 2016-04-11T21:50:00Z | 20 | 77 | SDFBK | 1.45 | 2016-04-11T21:49:00Z | 14 | 18 | FBZCA | 5.75 | 2016-04-11T22:22:00Z | 20 | 154 | < 25mph
111 | SDG&E | 20191017IG01 | October | 17 | 2019 | 4 | 2019-10-17 | 12:15 | 33.2736 | -116.3931 | Vegetation | Urban | Less Than .25 Acres | Utility | 120/240 | Overhead | No | Other |  |  |  | Human Error | Non- HFTD | RA | GOSC1 | 1.64 | 2018-06-18T12:52:00Z | 5.99 | 37 | WCKSD | 7.03 | 2018-06-18T13:20:00Z | 7 | 122 | GOSC1 | 1.64 | 2018-06-18T13:52:00Z | 8.01 | 74 | POVSD | 5.39 | 2018-06-18T14:00:00Z | 8.01 | 243 | < 25mph
67 | SDG&E | 20170830IG01 | August | 30 | 2017 | 3 | 2017-08-30 | 14:12 | 33.3875 | -117.2459 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Other | Tier 2 | NE | EWNSD | 3.51 | 2016-03-18T15:50:00Z | 5.99 | 24 | SHCSD | 7.22 | 2016-03-18T15:20:00Z | 14.99 | 67 | EWNSD | 3.51 | 2016-03-18T15:50:00Z | 5.99 | 48 | SHCSD | 7.22 | 2016-03-18T15:20:00Z | 14.99 | 134 | < 25mph
76 | SDG&E | 20171210IG01 | December | 10 | 2017 | 4 | 2017-12-10 | 5:26 | 33.28 | -116.955 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 3 | NE | BLCSD | 2.89 | 2020-07-31T06:10:00Z | 4.32 | 57 | HP005 | 7.6 | 2020-07-31T06:13:00Z | 7.38 | 141 | SSOSD | 2.69 | 2020-07-31T07:40:00Z | 5.34 | 114 | HP005 | 7.6 | 2020-07-31T06:13:00Z | 7.38 | 282 | < 25mph
88 | SDG&E | 20180629IG01 | June | 29 | 2018 | 2 | 2018-06-29 | 13:06 | 32.645 | -117.056 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Unknown | Non- HFTD | CM | E4521 | 3.76 | 2017-01-02T02:23:00Z | 7 | 24 | OTYSD | 4.92 | 2017-01-02T02:20:00Z | 13 | 200 | E4521 | 3.76 | 2017-01-02T02:23:00Z | 7 | 48 | MIGC1 | 7.97 | 2017-01-02T03:50:00Z | 14 | 397 | < 25mph
29 | SDG&E | 20160109IG01 | January | 9 | 2016 | 1 | 2016-01-09 | 4:30 | 33.082 | -117.091 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Non- HFTD | NE | CSTSD | 1.38 | 2020-03-11T13:40:00Z | 5.99 | 28 | HF005 | 7.84 | 2020-03-11T14:00:00Z | 8.05 | 146 | CSTSD | 1.38 | 2020-03-11T15:10:00Z | 8.01 | 56 | HF005 | 7.84 | 2020-03-11T14:45:00Z | 11.86 | 292 | < 25mph
109 | SDG&E | 20190913IG01 | September | 13 | 2019 | 3 | 2019-09-13 | 11:27 | 32.787 | -117.007 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | EA | BFDSD | 3.99 | 2019-02-11T16:10:00Z | 11.01 | 12 | BFDSD | 3.99 | 2019-02-11T16:10:00Z | 11.01 | 56 | BFDSD | 3.99 | 2019-02-11T16:10:00Z | 11.01 | 24 | BFDSD | 3.99 | 2019-02-11T16:10:00Z | 11.01 | 111 | < 25mph
48 | SDG&E | 20160731IG01 | July | 31 | 2016 | 3 | 2016-07-31 | 13:43 | 33.3663 | -117.2033 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Unknown | Tier 2 | NE | SPVSD | 3.81 | 2016-12-26T05:50:00Z | 8.01 | 22 | HDMSD | 7.44 | 2016-12-26T05:20:00Z | 14 | 133 | SPVSD | 3.81 | 2016-12-26T05:50:00Z | 8.01 | 43 | HDMSD | 7.44 | 2016-12-26T05:20:00Z | 14 | 264 | < 25mph
85 | SDG&E | 20180612IG01 | June | 12 | 2018 | 2 | 2018-06-12 | 9:00 | 32.706 | -116.396 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | ME | ESCSD | 2.77 | 2019-08-20T19:40:00Z | 20 | 18 | ESCSD | 2.77 | 2019-08-20T19:40:00Z | 20 | 209 | ESCSD | 2.77 | 2019-08-20T20:40:00Z | 21 | 35 | WRBSD | 7.79 | 2019-08-20T20:00:00Z | 21 | 415 | < 25mph
122 | SDG&E | 20200602IG01 | June | 2 | 2020 | 2 | 2020-06-02 | 18:00 | 33.07 | -116.863 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 3 | RA | ESCSD | 2.53 | 2015-05-01T14:40:00Z | 4.99 | 37 | HVWSD | 6.17 | 2015-05-01T14:50:00Z | 8.99 | 150 | ESCSD | 2.53 | 2015-05-01T16:30:00Z | 7 | 74 | HIDSD | 7.27 | 2015-05-01T16:30:00Z | 12.01 | 292 | < 25mph
125 | SDG&E | 20200717IG01 | July | 17 | 2020 | 3 | 2020-07-17 | 16:30 | 33.0904 | -116.5798 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | RA | HDMSD | 3.87 | 2018-09-16T14:30:00Z | 12.01 | 62 | HDMSD | 3.87 | 2018-09-16T14:30:00Z | 12.01 | 153 | HDMSD | 3.87 | 2018-09-16T14:30:00Z | 12.01 | 123 | HDMSD | 3.87 | 2018-09-16T14:30:00Z | 12.01 | 307 | < 25mph
100 | SDG&E | 20190415IG01 | April | 15 | 2019 | 2 | 2019-04-15 | 14:05 | 32.7883 | -116.8896 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12 kV | Overhead | Yes | Wire-Wire Contact |  |  |  | Outside Force | Non- HFTD | EA | C2635 | 3.75 | 2015-12-11T21:15:00Z | 24 | 46 | TLKSD | 7.51 | 2015-12-11T21:10:00Z | 24 | 115 | C2635 | 3.75 | 2015-12-11T21:15:00Z | 24 | 92 | HMDSD | 6.54 | 2015-12-11T22:10:00Z | 28.01 | 228 | < 25mph
69 | SDG&E | 20170927IG01 | September | 27 | 2017 | 3 | 2017-09-27 | 14:28 | 33.2327 | -116.9748 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Unknown |  |  |  | Unknown | Tier 2 | NE | WYNSD | 2.96 | 2017-01-26T19:10:00Z | 30 | 44 | WYNSD | 2.96 | 2017-01-26T19:10:00Z | 30 | 111 | WYNSD | 2.96 | 2017-01-26T19:10:00Z | 30 | 89 | WYNSD | 2.96 | 2017-01-26T19:10:00Z | 30 | 220 | 25-40mph
106 | SDG&E | 20190805IG01 | August | 5 | 2019 | 3 | 2019-08-05 | 14:14 | 32.7886 | -117.1233 | Vegetation | Urban | Less Than .25 Acres | Utility | 12 kV | Overhead | No | Equipment/Facility Failure | Other |  |  | None | Non- HFTD | BC | DYESD | 1.89 | 2015-07-18T04:00:00Z | 4 | 24 | POVSD | 7.9 | 2015-07-18T03:10:00Z | 12.01 | 138 | STVSD | 1.13 | 2015-07-18T04:50:00Z | 4.99 | 48 | POVSD | 7.9 | 2015-07-18T03:10:00Z | 12.01 | 276 | < 25mph
105 | SDG&E | 20190716IG02 | July | 16 | 2019 | 3 | 2019-07-16 | 7:36 | 33.1675 | -117.1462 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Wire-Wire Contact |  |  |  | Other | Tier 2 | NE | KL08 | 3.38 | 2020-02-29T23:55:00Z | 31.07 | 21 | KL08 | 3.38 | 2020-02-29T23:55:00Z | 31.07 | 27 | KL08 | 3.38 | 2020-03-01T00:55:00Z | 34.52 | 41 | KL08 | 3.38 | 2020-03-01T00:55:00Z | 34.52 | 53 | 25-40mph
131 | SDG&E | 20200831IG01 | August | 31 | 2020 | 3 | 2020-08-31 | 14:05 | 33.1128 | -117.0055 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Other | Tier 2 | NE | OTYSD | 3.97 | 2017-04-29T19:40:00Z | 18.99 | 15 | RODB1 | 6.5 | 2017-04-29T20:10:00Z | 22.44 | 86 | OTYSD | 3.97 | 2017-04-29T19:40:00Z | 18.99 | 31 | RODB1 | 6.5 | 2017-04-29T21:00:00Z | 27.78 | 178 | < 25mph
63 | SDG&E | 20170716IG01 | July | 16 | 2017 | 3 | 2017-07-16 | 11:53 | 32.829 | -117.136 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | BC | AVYSD | 2.4 | 2019-06-21T06:10:00Z | 7 | 68 | WDCSD | 5.61 | 2019-06-21T06:00:00Z | 10 | 231 | CRVSD | 3.61 | 2019-06-21T07:10:00Z | 8.19 | 127 | WDCSD | 5.61 | 2019-06-21T06:40:00Z | 12.01 | 445 | < 25mph
34 | SDG&E | 20160218IG01 | February | 18 | 2016 | 1 | 2016-02-18 | 0:00 | 32.7063 | -116.397 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | None | Tier 3 | ME | ECJSD | 2.76 | 2015-04-07T11:40:00Z | 3 | 32 | MIGSD | 6.97 | 2015-04-07T12:30:00Z | 8.01 | 158 | OTYSD | 3.89 | 2015-04-07T13:20:00Z | 4 | 64 | MIGC1 | 6.79 | 2015-04-07T12:50:00Z | 8.99 | 315 | < 25mph
70 | SDG&E | 20170927IG02 | September | 27 | 2017 | 3 | 2017-09-27 | 16:10 | 32.7272 | -116.7788 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | None | Tier 3 | EA | E5843 | 3.81 | 2020-07-02T15:40:00Z | 4 | 11 | PZAC1 | 7.39 | 2020-07-02T15:50:00Z | 7 | 94 | E5843 | 3.81 | 2020-07-02T15:40:00Z | 4 | 22 | PZAC1 | 7.39 | 2020-07-02T16:50:00Z | 9 | 191 | < 25mph
70 | SDG&E | 20170927IG02 | September | 27 | 2017 | 3 | 2017-09-27 | 16:10 | 32.7272 | -116.7788 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | None | Tier 3 | EA | SDFBK | 1.45 | 2015-10-01T19:49:00Z | 12.01 | 5 | PZAC1 | 7.39 | 2015-10-01T19:50:00Z | 15.99 | 78 | SDFBK | 1.45 | 2015-10-01T20:49:00Z | 12.01 | 10 | PZAC1 | 7.39 | 2015-10-01T19:50:00Z | 15.99 | 156 | < 25mph
2 | SDG&E | 20150319IG01 | March | 19 | 2015 | 1 | 2015-03-19 | 23:50 | 33.0565 | -117.0332 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 2 | NE | WIRC1 | 3.14 | 2018-12-17T06:23:00Z | 7 | 16 | WIRC1 | 3.14 | 2018-12-17T06:23:00Z | 7 | 40 | WIRC1 | 3.14 | 2018-12-17T07:23:00Z | 8.01 | 32 | WIRC1 | 3.14 | 2018-12-17T07:23:00Z | 8.01 | 80 | < 25mph
8 | SDG&E | 20150428IG01 | April | 28 | 2015 | 2 | 2015-04-28 | 13:30 | 32.8917 | -116.8419 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Tier 3 | EA | E4521 | 3.76 | 2018-12-06T18:15:00Z | 15.99 | 30 | LLDSD | 7.68 | 2018-12-06T18:10:00Z | 27 | 144 | E4521 | 3.76 | 2018-12-06T18:15:00Z | 15.99 | 59 | LLDSD | 7.68 | 2018-12-06T18:10:00Z | 27 | 287 | 25-40mph
14 | SDG&E | 20150727IG01 | July | 27 | 2015 | 3 | 2015-07-27 | 14:30 | 33.0665 | -116.579 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | None | Tier 3 | RA | E4521 | 3.76 | 2020-10-02T00:16:00Z | 10 | 31 | EUCSD | 5.87 | 2020-10-02T00:20:00Z | 13.59 | 229 | E4521 | 3.76 | 2020-10-02T00:16:00Z | 10 | 61 | EUCSD | 5.87 | 2020-10-02T00:20:00Z | 13.59 | 453 | < 25mph
121 | SDG&E | 20200531IG01 | May | 31 | 2020 | 2 | 2020-05-31 | 2:01 | 32.543 | -117.0277 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Outside Force | Non- HFTD | CM | MGYSD | 1.96 | 2020-07-14T03:50:00Z | 11.98 | 24 | EWNSD | 5.67 | 2020-07-14T03:10:00Z | 14.03 | 79 | MGYSD | 1.96 | 2020-07-14T04:20:00Z | 15.42 | 48 | MGYSD | 1.96 | 2020-07-14T04:20:00Z | 15.42 | 157 | < 25mph
103 | SDG&E | 20190705IG01 | July | 5 | 2019 | 3 | 2019-07-05 | 12:32 | 33.1584 | -117.222 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 2 | NC | SPVSD | 3.81 | 2019-10-05T01:00:00Z | 8.01 | 33 | WRBSD | 7.25 | 2019-10-05T01:20:00Z | 12.01 | 172 | SPVSD | 3.81 | 2019-10-05T01:00:00Z | 8.01 | 66 | WRBSD | 7.25 | 2019-10-05T01:20:00Z | 12.01 | 341 | < 25mph
56 | SDG&E | 20170120IG01 | January | 20 | 2017 | 1 | 2017-01-20 | 14:00 | 32.6274 | -117.0767 | Building | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Conductor | Vegetation | Pole | Weather | Non- HFTD | CM | E4521 | 3.76 | 2020-05-30T04:31:00Z | 11 | 31 | E3619 | 6.4 | 2020-05-30T04:14:00Z | 12 | 214 | E4521 | 3.76 | 2020-05-30T04:31:00Z | 11 | 62 | E3619 | 6.4 | 2020-05-30T04:14:00Z | 12 | 424 | < 25mph
1 | SDG&E | 20150211IG01 | February | 11 | 2015 | 1 | 2015-02-11 | 15:30 | 32.8941 | -116.9393 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | EA | BFDSD | 3.99 | 2020-03-13T07:00:00Z | 12.71 | 12 | BFDSD | 3.99 | 2020-03-13T07:00:00Z | 12.71 | 67 | BFDSD | 3.99 | 2020-03-13T07:00:00Z | 12.71 | 24 | BFDSD | 3.99 | 2020-03-13T07:00:00Z | 12.71 | 133 | < 25mph
107 | SDG&E | 20190910IG01 | September | 10 | 2019 | 3 | 2019-09-10 | 12:59 | 32.5638 | -117.0333 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | None | Tier 2 | CM | LJHSD | 3.27 | 2016-12-14T21:30:00Z | 15.99 | 34 | LJHSD | 3.27 | 2016-12-14T21:30:00Z | 15.99 | 176 | LJHSD | 3.27 | 2016-12-14T22:40:00Z | 17 | 67 | LJHSD | 3.27 | 2016-12-14T22:40:00Z | 17 | 356 | < 25mph
142 | SDG&E | 20201130IG01 | November | 30 | 2020 | 4 | 2020-11-30 | 9:10 | 33.266 | -117.223 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 2 | NE | VGDSD | 2.96 | 2017-04-11T20:00:00Z | 20 | 37 | VGDSD | 2.96 | 2017-04-11T20:00:00Z | 20 | 188 | VGDSD | 2.96 | 2017-04-11T20:30:00Z | 20 | 74 | VGDSD | 2.96 | 2017-04-11T20:30:00Z | 20 | 370 | < 25mph
23 | SDG&E | 20150909IG01 | September | 9 | 2015 | 3 | 2015-09-09 | 20:40 | 32.644 | -117.072 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Non- HFTD | CM | SPPSD | 3.6 | 2019-07-08T22:30:00Z | 18.01 | 28 | GOSC1 | 5.3 | 2019-07-08T22:52:00Z | 20 | 119 | SPPSD | 3.6 | 2019-07-08T22:30:00Z | 18.01 | 52 | GOSC1 | 5.3 | 2019-07-08T22:52:00Z | 20 | 222 | < 25mph
29 | SDG&E | 20160109IG01 | January | 9 | 2016 | 1 | 2016-01-09 | 4:30 | 33.082 | -117.091 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Non- HFTD | NE | HARSD | 2.98 | 2018-11-15T12:20:00Z | 12.01 | 39 | HARSD | 2.98 | 2018-11-15T12:20:00Z | 12.01 | 138 | HARSD | 2.98 | 2018-11-15T13:20:00Z | 12.01 | 79 | HARSD | 2.98 | 2018-11-15T13:20:00Z | 12.01 | 275 | < 25mph
74 | SDG&E | 20171022IG01 | October | 22 | 2017 | 4 | 2017-10-22 | 10:22 | 33.099 | -117.135 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Tier 2 | NE | GOSC1 | 2.63 | 2015-05-22T22:52:00Z | 25.99 | 47 | STVSD | 5.94 | 2015-05-22T22:40:00Z | 25.99 | 137 | GOSC1 | 2.63 | 2015-05-22T22:52:00Z | 25.99 | 95 | STVSD | 5.94 | 2015-05-22T22:40:00Z | 25.99 | 275 | 25-40mph
109 | SDG&E | 20190913IG01 | September | 13 | 2019 | 3 | 2019-09-13 | 11:27 | 32.787 | -117.007 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | EA | BFDSD | 3.99 | 2017-11-22T11:20:00Z | 8.99 | 12 | BFDSD | 3.99 | 2017-11-22T11:20:00Z | 8.99 | 50 | BFDSD | 3.99 | 2017-11-22T11:20:00Z | 8.99 | 24 | BFDSD | 3.99 | 2017-11-22T11:20:00Z | 8.99 | 100 | < 25mph
96 | SDG&E | 20180914IG02 | September | 14 | 2018 | 3 | 2018-09-14 | 10:00 | 33.3177 | -117.2228 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact Between Third Party Facility on Pole and Supply Lines |  | Vehicle | Communication Facility | Human Error | Tier 2 | NE | KL08 | 2.87 | 2019-09-01T23:55:00Z | 16.11 | 27 | KL08 | 2.87 | 2019-09-01T23:55:00Z | 16.11 | 40 | KL08 | 2.87 | 2019-09-01T23:55:00Z | 16.11 | 51 | KL08 | 2.87 | 2019-09-01T23:55:00Z | 16.11 | 76 | < 25mph
66 | SDG&E | 20170820IG01 | August | 20 | 2017 | 3 | 2017-08-20 | 22:15 | 32.7522 | -117.1184 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 4kV | Overhead | Yes | Equipment/Facility Failure | Fuse |  |  | None | Non- HFTD | CM | LPTSD | 0.64 | 2019-10-28T10:10:00Z | 26.75 | 12 | LPTSD | 0.64 | 2019-10-28T10:10:00Z | 26.75 | 49 | LPTSD | 0.64 | 2019-10-28T11:00:00Z | 32.95 | 24 | LPTSD | 0.64 | 2019-10-28T11:00:00Z | 32.95 | 98 | 25-40mph
93 | SDG&E | 20180809IG01 | August | 9 | 2018 | 3 | 2018-08-09 | 12:00 | 33.213 | -117.335 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Other |  |  | Other | Non- HFTD | NC | LPTSD | 0.64 | 2018-03-01T16:30:00Z | 7 | 12 | CMCSD | 7.19 | 2018-03-01T16:00:00Z | 8.99 | 43 | CWDSD | 1.65 | 2018-03-01T17:20:00Z | 10 | 24 | BVDSD | 6.93 | 2018-03-01T17:30:00Z | 13 | 86 | < 25mph
109 | SDG&E | 20190913IG01 | September | 13 | 2019 | 3 | 2019-09-13 | 11:27 | 32.787 | -117.007 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | EA | BFDSD | 3.99 | 2018-04-25T18:30:00Z | 15.99 | 12 | OMBSD | 7.75 | 2018-04-25T18:00:00Z | 18.99 | 49 | BFDSD | 3.99 | 2018-04-25T18:30:00Z | 15.99 | 24 | OMBSD | 7.75 | 2018-04-25T18:00:00Z | 18.99 | 90 | < 25mph
71 | SDG&E | 20171007IG01 | October | 7 | 2017 | 4 | 2017-10-07 | 17:40 | 32.5914 | -116.6216 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Conductor |  |  | Other | Tier 3 | ME | E4858 | 0.85 | 2019-04-25T07:30:00Z | 4 | 30 | LLDSD | 7.68 | 2019-04-25T08:10:00Z | 5.99 | 216 | E4858 | 0.85 | 2019-04-25T07:30:00Z | 4 | 61 | LLDSD | 7.68 | 2019-04-25T08:40:00Z | 5.99 | 428 | < 25mph
89 | SDG&E | 20180706IG01 | July | 6 | 2018 | 3 | 2018-07-06 | 10:26 | 32.6203 | -116.7649 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Transformer |  |  |  | Tier 3 | ME | BRJSD | 3.74 | 2020-07-26T06:10:00Z | 5.7 | 31 | CPOSD | 7.51 | 2020-07-26T06:10:00Z | 8.11 | 38 | BRJSD | 3.74 | 2020-07-26T06:50:00Z | 6.94 | 62 | CPOSD | 7.51 | 2020-07-26T07:10:00Z | 8.84 | 76 | < 25mph
43 | SDG&E | 20160702IG01 | July | 2 | 2016 | 3 | 2016-07-02 | 7:51 | 32.81 | -116.878 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Capacitor Bank |  |  | None | Tier 2 | EA | LPTSD | 0.58 | 2019-02-23T22:40:00Z | 12.01 | 14 | TDSSD | 5.19 | 2019-02-23T23:20:00Z | 13 | 57 | LPTSD | 0.58 | 2019-02-23T22:40:00Z | 12.01 | 26 | CMCSD | 7.15 | 2019-02-24T00:30:00Z | 18.01 | 106 | < 25mph
73 | SDG&E | 20171018IG01 | October | 18 | 2017 | 4 | 2017-10-18 | 7:20 | 33.1659 | -117.2053 | Vegetation | Urban | Less Than .25 Acres | Unknown | 12kV | Overhead | No | Contact From Object |  | Vehicle | Pole | Human Error | Non- HFTD | NC | HDMSD | 2.89 | 2020-03-04T12:00:00Z | 13 | 131 | HF004 | 5.39 | 2020-03-04T11:30:00Z | 21.18 | 289 | HDMSD | 2.89 | 2020-03-04T12:30:00Z | 14 | 261 | HF004 | 5.39 | 2020-03-04T11:30:00Z | 21.18 | 575 | < 25mph
74 | SDG&E | 20171022IG01 | October | 22 | 2017 | 4 | 2017-10-22 | 10:22 | 33.099 | -117.135 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Tier 2 | NE | GOSC1 | 2.63 | 2017-02-08T21:52:00Z | 14.99 | 69 | HVYSD | 4.47 | 2017-02-08T21:30:00Z | 14.99 | 182 | GOSC1 | 2.63 | 2017-02-08T21:52:00Z | 14.99 | 131 | HVYSD | 4.47 | 2017-02-08T21:30:00Z | 14.99 | 343 | < 25mph
96 | SDG&E | 20180914IG02 | September | 14 | 2018 | 3 | 2018-09-14 | 10:00 | 33.3177 | -117.2228 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact Between Third Party Facility on Pole and Supply Lines |  | Vehicle | Communication Facility | Human Error | Tier 2 | NE | UCI08 | 1.84 | 2019-01-15T10:00:00Z | 4.56 | 26 | RCHC1 | 7.83 | 2019-01-15T10:07:00Z | 14 | 41 | BRGSD | 1.29 | 2019-01-15T11:20:00Z | 7 | 51 | UCI11 | 7.36 | 2019-01-15T11:00:00Z | 15.66 | 82 | < 25mph
42 | SDG&E | 20160627IG01 | June | 27 | 2016 | 2 | 2016-06-27 | 15:30 | 33.2837 | -116.6174 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Human Error | Tier 2 | RA | E4521 | 2.92 | 2016-11-03T17:55:00Z | 10 | 57 | E9888 | 6.92 | 2016-11-03T18:15:00Z | 12.01 | 120 | E3070 | 3.4 | 2016-11-03T19:10:00Z | 12.01 | 113 | E9888 | 6.92 | 2016-11-03T18:15:00Z | 12.01 | 240 | < 25mph
70 | SDG&E | 20170927IG02 | September | 27 | 2017 | 3 | 2017-09-27 | 16:10 | 32.7272 | -116.7788 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | None | Tier 3 | EA | E8406 | 1.9 | 2019-06-24T07:47:00Z | 3 | 11 | PZAC1 | 7.39 | 2019-06-24T07:50:00Z | 7 | 92 | E8406 | 1.9 | 2019-06-24T08:33:00Z | 4 | 22 | FBZC1 | 5.78 | 2019-06-24T08:22:00Z | 7 | 183 | < 25mph
50 | SDG&E | 20160923IG01 | September | 23 | 2016 | 3 | 2016-09-23 | 11:25 | 32.7372 | -116.7343 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Transformer |  |  | None | Tier 3 | EA | GOSC1 | 1.04 | 2016-11-20T17:52:00Z | 8.99 | 62 | HP005 | 6.69 | 2016-11-20T18:25:00Z | 12.75 | 143 | SSOSD | 3.93 | 2016-11-20T19:20:00Z | 14.99 | 122 | E8894 | 6.8 | 2016-11-20T19:40:00Z | 21 | 283 | < 25mph
75 | SDG&E | 20171025IG01 | October | 25 | 2017 | 4 | 2017-10-25 | 13:02 | 33.2857 | -117.0275 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Other |  |  | Weather | Tier 2 | NE | DLZSD | 0.55 | 2019-04-10T08:50:00Z | 14 | 6 | CSPC1 | 6.63 | 2019-04-10T08:22:00Z | 15.99 | 64 | DLZSD | 0.55 | 2019-04-10T08:50:00Z | 14 | 12 | E4050 | 7.49 | 2019-04-10T09:45:00Z | 20 | 128 | < 25mph
45 | SDG&E | 20160711IG02 | July | 11 | 2016 | 3 | 2016-07-11 | 13:19 | 33.1146 | -116.5843 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  |  | Tier 3 | RA | MIGC1 | 3.93 | 2019-01-06T16:50:00Z | 11.01 | 61 | MIGC1 | 3.93 | 2019-01-06T16:50:00Z | 11.01 | 116 | OTYSD | 2.79 | 2019-01-06T17:40:00Z | 11.01 | 121 | OTYSD | 2.79 | 2019-01-06T17:40:00Z | 11.01 | 231 | < 25mph
13 | SDG&E | 20150717IG01 | July | 17 | 2015 | 3 | 2015-07-17 | 9:48 | 33.3012 | -117.0222 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Communication Facility | Human Error | Tier 3 | NE | WRBSD | 3.95 | 2020-09-21T03:40:00Z | 7.38 | 51 | HF004 | 7.08 | 2020-09-21T04:30:00Z | 16.8 | 261 | WRBSD | 3.95 | 2020-09-21T03:40:00Z | 7.38 | 97 | HF004 | 7.08 | 2020-09-21T05:00:00Z | 18.64 | 501 | < 25mph
28 | SDG&E | 20160103IG01 | January | 3 | 2016 | 1 | 2016-01-03 | 4:30 | 33.1915 | -117.3655 | Other | Urban | Less Than .25 Acres | Fire Agency | 12kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | Other | Non- HFTD | NC | AU219 | 1.08 | 2018-11-07T12:00:00Z | 4 | 8 | SPVSD | 7.17 | 2018-11-07T11:30:00Z | 8.99 | 166 | AU219 | 1.08 | 2018-11-07T12:00:00Z | 4 | 16 | SPVSD | 7.17 | 2018-11-07T13:00:00Z | 8.99 | 332 | < 25mph
72 | SDG&E | 20171016IG01 | October | 16 | 2017 | 4 | 2017-10-16 | 10:20 | 33.0697 | -116.8813 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | RA | AT382 | 3.69 | 2016-08-14T15:55:00Z | 8.01 | 34 | E1589 | 6.37 | 2016-08-14T15:41:00Z | 11.01 | 185 | TCNSD | 3.83 | 2016-08-14T16:50:00Z | 10 | 69 | LJHSD | 6.11 | 2016-08-14T16:50:00Z | 12.01 | 375 | < 25mph
61 | SDG&E | 20170629IG01 | June | 29 | 2017 | 2 | 2017-06-29 | 13:07 | 33.1355 | -117.098 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility |  | Non- HFTD | NE | RAMSD | 3.65 | 2016-12-27T08:40:00Z | 7 | 64 | SSOSD | 5.46 | 2016-12-27T08:20:00Z | 24.99 | 140 | RAMSD | 3.65 | 2016-12-27T09:50:00Z | 12.01 | 121 | SSOSD | 5.46 | 2016-12-27T08:20:00Z | 24.99 | 273 | < 25mph
126 | SDG&E | 20200726IG01 | July | 26 | 2020 | 3 | 2020-07-26 | 0:00 | 32.819 | -116.9561 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Fuse |  |  | Unknown | Non- HFTD | EA | ESCSD | 2.53 | 2018-01-03T21:00:00Z | 5.99 | 31 | HDMSD | 7.76 | 2018-01-03T20:10:00Z | 12.01 | 188 | ESCSD | 2.53 | 2018-01-03T21:40:00Z | 5.99 | 61 | HDMSD | 7.76 | 2018-01-03T20:10:00Z | 12.01 | 373 | < 25mph
108 | SDG&E | 20190911IG01 | September | 11 | 2019 | 3 | 2019-09-11 | 14:17 | 33.226 | -117.085 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 2 | NE | EWNSD | 3.96 | 2019-06-21T11:20:00Z | 14.99 | 19 | EWNSD | 3.96 | 2019-06-21T11:20:00Z | 14.99 | 50 | EWNSD | 3.96 | 2019-06-21T12:20:00Z | 18.99 | 37 | EWNSD | 3.96 | 2019-06-21T12:20:00Z | 18.99 | 98 | < 25mph
20 | SDG&E | 20150901IG02 | September | 1 | 2015 | 3 | 2015-09-01 | 8:50 | 32.669 | -116.286 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | None | Tier 2 | ME | E5953 | 2.06 | 2020-07-09T12:32:00Z | 5 | 38 | CBDSD | 5.25 | 2020-07-09T12:00:00Z | 5.26 | 87 | E5953 | 2.06 | 2020-07-09T12:32:00Z | 5 | 76 | CBDSD | 5.25 | 2020-07-09T13:00:00Z | 6.35 | 172 | < 25mph
80 | SDG&E | 20180412IG01 | April | 12 | 2018 | 2 | 2018-04-12 | 19:33 | 32.6965 | -117.0493 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | CM | MIGC1 | 2.33 | 2019-06-21T20:50:00Z | 18.99 | 45 | MIGC1 | 2.33 | 2019-06-21T20:50:00Z | 18.99 | 138 | MIGC1 | 2.33 | 2019-06-21T20:50:00Z | 18.99 | 90 | MIGC1 | 2.33 | 2019-06-21T20:50:00Z | 18.99 | 275 | < 25mph
11 | SDG&E | 20150528IG01 | May | 28 | 2015 | 2 | 2015-05-28 | 12:45 | 32.7265 | -116.9922 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | EA | RODB1 | 1.87 | 2019-12-05T01:20:00Z | 5.59 | 10 | OTYC1 | 5.88 | 2019-12-05T02:14:00Z | 17 | 78 | RODB1 | 1.87 | 2019-12-05T01:20:00Z | 5.59 | 20 | OTYC1 | 5.88 | 2019-12-05T03:14:00Z | 17 | 158 | < 25mph
14 | SDG&E | 20150727IG01 | July | 27 | 2015 | 3 | 2015-07-27 | 14:30 | 33.0665 | -116.579 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | None | Tier 3 | RA | E4521 | 3.76 | 2020-09-18T12:31:00Z | 3 | 30 | HARSD | 5.68 | 2020-09-18T11:50:00Z | 10.08 | 158 | E4858 | 0.85 | 2020-09-18T12:45:00Z | 3 | 60 | OTYSD | 4.92 | 2020-09-18T12:40:00Z | 10.45 | 317 | < 25mph
94 | SDG&E | 20180819IG01 | August | 19 | 2018 | 3 | 2018-08-19 | 18:35 | 32.7002 | -116.8639 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | EA | DZRSD | 0.55 | 2017-06-05T05:00:00Z | 4.99 | 6 | OTYC1 | 4.63 | 2017-06-05T04:14:00Z | 21 | 51 | DZRSD | 0.55 | 2017-06-05T06:00:00Z | 5.99 | 12 | OTYC1 | 4.63 | 2017-06-05T04:14:00Z | 21 | 101 | < 25mph
9 | SDG&E | 20150429IG01 | April | 29 | 2015 | 2 | 2015-04-29 | 12:00 | 32.6061 | -116.696 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Unknown | Tier 3 | ME | SSOSD | 3.93 | 2018-10-31T12:40:00Z | 10 | 42 | STVSD | 6.92 | 2018-10-31T12:50:00Z | 14.99 | 113 | SSOSD | 3.93 | 2018-10-31T14:00:00Z | 11.01 | 87 | STVSD | 6.92 | 2018-10-31T13:50:00Z | 18.01 | 229 | < 25mph
74 | SDG&E | 20171022IG01 | October | 22 | 2017 | 4 | 2017-10-22 | 10:22 | 33.099 | -117.135 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Tier 2 | NE | SSOSD | 3.3 | 2016-07-18T07:50:00Z | 5.99 | 74 | HP005 | 6.91 | 2016-07-18T08:05:00Z | 6.49 | 189 | SSOSD | 3.3 | 2016-07-18T07:50:00Z | 5.99 | 142 | HP005 | 6.91 | 2016-07-18T08:05:00Z | 6.49 | 358 | < 25mph
20 | SDG&E | 20150901IG02 | September | 1 | 2015 | 3 | 2015-09-01 | 8:50 | 32.669 | -116.286 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | None | Tier 2 | ME | WIRC1 | 2.46 | 2017-09-08T07:23:00Z | 4.99 | 18 | WIRC1 | 2.46 | 2017-09-08T07:23:00Z | 4.99 | 60 | WIRC1 | 2.46 | 2017-09-08T08:23:00Z | 5.99 | 32 | WIRC1 | 2.46 | 2017-09-08T08:23:00Z | 5.99 | 116 | < 25mph
65 | SDG&E | 20170728IG01 | July | 28 | 2017 | 3 | 2017-07-28 | 16:31 | 32.7802 | -116.8722 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Pole /Conductor | Vehicle | Electric Facility | Outside Force | Tier 2 | EA | AVOSD | 0.61 | 2015-09-18T23:20:00Z | 11.01 | 30 | CTGC1 | 6.65 | 2015-09-18T23:22:00Z | 23 | 73 | AVOSD | 0.61 | 2015-09-18T23:20:00Z | 11.01 | 53 | CTGC1 | 6.65 | 2015-09-18T23:22:00Z | 23 | 135 | < 25mph
4 | SDG&E | 20150412IG01 | April | 12 | 2015 | 2 | 2015-04-12 | 12:31 | 33.0117 | -116.866 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility |  | Tier 2 | RA | AU219 | 1.08 | 2018-12-06T13:30:00Z | 3 | 8 | ROCSD | 5.88 | 2018-12-06T13:20:00Z | 24.99 | 177 | AU219 | 1.08 | 2018-12-06T13:45:00Z | 8.01 | 15 | ROCSD | 5.88 | 2018-12-06T14:40:00Z | 28.01 | 357 | < 25mph
132 | SDG&E | 20200902IG01 | September | 2 | 2020 | 3 | 2020-09-02 | 19:30 | 33.362 | -117.137 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Tier 3 | NE | CIRSD | 2.57 | 2018-12-02T17:20:00Z | 5.99 | 18 | AT107 | 6.73 | 2018-12-02T17:23:00Z | 12.01 | 131 | CIRSD | 2.57 | 2018-12-02T18:20:00Z | 10 | 36 | AT107 | 6.73 | 2018-12-02T17:23:00Z | 12.01 | 263 | < 25mph
32 | SDG&E | 20160205IG01 | February | 5 | 2016 | 1 | 2016-02-05 | 9:47 | 33.0739 | -117.0862 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | NE | MIGC1 | 3.93 | 2016-11-22T19:50:00Z | 14 | 64 | MIGC1 | 3.93 | 2016-11-22T19:50:00Z | 14 | 117 | D5256 | 3.11 | 2016-11-22T20:48:00Z | 14 | 126 | D5256 | 3.11 | 2016-11-22T20:48:00Z | 14 | 228 | < 25mph
19 | SDG&E | 20150901IG01 | September | 1 | 2015 | 3 | 2015-09-01 | 18:01 | 32.7595 | -117.0671 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished | 4kV | Overhead | No | Contact From Object |  | Vehicle | Electric Facility | Human Error | Non- HFTD | CM | E8894 | 2.73 | 2018-06-16T17:03:00Z | 8.99 | 22 | TLKSD | 7.68 | 2018-06-16T17:10:00Z | 17 | 105 | PSQC1 | 2.33 | 2018-06-16T17:50:00Z | 13 | 43 | TLKSD | 7.68 | 2018-06-16T17:20:00Z | 18.99 | 207 | < 25mph
74 | SDG&E | 20171022IG01 | October | 22 | 2017 | 4 | 2017-10-22 | 10:22 | 33.099 | -117.135 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Tier 2 | NE | GOSC1 | 2.63 | 2017-08-07T09:52:00Z | 4 | 64 | HP005 | 6.91 | 2017-08-07T09:45:00Z | 8.28 | 154 | BLCSD | 3.98 | 2017-08-07T10:20:00Z | 4 | 126 | HP005 | 6.91 | 2017-08-07T09:55:00Z | 8.95 | 306 | < 25mph
49 | SDG&E | 20160827IG01 | August | 27 | 2016 | 3 | 2016-08-27 | 12:43 | 33.1371 | -117.0761 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Unknown | Non- HFTD | NE | OTYSD | 2.08 | 2015-01-15T10:50:00Z | 11.01 | 24 | HP002 | 7.57 | 2015-01-15T10:25:00Z | 30.2 | 114 | OTYSD | 2.08 | 2015-01-15T10:50:00Z | 11.01 | 48 | HP002 | 7.57 | 2015-01-15T11:35:00Z | 34.67 | 230 | 25-40mph
8 | SDG&E | 20150428IG01 | April | 28 | 2015 | 2 | 2015-04-28 | 13:30 | 32.8917 | -116.8419 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Electric Facility | Human Error | Tier 3 | EA | ECJSD | 3.11 | 2017-09-04T08:10:00Z | 8.01 | 31 | MIGC1 | 7.97 | 2017-09-04T07:50:00Z | 17 | 205 | ECJSD | 3.11 | 2017-09-04T08:10:00Z | 8.01 | 57 | MIGC1 | 7.97 | 2017-09-04T08:50:00Z | 17 | 393 | < 25mph
121 | SDG&E | 20200531IG01 | May | 31 | 2020 | 2 | 2020-05-31 | 2:01 | 32.543 | -117.0277 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Outside Force | Non- HFTD | CM | MGDSD | 3.4 | 2020-05-15T15:00:00Z | 5.7 | 24 | HP016 | 6.11 | 2020-05-15T14:55:00Z | 8.72 | 78 | MGDSD | 3.4 | 2020-05-15T16:30:00Z | 8.05 | 48 | EWNSD | 5.67 | 2020-05-15T16:30:00Z | 11.1 | 156 | < 25mph
18 | SDG&E | 20150823IG01 | August | 23 | 2015 | 3 | 2015-08-23 | 15:00 | 33.2729 | -117.1521 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | NE | BVDSD | 0.5 | 2018-05-04T17:40:00Z | 24.99 | 6 | CWDSD | 5.27 | 2018-05-04T18:00:00Z | 28.01 | 12 | BVDSD | 0.5 | 2018-05-04T17:40:00Z | 24.99 | 12 | CWDSD | 5.27 | 2018-05-04T19:10:00Z | 34.99 | 24 | 25-40mph
33 | SDG&E | 20160212IG01 | February | 12 | 2016 | 1 | 2016-02-12 | 19:30 | 33.2427 | -116.9664 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Vandalism/Theft |  |  |  | Outside Force | Tier 3 | NE | E8894 | 1.45 | 2016-09-29T03:56:00Z | 4 | 28 | HP005 | 6.46 | 2016-09-29T03:55:00Z | 6.71 | 156 | SPVSD | 3.81 | 2016-09-29T04:50:00Z | 4.99 | 55 | HP005 | 6.46 | 2016-09-29T04:45:00Z | 8.5 | 306 | < 25mph
43 | SDG&E | 20160702IG01 | July | 2 | 2016 | 3 | 2016-07-02 | 7:51 | 32.81 | -116.878 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Capacitor Bank |  |  | None | Tier 2 | EA | CWDSD | 1.71 | 2016-08-17T04:40:00Z | 20 | 12 | BVDSD | 6.99 | 2016-08-17T04:20:00Z | 24 | 55 | CWDSD | 1.71 | 2016-08-17T04:40:00Z | 20 | 24 | BVDSD | 6.99 | 2016-08-17T04:20:00Z | 24 | 110 | < 25mph
54 | SDG&E | 20161102IG01 | November | 2 | 2016 | 4 | 2016-11-02 | 10:30 | 32.8373 | -116.7022 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Tier 3 | ME | PZAC1 | 3.98 | 2018-08-07T16:50:00Z | 15.99 | 18 | PAUSD | 5.61 | 2018-08-07T17:00:00Z | 15.99 | 132 | PZAC1 | 3.98 | 2018-08-07T17:50:00Z | 17 | 36 | PAUSD | 5.61 | 2018-08-07T17:30:00Z | 17 | 264 | < 25mph
77 | SDG&E | 20171210IG02 | December | 10 | 2017 | 4 | 2017-12-10 | 2:58 | 33.2739 | -116.9537 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Tier 3 | NE | CBDSD | 3.84 | 2018-12-29T07:40:00Z | 10 | 35 | SOBSD | 7.12 | 2018-12-29T07:20:00Z | 14 | 141 | CBDSD | 3.84 | 2018-12-29T08:30:00Z | 10 | 69 | SOBSD | 7.12 | 2018-12-29T07:20:00Z | 14 | 286 | < 25mph
124 | SDG&E | 20200705IG01 | July | 5 | 2020 | 3 | 2020-07-05 | 14:08 | 33.0872 | -116.9856 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Lightning Arrestor |  |  | Unknown | Tier 3 | NE | AT526 | 2.56 | 2016-12-01T01:50:00Z | 7 | 42 | MIGC1 | 7.2 | 2016-12-01T01:50:00Z | 8.01 | 88 | CVXSD | 2.09 | 2016-12-01T03:40:00Z | 7 | 84 | MIGSD | 6.84 | 2016-12-01T03:20:00Z | 11.01 | 175 | < 25mph
104 | SDG&E | 20190716IG01 | July | 16 | 2019 | 3 | 2019-07-16 | 19:08 | 33.182 | -117.1126 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Other | Tier 2 | NE | E4521 | 3.76 | 2017-03-26T05:15:00Z | 8.01 | 36 | CSTSD | 4.04 | 2017-03-26T04:40:00Z | 12.01 | 214 | E4521 | 3.76 | 2017-03-26T05:15:00Z | 8.01 | 72 | CSTSD | 4.04 | 2017-03-26T04:40:00Z | 12.01 | 429 | < 25mph
104 | SDG&E | 20190716IG01 | July | 16 | 2019 | 3 | 2019-07-16 | 19:08 | 33.182 | -117.1126 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Other | Tier 2 | NE | E4521 | 3.76 | 2016-12-29T12:13:00Z | 8.01 | 20 | LLDSD | 7.68 | 2016-12-29T12:20:00Z | 12.01 | 179 | E4521 | 3.76 | 2016-12-29T12:13:00Z | 8.01 | 42 | LLDSD | 7.68 | 2016-12-29T13:00:00Z | 12.01 | 355 | < 25mph
22 | SDG&E | 20150908IG01 | September | 8 | 2015 | 3 | 2015-09-08 | 11:45 | 33.0726 | -116.7436 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | None | Tier 3 | RA | MGYSD | 2.03 | 2017-11-13T01:40:00Z | 8.99 | 18 | TR119 | 5.9 | 2017-11-13T01:25:00Z | 15.99 | 61 | MGYSD | 2.03 | 2017-11-13T01:40:00Z | 8.99 | 36 | TR119 | 5.9 | 2017-11-13T01:25:00Z | 15.99 | 122 | < 25mph
20 | SDG&E | 20150901IG02 | September | 1 | 2015 | 3 | 2015-09-01 | 8:50 | 32.669 | -116.286 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | None | Tier 2 | ME | WIRC1 | 2.46 | 2018-10-25T09:23:00Z | 4 | 15 | CBDSD | 5.25 | 2018-10-25T09:50:00Z | 4.99 | 52 | WIRC1 | 2.46 | 2018-10-25T10:23:00Z | 4 | 32 | CBDSD | 5.25 | 2018-10-25T10:30:00Z | 5.99 | 105 | < 25mph
99 | SDG&E | 20190116IG01 | January | 16 | 2019 | 1 | 2019-01-16 | 16:55 | 33.421 | -117.61 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12 kV | Overhead | No | Equipment/Facility Failure | Crossarm |  |  | Weather | Non- HFTD | OC | SPVSD | 4 | 2018-03-18T08:50:00Z | 5.99 | 19 | HP005 | 6.79 | 2018-03-18T08:45:00Z | 12.75 | 134 | SPVSD | 4 | 2018-03-18T08:50:00Z | 5.99 | 37 | HDMSD | 7.42 | 2018-03-18T10:00:00Z | 13 | 260 | < 25mph
37 | SDG&E | 20160406IG01 | April | 6 | 2016 | 2 | 2016-04-06 | 10:38 | 33.1865 | -117.1967 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Conductor | Vegetation | Electric Facility | Human Error | Non- HFTD | NC | CIRSD | 0.95 | 2015-06-06T16:00:00Z | 7 | 18 | TLKSD | 5.47 | 2015-06-06T15:50:00Z | 8.99 | 110 | CIRSD | 0.95 | 2015-06-06T17:00:00Z | 8.99 | 36 | PZAC1 | 6.65 | 2015-06-06T16:50:00Z | 12.01 | 221 | < 25mph
92 | SDG&E | 20180730IG01 | July | 30 | 2018 | 3 | 2018-07-30 | 12:11 | 32.8681 | -117.1902 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | BC | JAMSD | 1.67 | 2019-07-22T02:20:00Z | 8.99 | 6 | E3070 | 5.79 | 2019-07-22T02:45:00Z | 13 | 78 | JAMSD | 1.67 | 2019-07-22T02:20:00Z | 8.99 | 12 | E3070 | 5.79 | 2019-07-22T02:45:00Z | 13 | 156 | < 25mph
43 | SDG&E | 20160702IG01 | July | 2 | 2016 | 3 | 2016-07-02 | 7:51 | 32.81 | -116.878 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Capacitor Bank |  |  | None | Tier 2 | EA | LPTSD | 0.58 | 2016-03-27T04:40:00Z | 12.01 | 14 | LPTSD | 0.58 | 2016-03-27T04:40:00Z | 12.01 | 64 | LPTSD | 0.58 | 2016-03-27T04:40:00Z | 12.01 | 26 | LPTSD | 0.58 | 2016-03-27T04:40:00Z | 12.01 | 119 | < 25mph
101 | SDG&E | 20190612IG01 | June | 12 | 2019 | 2 | 2019-06-12 | 22:05 | 33.0484 | -116.8578 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12 kV | Padmounted | Yes | Contact From Object |  | Vehicle | Electric Facility | None | Tier 2 | RA | E6321 | 3.62 | 2015-10-31T19:32:00Z | 12.01 | 36 | E6321 | 3.62 | 2015-10-31T19:32:00Z | 12.01 | 140 | E6321 | 3.62 | 2015-10-31T20:27:00Z | 14.99 | 72 | OLVSD | 6.11 | 2015-10-31T20:20:00Z | 18.99 | 279 | < 25mph
92 | SDG&E | 20180730IG01 | July | 30 | 2018 | 3 | 2018-07-30 | 12:11 | 32.8681 | -117.1902 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Balloons | Electric Facility | Other | Non- HFTD | BC | LSVSD | 3.56 | 2019-01-28T18:40:00Z | 12.01 | 12 | DEHSD | 6.63 | 2019-01-28T18:20:00Z | 12.01 | 78 | LSVSD | 3.56 | 2019-01-28T18:40:00Z | 12.01 | 24 | DZRSD | 7.85 | 2019-01-28T19:40:00Z | 12.01 | 157 | < 25mph
32 | SDG&E | 20160205IG01 | February | 5 | 2016 | 1 | 2016-02-05 | 9:47 | 33.0739 | -117.0862 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | NE | C7369 | 3.27 | 2016-03-25T15:57:00Z | 5.99 | 68 | C3287 | 7.05 | 2016-03-25T16:46:00Z | 7 | 109 | OTYSD | 2.79 | 2016-03-25T17:40:00Z | 8.01 | 135 | OTYSD | 2.79 | 2016-03-25T17:40:00Z | 8.01 | 219 | < 25mph
108 | SDG&E | 20190911IG01 | September | 11 | 2019 | 3 | 2019-09-11 | 14:17 | 33.226 | -117.085 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 2 | NE | EWNSD | 3.96 | 2016-02-14T06:10:00Z | 10 | 18 | CHHSD | 7.51 | 2016-02-14T05:20:00Z | 13 | 55 | EWNSD | 3.96 | 2016-02-14T06:10:00Z | 10 | 36 | CHHSD | 7.51 | 2016-02-14T05:20:00Z | 13 | 110 | < 25mph
125 | SDG&E | 20200717IG01 | July | 17 | 2020 | 3 | 2020-07-17 | 16:30 | 33.0904 | -116.5798 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | RA | E9915 | 2.32 | 2019-03-16T18:31:00Z | 12.01 | 65 | ESCSD | 6.96 | 2019-03-16T18:30:00Z | 14 | 170 | E9915 | 2.32 | 2019-03-16T19:16:00Z | 14.99 | 121 | ESCSD | 6.96 | 2019-03-16T19:10:00Z | 18.01 | 332 | < 25mph
25 | SDG&E | 20151002IG01 | October | 2 | 2015 | 4 | 2015-10-02 | 14:30 | 33.1354 | -117.0588 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | NE | E2487 | 2.98 | 2015-08-19T08:25:00Z | 4.99 | 52 | E1401 | 7.78 | 2015-08-19T08:26:00Z | 14 | 171 | FTVSD | 1.29 | 2015-08-19T10:10:00Z | 5.99 | 95 | E1401 | 7.78 | 2015-08-19T08:26:00Z | 14 | 319 | < 25mph
139 | SDG&E | 20200930IG01 | September | 30 | 2020 | 3 | 2020-09-30 | 10:45 | 33.0207 | -116.8783 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Secondary | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | RA | WIRC1 | 2.46 | 2020-08-15T05:23:00Z | 5.99 | 36 | CBDSD | 5.25 | 2020-08-15T05:00:00Z | 7.24 | 84 | E3174 | 3.44 | 2020-08-15T06:46:00Z | 7 | 73 | CBDSD | 5.25 | 2020-08-15T05:00:00Z | 7.24 | 169 | < 25mph
65 | SDG&E | 20170728IG01 | July | 28 | 2017 | 3 | 2017-07-28 | 16:31 | 32.7802 | -116.8722 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Pole /Conductor | Vehicle | Electric Facility | Outside Force | Tier 2 | EA | FBZC1 | 2.31 | 2019-05-30T22:22:00Z | 22 | 33 | FBZC1 | 2.31 | 2019-05-30T22:22:00Z | 22 | 79 | FBZC1 | 2.31 | 2019-05-30T23:22:00Z | 22.99 | 63 | FBZC1 | 2.31 | 2019-05-30T23:22:00Z | 22.99 | 154 | < 25mph
43 | SDG&E | 20160702IG01 | July | 2 | 2016 | 3 | 2016-07-02 | 7:51 | 32.81 | -116.878 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Capacitor Bank |  |  | None | Tier 2 | EA | LPTSD | 0.58 | 2016-12-11T21:40:00Z | 18.99 | 6 | BVDSD | 6.99 | 2016-12-11T21:40:00Z | 25.99 | 49 | LPTSD | 0.58 | 2016-12-11T22:20:00Z | 20 | 12 | BVDSD | 6.99 | 2016-12-11T21:50:00Z | 27 | 98 | 25-40mph
29 | SDG&E | 20160109IG01 | January | 9 | 2016 | 1 | 2016-01-09 | 4:30 | 33.082 | -117.091 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Non- HFTD | NE | HARSD | 2.98 | 2019-07-11T13:30:00Z | 4 | 85 | SQTSD | 5.8 | 2019-07-11T13:30:00Z | 8.01 | 193 | DEHSD | 2.95 | 2019-07-11T14:30:00Z | 4.68 | 168 | SQTSD | 5.8 | 2019-07-11T13:30:00Z | 8.01 | 387 | < 25mph
27 | SDG&E | 20151226IG01 | December | 26 | 2015 | 4 | 2015-12-26 | 3:04 | 33.1323 | -117.0695 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | NE | WYNSD | 2.54 | 2018-02-07T12:20:00Z | 31 | 35 | SHCSD | 6.16 | 2018-02-07T12:40:00Z | 35.99 | 100 | WYNSD | 2.54 | 2018-02-07T13:30:00Z | 31.99 | 70 | SHCSD | 6.16 | 2018-02-07T12:40:00Z | 35.99 | 200 | 25-40mph
56 | SDG&E | 20170120IG01 | January | 20 | 2017 | 1 | 2017-01-20 | 14:00 | 32.6274 | -117.0767 | Building | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object | Conductor | Vegetation | Pole | Weather | Non- HFTD | CM | ECJSD | 3.11 | 2015-12-22T05:00:00Z | 4 | 29 | OTYSD | 4.92 | 2015-12-22T05:10:00Z | 7 | 215 | ECJSD | 3.11 | 2015-12-22T06:50:00Z | 4 | 58 | MIGC1 | 7.97 | 2015-12-22T06:50:00Z | 12.01 | 431 | < 25mph
115 | SDG&E | 20191101IG01 | November | 1 | 2019 | 4 | 2019-11-01 | 5:49 | 33.0924 | -117.0206 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Vehicle | Pole | None | Non- HFTD | NE | TLKSD | 3.72 | 2019-01-28T03:10:00Z | 8.01 | 42 | OLVSD | 7.1 | 2019-01-28T02:20:00Z | 8.01 | 164 | TLKSD | 3.72 | 2019-01-28T03:10:00Z | 8.01 | 83 | OLVSD | 7.1 | 2019-01-28T02:20:00Z | 8.01 | 322 | < 25mph
87 | SDG&E | 20180622IG01 | June | 22 | 2018 | 2 | 2018-06-22 | 9:46 | 32.567 | -116.941 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | Unknown | Tier 2 | CM | HP002 | 1.96 | 2016-08-26T15:05:00Z | 8.28 | 25 | HP002 | 1.96 | 2016-08-26T15:05:00Z | 8.28 | 114 | DHVSD | 2.94 | 2016-08-26T16:40:00Z | 12.01 | 49 | DHVSD | 2.94 | 2016-08-26T16:40:00Z | 12.01 | 227 | < 25mph
48 | SDG&E | 20160731IG01 | July | 31 | 2016 | 3 | 2016-07-31 | 13:43 | 33.3663 | -117.2033 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Unknown | Tier 2 | NE | E8894 | 1.45 | 2016-06-08T21:32:00Z | 15.99 | 25 | HDMSD | 7.44 | 2016-06-08T21:10:00Z | 18.99 | 129 | E8894 | 1.45 | 2016-06-08T21:32:00Z | 15.99 | 47 | HDMSD | 7.44 | 2016-06-08T21:10:00Z | 18.99 | 255 | < 25mph
68 | SDG&E | 20170905IG01 | September | 5 | 2017 | 3 | 2017-09-05 | 14:49 | 32.6191 | -116.6949 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Unknown | Tier 3 | ME | KSDM | 2.47 | 2018-04-06T00:53:00Z | 17.27 | 13 | KSDM | 2.47 | 2018-04-06T00:53:00Z | 17.27 | 52 | KSDM | 2.47 | 2018-04-06T00:53:00Z | 17.27 | 25 | KSDM | 2.47 | 2018-04-06T00:53:00Z | 17.27 | 101 | < 25mph
131 | SDG&E | 20200831IG01 | August | 31 | 2020 | 3 | 2020-08-31 | 14:05 | 33.1128 | -117.0055 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Other | Tier 2 | NE | OTYSD | 3.97 | 2018-08-27T06:20:00Z | 4.99 | 26 | RODB1 | 6.5 | 2018-08-27T06:20:00Z | 7.14 | 105 | OTYSD | 3.97 | 2018-08-27T06:20:00Z | 4.99 | 47 | RODB1 | 6.5 | 2018-08-27T06:20:00Z | 7.14 | 196 | < 25mph
52 | SDG&E | 20160929IG01 | September | 29 | 2016 | 3 | 2016-09-28 | 14:29 | 32.7418 | -116.9653 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact Between Third Party Facility on Pole and Supply Lines |  |  |  | Outside Force | Non- HFTD | EA | D5683 | 3.27 | 2015-03-01T06:18:00Z | 10 | 27 | E0995 | 7.15 | 2015-03-01T05:49:00Z | 10.98 | 115 | D5683 | 3.27 | 2015-03-01T07:48:00Z | 14 | 53 | D5683 | 3.27 | 2015-03-01T07:48:00Z | 14 | 224 | < 25mph
87 | SDG&E | 20180622IG01 | June | 22 | 2018 | 2 | 2018-06-22 | 9:46 | 32.567 | -116.941 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Switch |  |  | Unknown | Tier 2 | CM | DHVSD | 2.94 | 2019-07-29T20:20:00Z | 15.99 | 30 | SVLSD | 4.46 | 2019-07-29T20:30:00Z | 27 | 175 | DHVSD | 2.94 | 2019-07-29T20:20:00Z | 15.99 | 60 | SVLSD | 4.46 | 2019-07-29T20:30:00Z | 27 | 341 | 25-40mph
13 | SDG&E | 20150717IG01 | July | 17 | 2015 | 3 | 2015-07-17 | 9:48 | 33.3012 | -117.0222 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vegetation | Communication Facility | Human Error | Tier 3 | NE | HDMSD | 3.7 | 2019-01-13T08:40:00Z | 12.01 | 38 | HDMSD | 3.7 | 2019-01-13T08:40:00Z | 12.01 | 149 | HDMSD | 3.7 | 2019-01-13T09:20:00Z | 15.99 | 77 | HDMSD | 3.7 | 2019-01-13T09:20:00Z | 15.99 | 298 | < 25mph
31 | SDG&E | 20160131IG01 | January | 31 | 2016 | 1 | 2016-01-31 | 15:00 | 33.3217 | -117.156 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Weather | Tier 2 | NE | ESCSD | 2.91 | 2015-12-26T22:10:00Z | 14.99 | 40 | SPVSD | 7.17 | 2015-12-26T21:50:00Z | 28.99 | 173 | ESCSD | 2.91 | 2015-12-26T22:10:00Z | 14.99 | 79 | SPVSD | 7.17 | 2015-12-26T21:50:00Z | 28.99 | 346 | 25-40mph
131 | SDG&E | 20200831IG01 | August | 31 | 2020 | 3 | 2020-08-31 | 14:05 | 33.1128 | -117.0055 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Other | Tier 2 | NE | OTYSD | 3.97 | 2017-08-20T19:30:00Z | 13 | 25 | E3070 | 5.13 | 2017-08-20T19:25:00Z | 15.99 | 109 | OTYSD | 3.97 | 2017-08-20T20:10:00Z | 18.01 | 47 | OTYSD | 3.97 | 2017-08-20T20:10:00Z | 18.01 | 206 | < 25mph
110 | SDG&E | 20190930IG01 | September | 30 | 2019 | 3 | 2019-09-30 | 2:59 | 33.2618 | -116.3705 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Guy/Span Wire |  |  | Other | Non- HFTD | RA | EWNSD | 3.51 | 2015-04-08T15:20:00Z | 13 | 24 | EWNSD | 3.51 | 2015-04-08T15:20:00Z | 13 | 61 | EWNSD | 3.51 | 2015-04-08T16:20:00Z | 15.99 | 48 | EWNSD | 3.51 | 2015-04-08T16:20:00Z | 15.99 | 122 | < 25mph
139 | SDG&E | 20200930IG01 | September | 30 | 2020 | 3 | 2020-09-30 | 10:45 | 33.0207 | -116.8783 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Secondary | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | RA | WIRC1 | 2.46 | 2019-06-11T06:23:00Z | 5.99 | 22 | WIRC1 | 2.46 | 2019-06-11T06:23:00Z | 5.99 | 58 | WIRC1 | 2.46 | 2019-06-11T06:23:00Z | 5.99 | 42 | WIRC1 | 2.46 | 2019-06-11T06:23:00Z | 5.99 | 114 | < 25mph
2 | SDG&E | 20150319IG01 | March | 19 | 2015 | 1 | 2015-03-19 | 23:50 | 33.0565 | -117.0332 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 2 | NE | WIRC1 | 3.14 | 2016-04-22T17:23:00Z | 14 | 17 | WIRC1 | 3.14 | 2016-04-22T17:23:00Z | 14 | 53 | WIRC1 | 3.14 | 2016-04-22T18:23:00Z | 15.99 | 33 | E0995 | 6.45 | 2016-04-22T18:51:00Z | 18.01 | 105 | < 25mph
103 | SDG&E | 20190705IG01 | July | 5 | 2019 | 3 | 2019-07-05 | 12:32 | 33.1584 | -117.222 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 2 | NC | E8894 | 1.45 | 2017-09-25T20:03:00Z | 14 | 22 | OLVSD | 6.37 | 2017-09-25T19:40:00Z | 22.01 | 141 | E8894 | 1.45 | 2017-09-25T21:03:00Z | 18.99 | 45 | WRBSD | 7.25 | 2017-09-25T20:30:00Z | 24.99 | 286 | < 25mph
84 | SDG&E | 20180601IG01 | June | 1 | 2018 | 2 | 2018-06-01 | 14:00 | 33.099 | -117.044 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | No | Wire-Wire Contact |  |  |  | Other | Non- HFTD | NE | MVNSD | 1.8 | 2018-12-05T08:40:00Z | 7 | 58 | MTLSD | 5.84 | 2018-12-05T07:40:00Z | 14 | 155 | MVNSD | 1.8 | 2018-12-05T09:40:00Z | 8.01 | 117 | MTLSD | 5.84 | 2018-12-05T07:40:00Z | 14 | 308 | < 25mph
23 | SDG&E | 20150909IG01 | September | 9 | 2015 | 3 | 2015-09-09 | 20:40 | 32.644 | -117.072 | Vegetation | Urban | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Non- HFTD | CM | CESSD | 3.48 | 2015-12-06T14:00:00Z | 14 | 58 | BLCSD | 6.16 | 2015-12-06T14:30:00Z | 18.99 | 148 | CESSD | 3.48 | 2015-12-06T15:30:00Z | 14.99 | 113 | BLCSD | 6.16 | 2015-12-06T14:50:00Z | 20 | 293 | < 25mph
89 | SDG&E | 20180706IG01 | July | 6 | 2018 | 3 | 2018-07-06 | 10:26 | 32.6203 | -116.7649 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Transformer |  |  |  | Tier 3 | ME | BRJSD | 3.74 | 2017-08-26T18:50:00Z | 20 | 31 | BRJSD | 3.74 | 2017-08-26T18:50:00Z | 20 | 38 | BRJSD | 3.74 | 2017-08-26T19:30:00Z | 20 | 62 | BRJSD | 3.74 | 2017-08-26T19:30:00Z | 20 | 76 | < 25mph
34 | SDG&E | 20160218IG01 | February | 18 | 2016 | 1 | 2016-02-18 | 0:00 | 32.7063 | -116.397 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | None | Tier 3 | ME | ECJSD | 2.76 | 2019-12-07T23:30:00Z | 3 | 36 | MIGSD | 6.97 | 2019-12-07T22:50:00Z | 9.42 | 159 | ECJSD | 2.76 | 2019-12-07T23:40:00Z | 3 | 72 | MIGC1 | 6.79 | 2019-12-07T23:50:00Z | 10 | 315 | < 25mph
97 | SDG&E | 20181015IG01 | October | 15 | 2018 | 4 | 2018-10-15 | 10:21 | 33.3191 | -117.2597 | Vegetation | Rural | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure |  |  |  | None | Tier 2 | NE | TLKSD | 3.72 | 2018-05-08T08:20:00Z | 8.01 | 65 | TLKSD | 3.72 | 2018-05-08T08:20:00Z | 8.01 | 170 | TLKSD | 3.72 | 2018-05-08T08:20:00Z | 8.01 | 129 | TLKSD | 3.72 | 2018-05-08T08:20:00Z | 8.01 | 339 | < 25mph
91 | SDG&E | 20180722IG01 | July | 22 | 2018 | 3 | 2018-07-22 | 23:19 | 33.301 | -116.351 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | None | Non- HFTD | RA | RODB1 | 2.12 | 2019-07-20T13:10:00Z | 8.5 | 10 | MIGSD | 4.59 | 2019-07-20T13:40:00Z | 10 | 69 | RODB1 | 2.12 | 2019-07-20T13:10:00Z | 8.5 | 20 | MIGSD | 4.59 | 2019-07-20T13:40:00Z | 10 | 137 | < 25mph
25 | SDG&E | 20151002IG01 | October | 2 | 2015 | 4 | 2015-10-02 | 14:30 | 33.1354 | -117.0588 | Vegetation | Urban | Less Than .25 Acres | Customer | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown | Non- HFTD | NE | ROVSD | 3.23 | 2020-10-17T04:50:00Z | 8.55 | 108 | HP014 | 6.9 | 2020-10-17T03:55:00Z | 20.36 | 234 | ROVSD | 3.23 | 2020-10-17T04:50:00Z | 8.55 | 215 | HP014 | 6.9 | 2020-10-17T03:55:00Z | 20.36 | 466 | < 25mph
15 | SDG&E | 20150808IG01 | August | 8 | 2015 | 3 | 2015-08-08 | 10:00 | 33.1973 | -117.2308 | Vegetation | Urban | Less Than .25 Acres | Customer | 4kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | None | Non- HFTD | NC | CHOSD | 3.4 | 2018-02-27T10:50:00Z | 14.99 | 71 | UCEL | 7.93 | 2018-02-27T10:20:00Z | 19.39 | 179 | CHOSD | 3.4 | 2018-02-27T10:50:00Z | 14.99 | 148 | UCEL | 7.93 | 2018-02-27T10:20:00Z | 19.39 | 364 | < 25mph
78 | SDG&E | 20180208IG01 | February | 8 | 2018 | 1 | 2018-02-08 | 10:07 | 33.2071 | -117.2072 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Human Error | Non- HFTD | NC | HVYSD | 2.68 | 2017-04-26T14:10:00Z | 4.99 | 70 | HP005 | 4.91 | 2017-04-26T14:25:00Z | 8.28 | 148 | RAMSD | 3.65 | 2017-04-26T16:00:00Z | 8.01 | 125 | BNASD | 6.44 | 2017-04-26T15:40:00Z | 11.01 | 279 | < 25mph
76 | SDG&E | 20171210IG01 | December | 10 | 2017 | 4 | 2017-12-10 | 5:26 | 33.28 | -116.955 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 3 | NE | SSOSD | 2.69 | 2015-01-23T17:20:00Z | 23 | 60 | HP016 | 7.13 | 2015-01-23T16:37:00Z | 41.61 | 160 | SSOSD | 2.69 | 2015-01-23T17:40:00Z | 24.99 | 117 | HP016 | 7.13 | 2015-01-23T16:37:00Z | 41.61 | 307 | 40-55mph
85 | SDG&E | 20180612IG01 | June | 12 | 2018 | 2 | 2018-06-12 | 9:00 | 32.706 | -116.396 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | ME | ESCSD | 2.77 | 2017-08-24T04:20:00Z | 4.99 | 33 | OLVSD | 5.01 | 2017-08-24T04:10:00Z | 8.01 | 201 | ESCSD | 2.77 | 2017-08-24T04:30:00Z | 5.99 | 65 | AV241 | 7.6 | 2017-08-24T04:38:00Z | 8.99 | 400 | < 25mph
69 | SDG&E | 20170927IG01 | September | 27 | 2017 | 3 | 2017-09-27 | 14:28 | 33.2327 | -116.9748 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Unknown |  |  |  | Unknown | Tier 2 | NE | VCMSD | 2.52 | 2020-08-02T03:10:00Z | 23.17 | 37 | VCMSD | 2.52 | 2020-08-02T03:10:00Z | 23.17 | 103 | VCMSD | 2.52 | 2020-08-02T03:30:00Z | 25.21 | 73 | VCMSD | 2.52 | 2020-08-02T03:30:00Z | 25.21 | 202 | < 25mph
121 | SDG&E | 20200531IG01 | May | 31 | 2020 | 2 | 2020-05-31 | 2:01 | 32.543 | -117.0277 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Outside Force | Non- HFTD | CM | MGDSD | 3.4 | 2018-03-12T11:50:00Z | 5.99 | 27 | SHCSD | 5.42 | 2018-03-12T12:40:00Z | 20 | 82 | MGDSD | 3.4 | 2018-03-12T11:50:00Z | 5.99 | 51 | SHCSD | 5.42 | 2018-03-12T13:00:00Z | 21 | 154 | < 25mph
117 | SDG&E | 20191112IG01 | November | 12 | 2019 | 4 | 2019-11-12 | 7:51 | 33.1903 | -117.3698 | Other | Urban | Less Than .25 Acres | Fire Agency | 120/240 | Overhead | Yes | Equipment/Facility Failure | Conductor |  |  | Unknown | Tier 2 | NC | VISSD | 2.7 | 2015-04-11T17:20:00Z | 8.99 | 30 | C2635 | 4.49 | 2015-04-11T16:46:00Z | 15.99 | 102 | TWOSD | 3.27 | 2015-04-11T18:00:00Z | 10 | 60 | C2635 | 4.49 | 2015-04-11T16:46:00Z | 15.99 | 204 | < 25mph
132 | SDG&E | 20200902IG01 | September | 2 | 2020 | 3 | 2020-09-02 | 19:30 | 33.362 | -117.137 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Tier 3 | NE | PZAC1 | 3.98 | 2016-07-24T18:50:00Z | 18.01 | 18 | AT107 | 6.73 | 2016-07-24T18:58:00Z | 20 | 136 | PZAC1 | 3.98 | 2016-07-24T19:50:00Z | 24.99 | 36 | PZAC1 | 3.98 | 2016-07-24T19:50:00Z | 24.99 | 274 | < 25mph
94 | SDG&E | 20180819IG01 | August | 19 | 2018 | 3 | 2018-08-19 | 18:35 | 32.7002 | -116.8639 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility | Other | Tier 3 | EA | DZRSD | 0.55 | 2017-01-29T13:10:00Z | 4 | 6 | DHVSD | 4.61 | 2017-01-29T12:30:00Z | 24.99 | 26 | DZRSD | 0.55 | 2017-01-29T13:40:00Z | 7 | 12 | DHVSD | 4.61 | 2017-01-29T12:30:00Z | 24.99 | 52 | < 25mph
68 | SDG&E | 20170905IG01 | September | 5 | 2017 | 3 | 2017-09-05 | 14:49 | 32.6191 | -116.6949 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Unknown | Tier 3 | ME | BFDSD | 3.99 | 2016-01-01T23:30:00Z | 11.01 | 12 | BFDSD | 3.99 | 2016-01-01T23:30:00Z | 11.01 | 37 | BFDSD | 3.99 | 2016-01-01T23:30:00Z | 11.01 | 24 | BFDSD | 3.99 | 2016-01-01T23:30:00Z | 11.01 | 77 | < 25mph
27 | SDG&E | 20151226IG01 | December | 26 | 2015 | 4 | 2015-12-26 | 3:04 | 33.1323 | -117.0695 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | NE | VCMSD | 1.98 | 2015-03-22T00:40:00Z | 28.99 | 51 | VCMSD | 1.98 | 2015-03-22T00:40:00Z | 28.99 | 112 | HRPSD | 2.59 | 2015-03-22T01:10:00Z | 31.99 | 103 | HRPSD | 2.59 | 2015-03-22T01:10:00Z | 31.99 | 225 | 25-40mph
135 | SDG&E | 20200906IG01 | September | 6 | 2020 | 3 | 2020-09-06 | 23:00 | 33.0965 | -117.0237 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Transformer |  |  | None | Tier 2 | NE | AT125 | 3.8 | 2020-07-27T00:20:00Z | 11 | 30 | CIRSD | 6.48 | 2020-07-27T00:30:00Z | 14.25 | 125 | AT125 | 3.8 | 2020-07-27T00:20:00Z | 11 | 60 | CIRSD | 6.48 | 2020-07-27T00:30:00Z | 14.25 | 250 | < 25mph
123 | SDG&E | 20200603IG01 | June | 3 | 2020 | 2 | 2020-06-03 | 11:17 | 33.1234 | -117.025 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kv | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | NE | E8699 | 3.84 | 2018-07-20T09:18:00Z | 4.99 | 62 | E8699 | 3.84 | 2018-07-20T09:18:00Z | 4.99 | 163 | E8699 | 3.84 | 2018-07-20T09:18:00Z | 4.99 | 124 | E8699 | 3.84 | 2018-07-20T09:18:00Z | 4.99 | 323 | < 25mph
113 | SDG&E | 20191024IG01 | October | 24 | 2019 | 4 | 2019-10-24 | 10:16 | 32.8357 | -116.7252 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Fuse |  |  | None | Tier 3 | ME | JAMSD | 2.55 | 2016-07-07T10:00:00Z | 3 | 10 | OTYC1 | 5.44 | 2016-07-07T09:14:00Z | 7 | 82 | JAMSD | 2.55 | 2016-07-07T10:40:00Z | 4.99 | 20 | WCVSD | 6.85 | 2016-07-07T10:30:00Z | 11.01 | 165 | < 25mph
132 | SDG&E | 20200902IG01 | September | 2 | 2020 | 3 | 2020-09-02 | 19:30 | 33.362 | -117.137 | Vegetation | Rural | Less Than .25 Acres | Utility | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | None | Tier 3 | NE | PZAC1 | 3.98 | 2020-10-14T11:50:00Z | 14.01 | 24 | RNBSD | 6.75 | 2020-10-14T11:40:00Z | 22.58 | 167 | PZAC1 | 3.98 | 2020-10-14T12:50:00Z | 16 | 48 | RNBSD | 6.75 | 2020-10-14T11:40:00Z | 22.58 | 332 | < 25mph
78 | SDG&E | 20180208IG01 | February | 8 | 2018 | 1 | 2018-02-08 | 10:07 | 33.2071 | -117.2072 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Human Error | Non- HFTD | NC | RAMSD | 3.65 | 2018-12-09T22:10:00Z | 14.99 | 46 | STVSD | 7.92 | 2018-12-09T21:40:00Z | 22.01 | 123 | RAMSD | 3.65 | 2018-12-09T22:10:00Z | 14.99 | 102 | STVSD | 7.92 | 2018-12-09T21:40:00Z | 22.01 | 256 | < 25mph
59 | SDG&E | 20170619IG01 | June | 19 | 2017 | 2 | 2017-06-19 | 9:52 | 32.7829 | -117.0488 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Balloons | Electric Facility |  | Non- HFTD | EA | E8894 | 3.31 | 2019-07-09T23:01:00Z | 14 | 33 | WRBSD | 5.45 | 2019-07-09T22:20:00Z | 20 | 177 | E8894 | 3.31 | 2019-07-09T23:01:00Z | 14 | 65 | WRBSD | 5.45 | 2019-07-09T22:20:00Z | 20 | 353 | < 25mph
2 | SDG&E | 20150319IG01 | March | 19 | 2015 | 1 | 2015-03-19 | 23:50 | 33.0565 | -117.0332 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vehicle | Pole | Human Error | Tier 2 | NE | E3370 | 0.14 | 2017-02-24T18:55:00Z | 11.01 | 16 | E0995 | 6.45 | 2017-02-24T18:54:00Z | 18.01 | 46 | E3370 | 0.14 | 2017-02-24T19:45:00Z | 12.01 | 32 | E0995 | 6.45 | 2017-02-24T19:55:00Z | 20 | 92 | < 25mph
10 | SDG&E | 20150517IG01 | May | 17 | 2015 | 2 | 2015-05-17 | 6:55 | 33.1808 | -117.2064 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility |  | Non- HFTD | NC | SE769 | 1.43 | 2020-05-25T01:20:00Z | 10.23 | 12 | FBZC1 | 4.97 | 2020-05-25T01:22:00Z | 19 | 75 | SE452 | 3.79 | 2020-05-25T02:30:00Z | 10.89 | 24 | FBZC1 | 4.97 | 2020-05-25T01:22:00Z | 19 | 151 | < 25mph
5 | SDG&E | 20150412IG02 | April | 12 | 2015 | 2 | 2015-04-12 | 14:30 | 33.2754 | -117.3306 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | 12kV | Overhead | No | Contact From Object |  | Vehicle | Pole |  | Tier 2 | NC | AMOSD | 2.8 | 2017-04-21T15:40:00Z | 4.99 | 11 | RBVSD | 7.67 | 2017-04-21T15:30:00Z | 10 | 70 | AMOSD | 2.8 | 2017-04-21T16:20:00Z | 5.99 | 21 | RBVSD | 7.67 | 2017-04-21T15:30:00Z | 10 | 134 | < 25mph
74 | SDG&E | 20171022IG01 | October | 22 | 2017 | 4 | 2017-10-22 | 10:22 | 33.099 | -117.135 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Other | Electric Facility | Human Error | Tier 2 | NE | GOSC1 | 2.63 | 2016-11-01T11:52:00Z | 7 | 70 | CESSD | 4.21 | 2016-11-01T12:20:00Z | 8.99 | 179 | GOSC1 | 2.63 | 2016-11-01T12:52:00Z | 7 | 140 | CESSD | 4.21 | 2016-11-01T12:50:00Z | 10 | 352 | < 25mph
85 | SDG&E | 20180612IG01 | June | 12 | 2018 | 2 | 2018-06-12 | 9:00 | 32.706 | -116.396 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Animal | Electric Facility | None | Tier 3 | ME | ESCSD | 2.77 | 2017-01-07T00:50:00Z | 5.99 | 30 | OLVSD | 5.01 | 2017-01-07T01:10:00Z | 8.99 | 172 | ESCSD | 2.77 | 2017-01-07T00:50:00Z | 5.99 | 60 | OLVSD | 5.01 | 2017-01-07T01:10:00Z | 8.99 | 347 | < 25mph
75 | SDG&E | 20171025IG01 | October | 25 | 2017 | 4 | 2017-10-25 | 13:02 | 33.2857 | -117.0275 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | 12kV | Overhead | No | Equipment/Facility Failure | Other |  |  | Weather | Tier 2 | NE |  |  |  | 0 | 0 | FBZCA | 5.03 | 2016-06-20T17:22:00Z | 14.99 | 37 |  |  |  | 0 | 0 | FBZCA | 5.03 | 2016-06-20T18:22:00Z | 15.99 | 74 | < 25mph
118 | SDG&E | 20200211IG01 | February | 11 | 2020 | 1 | 2020-02-11 | 1:30 | 32.791 | -116.9194 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | 12kV | Overhead | Yes | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Outside Force | Non- HFTD | EA | WIRC1 | 2.46 | 2016-12-04T06:23:00Z | 8.99 | 22 | CBDSD | 5.25 | 2016-12-04T06:00:00Z | 10 | 49 | WIRC1 | 2.46 | 2016-12-04T07:23:00Z | 8.99 | 39 | CBDSD | 5.25 | 2016-12-04T07:50:00Z | 10 | 94 | < 25mph
18 | SDG&E | 20150823IG01 | August | 23 | 2015 | 3 | 2015-08-23 | 15:00 | 33.2729 | -117.1521 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | 12kV | Overhead | Yes | Contact From Object |  | Vegetation | Electric Facility | Weather | Tier 2 | NE | TDSSD | 3.89 | 2016-11-10T14:30:00Z | 18.01 | 12 | CWDSD | 5.27 | 2016-11-10T14:20:00Z | 34.99 | 24 | BVDSD | 0.5 | 2016-11-10T16:10:00Z | 23 | 24 | CWDSD | 5.27 | 2016-11-10T14:20:00Z | 34.99 | 48 | 25-40mph

## IgnitionAnalysis
SDGE Ignitions | [8 empty] | Wind gust | Ignition | Ignition | MC | Monte Carlo | Veg | Equip | Agent
Row Labels | Agent | Equipment | Unknown | Vegetation | (blank) | Grand Total |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
< 25mph | 52 | 47 | 7 | 12 |  | 118 |  |  | 5 | 1 | 0.72993 | 9 | 1.8 | 0 | 1 | 0
25-40mph | 2 | 5 |  | 3 |  | 10 |  |  | 10 | 19 | 13.8686 | 152 | 30.4 | 0 | 9 | 10
40-55mph |  | 4 | 1 | 1 |  | 6 |  |  | 15 | 30 | 21.8978 | 139 | 27.8 | 2 | 11 | 13
55mph+ |  | 2 |  | 1 |  | 3 |  |  | 20 | 37 | 27.0073 | 94 | 18.8 | 4 | 12 | 19
Category | [8 empty] | 25 | 31 | 22.6277 | 50 | 10 | 6 | 14 | 10
(blank) | [8 empty] | 30 | 6 | 4.3796 | 28 | 5.6 | 1 | 4 | 1
Grand Total | 54 | 58 | 8 | 17 |  | 137 |  |  | 35 | 1 | 0.72993 | 13 | 2.6 | 1 | 0 | 0
[9 empty] | 40 | 3 | 2.1898 | 5 | 1 | 1 | 1 | 1
[9 empty] | 45 | 1 | 0.72993 | 5 | 1 | 0 | 1 | 0
Wind Gust | Count of 8 mi / 1 hr | Fraction | Expected | Excess |  | Wind Gust | Expected | Observed | 50 | 2 | 1.4599 | 2 | 0.4 | 1 | 1 | 0
< 25mph | 443 | 0.88423 | 121.1397 |  |  | <40 mph | 133.992 | 128 | 55 | 3 | 2.1898 | 1 | 0.2 | 0 | 2 | 0
25-40mph | 47 | 0.093812 | 12.8523 | 0.77807 |  | >40 mph | 2.7345 | 9 | 60 | 0 | 0 | 2 | 0.4 | 0 | 0 | 0
40-55mph | 8 | 0.015968 | 2.1876 | 4.5712 |  |  |  |  | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55mph+ | 2 | 0.003992 | 0.54691 | 18.2847 |  | P>40 chi-squared |  |  | 70 | 1 | 0.72993 | 0 | 0 | 0 | 1 | 0
Category | 1 |  |  |  |  | 0.00013126 |  |  | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(blank) | [8 empty] | 80 | 1 | 0.72993 | 0 | 0 | 1 | 0 | 0
Grand Total | 501 |  |  |  |  | P chi-squared |  |  | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0.00037047 |  |  | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | 100 | 1 | 0.72993 | 0 | 0 | 0 | 1 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0